## Sheet1. Weeks 1-10
FIELD-SET 1: PILOT-SCALE MEMBRANE RESULTS: WEEKS 1-10 (FILE: mempilot.xls)
Field 1-1: PWS And Treatment Plant Data |  | Field 1-2: Manufacturer Reported Membrane Characteristics1 |  | Field 1-3: 2-Stage Membrane Pilot System Design Parameters |  | Field 1-4: Foulants And Fouling Indices1 |  | Field 1-5: Pretreatment Used Prior To Membranes1 |  |  | Field 1-6: Membrane Performance Data During Operation With The Test Water | [18 empty] | Field 1-6: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 1-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 1-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 1-7: System And Stage Water Quality For Week 2 | [9 empty] | Field 1-7: System And Stage Water Quality For Week 2 (continued) | [7 empty] | Field 1-9: System And Stage Water Quality For Week 6 | [9 empty] | Field 1-9: System And Stage Water Quality For Week 6 (continued) | [7 empty] | Field 1-11: System And Stage Water Quality For Week 10 | [9 empty] | Field 1-11: System And Stage Water Quality For Week 10 (continued) | [7 empty] | Field 1-10: System And Stage Water Quality For Week 8 | [9 empty] | Field 1-10: System And Stage Water Quality For Week 8 (continued) | [7 empty] | Field 1-11: System And Stage Water Quality For Week 10 | [9 empty] | Field 1-11: System And Stage Water Quality For Week 10 (continued) | [7 empty] | Field 1-12: Duplicate Analysis Of System And Stage Water Quality For Week 10 | [9 empty] | Field 1-12: Duplicate Analysis Of System And Stage Water Quality For Week 10 (continued) | [7 empty] | Field 1-13: Membrane Cost Parameters
|  | General Information |  | Calculate Temperature Normalized MTCW |  | Parameters Evaluated Prior to Pretreatment |  |  |  |  | System Operating Parameters | [30 empty] | Stage 1 Operating Parameters | [23 empty] | Stage 2 Operating Parameters | [23 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | General Cost Parameters
PWS Name | City of Melbourne Water System | Membrane manufacturer | Osmonics Desal | Average yearly temperature of feed water, TavgoC (oC) | 24.49 | Alkalinity (mg/L as CaCO3) | 92 | Process | Description | Scale | Date | Time | Operation |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  |  |  | System recovery during sample collection (decimal) | 0.63 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.41 | [6 empty] | System recovery during sample collection (decimal) | 0.602 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.38 | [6 empty] | System recovery during sample collection (decimal) | 0.42 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.27 | [6 empty] | System recovery during sample collection (decimal) | [9 empty] | Stage 1 recovery during sample collection (decimal) | [7 empty] | System recovery during sample collection (decimal) | [9 empty] | Stage 1 recovery during sample collection (decimal) | [7 empty] | System recovery during sample collection (decimal) | [9 empty] | Stage 1 recovery during sample collection (decimal) | [5 empty] | Cost Parameter | Parameter value
Public Water System Identification Number | FL3051447 | Membrane trade name | DS5 | Temperature normalized MTCW (gfd/psi) | 0.19701 | Calcium Hardness (mg/L as CaCO3) | 100 | Alum Coagulation | Aluminum sulfate dose: 151.4 mg/L | Full-scale |  |  | time | Influent | PI | PC | PP | QR | Qp | QW | Cleaning Event | QF | QI | Recovery | Recycle | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) |  |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) | [6 empty] | System feed flow rate during sample collection (gpm) | 9.1 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 3.8 | [6 empty] | System feed flow rate during sample collection (gpm) | 12.9 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 4.9 | [6 empty] | System feed flow rate during sample collection (gpm) | 12.5 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 3.4 | [6 empty] | System feed flow rate during sample collection (gpm) | [9 empty] | Stage 1 permeate flow rate during sample collection (gpm) | [7 empty] | System feed flow rate during sample collection (gpm) | [9 empty] | Stage 1 permeate flow rate during sample collection (gpm) | [7 empty] | System feed flow rate during sample collection (gpm) | [9 empty] | Stage 1 permeate flow rate during sample collection (gpm) | [5 empty] | Capital Recovery Interest Rate (%) | 6
Water Industry Data Base Number (optional) |  | Membrane element model number | DK4040F |  |  | LSI | 7.3 | Sedimentation | Circular clarifier | Full-scale | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | Indicate with "X" | (gpm) | (gpm) | (decimal) | ratio | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHF (before acid) | pHF (after acid) | TDSp | TDSF (before acid) | TDSF (after acid) | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) |  |  | System influent flow rate during sample collection (gpm) | 9.1 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 9.2 | [6 empty] | System influent flow rate during sample collection (gpm) | 12.9 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 12.8 | [6 empty] | System influent flow rate during sample collection (gpm) | 12.5 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 12.7 | [6 empty] | System influent flow rate during sample collection (gpm) | [9 empty] | Stage 1 influent flow rate during sample collection (gpm) | [7 empty] | System influent flow rate during sample collection (gpm) | [9 empty] | Stage 1 influent flow rate during sample collection (gpm) | [7 empty] | System influent flow rate during sample collection (gpm) | [9 empty] | Stage 1 influent flow rate during sample collection (gpm) | [5 empty] | Capital Recovery Period (years) | 20
|  | Molecular weight cutoff (Daltons) | 150 - 300 | Calculate System Permeate, Feed and Waste Flow Rates |  | Dissolved iron (mg/L) |  | Dual Media Filtration | Sand/anthracite | Full-scale | 1991-02-03 | 17:00 | 0 | 20 | 83 | 74 | 49 | 0 | 6.3 | 3.5 |  | 9.8 | 9.8 | 0.64286 | 0 | 11.2 | 12.7896 | 6.25 | 23.25 | 0.55009 | [11 empty] | 83 | 80 | 53 | 4.2 | 5.6 | 9.8 | 9.8 | 0.19495 | 0.42857 | 11.2 | 12.7896 | 3.5 | 25 | 0.51158 | [10 empty] | 80 | 74 | 41 | 2.1 | 3.5 | 5.6 | 5.6 | 0.2304 | 0.375 | 11.2 | 12.7896 | 6.4843 | 29.5157 | 0.43332 | [118 empty] | Overhead & Profit Factor (% of construction costs) | 10
Official ICR Contact Person |  | Membrane material (e.g., PVD, polyamide, etc.) | Proprietary | Design system recovery, R (decimal) | 0.65 | Total iron (mg/L) | 0.28 | Sulfuric Acid Feed | Approx. 85 mg/L to pH 3.5 to 4.5 | Pilot-scale | 1991-02-04 | 16:00 | 23 | 20 | 86 | 78 | 53.069 | 0 | 5.8 | 3.5 |  | 9.3 | 9.3 | 0.62366 | 0 | 10.3111 | 11.7746 | 6.25 | 22.681 | 0.51914 | [11 empty] | 86 | 81 | 57 | 3.9 | 5.4 | 9.3 | 9.3 | 0.18609 | 0.41935 | 10.4 | 11.8761 | 3.5148 | 22.9852 | 0.51668 | [10 empty] | 81 | 78 | 45 | 1.9 | 3.5 | 5.4 | 5.4 | 0.22533 | 0.35185 | 10.1333 | 11.5715 | 6.4843 | 28.0157 | 0.41304 | [10 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | Special Sitework Factor (% of construction costs) | 6.5
Mailing Address |  | Membrane construction (e.g., thin-film composite) | Thin-Film Composite | Design average system flux, FW (gfd) | 15 | Dissolved aluminum (mg/L) |  | Microfiltration | 5um filter Filter Specialists Bag Filter | Pilot-scale | 1991-02-05 | 6:00 | 37 | 18.9 | 86 | 75 | 50.7241 | 0 | 5.8 | 3.4 |  | 9.2 | 9.2 | 0.63043 | 0 | 10.3111 | 12.1637 | 6.25 | 23.5259 | 0.51704 | [11 empty] | 86 | 81 | 54 | 3.9 | 5.3 | 9.2 | 9.2 | 0.18356 | 0.42391 | 10.4 | 12.2686 | 3.5148 | 25.9852 | 0.47214 | [10 empty] | 81 | 75 | 44 | 1.9 | 3.4 | 5.3 | 5.3 | 0.22027 | 0.35849 | 10.1333 | 11.954 | 6.4843 | 27.5157 | 0.43444 | [10 empty] | Parameter | Units | Cp-sys-2 | CF-sys-2 | CC-sys-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-2 | CI-s1-2 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-6 | CF-sys-6 | CC-sys-6 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-6 | CI-s1-6 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-10 | CF-sys-10 | CC-sys-10 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-10 | CI-s1-10 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-8 | CF-sys-8 | CC-sys-8 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-8 | CI-s1-8 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-10 | CF-sys-10 | CC-sys-10 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-10 | CI-s1-10 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-10 (dup) | CF-sys-10 (dup) | CC-sys-10 (dup) | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-10 (dup) | CI-s1-10 (dup) | CC(calc) | RF (%) | CB | RB (%) | Construction Contingencies (% of construction costs) | 10
|  | Membrane hydrophobicity | Hydrophilic | Number of elements per pressure vessel, Ne | 3 | Total aluminum (mg/L) |  |  |  |  | 1991-02-05 | 11:15 | 42.3 | 18.9 | 86 | 78 | 51.0517 | 0 | 5.8 | 3.4 |  | 9.2 | 9.2 | 0.63043 | 0 | 10.3111 | 12.1637 | 6.25 | 24.6983 | 0.49249 | [11 empty] | 86 | 81 | 54 | 3.9 | 5.3 | 9.2 | 9.2 | 0.18356 | 0.42391 | 10.4 | 12.2686 | 3.5148 | 25.9852 | 0.47214 | [10 empty] | 81 | 78 | 45 | 1.9 | 3.4 | 5.3 | 5.3 | 0.22027 | 0.35849 | 10.1333 | 11.954 | 6.4843 | 28.0157 | 0.42669 | [10 empty] | Sampling date | MM/DD/YY | 1991-02-07 | 1991-02-07 | 1991-02-07 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1991-02-07 | 1991-02-07 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1991-03-05 | 1991-03-05 | 1991-03-05 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1991-03-05 | 1991-03-05 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1991-04-03 | 1991-04-03 | 1991-04-03 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1991-04-03 | 1991-04-03 | --- | --- | --- | --- | Sampling date | MM/DD/YY |  |  |  | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY |  |  | --- | --- | --- | --- | Sampling date | MM/DD/YY |  |  |  | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY |  |  | --- | --- | --- | --- | Sampling date | MM/DD/YY |  |  |  | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY |  |  | --- | --- | --- | --- | Engineering Fee Factor (% of construction costs) | 10
Phone Number |  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Negative | Number of parallel pressure vessels in stage 1, Nv-s(1) | 2 | Fluoride (mg/L) |  |  |  |  | 1991-02-05 | 18:00 | 49 | 18.9 | 86 | 78 | 50.7241 | 0 | 5.8 | 3.4 |  | 9.2 | 9.2 | 0.63043 | 0 | 10.3111 | 12.1637 | 6.25 | 25.0259 | 0.48605 | [11 empty] | 86 | 81 | 54 | 3.9 | 5.3 | 9.2 | 9.2 | 0.18356 | 0.42391 | 10.4 | 12.2686 | 3.5148 | 25.9852 | 0.47214 | [10 empty] | 81 | 78 | 44 | 1.9 | 3.4 | 5.3 | 5.3 | 0.22027 | 0.35849 | 10.1333 | 11.954 | 6.4843 | 29.0157 | 0.41198 | [10 empty] | Sampling time | hh:mm | 14:00 | 14:00 | 14:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 14:00 | 14:00 | --- | --- | --- | --- | Sampling time | hh:mm | 13:06 | 13:06 | 13:06 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 13:06 | 13:06 | --- | --- | --- | --- | Sampling time | hh:mm | 15:00 | 15:00 | 15:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 15:00 | 15:00 | --- | --- | --- | --- | Sampling time | hh:mm |  |  |  | --- | --- | --- | --- | --- | Sampling time | hh:mm |  |  | --- | --- | --- | --- | Sampling time | hh:mm |  |  |  | --- | --- | --- | --- | --- | Sampling time | hh:mm |  |  | --- | --- | --- | --- | Sampling time | hh:mm |  |  |  | --- | --- | --- | --- | --- | Sampling time | hh:mm |  |  | --- | --- | --- | --- | 1998 ENR Construction Cost Index (CCI base year 1913) | 5881.41
FAX Number |  |  |  | Number of parallel pressure vessels in stage 2, Nv-s(2) | 1 | Phosphate (mg/L) |  |  |  |  | 1991-02-06 | 5:00 | 60 | 19.4 | 84 | 74 | 51.3333 | 0 | 5.7 | 3.4 |  | 9.1 | 9.1 | 0.62637 | 0 | 10.1333 | 11.7786 | 6.25 | 21.4167 | 0.54997 | [11 empty] | 84 | 81 | 55 | 3.8 | 5.3 | 9.1 | 9.1 | 0.18229 | 0.41758 | 10.1333 | 11.7786 | 3.5148 | 23.9852 | 0.49108 | [10 empty] | 81 | 74 | 44 | 1.9 | 3.4 | 5.3 | 5.3 | 0.22027 | 0.35849 | 10.1333 | 11.7786 | 6.4843 | 27.0157 | 0.43599 | [10 empty] | Operation time | hh.hh | 93 | 93 | 93 | --- | --- | --- | --- | --- | Operation time | hh.hh | 93 | 93 | --- | --- | --- | --- | Operation time | hh.hh | 546.8 | 546.8 | 546.8 | --- | --- | --- | --- | --- | Operation time | hh.hh | 546.8 | 546.8 | --- | --- | --- | --- | Operation time | hh.hh | 1192.3 | 1192.3 | 1192.3 | --- | --- | --- | --- | --- | Operation time | hh.hh | 1192.3 | 1192.3 | --- | --- | --- | --- | Operation time | hh.hh |  |  |  | --- | --- | --- | --- | --- | Operation time | hh.hh |  |  | --- | --- | --- | --- | Operation time | hh.hh |  |  |  | --- | --- | --- | --- | --- | Operation time | hh.hh |  |  | --- | --- | --- | --- | Operation time | hh.hh |  |  |  | --- | --- | --- | --- | --- | Operation time | hh.hh |  |  | --- | --- | --- | --- | 1998 Producers Price Index (PPI base year 1967 = 100) | NR
E-Mail Address (optional) |  | Design Parameters |  | Permeate flow rate per element, Qp-e (gpm) | 0.9375 | Sulfate (mg/L) | BDL |  |  |  | 1991-02-06 | 10:00 | 65 | 19.4 | 85 | 75 | 51.3966 | 0 | 5.8 | 3.4 |  | 9.2 | 9.2 | 0.63043 | 0 | 10.3111 | 11.9852 | 6.25 | 22.3534 | 0.53617 | [11 empty] | 85 | 80 | 55 | 3.9 | 5.3 | 9.2 | 9.2 | 0.18356 | 0.42391 | 10.4 | 12.0886 | 3.5148 | 23.9852 | 0.504 | [10 empty] | 80 | 75 | 44 | 1.9 | 3.4 | 5.3 | 5.3 | 0.22027 | 0.35849 | 10.1333 | 11.7786 | 6.4843 | 27.0157 | 0.43599 | [10 empty] | pH | --- | 3.3 | 3.5 | 5.5 | --- | --- | --- | --- | --- | pH | --- | 3.5 | 3.5 | --- | --- | --- | --- | pH | --- | 2.7 | 7.3 | 3.5 | --- | --- | --- | --- | --- | pH | --- | 3.6 | 7.3 | --- | --- | --- | --- | pH | --- | 2.7 | 7.3 | 3.2 | --- | --- | --- | --- | --- | pH | --- | 3.6 | 7.3 | --- | --- | --- | --- | pH | --- |  |  |  | --- | --- | --- | --- | --- | pH | --- |  |  | --- | --- | --- | --- | pH | --- |  |  |  | --- | --- | --- | --- | --- | pH | --- |  |  | --- | --- | --- | --- | pH | --- |  |  |  | --- | --- | --- | --- | --- | pH | --- |  |  | --- | --- | --- | --- | Labor Rate + Fringe ($/work-hour) | 40.03
|  | Element size (e.g., 2.5" x 40", 4" x 40", etc.) | 4" X 40" | Permeate flow rate per pressure vessel, Qp-v (gpm) | 2.8125 | Calcium (mg/L) |  |  |  |  | 1991-02-06 | 21:00 | 76 | 19.4 | 84 | 75 | 52.0517 | 0 | 5.8 | 3.4 |  | 9.2 | 9.2 | 0.63043 | 0 | 10.3111 | 11.9852 | 6.25 | 21.1983 | 0.56539 | [11 empty] | 84 | 80 | 55 | 3.9 | 5.3 | 9.2 | 9.2 | 0.18356 | 0.42391 | 10.4 | 12.0886 | 3.5148 | 23.4852 | 0.51473 | [10 empty] | 80 | 75 | 46 | 1.9 | 3.4 | 5.3 | 5.3 | 0.22027 | 0.35849 | 10.1333 | 11.7786 | 6.4843 | 25.0157 | 0.47085 | [10 empty] | Temperature | oC | 19.4 | 19.4 | 19.4 | --- | --- | --- | --- | --- | Temperature | oC | 19.4 | 19.4 | --- | --- | --- | --- | Temperature | oC | 18.3 | 18.3 | 18.3 | --- | --- | --- | --- | --- | Temperature | oC | 18.3 | 18.3 | --- | --- | --- | --- | Temperature | oC | 21.1 | 21.1 | 21.1 | --- | --- | --- | --- | --- | Temperature | oC | 21.1 | 21.1 | --- | --- | --- | --- | Temperature | oC |  |  |  | --- | --- | --- | --- | --- | Temperature | oC |  |  | --- | --- | --- | --- | Temperature | oC |  |  |  | --- | --- | --- | --- | --- | Temperature | oC |  |  | --- | --- | --- | --- | Temperature | oC |  |  |  | --- | --- | --- | --- | --- | Temperature | oC |  |  | --- | --- | --- | --- | Labor Overhead Factor (% of labor) | 35
Technical ICR Contact Person |  | Active membrane area of membrane element used, A (ft2) | 90 | Permeate flow rate from stage 1, Qp-s(1) (gpm) | 5.625 | Barium (mg/L) |  |  |  |  | 1991-02-07 | 5:00 | 84 | 19.4 | 87 | 72 | 50.7241 | 0 | 5.8 | 3.4 |  | 9.2 | 9.2 | 0.63043 | 0 | 10.3111 | 11.9852 | 6.25 | 22.5259 | 0.53207 | [11 empty] | 87 | 82 | 54 | 3.9 | 5.3 | 9.2 | 9.2 | 0.18356 | 0.42391 | 10.4 | 12.0886 | 3.5148 | 26.9852 | 0.44797 | [10 empty] | 82 | 72 | 44 | 1.9 | 3.4 | 5.3 | 5.3 | 0.22027 | 0.35849 | 10.1333 | 11.7786 | 6.4843 | 26.5157 | 0.44421 | [10 empty] | Alkalinity | mg/L as CaCO3 | BMRL | NR | 9 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | BMRL | NR | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | BMRL | NR | BMRL | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | BMRL | NR | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | BMRL | NR | BMRL | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | BMRL | NR | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Electric Rate ($/kW-h) | 0.09
Mailing Address |  | Design flux, FW (gfd) | 20 | Permeate flow rate from stage 2, Qp-s(2) (gpm) | 2.8125 | Strontium (mg/L) |  |  |  |  | 1991-02-07 | 14:00 | 93 | 19.4 | 85 | 74 | 50.6667 | 0 | 5.7 | 3.5 |  | 9.2 | 9.2 | 0.61957 | 0 | 10.1333 | 11.7786 | 6.1686 | 22.6648 | 0.51969 | 7.6 | 3.5 | 160 | 420 | 500 | 1100 | 1053.7143 | 4.2078 | 68 | 776.8571 | 79.4042 | 85 | 82 | 54 | 3.8 | 5.4 | 9.2 | 9.2 | 0.18482 | 0.41304 | 10.1333 | 11.7786 | 3.5148 | 25.9852 | 0.45328 | 3.5 | 3.8 | 240 | 500 | 730 | 682.963 | 6.4434 | 52 | 591.4815 | 59.4239 | 82 | 74 | 44 | 1.9 | 3.5 | 5.4 | 5.4 | 0.22533 | 0.35185 | 10.1333 | 11.7786 | 6.4843 | 27.5157 | 0.42807 | 3.8 | 5.5 | 220 | 730 | 1100 | 1006.8571 | 8.4675 | 56 | 868.4286 | 74.6669 | Total dissolved solids | mg/L | 160 | 500 | 1100 | 1078.9189 | 1.9165 | 68 | 789.4595 | 79.733 | Total dissolved solids | mg/L | 240 | 500 | 682.963 | 52 | 591.4815 | 59.4239 | Total dissolved solids | mg/L | 120 | 470 | 860 | 999.397 | -16.209 | 74.4681 | 734.6985 | 83.6668 | Total dissolved solids | mg/L | 120 | 470 | 687.0886 | 74.4681 | 578.5443 | 79.2583 | Total dissolved solids | mg/L | 150 | 460 | 650 | 684.4828 | -5.305 | 67.3913 | 572.2414 | 73.7873 | Total dissolved solids | mg/L | 150 | 460 | 573.3333 | 67.3913 | 516.6667 | 70.9677 | Total dissolved solids | mg/L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Fuel Oil Rate ($/gal) | 0.911
|  | Net driving pressure at the design flux, NDP (psi) | 100 | Permeate flow rate from system, Qp-sys (gpm) | 8.4375 | Reactive silica (mg/L as SiO2) |  |  |  |  | 1991-02-07 | 21:00 | 100 | 19.4 | 86 | 74 | 51.6667 | 0 | 5.7 | 3.5 |  | 9.2 | 9.2 | 0.61957 | 0 | 10.1333 | 11.7786 | 6.25 | 22.0833 | 0.53337 | [11 empty] | 86 | 80 | 55 | 3.8 | 5.4 | 9.2 | 9.2 | 0.18482 | 0.41304 | 10.1333 | 11.7786 | 3.5148 | 24.4852 | 0.48105 | [10 empty] | 80 | 74 | 45 | 1.9 | 3.5 | 5.4 | 5.4 | 0.22533 | 0.35185 | 10.1333 | 11.7786 | 6.4843 | 25.5157 | 0.46162 | [10 empty] | Total hardness | mg/L as CaCO3 | 24 | 210 | 510 | 526.7027 | -3.275 | 88.5714 | 368.3514 | 93.4845 | Total hardness | mg/L as CaCO3 | 20 | 210 | 343.7037 | 90.4762 | 276.8519 | 92.7759 | Total hardness | mg/L as CaCO3 | 14 | 190 | 400 | 456.2111 | -14.0528 | 92.6316 | 323.1055 | 95.6671 | Total hardness | mg/L as CaCO3 | 19 | 190 | 296.0633 | 90 | 243.0316 | 92.1821 | Total hardness | mg/L as CaCO3 | 26 | 200 | 310 | 326 | -5.1613 | 87 | 263 | 90.1141 | Total hardness | mg/L as CaCO3 | 22 | 200 | 265.0753 | 89 | 232.5376 | 90.5392 | Total hardness | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Natural Gas Rate ($/ft3) | NR
Phone Number |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.2 | Feed flow rate to system, QF-sys (gpm) | 12.9808 | Turbidity (ntu) | 12 |  |  |  | 1991-02-08 | 5:00 | 108 | 18.9 | 89 | 72 | 50.7241 | 0 | 5.8 | 3.4 |  | 9.2 | 9.2 | 0.63043 | 0 | 10.3111 | 12.1637 | 6.25 | 23.5259 | 0.51704 | [11 empty] | 89 | 82 | 54 | 3.9 | 5.3 | 9.2 | 9.2 | 0.18356 | 0.42391 | 10.4 | 12.2686 | 3.5148 | 27.9852 | 0.43839 | [10 empty] | 82 | 72 | 44 | 1.9 | 3.4 | 5.3 | 5.3 | 0.22027 | 0.35849 | 10.1333 | 11.954 | 6.4843 | 26.5157 | 0.45083 | [10 empty] | Calcium hardness | mg/L as CaCO3 | 14 | 150 | 400 | 381.5676 | 4.6081 | 90.6667 | 265.7838 | 94.7326 | Calcium hardness | mg/L as CaCO3 | 14 | 150 | 245.7037 | 90.6667 | 197.8519 | 92.924 | Calcium hardness | mg/L as CaCO3 | 9 | 140 | 320 | 338.1457 | -5.6705 | 93.5714 | 239.0729 | 96.2355 | Calcium hardness | mg/L as CaCO3 | 12 | 140 | 219.3924 | 91.4286 | 179.6962 | 93.3221 | Calcium hardness | mg/L as CaCO3 | 15 | 150 | 250 | 247.7586 | 0.89655 | 90 | 198.8793 | 92.4577 | Calcium hardness | mg/L as CaCO3 | 16 | 150 | 198.9892 | 89.3333 | 174.4946 | 90.8307 | Calcium hardness | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Current Process Water Rate ($/1000 gal) | 1.882
FAX Number |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | Concentrate-waste flow rate from system, QW-sys (gpm) | 4.5433 | SDI |  |  |  |  | 1991-02-08 | 15:00 | 111 | 18.9 | 86 | 74 | 51.6667 | 0 | 5.7 | 3.5 |  | 9.2 | 9.2 | 0.61957 | 0 | 10.1333 | 11.954 | 6.25 | 22.0833 | 0.54131 | [11 empty] | 86 | 82 | 55 | 3.8 | 5.4 | 9.2 | 9.2 | 0.18482 | 0.41304 | 10.1333 | 11.954 | 3.5148 | 25.4852 | 0.46906 | [10 empty] | 82 | 74 | 45 | 1.9 | 3.5 | 5.4 | 5.4 | 0.22533 | 0.35185 | 10.1333 | 11.954 | 6.4843 | 26.5157 | 0.45083 | [10 empty] | Turbidity | ntu | BMRL | 0.2 | 0.2 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | 0.2 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | 0.6 | 45 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | 0.6 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | 0.2 | 0.2 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | 0.2 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Modifications to Existing Plant (% of construction costs) | NR
E-Mail Address (optional) |  | Maximum flow rate to the element, QI, max (gpm) | 12 |  |  | MFI |  |  |  |  | 1991-02-08 | 21:00 | 117 | 18.9 | 87 | 73 | 50.6667 | 0 | 5.7 | 3.4 |  | 9.1 | 9.1 | 0.62637 | 0 | 10.1333 | 11.954 | 6.25 | 23.0833 | 0.51786 | [11 empty] | 87 | 82 | 54 | 3.8 | 5.3 | 9.1 | 9.1 | 0.18229 | 0.41758 | 10.1333 | 11.954 | 3.5148 | 26.9852 | 0.44298 | [10 empty] | 82 | 73 | 44 | 1.9 | 3.4 | 5.3 | 5.3 | 0.22027 | 0.35849 | 10.1333 | 11.954 | 6.4843 | 27.0157 | 0.44248 | [10 empty] | Ammonia | mg NH3-N / L | NA | NA | NR | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.7 | 9.7 | 16.0333 | 92.7835 | 12.8667 | 94.5596 | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 6.2 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.3 | 7 | 9.4495 | 95.7143 | 8.2247 | 96.3525 | Ammonia | mg NH3-N / L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Minimum flow rate to the element, QI, min (gpm) | 6.25 | Calculate the Feed Flow Rates at the End of Each Stage |  | MPFI |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | 1991-02-09 | 4:00 | 124 | 18.3 | 90 | 72 | 50.3934 | 0 | 6.1 | 3.4 |  | 9.5 | 9.5 | 0.64211 | 0 | 10.8444 | 13.0218 | 6.25 | 24.3566 | 0.53463 | [11 empty] | 90 | 82 | 54 | 3.9 | 5.6 | 9.5 | 9.5 | 0.19115 | 0.41053 | 10.4 | 12.4881 | 3.5148 | 28.4852 | 0.43841 | [10 empty] | 82 | 72 | 44 | 2.2 | 3.4 | 5.6 | 5.6 | 0.22786 | 0.39286 | 11.7333 | 14.0891 | 6.4843 | 26.5157 | 0.53135 | [10 empty] | Total organic carbon | mg/L | 0.8 | 9.7 | 21 | 24.8541 | -18.3526 | 91.7526 | 17.277 | 95.3696 | UV254 | cm-1 | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 6.2 | 12 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.4 | 7 | 12 | 11.7793 | 1.8391 | 94.2857 | 9.3897 | 95.74 | UV254 | cm-1 | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | UV254 | cm-1 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | UV254 | cm-1 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | UV254 | cm-1 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Plant Name | South WTP | Total width of all membrane envelopes in the element, w (ft) | 16 | Feed flow rate at the end of stage 1, (QF-s(1))end (gpm) | 9.2308 | Color | 240 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | 1991-02-09 | 11:00 | 131 | 18.3 | 86 | 75 | 50.3966 | 0 | 5.8 | 3.4 |  | 9.2 | 9.2 | 0.63043 | 0 | 10.3111 | 12.3813 | 6.25 | 23.8534 | 0.51906 | [11 empty] | 86 | 81 | 54 | 3.9 | 5.3 | 9.2 | 9.2 | 0.18356 | 0.42391 | 10.4 | 12.4881 | 3.5148 | 25.9852 | 0.48058 | [10 empty] | 81 | 75 | 43 | 1.9 | 3.4 | 5.3 | 5.3 | 0.22027 | 0.35849 | 10.1333 | 12.1679 | 6.4843 | 28.5157 | 0.42671 | [10 empty] | UV254 | cm-1 | NA | NA | NR | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | NR | --- | --- | --- | --- | UV254 | cm-1 | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | NR | --- | --- | --- | --- | UV254 | cm-1 | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | NR | --- | --- | --- | --- | UV254 | cm-1 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | --- | --- | --- | --- | UV254 | cm-1 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SUVA | L/(mg*m) | NR | NR | --- | --- | --- | --- | UV254 | cm-1 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | --- | --- | --- | ---
Treatment Plant Category | Full Treatment | Feed spacer thickness, T (ft) | 0.00275 | Feed flow rate at the end of stage 2, (QF-s(2))end (gpm) | 5.4808 | TDS | 430 | is to list the pretreatment processes used in this particular pilot-scale run. |  |  | 1991-02-09 | 22:00 | 142 | 18.3 | 86 | 75 | 48.6667 | 0 | 5.7 | 3.5 |  | 9.2 | 9.2 | 0.61957 | 0 | 10.1333 | 12.1679 | 6.25 | 25.5833 | 0.47562 | [11 empty] | 86 | 85 | 52 | 3.8 | 5.4 | 9.2 | 9.2 | 0.18482 | 0.41304 | 10.1333 | 12.1679 | 3.5148 | 29.9852 | 0.4058 | [10 empty] | 85 | 75 | 42 | 1.9 | 3.5 | 5.4 | 5.4 | 0.22533 | 0.35185 | 10.1333 | 12.1679 | 6.4843 | 31.5157 | 0.38609 | [10 empty] | SUVA | L/(mg*m) | NR | NR | NR | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | NR | #VALUE! | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | NR | NR | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | #DIV/0! | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) |  |  |  | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | #DIV/0! | --- | --- | --- | --- | ---
Process Train Name |  | Active membrane area of an equivalent 8" x 40" element (ft2) | 350 |  |  | NPDOC | 47 |  |  |  | 1991-02-10 | 5:00 | 149 | 18.9 | 88 | 72 | 48.6667 | 0 | 5.7 | 3.4 |  | 9.1 | 9.1 | 0.62637 | 0 | 10.1333 | 11.954 | 6.25 | 25.0833 | 0.47657 | [11 empty] | 88 | 81 | 52 | 3.8 | 5.3 | 9.1 | 9.1 | 0.18229 | 0.41758 | 10.1333 | 11.954 | 3.5148 | 28.9852 | 0.41242 | [10 empty] | 81 | 72 | 42 | 1.9 | 3.4 | 5.3 | 5.3 | 0.22027 | 0.35849 | 10.1333 | 11.954 | 6.4843 | 28.0157 | 0.42669 | [10 empty] | Bromide | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | [8 empty] | Bromide | mg/L |  |  |  | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | [8 empty] | Bromide | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0!
ICR Treatment Plant Identification Number | 283 | Purchase price for an equivalent 8" x 40 " element ($) | 1500 | Calculate the Minimum Recycle Flow Rates for Each Stage1 |  | Chloride | 100 |  |  |  | 1991-02-10 | 12:15 | 156.2 | 18.9 | 85 | 78 | 48 | 0 | 5.7 | 3.4 |  | 9.1 | 9.1 | 0.62637 | 0 | 10.1333 | 11.954 | 6.25 | 27.25 | 0.43868 | [11 empty] | 85 | 81 | 51 | 3.8 | 5.3 | 9.1 | 9.1 | 0.18229 | 0.41758 | 10.1333 | 11.954 | 3.5148 | 28.4852 | 0.41966 | [10 empty] | 81 | 78 | 42 | 1.9 | 3.4 | 5.3 | 5.3 | 0.22027 | 0.35849 | 10.1333 | 11.954 | 6.4843 | 31.0157 | 0.38542 | [10 empty] | SDS-Cl2 dose | mg/L | 5 | 25 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 5 | 25 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 5 | 25 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L |  |  | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L |  |  |  | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L |  |  | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection
PWSID Number of Plant (if assigned) | FL 3051447 |  |  | Minimum recycle flow rate for stage 1, (QR-s(1))min (gpm) | 3.2692 | Total Hardness | 150 |  |  |  | 1991-02-11 | 21:00 | 183 | 16.7 | 94 | 75 | 49.3934 | 0 | 6.1 | 5.1 |  | 11.2 | 11.2 | 0.54464 | 0 | 10.8444 | 13.6524 | 6.25 | 28.8566 | 0.47311 | [11 empty] | 94 | 92 | 53 | 3.9 | 7.3 | 11.2 | 11.2 | 0.23419 | 0.34821 | 10.4 | 13.0929 | 3.5148 | 36.4852 | 0.35885 | [10 empty] | 92 | 75 | 43 | 2.2 | 5.1 | 7.3 | 7.3 | 0.31395 | 0.30137 | 11.7333 | 14.7715 | 6.4843 | 34.0157 | 0.43425 | [10 empty] | SDS-Free Cl2 residual | mg/L | 0.2 | 0.2 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.35 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 0.2 | 0.2 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.35 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 0.2 | 0.2 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.19 |  |  |  |  | SDS-Free Cl2 residual | mg/L |  |  | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | [5 empty] | SDS-Free Cl2 residual | mg/L |  |  |  | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.19 |  |  |  |  | SDS-Free Cl2 residual | mg/L |  |  | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal)
Historical Minimum Water Temperature (oC) | 13.3 | Additional Information |  | Minimum recycle flow rate for stage 2, (QR-s(2))min (gpm) | 0.76923 | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | 1991-02-11 | 3:00 | 165 | 16.7 | 85 | 76 | 48.6667 | 0 | 5.4 | 3.5 |  | 8.9 | 8.9 | 0.60674 | 0 | 9.6 | 12.0857 | 6.25 | 25.5833 | 0.47241 | [11 empty] | 85 | 82 | 52 | 3.6 | 5.3 | 8.9 | 8.9 | 0.17976 | 0.40449 | 9.6 | 12.0857 | 3.5148 | 27.9852 | 0.43186 | [10 empty] | 82 | 76 | 42 | 1.8 | 3.5 | 5.3 | 5.3 | 0.2228 | 0.33962 | 9.6 | 12.0857 | 6.4843 | 30.5157 | 0.39605 | [10 empty] | SDS-Cl2 demand | mg/L | 4.8 | 24.8 | --- | 58.8541 | --- | 80.6452 | 41.827 | 88.5242 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 1.9 |  |  |  |  | SDS-Cl2 demand | mg/L | 4.8 | 24.8 | --- | 55.0513 | --- | 80.6452 | 39.9256 | 87.9776 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 2.8 |  |  |  |  | SDS-Cl2 demand | mg/L | 4.8 | 24.8 | --- | 39.2828 | --- | 80.6452 | 32.0414 | 85.0194 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 1.8 |  |  |  |  | SDS-Cl2 demand | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! |  |  | Stage 2 permeate flow rate during sample collection (gpm) | [5 empty] | SDS-Cl2 demand | mg/L |  |  |  | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 1.8 |  |  |  |  | SDS-Cl2 demand | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! |  |  | Stage 2 permeate flow rate during sample collection (gpm)
Historical Average Water Temperature (oC) | 24.5 | Design cross-flow velocity (fps) | 0.001 | 1: A negative minimum recycle flow rate indicates that recycle is not required to |  | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | 1991-02-12 | 11:00 | 197 | 16.7 | 85 | 72 | 43.9636 | 0 | 5.5 | 3.4 |  | 8.9 | 8.9 | 0.61798 | 0 | 9.7778 | 12.3095 | 6.25 | 28.2864 | 0.43518 | [11 empty] | 85 | 82 | 45 | 3.6 | 5.3 | 8.9 | 8.9 | 0.17976 | 0.40449 | 9.6 | 12.0857 | 3.5148 | 34.9852 | 0.34545 | [10 empty] | 82 | 72 | 42 | 1.9 | 3.4 | 5.3 | 5.3 | 0.22027 | 0.35849 | 10.1333 | 12.7572 | 6.4843 | 28.5157 | 0.44737 | [10 empty] | SDS-Chlorination temp. | oC | 22 | 22 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 5.4 |  |  |  |  | SDS-Chlorination temp. | oC | 22 | 22 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 7.9 |  |  |  |  | SDS-Chlorination temp. | oC | 22 | 22 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 9.3 |  |  |  |  | SDS-Chlorination temp. | oC |  |  | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | [5 empty] | SDS-Chlorination temp. | oC |  |  |  | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 9.3 |  |  |  |  | SDS-Chlorination temp. | oC |  |  | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm)
State Approved Plant Capacity (MGD) | 16.5 | Required influent flow to permeate flow rate ratio, QI:Qp | 5 | meet the manufacturer's minimum flow requirement. | [6 empty] | 1991-02-12 | 21:00 | 207 | 16.7 | 85 | 74 | 45.3333 | 0 | 5.4 | 3.4 |  | 8.8 | 8.8 | 0.61364 | 0 | 9.6 | 12.0857 | 6.25 | 27.9167 | 0.43292 | [11 empty] | 85 | 82 | 47 | 3.6 | 5.2 | 8.8 | 8.8 | 0.17723 | 0.40909 | 9.6 | 12.0857 | 3.5148 | 32.9852 | 0.3664 | [10 empty] | 82 | 74 | 42 | 1.8 | 3.4 | 5.2 | 5.2 | 0.21774 | 0.34615 | 9.6 | 12.0857 | 6.4843 | 29.5157 | 0.40947 | [10 empty] | SDS-Chlorination pH | --- | 7.6 | 7.6 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 7.6 | 7.6 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 7.6 | 7.6 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- |  |  | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- |  |  |  | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- |  |  | --- | --- | --- | --- | --- | ---
|  | Maximum element recovery (%) | 20 | [7 empty] | 1991-02-13 | 5:00 | 215 | 17.2 | 88 | 73 | 42.7143 | 0 | 5.6 | 3.4 |  | 9 | 9 | 0.62222 | 0 | 9.9556 | 12.3495 | 6.25 | 31.5357 | 0.3916 | [11 empty] | 88 | 82 | 53 | 3.8 | 5.2 | 9 | 9 | 0.17976 | 0.42222 | 10.1333 | 12.57 | 3.5148 | 28.4852 | 0.44128 | [10 empty] | 82 | 73 | 21 | 1.8 | 3.4 | 5.2 | 5.2 | 0.21774 | 0.34615 | 9.6 | 11.9084 | 6.4843 | 50.0157 | 0.23809 | [10 empty] | SDS-Incubation time | hours | 96 | 96 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 96 | 96 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 96 | 96 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours |  |  | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours |  |  |  | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours |  |  | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters
|  | Variability of design flux (%) | 15 | Calculate the Maximum Recycle Flow Rates for Each Stage | [6 empty] | 1991-02-13 | 10:30 | 218.5 | 17.2 | 88 | 74 | 41.2909 | 0 | 5.5 | 3.4 |  | 8.9 | 8.9 | 0.61798 | 0 | 9.7778 | 12.129 | 6.25 | 33.4591 | 0.3625 | [11 empty] | 88 | 82 | 52 | 3.6 | 5.3 | 8.9 | 8.9 | 0.17976 | 0.40449 | 9.6 | 11.9084 | 3.5148 | 29.4852 | 0.40388 | [10 empty] | 82 | 74 | 21 | 1.9 | 3.4 | 5.3 | 5.3 | 0.22027 | 0.35849 | 10.1333 | 12.57 | 6.4843 | 50.5157 | 0.24883 | [10 empty] | SDS-TOX | mg Cl- /L | 73 | 1200 | --- | 3118.9459 | --- | 93.9167 | 2159.473 | 96.6195 | Parameter | Units | Cp-s2-2 | CI-s2-2 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | 73 | 950 | --- | 2276.5176 | --- | 92.3158 | 1613.2588 | 95.475 | Parameter | Units | Cp-s2-6 | CI-s2-6 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | 74 | 1600 | --- | 2705.0345 | --- | 95.375 | 2152.5172 | 96.5622 | Parameter | Units | Cp-s2-10 | CI-s2-10 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Parameter | Units | Cp-s2-8 | CI-s2-8 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L |  |  |  | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Parameter | Units | Cp-s2-10 | CI-s2-10 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Parameter | Units | Cp-s2-10 (dup) | CI-s2-10 (dup) | CC(calc) | RF (%) | CB | RB (%)
|  | Rejection of reference solute and conditions of test | 98% of 2000 mg/L MgSO4 at 100 psig | Maximum recycle flow rate for stage 1, (QR-s(1))max (gpm) | 11.0192 | [5 empty] | 1991-02-13 | 17:45 | 225.8 | 17.2 | 85 | 75 | 51.3333 | 0 | 5.7 | 3.5 |  | 9.2 | 9.2 | 0.61957 | 0 | 10.1333 | 12.57 | 6.25 | 22.4167 | 0.56074 | [11 empty] | 85 | 82 | 55 | 3.8 | 5.4 | 9.2 | 9.2 | 0.18482 | 0.41304 | 10.1333 | 12.57 | 3.5148 | 24.9852 | 0.5031 | [10 empty] | 82 | 75 | 44 | 1.9 | 3.5 | 5.4 | 5.4 | 0.22533 | 0.35185 | 10.1333 | 12.57 | 6.4843 | 28.0157 | 0.44868 | [10 empty] | SDS-CHCl3 | mg/L | 4 | 110 | --- | 290.4865 | --- | 96.3636 | 200.2432 | 98.0024 | Sampling date | MM/DD/YY | 1991-02-07 | 1991-02-07 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 4 | 160 | --- | 395.9598 | --- | 97.5 | 277.9799 | 98.561 | Sampling date | MM/DD/YY | 1991-03-05 | 1991-03-05 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 4 | 200 | --- | 341.931 | --- | 98 | 270.9655 | 98.5238 | Sampling date | MM/DD/YY | 1991-04-03 | 1991-04-03 | --- | --- | --- | --- | SDS-CHCl3 | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Sampling date | MM/DD/YY |  |  | --- | --- | --- | --- | SDS-CHCl3 | mg/L |  |  |  | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Sampling date | MM/DD/YY |  |  | --- | --- | --- | --- | SDS-CHCl3 | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Sampling date | MM/DD/YY |  |  | --- | --- | --- | ---
|  | (e.g., solute type and concentration) |  | Maximum recycle flow rate for stage 2, (QR-s(2))max (gpm) | 4.6442 | [5 empty] | 1991-02-14 | 3:00 | 235 | 17.8 | 88 | 75 | 49.7273 | 0 | 5.5 | 3.5 |  | 9 | 9 | 0.61111 | 0 | 9.7778 | 11.9157 | 6.25 | 25.5227 | 0.46687 | [11 empty] | 88 | 82 | 53 | 3.7 | 5.3 | 9 | 9 | 0.18103 | 0.41111 | 9.8667 | 12.0241 | 3.5148 | 28.4852 | 0.42212 | [10 empty] | 82 | 75 | 43 | 1.8 | 3.5 | 5.3 | 5.3 | 0.2228 | 0.33962 | 9.6 | 11.6991 | 6.4843 | 29.0157 | 0.4032 | [10 empty] | SDS-BDCM | mg/L | 12 | 96 | --- | 239.027 | --- | 87.5 | 167.5135 | 92.8364 | Sampling time | hh:mm | 14:00 | 14:00 | --- | --- | --- | --- | SDS-BDCM | mg/L | 10 | 93 | --- | 218.5427 | --- | 89.2473 | 155.7714 | 93.5803 | Sampling time | hh:mm | 13:06 | 13:06 | --- | --- | --- | --- | SDS-BDCM | mg/L | 10 | 88 | --- | 144.4828 | --- | 88.6364 | 116.2414 | 91.3972 | Sampling time | hh:mm | 15:00 | 15:00 | --- | --- | --- | --- | SDS-BDCM | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Sampling time | hh:mm |  |  | --- | --- | --- | --- | SDS-BDCM | mg/L |  |  |  | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Sampling time | hh:mm |  |  | --- | --- | --- | --- | SDS-BDCM | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Sampling time | hh:mm |  |  | --- | --- | --- | ---
|  | Variability of rejection of reference solute (%) | [8 empty] | 1991-02-14 | 11:00 | 243 | 17.8 | 88 | 76 | 49.5455 | 0 | 5.5 | 3.5 |  | 9 | 9 | 0.61111 | 0 | 9.7778 | 11.9157 | 6.25 | 26.2045 | 0.45472 | [11 empty] | 88 | 82 | 53 | 3.6 | 5.4 | 9 | 9 | 0.18229 | 0.4 | 9.6 | 11.6991 | 3.5148 | 28.4852 | 0.41071 | [10 empty] | 82 | 76 | 43 | 1.9 | 3.5 | 5.4 | 5.4 | 0.22533 | 0.35185 | 10.1333 | 12.349 | 6.4843 | 29.5157 | 0.41839 | [10 empty] | SDS-DBCM | mg/L | 23 | 49 | --- | 93.2703 | --- | 53.0612 | 71.1351 | 67.6672 | Operation time | hh.hh | 93 | 93 | --- | --- | --- | --- | SDS-DBCM | mg/L | 18 | 40 | --- | 73.2764 | --- | 55 | 56.6382 | 68.2193 | Operation time | hh.hh | 546.8 | 546.8 | --- | --- | --- | --- | SDS-DBCM | mg/L | 19 | 40 | --- | 55.2069 | --- | 52.5 | 47.6034 | 60.0869 | Operation time | hh.hh | 1192.3 | 1192.3 | --- | --- | --- | --- | SDS-DBCM | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Operation time | hh.hh |  |  | --- | --- | --- | --- | SDS-DBCM | mg/L |  |  |  | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Operation time | hh.hh |  |  | --- | --- | --- | --- | SDS-DBCM | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Operation time | hh.hh |  |  | --- | --- | --- | ---
|  | Standard testing recovery (%) | 10 | Select the Design System Recycle Flow Rate2 | [6 empty] | 1991-02-14 | 21:00 | 253 | 17.8 | 88 | 76 | 49.5455 | 0 | 5.5 | 3.5 |  | 9 | 9 | 0.61111 | 0 | 9.7778 | 11.9157 | 6.25 | 26.2045 | 0.45472 | [11 empty] | 88 | 84 | 53 | 3.6 | 5.4 | 9 | 9 | 0.18229 | 0.4 | 9.6 | 11.6991 | 3.5148 | 29.4852 | 0.39678 | [10 empty] | 84 | 76 | 43 | 1.9 | 3.5 | 5.4 | 5.4 | 0.22533 | 0.35185 | 10.1333 | 12.349 | 6.4843 | 30.5157 | 0.40468 | [10 empty] | SDS-CHBr3 | mg/L | 15 | 15 | --- | 15 | --- | 0 | 15 | 0 | pH | --- | 3.3 | 3.8 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | 14 | 11 | --- | 6.4623 | --- | -27.2727 | 8.7312 | -60.3453 | pH | --- | 3.5 | 3.6 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | 13 | 16 | --- | 18.1724 | --- | 18.75 | 17.0862 | 23.9152 | pH | --- | 3.7 | 3.6 | --- | --- | --- | --- | SDS-CHBr3 | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | pH | --- |  |  | --- | --- | --- | --- | SDS-CHBr3 | mg/L |  |  |  | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | pH | --- |  |  | --- | --- | --- | --- | SDS-CHBr3 | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | pH | --- |  |  | --- | --- | --- | ---
|  | Standard testing pH | 7 | Minimum system recycle flow rate, (QR-sys)min (gpm) | 3.2692 | [5 empty] | 1991-02-15 | 3:00 | 259 | 17.2 | 88 | 76 | 49.3636 | 0 | 5.5 | 3.5 |  | 9 | 9 | 0.61111 | 0 | 9.7778 | 12.129 | 6.25 | 26.3864 | 0.45967 | [11 empty] | 88 | 82 | 53 | 3.5 | 5.5 | 9 | 9 | 0.18356 | 0.38889 | 9.3333 | 11.5776 | 3.5148 | 28.4852 | 0.40644 | [10 empty] | 82 | 76 | 43 | 2 | 3.5 | 5.5 | 5.5 | 0.22786 | 0.36364 | 10.6667 | 13.2316 | 6.4843 | 29.5157 | 0.44829 | [10 empty] | SDS-THM4 | mg/L | 54 | 270 | --- | 637.7838 | --- | 80 | 453.8919 | 88.1029 | Temperature | oC | 19.4 | 19.4 | --- | --- | --- | --- | SDS-THM4 | mg/L | 46 | 304 | --- | 694.2412 | --- | 84.8684 | 499.1206 | 90.7838 | Temperature | oC | 18.3 | 18.3 | --- | --- | --- | --- | SDS-THM4 | mg/L | 46 | 344 | --- | 559.7931 | --- | 86.6279 | 451.8966 | 89.8207 | Temperature | oC | 21.1 | 21.1 | --- | --- | --- | --- | SDS-THM4 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Temperature | oC |  |  | --- | --- | --- | --- | SDS-THM4 | mg/L |  |  |  | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Temperature | oC |  |  | --- | --- | --- | --- | SDS-THM4 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Temperature | oC |  |  | --- | --- | --- | ---
|  | Acceptable range of operating pressures | 70 - 500 psig | Maximum system recycle flow rate, (QR-sys)max (gpm) | 4.6442 | [5 empty] | 1991-02-15 | 11:30 | 266.2 | 17.2 | 88 | 75 | 50.3333 | 0 | 5.7 | 3.5 |  | 9.2 | 9.2 | 0.61957 | 0 | 10.1333 | 12.57 | 6.25 | 24.9167 | 0.50448 | [11 empty] | 88 | 82 | 54 | 3.8 | 5.4 | 9.2 | 9.2 | 0.18482 | 0.41304 | 10.1333 | 12.57 | 3.5148 | 27.4852 | 0.45734 | [10 empty] | 82 | 75 | 43 | 1.9 | 3.5 | 5.4 | 5.4 | 0.22533 | 0.35185 | 10.1333 | 12.57 | 6.4843 | 29.0157 | 0.43321 | [10 empty] | SDS-MCAA* | mg/L | 13 | 20 | --- | 31.9189 | --- | 35 | 25.9595 | 49.9219 | Alkalinity | mg/L as CaCO3 | BMRL | BMRL | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | 7 | 10 | --- | 14.5377 | --- | 30 | 12.2688 | 42.9449 | Alkalinity | mg/L as CaCO3 | BMRL | BMRL | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | 3 | 16 | --- | 25.4138 | --- | 81.25 | 20.7069 | 85.5121 | Alkalinity | mg/L as CaCO3 | BMRL | BMRL | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L |  |  |  | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  | 0 | #DIV/0! | 0 | #DIV/0! | SDS-MCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Acceptable range of operating pH values | 2 - 11 | Design system recycle flow rate, QR-sys (gpm) | [6 empty] | 1991-02-16 | 12:00 | 268.8 | 13.3 | 89 | 81 | 49.6667 | 0 | 5.7 | 2.9 |  | 8.6 | 8.6 | 0.66279 | 0 | 10.1333 | 14.1059 | 6.25 | 29.0833 | 0.48502 | [11 empty] | 89 | 85 | 53 | 3.8 | 4.8 | 8.6 | 8.6 | 0.16963 | 0.44186 | 10.1333 | 14.1059 | 3.5148 | 30.4852 | 0.46271 | [10 empty] | 85 | 81 | 43 | 1.9 | 2.9 | 4.8 | 4.8 | 0.19495 | 0.39583 | 10.1333 | 14.1059 | 6.4843 | 33.5157 | 0.42087 | [10 empty] | SDS-DCAA* | mg/L | 3 | 110 | --- | 292.1892 | --- | 97.2727 | 201.0946 | 98.5082 | Total dissolved solids | mg/L | 220 | 730 | 1006.8571 | 56 | 868.4286 | 74.6669 | SDS-DCAA* | mg/L | 4 | 98 | --- | 240.1809 | --- | 95.9184 | 169.0905 | 97.6344 | Total dissolved solids | mg/L | 130 | 650 | 935.4902 | 72.3404 | 792.7451 | 83.6013 | SDS-DCAA* | mg/L | 4 | 130 | --- | 221.2414 | --- | 96.9231 | 175.6207 | 97.7224 | Total dissolved solids | mg/L | 190 | 560 | 648.8 | 58.6957 | 604.4 | 68.5639 | SDS-DCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCAA* | mg/L |  |  |  | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  | 0 | #DIV/0! | 0 | #DIV/0! | SDS-DCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Typical pressure drop across a single element (psi) | <10 | System influent flow rate, QI-sys (gpm) | 12.9808 | [5 empty] | 1991-02-18 | 4:00 | 284.7 | 16.1 | 104 | 90 | 33.375 | 0 | 4.8 | 3.4 |  | 8.2 | 8.2 | 0.58537 | 0 | 8.5333 | 10.9351 | 6.25 | 57.375 | 0.19059 | [11 empty] | 104 | 100 | 34 | 3.3 | 4.9 | 8.2 | 8.2 | 0.16583 | 0.40244 | 8.8 | 11.2768 | 3.5148 | 64.4852 | 0.17487 | [10 empty] | 100 | 90 | 32 | 1.5 | 3.4 | 4.9 | 4.9 | 0.21014 | 0.30612 | 8 | 10.2517 | 6.4843 | 56.5157 | 0.18139 | [10 empty] | SDS-TCAA* | mg/L | 1 | 110 | --- | 295.5946 | --- | 99.0909 | 202.7973 | 99.5069 | Total hardness | mg/L as CaCO3 | 24 | 320 | 480.6857 | 88.5714 | 400.3429 | 94.0051 | SDS-TCAA* | mg/L | 1 | 120 | --- | 299.995 | --- | 99.1667 | 209.9975 | 99.5238 | Total hardness | mg/L as CaCO3 | 17 | 270 | 408.902 | 91.0526 | 339.451 | 94.9919 | SDS-TCAA* | mg/L | 1 | 130 | --- | 223.4138 | --- | 99.2308 | 176.7069 | 99.4341 | Total hardness | mg/L as CaCO3 | 34 | 250 | 301.84 | 83 | 275.92 | 87.6776 | SDS-TCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TCAA* | mg/L |  |  |  | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  | 0 | #DIV/0! | 0 | #DIV/0! | SDS-TCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Maximum permissible SDI | 5 | Recycle ratio, r | 0 | [5 empty] | 1991-02-18 | 13:00 | 293.7 | 16.1 | 90 | 80 | 48.0517 | 0 | 5.8 | 3 |  | 8.8 | 8.8 | 0.65909 | 0 | 10.3111 | 13.2133 | 6.25 | 30.6983 | 0.43042 | [11 empty] | 90 | 87 | 51 | 3.9 | 4.9 | 8.8 | 8.8 | 0.17343 | 0.44318 | 10.4 | 13.3272 | 3.5148 | 33.9852 | 0.39215 | [10 empty] | 87 | 80 | 42 | 1.9 | 3 | 4.9 | 4.9 | 0.20001 | 0.38776 | 10.1333 | 12.9854 | 6.4843 | 35.0157 | 0.37085 | [10 empty] | SDS-MBAA* | mg/L | 1 | 3 | --- | 6.4054 | --- | 66.6667 | 4.7027 | 78.7356 | Calcium hardness | mg/L as CaCO3 | 21 | 250 | 374.3143 | 86 | 312.1571 | 93.2726 | SDS-MBAA* | mg/L | 1 | 6 | --- | 13.5628 | --- | 83.3333 | 9.7814 | 89.7765 | Calcium hardness | mg/L as CaCO3 | 11 | 210 | 319.2549 | 92.1429 | 264.6275 | 95.8432 | SDS-MBAA* | mg/L | BMRL | 4 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 13 | 200 | 244.88 | 91.3333 | 222.44 | 94.1557 | SDS-MBAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L |  |  |  | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  | 0 | #DIV/0! | 0 | #DIV/0! | SDS-MBAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Maximum permissible turbidity (ntu) | 1 | 2: The design system recycle flow rate must fall between the minimum and | [6 empty] | 1991-02-18 | 19:00 | 299.7 | 16.1 | 90 | 80 | 48.5862 | 0 | 5.8 | 4.4 |  | 10.2 | 10.2 | 0.56863 | 0 | 10.3111 | 13.2133 | 6.25 | 30.1638 | 0.43805 | [11 empty] | 90 | 87 | 52 | 3.6 | 6.6 | 10.2 | 10.2 | 0.21267 | 0.35294 | 9.6 | 12.302 | 3.5148 | 32.9852 | 0.37296 | [10 empty] | 87 | 80 | 43 | 2.2 | 4.4 | 6.6 | 6.6 | 0.2785 | 0.33333 | 11.7333 | 15.0358 | 6.4843 | 34.0157 | 0.44202 | [10 empty] | SDS-DBAA* | mg/L | 6 | 11 | --- | 19.5135 | --- | 45.4545 | 15.2568 | 60.6732 | Turbidity | ntu | BMRL | BMRL | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | 5 | 9 | --- | 15.0503 | --- | 44.4444 | 12.0251 | 58.4204 | Turbidity | ntu | BMRL | 7.6 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | 6 | 13 | --- | 18.069 | --- | 53.8462 | 15.5345 | 61.3762 | Turbidity | ntu | BMRL | 0.1 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DBAA* | mg/L |  |  |  | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  | 0 | #DIV/0! | 0 | #DIV/0! | SDS-DBAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | 1000 ppm - hours | maximum system recycle flow rates. | [6 empty] | 1991-02-19 | 1:00 | 305.7 | 16.7 | 90 | 80 | 49.4516 | 0 | 6.2 | 3 |  | 9.2 | 9.2 | 0.67391 | 0 | 11.0222 | 13.8762 | 6.25 | 29.2984 | 0.47362 | [11 empty] | 90 | 87 | 53 | 4 | 5.2 | 9.2 | 9.2 | 0.18229 | 0.43478 | 10.6667 | 13.4286 | 3.5148 | 31.9852 | 0.41984 | [10 empty] | 87 | 80 | 43 | 2.2 | 3 | 5.2 | 5.2 | 0.20761 | 0.42308 | 11.7333 | 14.7715 | 6.4843 | 34.0157 | 0.43425 | [10 empty] | SDS-BCAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 2 | 14 | 20.5143 | 79.3814 | 17.2571 | 88.4106 | SDS-BCAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 12 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.5 | 10 | 12.28 | 92.8571 | 11.14 | 95.5117 | SDS-BCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-BCAA* | mg/L |  |  |  | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  | 0 | #DIV/0! | 0 | #DIV/0! | SDS-BCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | 1: All of the information requested in this field may not be available, but values for all of the Design | [8 empty] | 1991-02-19 | 15:30 | 320.3 | 16.7 | 88 | 80 | 50.0517 | 0 | 5.8 | 3 |  | 8.8 | 8.8 | 0.65909 | 0 | 10.3111 | 12.981 | 6.25 | 27.6983 | 0.46866 | [11 empty] | 88 | 84 | 53 | 3.9 | 4.9 | 8.8 | 8.8 | 0.17343 | 0.44318 | 10.4 | 13.0929 | 3.5148 | 29.4852 | 0.44405 | [10 empty] | 84 | 80 | 44 | 1.9 | 3 | 4.9 | 4.9 | 0.20001 | 0.38776 | 10.1333 | 12.7572 | 6.4843 | 31.5157 | 0.40479 | [10 empty] | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | UV254 | cm-1 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L |  |  |  | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | UV254 | cm-1 |  |  | 0 | #DIV/0! | 0 | #DIV/0! | SDS-TBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | UV254 | cm-1 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Parameters must be entered in cells E15:E26, since these parameters are used in calculations. |  | Summary of the Stage and System Flow Rates | [6 empty] | 1991-02-20 | 3:00 | 331.8 | 17.8 | 90 | 80 | 44.7097 | 0 | 6.2 | 3 |  | 9.2 | 9.2 | 0.67391 | 0 | 11.0222 | 13.4323 | 6.25 | 34.0403 | 0.3946 | [11 empty] | 90 | 88 | 55 | 4 | 5.2 | 9.2 | 9.2 | 0.18229 | 0.43478 | 10.6667 | 12.999 | 3.5148 | 30.4852 | 0.4264 | [10 empty] | 88 | 80 | 26 | 2.2 | 3 | 5.2 | 5.2 | 0.20761 | 0.42308 | 11.7333 | 14.2989 | 6.4843 | 51.5157 | 0.27756 | [10 empty] | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | NR | --- | --- | --- | --- | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | NR | --- | --- | --- | --- | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | NR | --- | --- | --- | --- | SDS-CDBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | --- | --- | --- | --- | SDS-CDBAA | mg/L |  |  |  | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | SUVA | L/(mg*m) | NR | NR | --- | --- | --- | --- | SDS-CDBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | --- | --- | --- | ---
|  |  |  | Influent flow rate to stage 1, QI-s(1) (gpm) | 12.9808 | [5 empty] | 1991-02-20 | 12:00 | 340.8 | 17.8 | 88 | 80 | 51.0517 | 0 | 5.8 | 3 |  | 8.8 | 8.8 | 0.65909 | 0 | 10.3111 | 12.5657 | 6.25 | 26.6983 | 0.47066 | [11 empty] | 88 | 85 | 54 | 3.9 | 4.9 | 8.8 | 8.8 | 0.17343 | 0.44318 | 10.4 | 12.674 | 3.5148 | 28.9852 | 0.43726 | [10 empty] | 85 | 80 | 45 | 1.9 | 3 | 4.9 | 4.9 | 0.20001 | 0.38776 | 10.1333 | 12.349 | 6.4843 | 31.0157 | 0.39815 | [10 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | [8 empty] | SDS-DCBAA | mg/L |  |  |  | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | [8 empty] | SDS-DCBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  |  |  | Permeate flow rate from stage 1, Qp-s(1) (gpm) | 5.625 | [5 empty] | 1991-02-20 | 20:00 | 348.8 | 17.8 | 90 | 80 | 52.1404 | 0 | 5.7 | 3 |  | 8.7 | 8.7 | 0.65517 | 0 | 10.1333 | 12.349 | 6.25 | 26.6096 | 0.46408 | [11 empty] | 90 | 85 | 56 | 3.5 | 5.2 | 8.7 | 8.7 | 0.17596 | 0.4023 | 9.3333 | 11.3741 | 3.5148 | 27.9852 | 0.40643 | [10 empty] | 85 | 80 | 46 | 2.2 | 3 | 5.2 | 5.2 | 0.20761 | 0.42308 | 11.7333 | 14.2989 | 6.4843 | 30.0157 | 0.47638 | [10 empty] | SDS-HAA5 | mg/L | 24 | 254 | --- | 645.6216 | --- | 90.5512 | 449.8108 | 94.6644 | [8 empty] | SDS-HAA5 | mg/L | 18 | 243 | --- | 583.3266 | --- | 92.5926 | 413.1633 | 95.6434 | [8 empty] | SDS-HAA5 | mg/L | 14 | 293 | --- | 495.0345 | --- | 95.2218 | 394.0172 | 96.4469 | [8 empty] | SDS-HAA5 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | [8 empty] | SDS-HAA5 | mg/L |  |  |  | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | [8 empty] | SDS-HAA5 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  |  |  | Concentrate flow rate from stage 1, QC-s(1) (gpm) | 7.3558 | [5 empty] | 1991-02-24 | 11:00 | 349.8 | 20 | 85 | 80 | 55.3333 | 0 | 5.7 | 2.9 |  | 8.6 | 8.6 | 0.66279 | 0 | 10.1333 | 11.5715 | 6.25 | 20.9167 | 0.55322 | [11 empty] | 85 | 81 | 59 | 3.8 | 4.8 | 8.6 | 8.6 | 0.16963 | 0.44186 | 10.1333 | 11.5715 | 3.5148 | 20.4852 | 0.56487 | [10 empty] | 81 | 80 | 48 | 1.9 | 2.9 | 4.8 | 4.8 | 0.19495 | 0.39583 | 10.1333 | 11.5715 | 6.4843 | 26.0157 | 0.44479 | [10 empty] | SDS-HAA6 | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-HAA6 | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-HAA6 | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-HAA6 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | [8 empty] | SDS-HAA6 | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-HAA6 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  |  |  | Influent flow rate to stage 2, QI-s(2) (gpm) | 7.3558 | [5 empty] | 1991-02-24 | 19:00 | 357.7 | 20 | 85 | 80 | 54.6071 | 0 | 5.6 | 3 |  | 8.6 | 8.6 | 0.65116 | 0 | 9.9556 | 11.3685 | 6.25 | 21.6429 | 0.52528 | [11 empty] | 85 | 80 | 58 | 3.7 | 4.9 | 8.6 | 8.6 | 0.1709 | 0.43023 | 9.8667 | 11.267 | 3.5148 | 20.9852 | 0.5369 | [10 empty] | 80 | 80 | 48 | 1.9 | 3 | 4.9 | 4.9 | 0.20001 | 0.38776 | 10.1333 | 11.5715 | 6.4843 | 25.5157 | 0.45351 | [10 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
|  |  |  | Permeate flow rate from stage 2, Qp-s(2) (gpm) | 2.8125 | [5 empty] | 1991-02-25 | 6:00 | 368.8 | 21.1 | 88 | 79 | 54.3333 | 0 | 5.7 | 2.9 |  | 8.6 | 8.6 | 0.66279 | 0 | 10.1333 | 11.2014 | 6.25 | 22.9167 | 0.48879 | [11 empty] | 88 | 84 | 58 | 3.8 | 4.8 | 8.6 | 8.6 | 0.16963 | 0.44186 | 10.1333 | 11.2014 | 3.5148 | 24.4852 | 0.45747 | [10 empty] | 84 | 79 | 47 | 1.9 | 2.9 | 4.8 | 4.8 | 0.19495 | 0.39583 | 10.1333 | 11.2014 | 6.4843 | 28.0157 | 0.39982 | [10 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
|  |  |  | Concentrate flow rate from stage 2, QC-s(2) (gpm) | 4.5433 | [5 empty] | 1991-02-25 | 13:15 | 375.3 | 21.1 | 88 | 79 | 55.6667 | 0 | 5.7 | 2.9 |  | 8.6 | 8.6 | 0.66279 | 0 | 10.1333 | 11.2014 | 6.25 | 21.5833 | 0.51898 | [11 empty] | 88 | 84 | 59 | 3.8 | 4.8 | 8.6 | 8.6 | 0.16963 | 0.44186 | 10.1333 | 11.2014 | 3.5148 | 23.4852 | 0.47695 | [10 empty] | 84 | 79 | 49 | 1.9 | 2.9 | 4.8 | 4.8 | 0.19495 | 0.39583 | 10.1333 | 11.2014 | 6.4843 | 26.0157 | 0.43056
|  |  |  | System concentrate recycle flow rate, QR-sys (gpm) | 0 | [5 empty] | 1991-02-25 | 20:00 | 382 | 21.1 | 88 | 79 | 55 | 0 | 5.7 | 2.9 |  | 8.6 | 8.6 | 0.66279 | 0 | 10.1333 | 11.2014 | 6.25 | 22.25 | 0.50343 | [11 empty] | 88 | 84 | 58 | 3.8 | 4.8 | 8.6 | 8.6 | 0.16963 | 0.44186 | 10.1333 | 11.2014 | 3.5148 | 24.4852 | 0.45747 | [10 empty] | 84 | 79 | 49 | 1.9 | 2.9 | 4.8 | 4.8 | 0.19495 | 0.39583 | 10.1333 | 11.2014 | 6.4843 | 26.0157 | 0.43056 | [10 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs
|  |  |  | System concentrate waste flow rate, QW-sys (gpm) | 4.5433 | [5 empty] | 1991-02-26 | 11:00 | 388.3 | 20.6 | 88 | 80 | 55.6667 | 0 | 5.7 | 3.1 |  | 8.8 | 8.8 | 0.64773 | 0 | 10.1333 | 11.3681 | 6.25 | 22.0833 | 0.51478 | [11 empty] | 88 | 85 | 59 | 3.8 | 5 | 8.8 | 8.8 | 0.1747 | 0.43182 | 10.1333 | 11.3681 | 3.5148 | 23.9852 | 0.47396 | [10 empty] | 85 | 80 | 49 | 1.9 | 3.1 | 5 | 5 | 0.20508 | 0.38 | 10.1333 | 11.3681 | 6.4843 | 27.0157 | 0.4208 | [11 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls
|  |  |  | System permeate flow rate, Qp-sys (gpm) | 8.4375 | [5 empty] | 1991-02-26 | 18:00 | 395.3 | 20.6 | 88 | 79 | 54.6667 | 0 | 5.7 | 2.9 |  | 8.6 | 8.6 | 0.66279 | 0 | 10.1333 | 11.3681 | 6.25 | 22.5833 | 0.50339 | [11 empty] | 88 | 85 | 58 | 3.8 | 4.8 | 8.6 | 8.6 | 0.16963 | 0.44186 | 10.1333 | 11.3681 | 3.5148 | 24.9852 | 0.45499 | [10 empty] | 85 | 79 | 48 | 1.9 | 2.9 | 4.8 | 4.8 | 0.19495 | 0.39583 | 10.1333 | 11.3681 | 6.4843 | 27.5157 | 0.41315 | [11 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2
|  |  |  | System feed flow rate, QF-sys (gpm) | 12.9808 | [5 empty] | 1991-02-27 | 3:00 | 404.3 | 18.3 | 89 | 80 | 53.8909 | 0 | 5.5 | 2.9 |  | 8.4 | 8.4 | 0.65476 | 0 | 9.7778 | 11.7409 | 6.25 | 24.3591 | 0.48199 | [11 empty] | 89 | 85 | 57 | 3.6 | 4.8 | 8.4 | 8.4 | 0.1671 | 0.42857 | 9.6 | 11.5275 | 3.5148 | 26.4852 | 0.43524 | [10 empty] | 85 | 80 | 48 | 1.9 | 2.9 | 4.8 | 4.8 | 0.19495 | 0.39583 | 10.1333 | 12.1679 | 6.4843 | 28.0157 | 0.43432 | [10 empty] | Qp/QT (THM4), % | 91.6667 | 108.3333 |  | Qp/QT (HAA5), % | 86.9565 | 98.6957 | [11 empty] | Qp/QT (THM4), % | 89.9225 | 103.876 |  | Qp/QT (HAA5), % | 84 | 96 | [11 empty] | Qp/QT (THM4), % | 91.2752 | 103.3557 |  | Qp/QT (HAA5), % | 85.6631 | 95.3405 | [11 empty] | Qp/QT (THM4), % | #DIV/0! | #DIV/0! |  | Qp/QT (HAA5), % | #DIV/0! | #DIV/0! | [11 empty] | Qp/QT (THM4), % | #DIV/0! | #DIV/0! |  | Qp/QT (HAA5), % | #DIV/0! | #DIV/0! | [11 empty] | Qp/QT (THM4), % | #DIV/0! | #DIV/0! |  | Qp/QT (HAA5), % | #DIV/0! | #DIV/0!
[11 empty] | 1991-02-27 | 10:30 | 411.8 | 18.3 | 88 | 80 | 55.3333 | 0 | 5.7 | 2.9 |  | 8.6 | 8.6 | 0.66279 | 0 | 10.1333 | 12.1679 | 6.25 | 22.4167 | 0.5428 | [11 empty] | 88 | 85 | 59 | 3.8 | 4.8 | 8.6 | 8.6 | 0.16963 | 0.44186 | 10.1333 | 12.1679 | 3.5148 | 23.9852 | 0.50731 | [10 empty] | 85 | 80 | 48 | 1.9 | 2.9 | 4.8 | 4.8 | 0.19495 | 0.39583 | 10.1333 | 12.1679 | 6.4843 | 28.0157 | 0.43432 | [10 empty] | SDS-THM4b, mg/L | 72 | NA |  | SDS-THM4b, mg/L | 82.1739 | 56.8174 | [11 empty] | SDS-THM4b, mg/L | 72 | NA |  | SDS-THM4b, mg/L | 87.28 | 56.32 | [11 empty] | SDS-THM4b, mg/L | 72 | NA |  | SDS-THM4b, mg/L | 88.724 | 59.8853 | [11 empty] | SDS-THM4b, mg/L | #DIV/0! | #DIV/0! |  | SDS-THM4b, mg/L | #DIV/0! | #DIV/0! | [11 empty] | SDS-THM4b, mg/L | #DIV/0! | #DIV/0! |  | SDS-THM4b, mg/L | #DIV/0! | #DIV/0! | [11 empty] | SDS-THM4b, mg/L | #DIV/0! | #DIV/0! |  | SDS-THM4b, mg/L | #DIV/0! | #DIV/0!
|  |  |  | Calculate the Required System Influent Pressure | [6 empty] | 1991-02-27 | 18:00 | 419.3 | 18.3 | 88 | 80 | 54.6667 | 0 | 5.7 | 2.9 |  | 8.6 | 8.6 | 0.66279 | 0 | 10.1333 | 12.1679 | 6.25 | 23.0833 | 0.52713 | [11 empty] | 88 | 85 | 58 | 3.8 | 4.8 | 8.6 | 8.6 | 0.16963 | 0.44186 | 10.1333 | 12.1679 | 3.5148 | 24.9852 | 0.487 | [10 empty] | 85 | 80 | 48 | 1.9 | 2.9 | 4.8 | 4.8 | 0.19495 | 0.39583 | 10.1333 | 12.1679 | 6.4843 | 28.0157 | 0.43432 | [10 empty] | SDS-HAA5b, mg/L | 43.1667 | NA |  | SDS-HAA5b, mg/L | 54 | 27 | [11 empty] | SDS-HAA5b, mg/L | 40.6744 | NA |  | SDS-HAA5b, mg/L | 54 | 27 | [11 empty] | SDS-HAA5b, mg/L | 38.3423 | NA |  | SDS-HAA5b, mg/L | 54 | 27 | [11 empty] | SDS-HAA5b, mg/L | #DIV/0! | #DIV/0! |  | SDS-HAA5b, mg/L | #DIV/0! | #DIV/0! | [11 empty] | SDS-HAA5b, mg/L | #DIV/0! | #DIV/0! |  | SDS-HAA5b, mg/L | #DIV/0! | #DIV/0! | [11 empty] | SDS-HAA5b, mg/L | #DIV/0! | #DIV/0! |  | SDS-HAA5b, mg/L | #DIV/0! | #DIV/0!
|  |  |  | Osmotic pressure for stage 13, Dp1 (psi) | 3 | [5 empty] | 1991-02-28 | 3:00 | 428.3 | 18.9 | 90 | 80 | 52.6071 | 0 | 5.6 | 3 |  | 8.6 | 8.6 | 0.65116 | 0 | 9.9556 | 11.7443 | 6.25 | 26.1429 | 0.44923 | [11 empty] | 90 | 85 | 56 | 3.7 | 4.9 | 8.6 | 8.6 | 0.1709 | 0.43023 | 9.8667 | 11.6394 | 3.5148 | 27.9852 | 0.41591 | [10 empty] | 85 | 80 | 46 | 1.9 | 3 | 4.9 | 4.9 | 0.20001 | 0.38776 | 10.1333 | 11.954 | 6.4843 | 30.0157 | 0.39826 | [10 empty] | SDS-TOXb, mg Cl- /L | 166.9167 | NA |  | SDS-TOXb, mg Cl- /L | 220 | 87.7 | [11 empty] | SDS-TOXb, mg Cl- /L | 161.3798 | NA |  | SDS-TOXb, mg Cl- /L | 213.32 | 108.08 | [11 empty] | SDS-TOXb, mg Cl- /L | 207.1409 | NA |  | SDS-TOXb, mg Cl- /L | 292.7814 | 145.1039 | [11 empty] | SDS-TOXb, mg Cl- /L | #DIV/0! | #DIV/0! |  | SDS-TOXb, mg Cl- /L | #DIV/0! | #DIV/0! | [11 empty] | SDS-TOXb, mg Cl- /L | #DIV/0! | #DIV/0! |  | SDS-TOXb, mg Cl- /L | #DIV/0! | #DIV/0! | [11 empty] | SDS-TOXb, mg Cl- /L | #DIV/0! | #DIV/0! |  | SDS-TOXb, mg Cl- /L | #DIV/0! | #DIV/0!
|  |  |  | Osmotic pressure for stage 23, Dp2 (psi) | 6 | [5 empty] | 1991-02-28 | 11:00 | 436.3 | 18.9 | 88 | 80 | 51.6667 | 0 | 5.7 | 3.1 |  | 8.8 | 8.8 | 0.64773 | 0 | 10.1333 | 11.954 | 6.25 | 26.0833 | 0.4583 | [11 empty] | 88 | 85 | 55 | 3.8 | 5 | 8.8 | 8.8 | 0.1747 | 0.43182 | 10.1333 | 11.954 | 3.5148 | 27.9852 | 0.42715 | [10 empty] | 85 | 80 | 45 | 1.9 | 3.1 | 5 | 5 | 0.20508 | 0.38 | 10.1333 | 11.954 | 6.4843 | 31.0157 | 0.38542 | [10 empty] | SDS-CDb, mg/L | 6.4667 | NA |  | SDS-CDb, mg/L | 7.4087 | 5.0609 | [11 empty] | SDS-CDb, mg/L | 6.8155 | NA |  | SDS-CDb, mg/L | 8 | 5.6 | [11 empty] | SDS-CDb, mg/L | 6.545 | NA |  | SDS-CDb, mg/L | 7.6674 | 5.7319 | [11 empty] | SDS-CDb, mg/L | #DIV/0! | #DIV/0! |  | SDS-CDb, mg/L | #DIV/0! | #DIV/0! | [11 empty] | SDS-CDb, mg/L | #DIV/0! | #DIV/0! |  | SDS-CDb, mg/L | #DIV/0! | #DIV/0! | [11 empty] | SDS-CDb, mg/L | #DIV/0! | #DIV/0! |  | SDS-CDb, mg/L | #DIV/0! | #DIV/0!
|  |  |  | Pressure losses due to stage hardware, DPs (psi) | 3 | [5 empty] | 1991-02-28 | 15:00 | 440.3 | 18.9 | 88 | 79 | 53.3333 | 0 | 5.7 | 2.9 |  | 8.6 | 8.6 | 0.66279 | 0 | 10.1333 | 11.954 | 6.25 | 23.9167 | 0.49982 | [11 empty] | 88 | 82 | 57 | 3.8 | 4.8 | 8.6 | 8.6 | 0.16963 | 0.44186 | 10.1333 | 11.954 | 3.5148 | 24.4852 | 0.48821 | [10 empty] | 82 | 79 | 46 | 1.9 | 2.9 | 4.8 | 4.8 | 0.19495 | 0.39583 | 10.1333 | 11.954 | 6.4843 | 28.0157 | 0.42669 | [10 empty] | TOCb, mg/L | 1.5417 | NA |  | TOCb, mg/L | 1.9609 | 0.91609 | [11 empty] | TOCb, mg/L | #VALUE! | NA |  | TOCb, mg/L | #VALUE! | #VALUE! | [11 empty] | TOCb, mg/L | 0.97584 | NA |  | TOCb, mg/L | 1.3462 | 0.70753 | [11 empty] | TOCb, mg/L | #DIV/0! | #DIV/0! |  | TOCb, mg/L | #DIV/0! | #DIV/0! | [11 empty] | TOCb, mg/L | #DIV/0! | #DIV/0! |  | TOCb, mg/L | #DIV/0! | #DIV/0! | [11 empty] | TOCb, mg/L | #DIV/0! | #DIV/0! |  | TOCb, mg/L | #DIV/0! | #DIV/0!
|  |  |  | Pressure losses in a single element, DPe (psi) | 3 | [5 empty] | 1991-02-28 | 22:00 | 447.2 | 18.9 | 88 | 79 | 53.3333 | 0 | 5.7 | 2.9 |  | 8.6 | 8.6 | 0.66279 | 0 | 10.1333 | 11.954 | 6.25 | 23.9167 | 0.49982 | [11 empty] | 88 | 82 | 57 | 3.8 | 4.8 | 8.6 | 8.6 | 0.16963 | 0.44186 | 10.1333 | 11.954 | 3.5148 | 24.4852 | 0.48821 | [10 empty] | 82 | 79 | 46 | 1.9 | 2.9 | 4.8 | 4.8 | 0.19495 | 0.39583 | 10.1333 | 11.954 | 6.4843 | 28.0157 | 0.42669 | [10 empty] | UV254 b, cm-1 | #VALUE! | NA |  | UV254 b, cm-1 | #VALUE! | #VALUE! | [11 empty] | UV254 b, cm-1 | #VALUE! | NA |  | UV254 b, cm-1 | #VALUE! | #VALUE! | [11 empty] | UV254 b, cm-1 | #VALUE! | NA |  | UV254 b, cm-1 | #VALUE! | #VALUE! | [11 empty] | UV254 b, cm-1 | #DIV/0! | #DIV/0! |  | UV254 b, cm-1 | #DIV/0! | #DIV/0! | [11 empty] | UV254 b, cm-1 | #DIV/0! | #DIV/0! |  | UV254 b, cm-1 | #DIV/0! | #DIV/0! | [11 empty] | UV254 b, cm-1 | #DIV/0! | #DIV/0! |  | UV254 b, cm-1 | #DIV/0! | #DIV/0!
|  |  |  | Design permeate pressure, Pp (psi) | 45 | [5 empty] | 1991-03-01 | 3:00 | 452.3 | 20 | 89 | 80 | 52.6071 | 0 | 5.6 | 3 |  | 8.6 | 8.6 | 0.65116 | 0 | 9.9556 | 11.3685 | 6.25 | 25.6429 | 0.44334 | [11 empty] | 89 | 84 | 56 | 3.7 | 4.9 | 8.6 | 8.6 | 0.1709 | 0.43023 | 9.8667 | 11.267 | 3.5148 | 26.9852 | 0.41753 | [10 empty] | 84 | 80 | 46 | 1.9 | 3 | 4.9 | 4.9 | 0.20001 | 0.38776 | 10.1333 | 11.5715 | 6.4843 | 29.5157 | 0.39205 | [10 empty] | Bromideb, mg/L | #VALUE! | NA |  | Bromideb, mg/L | #VALUE! | #VALUE! | [11 empty] | Bromideb, mg/L | #VALUE! | NA |  | Bromideb, mg/L | #VALUE! | #VALUE! | [11 empty] | Bromideb, mg/L | #VALUE! | NA |  | Bromideb, mg/L | #VALUE! | #VALUE! | [11 empty] | Bromideb, mg/L | #DIV/0! | #DIV/0! |  | Bromideb, mg/L | #DIV/0! | #DIV/0! | [11 empty] | Bromideb, mg/L | #DIV/0! | #DIV/0! |  | Bromideb, mg/L | #DIV/0! | #DIV/0! | [11 empty] | Bromideb, mg/L | #DIV/0! | #DIV/0! |  | Bromideb, mg/L | #DIV/0! | #DIV/0!
|  |  |  | Mechanical pressure losses per stage, Ls (psi) | 12 | [5 empty] | 1991-03-01 | 11:00 | 460.3 | 20 | 88 | 80 | 52 | 0 | 5.7 | 2.9 |  | 8.6 | 8.6 | 0.66279 | 0 | 10.1333 | 11.5715 | 6.25 | 25.75 | 0.44938 | [11 empty] | 88 | 84 | 55 | 3.8 | 4.8 | 8.6 | 8.6 | 0.16963 | 0.44186 | 10.1333 | 11.5715 | 3.5148 | 27.4852 | 0.42101 | [10 empty] | 84 | 80 | 46 | 1.9 | 2.9 | 4.8 | 4.8 | 0.19495 | 0.39583 | 10.1333 | 11.5715 | 6.4843 | 29.5157 | 0.39205 | [10 empty] | Alkb, mg/L CaCO3 | #VALUE! | NA |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! | [11 empty] | Alkb, mg/L CaCO3 | #VALUE! | NA |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! | [11 empty] | Alkb, mg/L CaCO3 | #VALUE! | NA |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! | [11 empty] | Alkb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | Alkb, mg/L CaCO3 | #DIV/0! | #DIV/0! | [11 empty] | Alkb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | Alkb, mg/L CaCO3 | #DIV/0! | #DIV/0! | [11 empty] | Alkb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | Alkb, mg/L CaCO3 | #DIV/0! | #DIV/0!
|  |  |  | Net driving pressure required for permeation, NDP (psi) | 76.1392 | [5 empty] | 1991-03-01 | 22:00 | 471.2 | 20 | 89 | 80 | 53.9464 | 0 | 5.6 | 2.9 |  | 8.5 | 8.5 | 0.65882 | 0 | 9.9556 | 11.3685 | 6.25 | 24.3036 | 0.46777 | [11 empty] | 89 | 85 | 57 | 3.7 | 4.8 | 8.5 | 8.5 | 0.16837 | 0.43529 | 9.8667 | 11.267 | 3.5148 | 26.4852 | 0.42541 | [10 empty] | 85 | 80 | 48 | 1.9 | 2.9 | 4.8 | 4.8 | 0.19495 | 0.39583 | 10.1333 | 11.5715 | 6.4843 | 28.0157 | 0.41304 | [10 empty] | T-Hdb, mg/L CaCO3 | 39.5 | NA |  | T-Hdb, mg/L CaCO3 | 48.2609 | 26.4261 | [11 empty] | T-Hdb, mg/L CaCO3 | 31.7364 | NA |  | T-Hdb, mg/L CaCO3 | 42.16 | 21.04 | [11 empty] | T-Hdb, mg/L CaCO3 | 41.1812 | NA |  | T-Hdb, mg/L CaCO3 | 50.9462 | 34.1075 | [11 empty] | T-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | T-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! | [11 empty] | T-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | T-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! | [11 empty] | T-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | T-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0!
|  |  |  | Flow weighted system pressure losses, Lsys (psi) | 18 | [5 empty] | 1991-03-02 | 3:00 | 476.3 | 20 | 89 | 72 | 54 | 0 | 5.4 | 3 | X | 8.4 | 8.4 | 0.64286 | 0 | 9.6 | 10.9625 | 6.0913 | 20.4087 | 0.53715 | [11 empty] | 89 | 85 | 57 | 3.6 | 4.8 | 8.4 | 8.4 | 0.1671 | 0.42857 | 9.6 | 10.9625 | 4.5854 | 25.4146 | 0.43135 | [10 empty] | 85 | 72 | 48 | 1.8 | 3 | 4.8 | 4.8 | 0.19748 | 0.375 | 9.6 | 10.9625 | 6.6275 | 23.8725 | 0.45921 | [10 empty] | Ca-Hdb, mg/L CaCO3 | 25.3333 | NA |  | Ca-Hdb, mg/L CaCO3 | 31.7391 | 15.7739 | [11 empty] | Ca-Hdb, mg/L CaCO3 | 22.2016 | NA |  | Ca-Hdb, mg/L CaCO3 | 29.96 | 14.24 | [11 empty] | Ca-Hdb, mg/L CaCO3 | 26.7785 | NA |  | Ca-Hdb, mg/L CaCO3 | 34.3548 | 21.2903 | [11 empty] | Ca-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | Ca-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! | [11 empty] | Ca-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | Ca-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! | [11 empty] | Ca-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | Ca-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0!
|  |  |  | Required influent pressure to the system, PI (psi) | 139.1392 | [5 empty] | 1991-03-02 | 18:00 | 489.8 | 20 | 90 | 72 | 39.6552 | 0 | 8.7 | 5 |  | 13.7 | 13.7 | 0.63504 | 0 | 15.4667 | 17.6618 | 6.0913 | 35.2535 | 0.501 | [11 empty] | 90 | 82 | 45 | 5.6 | 8.1 | 13.7 | 13.7 | 0.27597 | 0.40876 | 14.9333 | 17.0528 | 4.5854 | 36.4146 | 0.4683 | [10 empty] | 82 | 72 | 30 | 3.1 | 5 | 8.1 | 8.1 | 0.33167 | 0.38272 | 16.5333 | 18.8799 | 6.6275 | 40.3725 | 0.46764 | [10 empty] | Notes: | [17 empty] | Notes: | [17 empty] | Notes: | [17 empty] | Notes: | [17 empty] | Notes: | [17 empty] | Notes:
|  |  |  | 3: The osmotic pressure can be estimated from Table 6-5 in Part 3 of the | [6 empty] | 1991-03-03 | 4:15 | 500 | 21.7 | 91 | 70 | 40.7805 | 0 | 8.2 | 5 |  | 13.2 | 13.2 | 0.62121 | 0 | 14.5778 | 15.831 | 6.0913 | 33.6282 | 0.47076 | [11 empty] | 91 | 85 | 47 | 5.2 | 8 | 13.2 | 13.2 | 0.26837 | 0.39394 | 13.8667 | 15.0587 | 4.5854 | 36.4146 | 0.41354 | [10 empty] | 85 | 70 | 30 | 3 | 5 | 8 | 8 | 0.32914 | 0.375 | 16 | 17.3754 | 6.6275 | 40.8725 | 0.42511 | [10 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be
|  |  |  | "ICR Manual for Bench- and Pilot-Scale Treatment Studies." | [6 empty] | 1991-03-03 | 9:15 | 505 | 21.7 | 92 | 72 | 41.4146 | 0 | 8.2 | 5.1 |  | 13.3 | 13.3 | 0.61654 | 0 | 14.5778 | 15.831 | 6.0913 | 34.494 | 0.45895 | [11 empty] | 92 | 85 | 48 | 5.2 | 8.1 | 13.3 | 13.3 | 0.27091 | 0.39098 | 13.8667 | 15.0587 | 4.5854 | 35.9146 | 0.41929 | [10 empty] | 85 | 72 | 30 | 3 | 5.1 | 8.1 | 8.1 | 0.3342 | 0.37037 | 16 | 17.3754 | 6.6275 | 41.8725 | 0.41496 | [10 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs.
[11 empty] | 1991-03-03 | 19:00 | 504.7 | 21.7 | 90 | 75 | 44.439 | 0 | 8.2 | 5.1 |  | 13.3 | 13.3 | 0.61654 | 0 | 14.5778 | 15.831 | 6.0913 | 31.9696 | 0.49519 | [11 empty] | 90 | 85 | 52 | 5.1 | 8.2 | 13.3 | 13.3 | 0.27217 | 0.38346 | 13.6 | 14.7691 | 4.5854 | 30.9146 | 0.47774 | [10 empty] | 85 | 75 | 32 | 3.1 | 5.1 | 8.2 | 8.2 | 0.33673 | 0.37805 | 16.5333 | 17.9546 | 6.6275 | 41.3725 | 0.43397 | [10 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5.
[11 empty] | 1991-03-04 | 5:00 | 514.8 | 20 | 92 | 75 | 41.9241 | 0 | 7.9 | 5.2 |  | 13.1 | 13.1 | 0.60305 | 0 | 14.0444 | 16.0378 | 6.0913 | 35.4846 | 0.45196 | [11 empty] | 92 | 88 | 48 | 4.9 | 8.2 | 13.1 | 13.1 | 0.26964 | 0.37405 | 13.0667 | 14.9212 | 4.5854 | 37.4146 | 0.39881 | [10 empty] | 88 | 75 | 32 | 3 | 5.2 | 8.2 | 8.2 | 0.33927 | 0.36585 | 16 | 18.2709 | 6.6275 | 42.8725 | 0.42617 | [10 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters.
[11 empty] | 1991-03-04 | 17:15 | 527 | 20 | 92 | 75 | 41.25 | 0 | 8 | 5.2 |  | 13.2 | 13.2 | 0.60606 | 0 | 14.2222 | 16.2408 | 6.0913 | 36.1587 | 0.44915 | [11 empty] | 92 | 88 | 48 | 5 | 8.2 | 13.2 | 13.2 | 0.27091 | 0.37879 | 13.3333 | 15.2257 | 4.5854 | 37.4146 | 0.40695 | [10 empty] | 88 | 75 | 30 | 3 | 5.2 | 8.2 | 8.2 | 0.33927 | 0.36585 | 16 | 18.2709 | 6.6275 | 44.8725 | 0.40717 | [10 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design.
[11 empty] | 1991-03-05 | 6:00 | 539.8 | 18.3 | 92 | 75 | 41.9241 | 0 | 7.9 | 5.2 |  | 13.1 | 13.1 | 0.60305 | 0 | 14.0444 | 16.8642 | 6.0913 | 35.4846 | 0.47526 | [11 empty] | 92 | 87 | 48 | 4.9 | 8.2 | 13.1 | 13.1 | 0.26964 | 0.37405 | 13.0667 | 15.6902 | 4.5854 | 36.9146 | 0.42504 | [10 empty] | 87 | 75 | 32 | 3 | 5.2 | 8.2 | 8.2 | 0.33927 | 0.36585 | 16 | 19.2124 | 6.6275 | 42.3725 | 0.45342 | [10 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[11 empty] | 1991-03-05 | 13:00 | 546.7 | 18.3 | 91 | 74 | 39.4545 | 0 | 7.7 | 5.1 |  | 12.8 | 12.8 | 0.60156 | 0 | 13.6889 | 16.4373 | 6.1422 | 36.9033 | 0.44542 | 7.3 | 3.6 | 120 | 430 | 470 | 860 | 998.4314 | -16.0967 | 74.4681 | 734.2157 | 83.656 | 91 | 84 | 46 | 4.9 | 7.9 | 12.8 | 12.8 | 0.26204 | 0.38281 | 13.0667 | 15.6902 | 4.5854 | 36.9146 | 0.42504 | 7.3 | 3.6 | 120 | 470 | 650 | 687.0886 | -5.7059 | 74.4681 | 578.5443 | 79.2583 | 84 | 74 | 28 | 2.8 | 5.1 | 7.9 | 7.9 | 0.32914 | 0.35443 | 14.9333 | 17.9316 | 6.6275 | 44.3725 | 0.40411 | 3.6 | 3.5 | 130 | 650 | 860 | 935.4902 | -8.7779 | 72.3404 | 792.7451 | 83.6013 | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[11 empty] | 1991-03-05 | 21:00 | 554.8 | 18.3 | 91 | 75 | 38.8182 | 0 | 7.7 | 5.1 |  | 12.8 | 12.8 | 0.60156 | 0 | 13.6889 | 16.4373 | 6.0913 | 38.0905 | 0.43153 | [11 empty] | 91 | 84 | 45 | 4.9 | 7.9 | 12.8 | 12.8 | 0.26204 | 0.38281 | 13.0667 | 15.6902 | 4.5854 | 37.9146 | 0.41383 | [10 empty] | 84 | 75 | 28 | 2.8 | 5.1 | 7.9 | 7.9 | 0.32914 | 0.35443 | 14.9333 | 17.9316 | 6.6275 | 44.8725 | 0.39961 | [10 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio.
[11 empty] | 1991-03-06 | 6:00 | 563.8 | 18.3 | 91 | 75 | 39.4545 | 0 | 7.7 | 5.1 |  | 12.8 | 12.8 | 0.60156 | 0 | 13.6889 | 16.4373 | 6.0913 | 37.4541 | 0.43887 | [11 empty] | 91 | 84 | 46 | 4.9 | 7.9 | 12.8 | 12.8 | 0.26204 | 0.38281 | 13.0667 | 15.6902 | 4.5854 | 36.9146 | 0.42504 | [10 empty] | 84 | 75 | 28 | 2.8 | 5.1 | 7.9 | 7.9 | 0.32914 | 0.35443 | 14.9333 | 17.9316 | 6.6275 | 44.8725 | 0.39961 | [10 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL.
[11 empty] | 1991-03-06 | 14:00 | 571.8 | 18.3 | 95 | 76 | 42.5 | 0 | 8 | 5.1 |  | 13.1 | 13.1 | 0.61069 | 0 | 14.2222 | 17.0777 | 6.0913 | 36.9087 | 0.4627 | [11 empty] | 95 | 89 | 50 | 5 | 8.1 | 13.1 | 13.1 | 0.26837 | 0.38168 | 13.3333 | 16.0104 | 4.5854 | 37.4146 | 0.42792 | [10 empty] | 89 | 76 | 30 | 3 | 5.1 | 8.1 | 8.1 | 0.3342 | 0.37037 | 16 | 19.2124 | 6.6275 | 45.8725 | 0.41882 | [10 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[11 empty] | 1991-03-06 | 21:00 | 578.8 | 18.3 | 90 | 70 | 40.7273 | 0 | 7.7 | 5.1 |  | 12.8 | 12.8 | 0.60156 | 0 | 13.6889 | 16.4373 | 6.0913 | 33.1814 | 0.49538 | [11 empty] | 90 | 84 | 48 | 4.9 | 7.9 | 12.8 | 12.8 | 0.26204 | 0.38281 | 13.0667 | 15.6902 | 4.5854 | 34.4146 | 0.45592 | [10 empty] | 84 | 70 | 28 | 2.8 | 5.1 | 7.9 | 7.9 | 0.32914 | 0.35443 | 14.9333 | 17.9316 | 6.6275 | 42.3725 | 0.42319
[11 empty] | 1991-03-07 | 6:00 | 587.8 | 18.9 | 90 | 76 | 42.8205 | 0 | 7.8 | 5.1 |  | 12.9 | 12.9 | 0.60465 | 0 | 13.8667 | 16.3581 | 6.0913 | 34.0881 | 0.47988 | [11 empty] | 90 | 84 | 50 | 5 | 7.9 | 12.9 | 12.9 | 0.26331 | 0.3876 | 13.3333 | 15.7289 | 4.5854 | 32.4146 | 0.48524 | [10 empty] | 84 | 76 | 30 | 2.8 | 5.1 | 7.9 | 7.9 | 0.32914 | 0.35443 | 14.9333 | 17.6164 | 6.6275 | 43.3725 | 0.40616
[11 empty] | 1991-03-07 | 14:00 | 595.8 | 18.9 | 89 | 70 | 39.16 | 0 | 7.5 | 4.9 |  | 12.4 | 12.4 | 0.60484 | 0 | 13.3333 | 15.7289 | 6.0913 | 34.2487 | 0.45926 | [11 empty] | 89 | 81 | 46 | 4.8 | 7.6 | 12.4 | 12.4 | 0.25318 | 0.3871 | 12.8 | 15.0998 | 4.5854 | 34.4146 | 0.43876 | [10 empty] | 81 | 70 | 27 | 2.7 | 4.9 | 7.6 | 7.6 | 0.31648 | 0.35526 | 14.4 | 16.9872 | 6.6275 | 41.8725 | 0.40569
[11 empty] | 1991-03-08 | 5:00 | 610.8 | 19.4 | 89 | 70 | 38.8 | 0 | 7.5 | 5.1 |  | 12.6 | 12.6 | 0.59524 | 0 | 13.3333 | 15.4982 | 6.0913 | 34.6087 | 0.44781 | [11 empty] | 89 | 81 | 46 | 4.8 | 7.8 | 12.6 | 12.6 | 0.25825 | 0.38095 | 12.8 | 14.8782 | 4.5854 | 34.4146 | 0.43232 | [10 empty] | 81 | 70 | 26 | 2.7 | 5.1 | 7.8 | 7.8 | 0.32661 | 0.34615 | 14.4 | 16.738 | 6.6275 | 42.8725 | 0.39041
[11 empty] | 1991-03-08 | 13:15 | 619 | 19.4 | 89 | 70 | 38.8 | 0 | 7.5 | 5.1 |  | 12.6 | 12.6 | 0.59524 | 0 | 13.3333 | 15.4982 | 6.0913 | 34.6087 | 0.44781 | [11 empty] | 89 | 81 | 46 | 4.8 | 7.8 | 12.6 | 12.6 | 0.25825 | 0.38095 | 12.8 | 14.8782 | 4.5854 | 34.4146 | 0.43232 | [10 empty] | 81 | 70 | 26 | 2.7 | 5.1 | 7.8 | 7.8 | 0.32661 | 0.34615 | 14.4 | 16.738 | 6.6275 | 42.8725 | 0.39041
[11 empty] | 1991-03-08 | 22:00 | 627.7 | 19.4 | 88 | 62 | 38.8 | 0 | 7.5 | 5.1 |  | 12.6 | 12.6 | 0.59524 | 0 | 13.3333 | 15.4982 | 6.0913 | 30.1087 | 0.51474 | [11 empty] | 88 | 79 | 46 | 4.8 | 7.8 | 12.6 | 12.6 | 0.25825 | 0.38095 | 12.8 | 14.8782 | 4.5854 | 32.9146 | 0.45203 | [10 empty] | 79 | 62 | 26 | 2.7 | 5.1 | 7.8 | 7.8 | 0.32661 | 0.34615 | 14.4 | 16.738 | 6.6275 | 37.8725 | 0.44196
[11 empty] | 1991-03-09 | 11:00 | 635.8 | 20.6 | 85 | 63 | 37.1389 | 0 | 7.2 | 4.8 |  | 12 | 12 | 0.6 | 0 | 12.8 | 14.3597 | 6.0913 | 30.7698 | 0.46668 | [11 empty] | 85 | 75 | 44 | 4.6 | 7.4 | 12 | 12 | 0.24559 | 0.38333 | 12.2667 | 13.7614 | 4.5854 | 31.4146 | 0.43806 | [10 empty] | 75 | 63 | 25 | 2.6 | 4.8 | 7.4 | 7.4 | 0.30888 | 0.35135 | 13.8667 | 15.5564 | 6.6275 | 37.3725 | 0.41625
[11 empty] | 1991-03-09 | 21:00 | 643 | 20.6 | 88 | 62 | 37.4167 | 0 | 7.2 | 4.8 |  | 12 | 12 | 0.6 | 0 | 12.8 | 14.3597 | 6.0913 | 31.492 | 0.45598 | [11 empty] | 88 | 78 | 45 | 4.6 | 7.4 | 12 | 12 | 0.24559 | 0.38333 | 12.2667 | 13.7614 | 4.5854 | 33.4146 | 0.41184 | [10 empty] | 78 | 62 | 24 | 2.6 | 4.8 | 7.4 | 7.4 | 0.30888 | 0.35135 | 13.8667 | 15.5564 | 6.6275 | 39.3725 | 0.39511
[11 empty] | 1991-03-10 | 6:00 | 652 | 17.8 | 84 | 62 | 37.8 | 0 | 7.5 | 5.1 |  | 12.6 | 12.6 | 0.59524 | 0 | 13.3333 | 16.2487 | 6.0913 | 29.1087 | 0.55821 | [11 empty] | 84 | 78 | 45 | 4.8 | 7.8 | 12.6 | 12.6 | 0.25825 | 0.38095 | 12.8 | 15.5988 | 4.5854 | 31.4146 | 0.49655 | [10 empty] | 78 | 62 | 25 | 2.7 | 5.1 | 7.8 | 7.8 | 0.32661 | 0.34615 | 14.4 | 17.5486 | 6.6275 | 38.3725 | 0.45732
[11 empty] | 1991-03-10 | 12:15 | 658.2 | 17.8 | 95 | 71 | 41.8519 | 0 | 8.1 | 5.1 |  | 13.2 | 13.2 | 0.61364 | 0 | 14.4 | 17.5486 | 6.0913 | 35.0568 | 0.50058 | [11 empty] | 95 | 81 | 50 | 5.1 | 8.1 | 13.2 | 13.2 | 0.26964 | 0.38636 | 13.6 | 16.5737 | 4.5854 | 33.4146 | 0.496 | [10 empty] | 81 | 71 | 28 | 3 | 5.1 | 8.1 | 8.1 | 0.3342 | 0.37037 | 16 | 19.4985 | 6.6275 | 41.3725 | 0.47129
[11 empty] | 1991-03-10 | 21:00 | 667 | 17.8 | 95 | 71 | 40.8947 | 0 | 7.6 | 5.1 |  | 12.7 | 12.7 | 0.59843 | 0 | 13.5111 | 16.4654 | 6.0913 | 36.0139 | 0.4572 | [11 empty] | 95 | 89 | 49 | 4.8 | 7.9 | 12.7 | 12.7 | 0.26078 | 0.37795 | 12.8 | 15.5988 | 4.5854 | 38.4146 | 0.40606 | [10 empty] | 89 | 71 | 27 | 2.8 | 5.1 | 7.9 | 7.9 | 0.32914 | 0.35443 | 14.9333 | 18.1986 | 6.6275 | 46.3725 | 0.39244
[11 empty] | 1991-03-11 | 6:00 | 676 | 17.2 | 93 | 75 | 40.6316 | 0 | 7.6 | 5.2 |  | 12.8 | 12.8 | 0.59375 | 0 | 13.5111 | 16.76 | 6.0913 | 37.2771 | 0.44961 | [11 empty] | 93 | 88 | 48 | 4.8 | 8 | 12.8 | 12.8 | 0.26331 | 0.375 | 12.8 | 15.8779 | 4.5854 | 37.9146 | 0.41878 | [10 empty] | 88 | 75 | 28 | 2.8 | 5.2 | 8 | 8 | 0.3342 | 0.35 | 14.9333 | 18.5242 | 6.6275 | 46.8725 | 0.3952
[11 empty] | 1991-03-11 | 11:15 | 681.3 | 17.2 | 95 | 77 | 42.2632 | 0 | 7.6 | 5.2 |  | 12.8 | 12.8 | 0.59375 | 0 | 13.5111 | 16.76 | 6.0913 | 37.6455 | 0.44521 | [11 empty] | 95 | 88 | 50 | 4.8 | 8 | 12.8 | 12.8 | 0.26331 | 0.375 | 12.8 | 15.8779 | 4.5854 | 36.9146 | 0.43013 | [10 empty] | 88 | 77 | 29 | 2.8 | 5.2 | 8 | 8 | 0.3342 | 0.35 | 14.9333 | 18.5242 | 6.6275 | 46.8725 | 0.3952
[11 empty] | 1991-03-11 | 22:00 | 692 | 17.2 | 93 | 77 | 41 | 0 | 7.6 | 5.1 |  | 12.7 | 12.7 | 0.59843 | 0 | 13.5111 | 16.76 | 6.0913 | 37.9087 | 0.44212 | [11 empty] | 93 | 88 | 48 | 4.8 | 7.9 | 12.7 | 12.7 | 0.26078 | 0.37795 | 12.8 | 15.8779 | 4.5854 | 37.9146 | 0.41878 | [10 empty] | 88 | 77 | 29 | 2.8 | 5.1 | 7.9 | 7.9 | 0.32914 | 0.35443 | 14.9333 | 18.5242 | 6.6275 | 46.8725 | 0.3952
[11 empty] | 1991-03-12 | 4:00 | 698 | 17.2 | 94 | 75 | 41.2632 | 0 | 7.6 | 5.2 |  | 12.8 | 12.8 | 0.59375 | 0 | 13.5111 | 16.76 | 6.0913 | 37.1455 | 0.4512 | [11 empty] | 94 | 88 | 49 | 4.8 | 8 | 12.8 | 12.8 | 0.26331 | 0.375 | 12.8 | 15.8779 | 4.5854 | 37.4146 | 0.42438 | [10 empty] | 88 | 75 | 28 | 2.8 | 5.2 | 8 | 8 | 0.3342 | 0.35 | 14.9333 | 18.5242 | 6.6275 | 46.8725 | 0.3952
[11 empty] | 1991-03-12 | 22:00 | 716 | 17.2 | 94 | 72 | 42.557 | 0 | 7.9 | 5.2 |  | 13.1 | 13.1 | 0.60305 | 0 | 14.0444 | 17.4216 | 6.0913 | 34.3517 | 0.50715 | [11 empty] | 94 | 88 | 50 | 5.1 | 8 | 13.1 | 13.1 | 0.26711 | 0.38931 | 13.6 | 16.8703 | 4.5854 | 36.4146 | 0.46328 | [10 empty] | 88 | 72 | 29 | 2.8 | 5.2 | 8 | 8 | 0.3342 | 0.35 | 14.9333 | 18.5242 | 6.6275 | 44.3725 | 0.41747
[11 empty] | 1991-03-13 | 3:00 | 721 | 17.2 | 94 | 75 | 41.8947 | 0 | 7.6 | 5.1 |  | 12.7 | 12.7 | 0.59843 | 0 | 13.5111 | 16.76 | 6.0913 | 36.5139 | 0.459 | [11 empty] | 94 | 88 | 50 | 4.8 | 7.9 | 12.7 | 12.7 | 0.26078 | 0.37795 | 12.8 | 15.8779 | 4.5854 | 36.4146 | 0.43603 | [10 empty] | 88 | 75 | 28 | 2.8 | 5.1 | 7.9 | 7.9 | 0.32914 | 0.35443 | 14.9333 | 18.5242 | 6.6275 | 46.8725 | 0.3952
[11 empty] | 1991-03-13 | 21:00 | 739 | 17.2 | 94 | 75 | 42.2025 | 0 | 7.9 | 5.2 |  | 13.1 | 13.1 | 0.60305 | 0 | 14.0444 | 17.4216 | 6.0913 | 36.2061 | 0.48118 | [11 empty] | 94 | 88 | 50 | 5.1 | 8 | 13.1 | 13.1 | 0.26711 | 0.38931 | 13.6 | 16.8703 | 4.5854 | 36.4146 | 0.46328 | [10 empty] | 88 | 75 | 28 | 2.8 | 5.2 | 8 | 8 | 0.3342 | 0.35 | 14.9333 | 18.5242 | 6.6275 | 46.8725 | 0.3952
[11 empty] | 1991-03-14 | 3:00 | 745 | 17.8 | 95 | 73 | 41.2632 | 0 | 7.6 | 5.1 |  | 12.7 | 12.7 | 0.59843 | 0 | 13.5111 | 16.4654 | 6.0913 | 36.6455 | 0.44932 | [11 empty] | 95 | 85 | 49 | 4.8 | 7.9 | 12.7 | 12.7 | 0.26078 | 0.37795 | 12.8 | 15.5988 | 4.5854 | 36.4146 | 0.42837 | [10 empty] | 85 | 73 | 28 | 2.8 | 5.1 | 7.9 | 7.9 | 0.32914 | 0.35443 | 14.9333 | 18.1986 | 6.6275 | 44.3725 | 0.41013
[11 empty] | 1991-03-14 | 11:00 | 747 | 17.8 | 93 | 72 | 41.2632 | 0 | 7.6 | 5 | X | 12.6 | 12.6 | 0.60317 | 0 | 13.5111 | 16.4654 | 6.0913 | 35.1455 | 0.46849 | [11 empty] | 93 | 84 | 49 | 4.8 | 7.8 | 12.6 | 12.6 | 0.25825 | 0.38095 | 12.8 | 15.5988 | 4.5854 | 34.9146 | 0.44677 | [10 empty] | 84 | 72 | 28 | 2.8 | 5 | 7.8 | 7.8 | 0.32407 | 0.35897 | 14.9333 | 18.1986 | 6.6275 | 43.3725 | 0.41959
[11 empty] | 1991-03-14 | 17:00 | 753 | 17.8 | 94 | 77 | 37.2989 | 0 | 8.7 | 5 |  | 13.7 | 13.7 | 0.63504 | 0 | 15.4667 | 18.8485 | 6.0913 | 42.1098 | 0.4476 | [11 empty] | 94 | 88 | 43 | 5.6 | 8.1 | 13.7 | 13.7 | 0.27597 | 0.40876 | 14.9333 | 18.1986 | 4.5854 | 43.4146 | 0.41918 | [10 empty] | 88 | 77 | 27 | 3.1 | 5 | 8.1 | 8.1 | 0.33167 | 0.38272 | 16.5333 | 20.1484 | 6.6275 | 48.8725 | 0.41226
[11 empty] | 1991-03-15 | 4:00 | 764 | 18.9 | 99 | 79 | 40.0488 | 0 | 8.2 | 5.1 |  | 13.3 | 13.3 | 0.61654 | 0 | 14.5778 | 17.1969 | 6.0913 | 42.8599 | 0.40124 | [11 empty] | 99 | 90 | 47 | 5.2 | 8.1 | 13.3 | 13.3 | 0.27091 | 0.39098 | 13.8667 | 16.3581 | 4.5854 | 42.9146 | 0.38118 | [10 empty] | 90 | 79 | 28 | 3 | 5.1 | 8.1 | 8.1 | 0.3342 | 0.37037 | 16 | 18.8747 | 6.6275 | 49.8725 | 0.37846
[11 empty] | 1991-03-15 | 13:35 | 773.6 | 18.9 | 95 | 79 | 40.5301 | 0 | 8.3 | 5.1 |  | 13.4 | 13.4 | 0.6194 | 0 | 14.7556 | 17.4067 | 6.0913 | 40.3785 | 0.43109 | [11 empty] | 95 | 90 | 48 | 5.2 | 8.2 | 13.4 | 13.4 | 0.27344 | 0.38806 | 13.8667 | 16.3581 | 4.5854 | 39.9146 | 0.40983 | [10 empty] | 90 | 79 | 28 | 3.1 | 5.1 | 8.2 | 8.2 | 0.33673 | 0.37805 | 16.5333 | 19.5039 | 6.6275 | 49.8725 | 0.39107
[11 empty] | 1991-03-15 | 22:00 | 782 | 18.9 | 94 | 79 | 39.5301 | 0 | 8.3 | 5.1 |  | 13.4 | 13.4 | 0.6194 | 0 | 14.7556 | 17.4067 | 6.0913 | 40.8785 | 0.42581 | [11 empty] | 94 | 90 | 47 | 5.2 | 8.2 | 13.4 | 13.4 | 0.27344 | 0.38806 | 13.8667 | 16.3581 | 4.5854 | 40.4146 | 0.40476 | [10 empty] | 90 | 79 | 27 | 3.1 | 5.1 | 8.2 | 8.2 | 0.33673 | 0.37805 | 16.5333 | 19.5039 | 6.6275 | 50.8725 | 0.38339
[11 empty] | 1991-03-16 | 6:00 | 790 | 17.8 | 100 | 79 | 41.7831 | 0 | 8.3 | 5 |  | 13.3 | 13.3 | 0.62406 | 0 | 14.7556 | 17.9819 | 6.0913 | 41.6255 | 0.43199 | [11 empty] | 100 | 91 | 50 | 5.2 | 8.1 | 13.3 | 13.3 | 0.27091 | 0.39098 | 13.8667 | 16.8987 | 4.5854 | 40.9146 | 0.41302 | [10 empty] | 91 | 79 | 28 | 3.1 | 5 | 8.1 | 8.1 | 0.33167 | 0.38272 | 16.5333 | 20.1484 | 6.6275 | 50.3725 | 0.39999
[11 empty] | 1991-03-16 | 10:30 | 818 | 17.8 | 95 | 79 | 41.4096 | 0 | 8.3 | 5.1 |  | 13.4 | 13.4 | 0.6194 | 0 | 14.7556 | 17.9819 | 6.0913 | 39.499 | 0.45525 | [11 empty] | 95 | 90 | 50 | 5.2 | 8.2 | 13.4 | 13.4 | 0.27344 | 0.38806 | 13.8667 | 16.8987 | 4.5854 | 37.9146 | 0.4457 | [10 empty] | 90 | 79 | 27 | 3.1 | 5.1 | 8.2 | 8.2 | 0.33673 | 0.37805 | 16.5333 | 20.1484 | 6.6275 | 50.8725 | 0.39606
[11 empty] | 1991-03-16 | 16:00 | 799.5 | 17.8 | 95 | 80 | 42.619 | 0 | 8.4 | 5.2 |  | 13.6 | 13.6 | 0.61765 | 0 | 14.9333 | 18.1986 | 6.0913 | 38.7896 | 0.46916 | [11 empty] | 95 | 90 | 51 | 5.2 | 8.4 | 13.6 | 13.6 | 0.2785 | 0.38235 | 13.8667 | 16.8987 | 4.5854 | 36.9146 | 0.45778 | [10 empty] | 90 | 80 | 29 | 3.2 | 5.2 | 8.4 | 8.4 | 0.34433 | 0.38095 | 17.0667 | 20.7984 | 6.6275 | 49.3725 | 0.42125
[11 empty] | 1991-03-16 | 22:00 | 805.5 | 17.8 | 95 | 79 | 41.7831 | 0 | 8.3 | 5.1 |  | 13.4 | 13.4 | 0.6194 | 0 | 14.7556 | 17.9819 | 6.0913 | 39.1255 | 0.4596 | [11 empty] | 95 | 90 | 50 | 5.2 | 8.2 | 13.4 | 13.4 | 0.27344 | 0.38806 | 13.8667 | 16.8987 | 4.5854 | 37.9146 | 0.4457 | [10 empty] | 90 | 79 | 28 | 3.1 | 5.1 | 8.2 | 8.2 | 0.33673 | 0.37805 | 16.5333 | 20.1484 | 6.6275 | 49.8725 | 0.404
[11 empty] | 1991-03-17 | 5:15 | 812.8 | 17.8 | 98 | 78 | 40.9036 | 0 | 8.3 | 5.3 |  | 13.6 | 13.6 | 0.61029 | 0 | 14.7556 | 17.9819 | 6.0913 | 41.005 | 0.43853 | [11 empty] | 98 | 90 | 49 | 5.1 | 8.5 | 13.6 | 13.6 | 0.27977 | 0.375 | 13.6 | 16.5737 | 4.5854 | 40.4146 | 0.41009 | [10 empty] | 90 | 78 | 28 | 3.2 | 5.3 | 8.5 | 8.5 | 0.34939 | 0.37647 | 17.0667 | 20.7984 | 6.6275 | 49.3725 | 0.42125
[11 empty] | 1991-03-17 | 11:35 | 819.1 | 17.8 | 99 | 78 | 41.061 | 0 | 8.2 | 5.2 |  | 13.4 | 13.4 | 0.61194 | 0 | 14.5778 | 17.7653 | 6.0913 | 41.3477 | 0.42966 | [11 empty] | 99 | 90 | 49 | 5.1 | 8.3 | 13.4 | 13.4 | 0.2747 | 0.3806 | 13.6 | 16.5737 | 4.5854 | 40.9146 | 0.40508 | [10 empty] | 90 | 78 | 28 | 3.1 | 5.2 | 8.3 | 8.3 | 0.3418 | 0.37349 | 16.5333 | 20.1484 | 6.6275 | 49.3725 | 0.40809
[11 empty] | 1991-03-17 | 21:00 | 828.5 | 17.8 | 98 | 78 | 41.061 | 0 | 8.2 | 5.1 |  | 13.3 | 13.3 | 0.61654 | 0 | 14.5778 | 17.7653 | 6.0913 | 40.8477 | 0.43492 | [11 empty] | 98 | 90 | 49 | 5.1 | 8.2 | 13.3 | 13.3 | 0.27217 | 0.38346 | 13.6 | 16.5737 | 4.5854 | 40.4146 | 0.41009 | [10 empty] | 90 | 78 | 28 | 3.1 | 5.1 | 8.2 | 8.2 | 0.33673 | 0.37805 | 16.5333 | 20.1484 | 6.6275 | 49.3725 | 0.40809
[11 empty] | 1991-03-18 | 8:15 | 839.8 | 18.9 | 98 | 78 | 41.061 | 0 | 8.2 | 5.2 |  | 13.4 | 13.4 | 0.61194 | 0 | 14.5778 | 17.1969 | 6.0913 | 40.8477 | 0.421 | [11 empty] | 98 | 90 | 49 | 5.1 | 8.3 | 13.4 | 13.4 | 0.2747 | 0.3806 | 13.6 | 16.0435 | 4.5854 | 40.4146 | 0.39697 | [10 empty] | 90 | 78 | 28 | 3.1 | 5.2 | 8.3 | 8.3 | 0.3418 | 0.37349 | 16.5333 | 19.5039 | 6.6275 | 49.3725 | 0.39503
[11 empty] | 1991-03-18 | 11:00 | 842.5 | 18.9 | 100 | 80 | 41.6829 | 0 | 8.2 | 5.1 |  | 13.3 | 13.3 | 0.61654 | 0 | 14.5778 | 17.1969 | 6.0913 | 42.2257 | 0.40726 | [11 empty] | 100 | 90 | 50 | 5.1 | 8.2 | 13.3 | 13.3 | 0.27217 | 0.38346 | 13.6 | 16.0435 | 4.5854 | 40.4146 | 0.39697 | [10 empty] | 90 | 80 | 28 | 3.1 | 5.1 | 8.2 | 8.2 | 0.33673 | 0.37805 | 16.5333 | 19.5039 | 6.6275 | 50.3725 | 0.38719
[11 empty] | 1991-03-18 | 21:00 | 852.5 | 18.9 | 100 | 78 | 41.6829 | 0 | 8.2 | 5.1 |  | 13.3 | 13.3 | 0.61654 | 0 | 14.5778 | 17.1969 | 6.0913 | 41.2257 | 0.41714 | [11 empty] | 100 | 90 | 50 | 5.1 | 8.2 | 13.3 | 13.3 | 0.27217 | 0.38346 | 13.6 | 16.0435 | 4.5854 | 40.4146 | 0.39697 | [10 empty] | 90 | 78 | 28 | 3.1 | 5.1 | 8.2 | 8.2 | 0.33673 | 0.37805 | 16.5333 | 19.5039 | 6.6275 | 49.3725 | 0.39503
[11 empty] | 1991-03-19 | 6:00 | 861.5 | 20 | 100 | 77 | 41.6829 | 0 | 8.2 | 5.1 |  | 13.3 | 13.3 | 0.61654 | 0 | 14.5778 | 16.6468 | 6.0913 | 40.7257 | 0.40875 | [11 empty] | 100 | 90 | 50 | 5.1 | 8.2 | 13.3 | 13.3 | 0.27217 | 0.38346 | 13.6 | 15.5302 | 4.5854 | 40.4146 | 0.38427 | [10 empty] | 90 | 77 | 28 | 3.1 | 5.1 | 8.2 | 8.2 | 0.33673 | 0.37805 | 16.5333 | 18.8799 | 6.6275 | 48.8725 | 0.38631
[11 empty] | 1991-03-19 | 11:00 | 866.5 | 20 | 100 | 77 | 41.6829 | 0 | 8.2 | 5.1 |  | 13.3 | 13.3 | 0.61654 | 0 | 14.5778 | 16.6468 | 6.0913 | 40.7257 | 0.40875 | [11 empty] | 100 | 90 | 50 | 5.1 | 8.2 | 13.3 | 13.3 | 0.27217 | 0.38346 | 13.6 | 15.5302 | 4.5854 | 40.4146 | 0.38427 | [10 empty] | 90 | 77 | 28 | 3.1 | 5.1 | 8.2 | 8.2 | 0.33673 | 0.37805 | 16.5333 | 18.8799 | 6.6275 | 48.8725 | 0.38631
[11 empty] | 1991-03-19 | 18:00 | 872.5 | 20 | 95 | 77 | 42.1975 | 0 | 8.1 | 5 |  | 13.1 | 13.1 | 0.61832 | 0 | 14.4 | 16.4438 | 6.0913 | 37.7111 | 0.43605 | [11 empty] | 95 | 88 | 51 | 5 | 8.1 | 13.1 | 13.1 | 0.26837 | 0.38168 | 13.3333 | 15.2257 | 4.5854 | 35.9146 | 0.42394 | [10 empty] | 88 | 77 | 28 | 3.1 | 5 | 8.1 | 8.1 | 0.33167 | 0.38272 | 16.5333 | 18.8799 | 6.6275 | 47.8725 | 0.39438
[11 empty] | 1991-03-20 | 12:00 | 876.5 | 20 | 95 | 80 | 43.5181 | 0 | 8.3 | 5.2 |  | 13.5 | 13.5 | 0.61481 | 0 | 14.7556 | 16.8498 | 6.0913 | 37.8906 | 0.4447 | [11 empty] | 95 | 89 | 52 | 5.1 | 8.4 | 13.5 | 13.5 | 0.27724 | 0.37778 | 13.6 | 15.5302 | 4.5854 | 35.4146 | 0.43853 | [10 empty] | 89 | 80 | 30 | 3.2 | 5.2 | 8.4 | 8.4 | 0.34433 | 0.38095 | 17.0667 | 19.4889 | 6.6275 | 47.8725 | 0.4071
[11 empty] | 1991-03-20 | 18:00 | 882.5 | 20 | 95 | 79 | 43.5181 | 0 | 8.3 | 5.1 |  | 13.4 | 13.4 | 0.6194 | 0 | 14.7556 | 16.8498 | 6.0913 | 37.3906 | 0.45064 | [11 empty] | 95 | 89 | 52 | 5.1 | 8.3 | 13.4 | 13.4 | 0.2747 | 0.3806 | 13.6 | 15.5302 | 4.5854 | 35.4146 | 0.43853 | [10 empty] | 89 | 79 | 30 | 3.2 | 5.1 | 8.3 | 8.3 | 0.33927 | 0.38554 | 17.0667 | 19.4889 | 6.6275 | 47.3725 | 0.4114
[11 empty] | 1991-03-21 | 5:00 | 893.5 | 21.7 | 95 | 79 | 43.5181 | 0 | 8.3 | 5.2 |  | 13.5 | 13.5 | 0.61481 | 0 | 14.7556 | 16.024 | 6.0913 | 37.3906 | 0.42856 | [11 empty] | 95 | 89 | 52 | 5.1 | 8.4 | 13.5 | 13.5 | 0.27724 | 0.37778 | 13.6 | 14.7691 | 4.5854 | 35.4146 | 0.41704 | [10 empty] | 89 | 79 | 30 | 3.2 | 5.2 | 8.4 | 8.4 | 0.34433 | 0.38095 | 17.0667 | 18.5338 | 6.6275 | 47.3725 | 0.39124
[11 empty] | 1991-03-21 | 10:00 | 898.5 | 21.7 | 95 | 79 | 43.5181 | 0 | 8.3 | 5.1 |  | 13.4 | 13.4 | 0.6194 | 0 | 14.7556 | 16.024 | 6.0913 | 37.3906 | 0.42856 | [11 empty] | 95 | 89 | 52 | 5.1 | 8.3 | 13.4 | 13.4 | 0.2747 | 0.3806 | 13.6 | 14.7691 | 4.5854 | 35.4146 | 0.41704 | [10 empty] | 89 | 79 | 30 | 3.2 | 5.1 | 8.3 | 8.3 | 0.33927 | 0.38554 | 17.0667 | 18.5338 | 6.6275 | 47.3725 | 0.39124
[11 empty] | 1991-03-21 | 22:00 | 910.5 | 21.7 | 90 | 72 | 41.475 | 0 | 8 | 5 |  | 13 | 13 | 0.61538 | 0 | 14.2222 | 15.4448 | 6.0913 | 33.4337 | 0.46195 | [11 empty] | 90 | 85 | 50 | 4.9 | 8.1 | 13 | 13 | 0.26711 | 0.37692 | 13.0667 | 14.1899 | 4.5854 | 32.9146 | 0.43111 | [10 empty] | 85 | 72 | 28 | 3.1 | 5 | 8.1 | 8.1 | 0.33167 | 0.38272 | 16.5333 | 17.9546 | 6.6275 | 43.8725 | 0.40925
[11 empty] | 1991-03-22 | 3:00 | 915.5 | 21.7 | 95 | 72 | 41.3086 | 0 | 8.1 | 5.1 |  | 13.2 | 13.2 | 0.61364 | 0 | 14.4 | 15.6379 | 6.0913 | 36.1 | 0.43318 | [11 empty] | 95 | 89 | 50 | 4.9 | 8.3 | 13.2 | 13.2 | 0.27217 | 0.37121 | 13.0667 | 14.1899 | 4.5854 | 37.4146 | 0.37926 | [10 empty] | 89 | 72 | 28 | 3.2 | 5.1 | 8.3 | 8.3 | 0.33927 | 0.38554 | 17.0667 | 18.5338 | 6.6275 | 45.8725 | 0.40403
[11 empty] | 1991-03-22 | 18:00 | 930.5 | 21.7 | 95 | 78 | 42.439 | 0 | 8.2 | 5 |  | 13.2 | 13.2 | 0.62121 | 0 | 14.5778 | 15.831 | 6.0913 | 37.9696 | 0.41694 | [11 empty] | 95 | 89 | 50 | 5.1 | 8.1 | 13.2 | 13.2 | 0.26964 | 0.38636 | 13.6 | 14.7691 | 4.5854 | 37.4146 | 0.39474 | [10 empty] | 89 | 78 | 30 | 3.1 | 5 | 8.1 | 8.1 | 0.33167 | 0.38272 | 16.5333 | 17.9546 | 6.6275 | 46.8725 | 0.38305
[11 empty] | 1991-03-23 | 6:00 | 942.5 | 23.3 | 100 | 75 | 44.1325 | 0 | 8.3 | 5.1 |  | 13.4 | 13.4 | 0.6194 | 0 | 14.7556 | 15.2838 | 6.0913 | 37.2761 | 0.41002 | [11 empty] | 100 | 91 | 53 | 5.1 | 8.3 | 13.4 | 13.4 | 0.2747 | 0.3806 | 13.6 | 14.0869 | 4.5854 | 37.9146 | 0.37154 | [10 empty] | 91 | 75 | 30 | 3.2 | 5.1 | 8.3 | 8.3 | 0.33927 | 0.38554 | 17.0667 | 17.6777 | 6.6275 | 46.3725 | 0.38121
[11 empty] | 1991-03-23 | 11:00 | 947.5 | 23.3 | 98 | 77 | 43.747 | 0 | 8.3 | 5.1 |  | 13.4 | 13.4 | 0.6194 | 0 | 14.7556 | 15.2838 | 6.0913 | 37.6617 | 0.40582 | [11 empty] | 98 | 90 | 53 | 5.1 | 8.3 | 13.4 | 13.4 | 0.2747 | 0.3806 | 13.6 | 14.0869 | 4.5854 | 36.4146 | 0.38685 | [10 empty] | 90 | 77 | 29 | 3.2 | 5.1 | 8.3 | 8.3 | 0.33927 | 0.38554 | 17.0667 | 17.6777 | 6.6275 | 47.8725 | 0.36927
[11 empty] | 1991-03-23 | 22:00 | 958.5 | 23.3 | 97 | 76 | 44.1325 | 0 | 8.3 | 5 |  | 13.3 | 13.3 | 0.62406 | 0 | 14.7556 | 15.2838 | 6.0913 | 36.2761 | 0.42132 | [11 empty] | 97 | 90 | 53 | 5.1 | 8.2 | 13.3 | 13.3 | 0.27217 | 0.38346 | 13.6 | 14.0869 | 4.5854 | 35.9146 | 0.39223 | [10 empty] | 90 | 76 | 30 | 3.2 | 5 | 8.2 | 8.2 | 0.3342 | 0.39024 | 17.0667 | 17.6777 | 6.6275 | 46.3725 | 0.38121
[11 empty] | 1991-03-24 | 5:00 | 965.5 | 22.8 | 98 | 76 | 44.1325 | 0 | 8.3 | 5 |  | 13.3 | 13.3 | 0.62406 | 0 | 14.7556 | 15.5114 | 6.0913 | 36.7761 | 0.42178 | [11 empty] | 98 | 90 | 53 | 5.1 | 8.2 | 13.3 | 13.3 | 0.27217 | 0.38346 | 13.6 | 14.2966 | 4.5854 | 36.4146 | 0.39261 | [10 empty] | 90 | 76 | 30 | 3.2 | 5 | 8.2 | 8.2 | 0.3342 | 0.39024 | 17.0667 | 17.9409 | 6.6275 | 46.3725 | 0.38689
[11 empty] | 1991-03-24 | 13:30 | 974 | 22.8 | 98 | 75 | 44.747 | 0 | 8.3 | 5.3 |  | 13.6 | 13.6 | 0.61029 | 0 | 14.7556 | 15.5114 | 6.0913 | 35.6617 | 0.43496 | [11 empty] | 98 | 90 | 54 | 5.1 | 8.5 | 13.6 | 13.6 | 0.27977 | 0.375 | 13.6 | 14.2966 | 4.5854 | 35.4146 | 0.40369 | [10 empty] | 90 | 75 | 30 | 3.2 | 5.3 | 8.5 | 8.5 | 0.34939 | 0.37647 | 17.0667 | 17.9409 | 6.6275 | 45.8725 | 0.3911
[11 empty] | 1991-03-24 | 20:00 | 980.5 | 22.8 | 95 | 75 | 43.747 | 0 | 8.3 | 5.1 |  | 13.4 | 13.4 | 0.6194 | 0 | 14.7556 | 15.5114 | 6.0913 | 35.1617 | 0.44114 | [11 empty] | 95 | 88 | 53 | 5.1 | 8.3 | 13.4 | 13.4 | 0.2747 | 0.3806 | 13.6 | 14.2966 | 4.5854 | 33.9146 | 0.42155 | [10 empty] | 88 | 75 | 29 | 3.2 | 5.1 | 8.3 | 8.3 | 0.33927 | 0.38554 | 17.0667 | 17.9409 | 6.6275 | 45.8725 | 0.3911
[11 empty] | 1991-03-25 | 7:00 | 991.5 | 23.9 | 98 | 75 | 43.1325 | 0 | 8.3 | 5.3 |  | 13.6 | 13.6 | 0.61029 | 0 | 14.7556 | 15.0151 | 6.0913 | 37.2761 | 0.40281 | [11 empty] | 98 | 89 | 52 | 5.1 | 8.5 | 13.6 | 13.6 | 0.27977 | 0.375 | 13.6 | 13.8393 | 4.5854 | 36.9146 | 0.3749 | [10 empty] | 89 | 75 | 29 | 3.2 | 5.3 | 8.5 | 8.5 | 0.34939 | 0.37647 | 17.0667 | 17.3669 | 6.6275 | 46.3725 | 0.37451
[11 empty] | 1991-03-25 | 11:00 | 995.5 | 23.9 | 97 | 75 | 42.5185 | 0 | 8.1 | 5.2 |  | 13.3 | 13.3 | 0.60902 | 0 | 14.4 | 14.6533 | 6.0913 | 37.3901 | 0.3919 | [11 empty] | 97 | 89 | 52 | 4.9 | 8.4 | 13.3 | 13.3 | 0.2747 | 0.36842 | 13.0667 | 13.2965 | 4.5854 | 36.4146 | 0.36514 | [10 empty] | 89 | 75 | 28 | 3.2 | 5.2 | 8.4 | 8.4 | 0.34433 | 0.38095 | 17.0667 | 17.3669 | 6.6275 | 47.3725 | 0.3666
[11 empty] | 1991-03-25 | 18:00 | 1001.3 | 23.9 | 96 | 77 | 44.6341 | 0 | 8.2 | 5.2 |  | 13.4 | 13.4 | 0.61194 | 0 | 14.5778 | 14.8342 | 6.0913 | 35.7745 | 0.41466 | [11 empty] | 96 | 89 | 54 | 5 | 8.4 | 13.4 | 13.4 | 0.27597 | 0.37313 | 13.3333 | 13.5679 | 4.5854 | 33.9146 | 0.40006 | [10 empty] | 89 | 77 | 30 | 3.2 | 5.2 | 8.4 | 8.4 | 0.34433 | 0.38095 | 17.0667 | 17.3669 | 6.6275 | 46.3725 | 0.37451
[11 empty] | 1991-03-26 | 4:15 | 1011.5 | 22.2 | 98 | 77 | 43.7 | 0 | 8 | 5.1 |  | 13.1 | 13.1 | 0.61069 | 0 | 14.2222 | 15.2182 | 6.0913 | 37.7087 | 0.40357 | [11 empty] | 98 | 90 | 53 | 4.9 | 8.2 | 13.1 | 13.1 | 0.26964 | 0.37405 | 13.0667 | 13.9818 | 4.5854 | 36.4146 | 0.38396 | [10 empty] | 90 | 77 | 29 | 3.1 | 5.1 | 8.2 | 8.2 | 0.33673 | 0.37805 | 16.5333 | 17.6912 | 6.6275 | 47.8725 | 0.36955
[11 empty] | 1991-03-26 | 9:30 | 1016.8 | 22.2 | 95 | 75 | 43.0244 | 0 | 8.2 | 5.1 |  | 13.3 | 13.3 | 0.61654 | 0 | 14.5778 | 15.5987 | 6.0913 | 35.8843 | 0.43469 | [11 empty] | 95 | 85 | 52 | 5 | 8.3 | 13.3 | 13.3 | 0.27344 | 0.37594 | 13.3333 | 14.2671 | 4.5854 | 33.4146 | 0.42697 | [10 empty] | 85 | 75 | 29 | 3.2 | 5.1 | 8.3 | 8.3 | 0.33927 | 0.38554 | 17.0667 | 18.2619 | 6.6275 | 44.3725 | 0.41156
[11 empty] | 1991-03-26 | 19:00 | 1025.2 | 22.2 | 90 | 72 | 42.9136 | 0 | 8.1 | 5.1 |  | 13.2 | 13.2 | 0.61364 | 0 | 14.4 | 15.4085 | 6.0913 | 31.9951 | 0.48159 | [11 empty] | 90 | 84 | 52 | 4.9 | 8.3 | 13.2 | 13.2 | 0.27217 | 0.37121 | 13.0667 | 13.9818 | 4.5854 | 30.4146 | 0.45971 | [10 empty] | 84 | 72 | 29 | 3.2 | 5.1 | 8.3 | 8.3 | 0.33927 | 0.38554 | 17.0667 | 18.2619 | 6.6275 | 42.3725 | 0.43098
[11 empty] | 1991-03-27 | 3:00 | 1033.3 | 22.8 | 97 | 75 | 43.7 | 0 | 8 | 5.1 |  | 13.1 | 13.1 | 0.61069 | 0 | 14.2222 | 14.9507 | 6.0913 | 36.2087 | 0.4129 | [11 empty] | 97 | 89 | 53 | 4.9 | 8.2 | 13.1 | 13.1 | 0.26964 | 0.37405 | 13.0667 | 13.736 | 4.5854 | 35.4146 | 0.38786 | [10 empty] | 89 | 75 | 29 | 3.1 | 5.1 | 8.2 | 8.2 | 0.33673 | 0.37805 | 16.5333 | 17.3802 | 6.6275 | 46.3725 | 0.3748
[11 empty] | 1991-03-27 | 11:00 | 1041.3 | 22.8 | 94 | 74 | 43.3614 | 0 | 8.3 | 5.1 |  | 13.4 | 13.4 | 0.6194 | 0 | 14.7556 | 15.5114 | 6.0913 | 34.5472 | 0.44899 | [11 empty] | 94 | 89 | 53 | 5.1 | 8.3 | 13.4 | 13.4 | 0.2747 | 0.3806 | 13.6 | 14.2966 | 4.5854 | 33.9146 | 0.42155 | [10 empty] | 89 | 74 | 28 | 3.2 | 5.1 | 8.3 | 8.3 | 0.33927 | 0.38554 | 17.0667 | 17.9409 | 6.6275 | 46.8725 | 0.38276
[11 empty] | 1991-03-27 | 19:00 | 1049.2 | 22.8 | 95 | 73 | 43.5185 | 0 | 8.1 | 5.1 |  | 13.2 | 13.2 | 0.61364 | 0 | 14.4 | 15.1376 | 6.0913 | 34.3901 | 0.44017 | [11 empty] | 95 | 86 | 53 | 4.9 | 8.3 | 13.2 | 13.2 | 0.27217 | 0.37121 | 13.0667 | 13.736 | 4.5854 | 32.9146 | 0.41732 | [10 empty] | 86 | 73 | 29 | 3.2 | 5.1 | 8.3 | 8.3 | 0.33927 | 0.38554 | 17.0667 | 17.9409 | 6.6275 | 43.8725 | 0.40893
[11 empty] | 1991-03-28 | 3:00 | 1057.3 | 23.9 | 95 | 73 | 43.747 | 0 | 8.3 | 5.1 |  | 13.4 | 13.4 | 0.6194 | 0 | 14.7556 | 15.0151 | 6.0913 | 34.1617 | 0.43953 | [11 empty] | 95 | 89 | 53 | 5.1 | 8.3 | 13.4 | 13.4 | 0.2747 | 0.3806 | 13.6 | 13.8393 | 4.5854 | 34.4146 | 0.40213 | [10 empty] | 89 | 73 | 29 | 3.2 | 5.1 | 8.3 | 8.3 | 0.33927 | 0.38554 | 17.0667 | 17.3669 | 6.6275 | 45.3725 | 0.38276
[11 empty] | 1991-03-28 | 11:00 | 1065.3 | 23.9 | 95 | 75 | 42.5185 | 0 | 8.1 | 5.1 |  | 13.2 | 13.2 | 0.61364 | 0 | 14.4 | 14.6533 | 6.0913 | 36.3901 | 0.40267 | [11 empty] | 95 | 88 | 52 | 4.9 | 8.3 | 13.2 | 13.2 | 0.27217 | 0.37121 | 13.0667 | 13.2965 | 4.5854 | 34.9146 | 0.38083 | [10 empty] | 88 | 75 | 28 | 3.2 | 5.1 | 8.3 | 8.3 | 0.33927 | 0.38554 | 17.0667 | 17.3669 | 6.6275 | 46.8725 | 0.37051
[11 empty] | 1991-03-28 | 4:45 | 1059 | 23.9 | 99 | 80 | 46.0244 | 0 | 8.2 | 5.1 |  | 13.3 | 13.3 | 0.61654 | 0 | 14.5778 | 14.8342 | 6.0913 | 37.3843 | 0.3968 | [11 empty] | 99 | 90 | 55 | 5 | 8.3 | 13.3 | 13.3 | 0.27344 | 0.37594 | 13.3333 | 13.5679 | 4.5854 | 34.9146 | 0.3886 | [10 empty] | 90 | 80 | 32 | 3.2 | 5.1 | 8.3 | 8.3 | 0.33927 | 0.38554 | 17.0667 | 17.3669 | 6.6275 | 46.3725 | 0.37451
[11 empty] | 1991-03-29 | 3:00 | 1081.3 | 25 | 98 | 76 | 44.1235 | 0 | 8.1 | 5.1 |  | 13.2 | 13.2 | 0.61364 | 0 | 14.4 | 14.1845 | 6.0913 | 36.7852 | 0.3856 | [11 empty] | 98 | 90 | 54 | 4.9 | 8.3 | 13.2 | 13.2 | 0.27217 | 0.37121 | 13.0667 | 12.8712 | 4.5854 | 35.4146 | 0.36344 | [10 empty] | 90 | 76 | 29 | 3.2 | 5.1 | 8.3 | 8.3 | 0.33927 | 0.38554 | 17.0667 | 16.8113 | 6.6275 | 47.3725 | 0.35487
[11 empty] | 1991-03-29 | 15:00 | 1081.3 | 25 | 95 | 75 | 45.6627 | 0 | 8.3 | 5.1 |  | 13.4 | 13.4 | 0.6194 | 0 | 14.7556 | 14.5348 | 6.0913 | 33.246 | 0.43719 | [11 empty] | 95 | 89 | 56 | 5 | 8.4 | 13.4 | 13.4 | 0.27597 | 0.37313 | 13.3333 | 13.1338 | 4.5854 | 31.4146 | 0.41808 | [10 empty] | 89 | 75 | 30 | 3.3 | 5.1 | 8.4 | 8.4 | 0.3418 | 0.39286 | 17.6 | 17.3367 | 6.6275 | 45.3725 | 0.3821
[11 empty] | 1991-03-29 | 22:00 | 1088.2 | 25 | 97 | 78 | 46.5366 | 0 | 8.2 | 5.1 |  | 13.3 | 13.3 | 0.61654 | 0 | 14.5778 | 14.3597 | 6.0913 | 34.8721 | 0.41178 | [11 empty] | 97 | 90 | 57 | 4.9 | 8.4 | 13.3 | 13.3 | 0.2747 | 0.36842 | 13.0667 | 12.8712 | 4.5854 | 31.9146 | 0.4033 | [10 empty] | 90 | 78 | 31 | 3.3 | 5.1 | 8.4 | 8.4 | 0.3418 | 0.39286 | 17.6 | 17.3367 | 6.6275 | 46.3725 | 0.37386
[11 empty] | 1991-03-30 | 3:00 | 1093.3 | 24.4 | 99 | 80 | 47.2439 | 0 | 8.2 | 5.1 |  | 13.3 | 13.3 | 0.61654 | 0 | 14.5778 | 14.6166 | 6.0913 | 36.1648 | 0.40417 | [11 empty] | 99 | 91 | 57 | 5 | 8.3 | 13.3 | 13.3 | 0.27344 | 0.37594 | 13.3333 | 13.3689 | 4.5854 | 33.4146 | 0.40009 | [10 empty] | 91 | 80 | 32 | 3.2 | 5.1 | 8.3 | 8.3 | 0.33927 | 0.38554 | 17.0667 | 17.1121 | 6.6275 | 46.8725 | 0.36508
[11 empty] | 1991-03-30 | 12:00 | 1093.3 | 24.4 | 73 | 50 | 38.5846 | 0 | 6.5 | 7.4 | X | 13.9 | 13.9 | 0.46763 | 0 | 11.5556 | 11.5863 | 6.0913 | 16.824 | 0.68868 | [11 empty] | 73 | 66 | 44 | 4.3 | 9.6 | 13.9 | 13.9 | 0.29749 | 0.30935 | 11.4667 | 11.4972 | 4.5854 | 20.9146 | 0.54972 | [10 empty] | 66 | 50 | 28 | 2.2 | 7.4 | 9.6 | 9.6 | 0.43041 | 0.22917 | 11.7333 | 11.7646 | 6.6275 | 23.3725 | 0.50335
[11 empty] | 1991-03-30 | 22:00 | 1103.2 | 24.4 | 73 | 50 | 39.5932 | 0 | 5.9 | 7.5 |  | 13.4 | 13.4 | 0.4403 | 0 | 10.4889 | 10.5168 | 4.2041 | 17.7027 | 0.59408 | [11 empty] | 73 | 68 | 46 | 3.8 | 9.6 | 13.4 | 13.4 | 0.29116 | 0.28358 | 10.1333 | 10.1603 | 3.6667 | 20.8333 | 0.4877 | [10 empty] | 68 | 50 | 28 | 2.1 | 7.5 | 9.6 | 9.6 | 0.43294 | 0.21875 | 11.2 | 11.2298 | 4.144 | 26.856 | 0.41815
[11 empty] | 1991-03-31 | 4:00 | 1109.2 | 22.8 | 72 | 50 | 38.9492 | 0 | 5.9 | 7.4 |  | 13.3 | 13.3 | 0.44361 | 0 | 10.4889 | 11.0262 | 4.2041 | 17.8467 | 0.61783 | [11 empty] | 72 | 68 | 45 | 3.8 | 9.5 | 13.3 | 13.3 | 0.28863 | 0.28571 | 10.1333 | 10.6524 | 3.6667 | 21.3333 | 0.49933 | [10 empty] | 68 | 50 | 28 | 2.1 | 7.4 | 9.5 | 9.5 | 0.42788 | 0.22105 | 11.2 | 11.7737 | 4.144 | 26.856 | 0.4384
[11 empty] | 1991-03-31 | 9:15 | 1114.5 | 22.8 | 72 | 50 | 40 | 0 | 5.7 | 7.4 |  | 13.1 | 13.1 | 0.43511 | 0 | 10.1333 | 10.6524 | 4.2041 | 16.7959 | 0.63423 | [11 empty] | 72 | 68 | 46 | 3.8 | 9.3 | 13.1 | 13.1 | 0.28356 | 0.29008 | 10.1333 | 10.6524 | 3.6667 | 20.3333 | 0.52389 | [10 empty] | 68 | 50 | 28 | 1.9 | 7.4 | 9.3 | 9.3 | 0.42282 | 0.2043 | 10.1333 | 10.6524 | 4.144 | 26.856 | 0.39665
[11 empty] | 1991-03-31 | 12:30 | 1117.8 | 22.8 | 74 | 50 | 40 | 0 | 5.7 | 7.4 |  | 13.1 | 13.1 | 0.43511 | 0 | 10.1333 | 10.6524 | 4.2041 | 17.7959 | 0.59859 | [11 empty] | 74 | 66 | 46 | 3.8 | 9.3 | 13.1 | 13.1 | 0.28356 | 0.29008 | 10.1333 | 10.6524 | 3.6667 | 20.3333 | 0.52389 | [10 empty] | 66 | 50 | 28 | 1.9 | 7.4 | 9.3 | 9.3 | 0.42282 | 0.2043 | 10.1333 | 10.6524 | 4.144 | 25.856 | 0.41199
[11 empty] | 1991-03-31 | 20:00 | 1125.3 | 22.8 | 75 | 51 | 41.8302 | 0 | 5.3 | 7.4 |  | 12.7 | 12.7 | 0.41732 | 0 | 9.4222 | 9.9049 | 4.2041 | 16.9657 | 0.58382 | [11 empty] | 75 | 69 | 49 | 3.4 | 9.3 | 12.7 | 12.7 | 0.2785 | 0.26772 | 9.0667 | 9.5311 | 3.6667 | 19.3333 | 0.49299 | [10 empty] | 69 | 51 | 29 | 1.9 | 7.4 | 9.3 | 9.3 | 0.42282 | 0.2043 | 10.1333 | 10.6524 | 4.144 | 26.856 | 0.39665
[11 empty] | 1991-04-01 | 7:00 | 1136.2 | 21.7 | 75 | 50 | 39.9216 | 0 | 5.1 | 7.3 |  | 12.4 | 12.4 | 0.41129 | 0 | 9.0667 | 9.8461 | 4.2041 | 18.3743 | 0.53586 | [11 empty] | 75 | 70 | 47 | 3.2 | 9.2 | 12.4 | 12.4 | 0.27344 | 0.25806 | 8.5333 | 9.2669 | 3.6667 | 21.8333 | 0.42444 | [10 empty] | 70 | 50 | 28 | 1.9 | 7.3 | 9.2 | 9.2 | 0.41775 | 0.20652 | 10.1333 | 11.0044 | 4.144 | 27.856 | 0.39505
[11 empty] | 1991-04-01 | 11:00 | 1140.3 | 21.7 | 75 | 50 | 39.7692 | 0 | 5.2 | 7.4 |  | 12.6 | 12.6 | 0.4127 | 0 | 9.2444 | 10.0391 | 4.2041 | 18.5267 | 0.54188 | [11 empty] | 75 | 68 | 46 | 3.4 | 9.2 | 12.6 | 12.6 | 0.27597 | 0.26984 | 9.0667 | 9.8461 | 3.6667 | 21.8333 | 0.45097 | [10 empty] | 68 | 50 | 28 | 1.8 | 7.4 | 9.2 | 9.2 | 0.42028 | 0.19565 | 9.6 | 10.4253 | 4.144 | 26.856 | 0.38819
[11 empty] | 1991-04-01 | 19:00 | 1148.2 | 21.7 | 75 | 50 | 40.1887 | 0 | 5.3 | 7.5 |  | 12.8 | 12.8 | 0.41406 | 0 | 9.4222 | 10.2322 | 4.2041 | 18.1072 | 0.56509 | [11 empty] | 75 | 68 | 47 | 3.4 | 9.4 | 12.8 | 12.8 | 0.28103 | 0.26562 | 9.0667 | 9.8461 | 3.6667 | 20.8333 | 0.47261 | [10 empty] | 68 | 50 | 28 | 1.9 | 7.5 | 9.4 | 9.4 | 0.42788 | 0.20213 | 10.1333 | 11.0044 | 4.144 | 26.856 | 0.40976
[11 empty] | 1991-04-02 | 6:00 | 1159.3 | 21.7 | 79 | 50 | 40.1887 | 0 | 5.3 | 7.3 |  | 12.6 | 12.6 | 0.42063 | 0 | 9.4222 | 10.2322 | 4.2041 | 20.1072 | 0.50888 | [11 empty] | 79 | 69 | 47 | 3.4 | 9.2 | 12.6 | 12.6 | 0.27597 | 0.26984 | 9.0667 | 9.8461 | 3.6667 | 23.3333 | 0.42197 | [10 empty] | 69 | 50 | 28 | 1.9 | 7.3 | 9.2 | 9.2 | 0.41775 | 0.20652 | 10.1333 | 11.0044 | 4.144 | 27.356 | 0.40227
[11 empty] | 1991-04-02 | 19:10 | 1172.4 | 21.7 | 75 | 50 | 39.5472 | 0 | 5.3 | 7.3 |  | 12.6 | 12.6 | 0.42063 | 0 | 9.4222 | 10.2322 | 4.2041 | 18.7487 | 0.54575 | [11 empty] | 75 | 69 | 46 | 3.4 | 9.2 | 12.6 | 12.6 | 0.27597 | 0.26984 | 9.0667 | 9.8461 | 3.6667 | 22.3333 | 0.44087 | [10 empty] | 69 | 50 | 28 | 1.9 | 7.3 | 9.2 | 9.2 | 0.41775 | 0.20652 | 10.1333 | 11.0044 | 4.144 | 27.356 | 0.40227
[11 empty] | 1991-04-02 | 23:00 | 1176.3 | 21.7 | 79 | 50 | 39.5472 | 0 | 5.3 | 7.5 |  | 12.8 | 12.8 | 0.41406 | 0 | 9.4222 | 10.2322 | 4.2041 | 20.7487 | 0.49315 | [11 empty] | 79 | 68 | 46 | 3.4 | 9.4 | 12.8 | 12.8 | 0.28103 | 0.26562 | 9.0667 | 9.8461 | 3.6667 | 23.8333 | 0.41312 | [10 empty] | 68 | 50 | 28 | 1.9 | 7.5 | 9.4 | 9.4 | 0.42788 | 0.20213 | 10.1333 | 11.0044 | 4.144 | 26.856 | 0.40976
[11 empty] | 1991-04-03 | 9:00 | 1186.3 | 21.1 | 74 | 50 | 40.4231 | 0 | 5.2 | 7.5 |  | 12.7 | 12.7 | 0.40945 | 0 | 9.2444 | 10.2188 | 4.1747 | 17.4023 | 0.58721 | 7.3 | 3.6 | 150 | 390 | 460 | 650 | 674.9333 | -3.8359 | 67.3913 | 567.4667 | 73.5667 | 74 | 68 | 47 | 3.4 | 9.3 | 12.7 | 12.7 | 0.2785 | 0.26772 | 9.0667 | 10.0223 | 3.6667 | 20.3333 | 0.4929 | 3.6 | 3.6 | 150 | 460 | 560 | 573.3333 | -2.381 | 67.3913 | 516.6667 | 70.9677 | 68 | 50 | 28 | 1.8 | 7.5 | 9.3 | 9.3 | 0.42535 | 0.19355 | 9.6 | 10.6118 | 4.144 | 26.856 | 0.39514 | 3.6 | 3.2 | 190 | 560 | 650 | 648.8 | 0.18462 | 58.6957 | 604.4 | 68.5639
[11 empty] | 1991-04-03 | 23:00 | 1200.3 | 21.1 | 75 | 50 | 41.54 | 0 | 5 | 7.6 |  | 12.6 | 12.6 | 0.39683 | 0 | 8.8889 | 9.8257 | 4.2041 | 16.7559 | 0.58641 | [11 empty] | 75 | 68 | 48 | 3.3 | 9.3 | 12.6 | 12.6 | 0.27724 | 0.2619 | 8.8 | 9.7275 | 3.6667 | 19.8333 | 0.49046 | [10 empty] | 68 | 50 | 29 | 1.7 | 7.6 | 9.3 | 9.3 | 0.42788 | 0.1828 | 9.0667 | 10.0223 | 4.144 | 25.856 | 0.38762
[11 empty] | 1991-04-04 | 6:00 | 1207.3 | 21.1 | 79 | 50 | 40.1887 | 0 | 5.3 | 7.3 |  | 12.6 | 12.6 | 0.42063 | 0 | 9.4222 | 10.4153 | 4.2041 | 20.1072 | 0.51799 | [11 empty] | 79 | 69 | 47 | 3.4 | 9.2 | 12.6 | 12.6 | 0.27597 | 0.26984 | 9.0667 | 10.0223 | 3.6667 | 23.3333 | 0.42953 | [10 empty] | 69 | 50 | 28 | 1.9 | 7.3 | 9.2 | 9.2 | 0.41775 | 0.20652 | 10.1333 | 11.2014 | 4.144 | 27.356 | 0.40947
[11 empty] | 1991-04-04 | 10:15 | 1211.5 | 21.1 | 79 | 50 | 40.1887 | 0 | 5.3 | 7.3 |  | 12.6 | 12.6 | 0.42063 | 0 | 9.4222 | 10.4153 | 4.2041 | 20.1072 | 0.51799 | [11 empty] | 79 | 69 | 47 | 3.4 | 9.2 | 12.6 | 12.6 | 0.27597 | 0.26984 | 9.0667 | 10.0223 | 3.6667 | 23.3333 | 0.42953 | [10 empty] | 69 | 50 | 28 | 1.9 | 7.3 | 9.2 | 9.2 | 0.41775 | 0.20652 | 10.1333 | 11.2014 | 4.144 | 27.356 | 0.40947
[11 empty] | 1991-04-04 | 20:15 | 1221.5 | 21.1 | 77 | 50 | 41.2941 | 0 | 5.1 | 7.5 |  | 12.6 | 12.6 | 0.40476 | 0 | 9.0667 | 10.0223 | 4.2041 | 18.0018 | 0.55674 | [11 empty] | 77 | 68 | 48 | 3.3 | 9.3 | 12.6 | 12.6 | 0.27724 | 0.2619 | 8.8 | 9.7275 | 3.6667 | 20.8333 | 0.46692 | [10 empty] | 68 | 50 | 29 | 1.8 | 7.5 | 9.3 | 9.3 | 0.42535 | 0.19355 | 9.6 | 10.6118 | 4.144 | 25.856 | 0.41042
[11 empty] | 1991-04-05 | 6:00 | 1231.3 | 21.7 | 79 | 50 | 40.7455 | 0 | 5.5 | 7.4 |  | 12.9 | 12.9 | 0.42636 | 0 | 9.7778 | 10.6183 | 4.2041 | 19.5504 | 0.54312 | [11 empty] | 79 | 70 | 48 | 3.4 | 9.5 | 12.9 | 12.9 | 0.28356 | 0.26357 | 9.0667 | 9.8461 | 3.6667 | 22.8333 | 0.43122 | [10 empty] | 70 | 50 | 29 | 2.1 | 7.4 | 9.5 | 9.5 | 0.42788 | 0.22105 | 11.2 | 12.1628 | 4.144 | 26.856 | 0.45289
[11 empty] | 1991-04-05 | 10:30 | 1235.8 | 21.7 | 77 | 50 | 41.2941 | 0 | 5.1 | 7.5 |  | 12.6 | 12.6 | 0.40476 | 0 | 9.0667 | 9.8461 | 4.2041 | 18.0018 | 0.54695 | [11 empty] | 77 | 68 | 48 | 3.3 | 9.3 | 12.6 | 12.6 | 0.27724 | 0.2619 | 8.8 | 9.5565 | 3.6667 | 20.8333 | 0.45871 | [10 empty] | 68 | 50 | 29 | 1.8 | 7.5 | 9.3 | 9.3 | 0.42535 | 0.19355 | 9.6 | 10.4253 | 4.144 | 25.856 | 0.4032
[11 empty] | 1991-04-05 | 22:00 | 1247.2 | 21.7 | 77 | 50 | 40.9412 | 0 | 5.1 | 7.4 |  | 12.5 | 12.5 | 0.408 | 0 | 9.0667 | 9.8461 | 4.2041 | 18.3547 | 0.53643 | [11 empty] | 77 | 68 | 48 | 3.3 | 9.2 | 12.5 | 12.5 | 0.2747 | 0.264 | 8.8 | 9.5565 | 3.6667 | 20.8333 | 0.45871 | [10 empty] | 68 | 50 | 28 | 1.8 | 7.4 | 9.2 | 9.2 | 0.42028 | 0.19565 | 9.6 | 10.4253 | 4.144 | 26.856 | 0.38819
[11 empty] | 1991-04-07 | 18:00 | 1247.3 | 24.4 | 74 | 50 | 42.9412 | 0 | 5.1 | 7.4 |  | 12.5 | 12.5 | 0.408 | 0 | 9.0667 | 9.0908 | 4.2041 | 14.8547 | 0.61198 | [11 empty] | 74 | 66 | 50 | 3.3 | 9.2 | 12.5 | 12.5 | 0.2747 | 0.264 | 8.8 | 8.8234 | 3.6667 | 16.3333 | 0.54021 | [10 empty] | 66 | 50 | 30 | 1.8 | 7.4 | 9.2 | 9.2 | 0.42028 | 0.19565 | 9.6 | 9.6256 | 4.144 | 23.856 | 0.40349
[11 empty] | 1991-04-08 | 7:10 | 1260.4 | 25.6 | 78 | 50 | 42.8302 | 0 | 5.3 | 7.3 |  | 12.6 | 12.6 | 0.42063 | 0 | 9.4222 | 9.1181 | 4.2041 | 16.9657 | 0.53744 | [11 empty] | 78 | 68 | 50 | 3.4 | 9.2 | 12.6 | 12.6 | 0.27597 | 0.26984 | 9.0667 | 8.774 | 3.6667 | 19.3333 | 0.45383 | [10 empty] | 68 | 50 | 30 | 1.9 | 7.3 | 9.2 | 9.2 | 0.41775 | 0.20652 | 10.1333 | 9.8063 | 4.144 | 24.856 | 0.39452
[11 empty] | 1991-04-08 | 20:00 | 1273.3 | 25.6 | 72 | 50 | 41.4231 | 0 | 5.2 | 7.5 |  | 12.7 | 12.7 | 0.40945 | 0 | 9.2444 | 8.9461 | 4.2041 | 15.3728 | 0.58194 | [11 empty] | 72 | 66 | 48 | 3.4 | 9.3 | 12.7 | 12.7 | 0.2785 | 0.26772 | 9.0667 | 8.774 | 3.6667 | 17.3333 | 0.50619 | [10 empty] | 66 | 50 | 29 | 1.8 | 7.5 | 9.3 | 9.3 | 0.42535 | 0.19355 | 9.6 | 9.2901 | 4.144 | 24.856 | 0.37376
[11 empty] | 1991-04-09 | 5:00 | 1282.3 | 25 | 75 | 50 | 42.2708 | 0 | 4.8 | 7.5 |  | 12.3 | 12.3 | 0.39024 | 0 | 8.5333 | 8.4057 | 4.2041 | 16.0251 | 0.52453 | [11 empty] | 75 | 68 | 49 | 3.1 | 9.2 | 12.3 | 12.3 | 0.27217 | 0.25203 | 8.2667 | 8.143 | 3.6667 | 18.8333 | 0.43237 | [10 empty] | 68 | 50 | 30 | 1.7 | 7.5 | 9.2 | 9.2 | 0.42282 | 0.18478 | 9.0667 | 8.931 | 4.144 | 24.856 | 0.35931
[11 empty] | 1991-04-09 | 11:00 | 1288.3 | 25 | 75 | 50 | 42.0769 | 0 | 5.2 | 7.5 |  | 12.7 | 12.7 | 0.40945 | 0 | 9.2444 | 9.1061 | 4.2041 | 16.219 | 0.56145 | [11 empty] | 75 | 68 | 49 | 3.4 | 9.3 | 12.7 | 12.7 | 0.2785 | 0.26772 | 9.0667 | 8.931 | 3.6667 | 18.8333 | 0.47421 | [10 empty] | 68 | 50 | 29 | 1.8 | 7.5 | 9.3 | 9.3 | 0.42535 | 0.19355 | 9.6 | 9.4564 | 4.144 | 25.856 | 0.36573
[11 empty] | 1991-04-09 | 20:00 | 1297.3 | 25 | 72 | 50 | 42.4 | 0 | 5 | 7.5 |  | 12.5 | 12.5 | 0.4 | 0 | 8.8889 | 8.7559 | 4.2041 | 14.3959 | 0.60822 | [11 empty] | 72 | 68 | 50 | 3.1 | 9.4 | 12.5 | 12.5 | 0.27724 | 0.248 | 8.2667 | 8.143 | 3.6667 | 16.3333 | 0.49855 | [10 empty] | 68 | 50 | 30 | 1.9 | 7.5 | 9.4 | 9.4 | 0.42788 | 0.20213 | 10.1333 | 9.9817 | 4.144 | 24.856 | 0.40158
[11 empty] | 1991-04-10 | 5:00 | 1306.3 | 25.6 | 73 | 49 | 42.1277 | 0 | 4.7 | 7.5 |  | 12.2 | 12.2 | 0.38525 | 0 | 8.3556 | 8.0859 | 4.2041 | 14.6682 | 0.55125 | [11 empty] | 73 | 67 | 49 | 3 | 9.2 | 12.2 | 12.2 | 0.27091 | 0.2459 | 8 | 7.7418 | 3.6667 | 17.3333 | 0.44664 | [10 empty] | 67 | 49 | 30 | 1.7 | 7.5 | 9.2 | 9.2 | 0.42282 | 0.18478 | 9.0667 | 8.774 | 4.144 | 23.856 | 0.36779
[11 empty] | 1991-04-10 | 10:30 | 1311.8 | 25.6 | 73 | 49 | 41.766 | 0 | 4.7 | 7.5 |  | 12.2 | 12.2 | 0.38525 | 0 | 8.3556 | 8.0859 | 4.2041 | 15.0299 | 0.53798 | [11 empty] | 73 | 67 | 49 | 3 | 9.2 | 12.2 | 12.2 | 0.27091 | 0.2459 | 8 | 7.7418 | 3.6667 | 17.3333 | 0.44664 | [10 empty] | 67 | 49 | 29 | 1.7 | 7.5 | 9.2 | 9.2 | 0.42282 | 0.18478 | 9.0667 | 8.774 | 4.144 | 24.856 | 0.35299
[11 empty] | 1991-04-10 | 20:00 | 1321.3 | 25.6 | 73 | 50 | 41.6531 | 0 | 4.9 | 7.5 |  | 12.4 | 12.4 | 0.39516 | 0 | 8.7111 | 8.4299 | 4.2041 | 15.6428 | 0.5389 | [11 empty] | 73 | 68 | 49 | 3.1 | 9.3 | 12.4 | 12.4 | 0.2747 | 0.25 | 8.2667 | 7.9998 | 3.6667 | 17.8333 | 0.44859 | [10 empty] | 68 | 50 | 29 | 1.8 | 7.5 | 9.3 | 9.3 | 0.42535 | 0.19355 | 9.6 | 9.2901 | 4.144 | 25.856 | 0.3593
[11 empty] | 1991-04-11 | 6:00 | 1331.3 | 26.1 | 73 | 50 | 40.9783 | 0 | 4.6 | 7.4 |  | 12 | 12 | 0.38333 | 0 | 8.1778 | 7.7977 | 4.2041 | 16.3176 | 0.47787 | [11 empty] | 73 | 67 | 48 | 2.9 | 9.1 | 12 | 12 | 0.26711 | 0.24167 | 7.7333 | 7.3739 | 3.6667 | 18.3333 | 0.40221 | [10 empty] | 67 | 50 | 29 | 1.7 | 7.4 | 9.1 | 9.1 | 0.41775 | 0.18681 | 9.0667 | 8.6453 | 4.144 | 25.356 | 0.34096
[11 empty] | 1991-04-11 | 13:00 | 1338.2 | 26.1 | 73 | 50 | 40.6087 | 0 | 4.6 | 7.3 |  | 11.9 | 11.9 | 0.38655 | 0 | 8.1778 | 7.7977 | 4.2041 | 16.6872 | 0.46729 | [11 empty] | 73 | 68 | 48 | 2.9 | 9 | 11.9 | 11.9 | 0.26458 | 0.2437 | 7.7333 | 7.3739 | 3.6667 | 18.8333 | 0.39154 | [10 empty] | 68 | 50 | 28 | 1.7 | 7.3 | 9 | 9 | 0.41269 | 0.18889 | 9.0667 | 8.6453 | 4.144 | 26.856 | 0.32191
[11 empty] | 1991-04-11 | 21:00 | 1346.3 | 26.1 | 70 | 50 | 42.766 | 0 | 4.7 | 7.3 |  | 12 | 12 | 0.39167 | 0 | 8.3556 | 7.9672 | 4.2041 | 13.0299 | 0.61146 | [11 empty] | 70 | 65 | 50 | 3 | 9 | 12 | 12 | 0.26584 | 0.25 | 8 | 7.6282 | 3.6667 | 13.8333 | 0.55144 | [10 empty] | 65 | 50 | 30 | 1.7 | 7.3 | 9 | 9 | 0.41269 | 0.18889 | 9.0667 | 8.6453 | 4.144 | 23.356 | 0.37015
[11 empty] | 1991-04-12 | 3:30 | 1352.8 | 26.1 | 73 | 48 | 41.6087 | 0 | 4.6 | 7.4 |  | 12 | 12 | 0.38333 | 0 | 8.1778 | 7.7977 | 4.2041 | 14.6872 | 0.53092 | [11 empty] | 73 | 65 | 49 | 2.9 | 9.1 | 12 | 12 | 0.26711 | 0.24167 | 7.7333 | 7.3739 | 3.6667 | 16.3333 | 0.45146 | [10 empty] | 65 | 48 | 29 | 1.7 | 7.4 | 9.1 | 9.1 | 0.41775 | 0.18681 | 9.0667 | 8.6453 | 4.144 | 23.356 | 0.37015
[11 empty] | 1991-04-12 | 11:30 | 1360 | 26.1 | 75 | 50 | 43.766 | 0 | 4.7 | 7.4 |  | 12.1 | 12.1 | 0.38843 | 0 | 8.3556 | 7.9672 | 4.2041 | 14.5299 | 0.54833 | [11 empty] | 75 | 68 | 51 | 3 | 9.1 | 12.1 | 12.1 | 0.26837 | 0.24793 | 8 | 7.6282 | 3.6667 | 16.8333 | 0.45316 | [10 empty] | 68 | 50 | 31 | 1.7 | 7.4 | 9.1 | 9.1 | 0.41775 | 0.18681 | 9.0667 | 8.6453 | 4.144 | 23.856 | 0.36239
[11 empty] | 1991-04-12 | 23:00 | 1371.5 | 26.1 | 74 | 50 | 42.5 | 0 | 4.8 | 7.5 |  | 12.3 | 12.3 | 0.39024 | 0 | 8.5333 | 8.1367 | 4.2041 | 15.2959 | 0.53196 | [11 empty] | 74 | 67 | 50 | 3 | 9.3 | 12.3 | 12.3 | 0.27344 | 0.2439 | 8 | 7.6282 | 3.6667 | 16.8333 | 0.45316 | [10 empty] | 67 | 50 | 30 | 1.8 | 7.5 | 9.3 | 9.3 | 0.42535 | 0.19355 | 9.6 | 9.1538 | 4.144 | 24.356 | 0.37584
[11 empty] | 1991-04-13 | 4:00 | 1376.5 | 26.1 | 75 | 50 | 42.6087 | 0 | 4.6 | 7.5 |  | 12.1 | 12.1 | 0.38017 | 0 | 8.1778 | 7.7977 | 4.2041 | 15.6872 | 0.49708 | [11 empty] | 75 | 68 | 50 | 2.9 | 9.2 | 12.1 | 12.1 | 0.26964 | 0.23967 | 7.7333 | 7.3739 | 3.6667 | 17.8333 | 0.41349 | [10 empty] | 68 | 50 | 30 | 1.7 | 7.5 | 9.2 | 9.2 | 0.42282 | 0.18478 | 9.0667 | 8.6453 | 4.144 | 24.856 | 0.34782
[11 empty] | 1991-04-13 | 10:30 | 1383 | 26.1 | 75 | 50 | 42.9783 | 0 | 4.6 | 7.5 |  | 12.1 | 12.1 | 0.38017 | 0 | 8.1778 | 7.7977 | 4.2041 | 15.3176 | 0.50907 | [11 empty] | 75 | 68 | 50 | 2.9 | 9.2 | 12.1 | 12.1 | 0.26964 | 0.23967 | 7.7333 | 7.3739 | 3.6667 | 17.8333 | 0.41349 | [10 empty] | 68 | 50 | 31 | 1.7 | 7.5 | 9.2 | 9.2 | 0.42282 | 0.18478 | 9.0667 | 8.6453 | 4.144 | 23.856 | 0.36239
[11 empty] | 1991-04-13 | 22:00 | 1394.5 | 26.1 | 71 | 49 | 41.2391 | 0 | 4.6 | 7.3 |  | 11.9 | 11.9 | 0.38655 | 0 | 8.1778 | 7.7977 | 4.2041 | 14.5568 | 0.53568 | [11 empty] | 71 | 63 | 49 | 2.9 | 9 | 11.9 | 11.9 | 0.26458 | 0.2437 | 7.7333 | 7.3739 | 3.6667 | 14.3333 | 0.51446 | [10 empty] | 63 | 49 | 28 | 1.7 | 7.3 | 9 | 9 | 0.41269 | 0.18889 | 9.0667 | 8.6453 | 4.144 | 23.856 | 0.36239
[11 empty] | 1991-04-14 | 14:00 | 1404.5 | 26.1 | 74 | 52 | 42.4918 | 0 | 6.1 | 7.2 | X | 13.3 | 13.3 | 0.45865 | 0 | 10.8444 | 10.3404 | 4.2041 | 16.3041 | 0.63422 | [11 empty] | 74 | 68 | 48 | 4 | 9.3 | 13.3 | 13.3 | 0.2861 | 0.30075 | 10.6667 | 10.1709 | 3.6667 | 19.3333 | 0.52608 | [10 empty] | 68 | 52 | 32 | 2.1 | 7.2 | 9.3 | 9.3 | 0.41775 | 0.22581 | 11.2 | 10.6795 | 4.144 | 23.856 | 0.44766
[11 empty] | 1991-04-14 | 21:00 | 1411.5 | 26.1 | 74 | 52 | 42.3051 | 0 | 5.9 | 7.1 |  | 13 | 13 | 0.45385 | 0 | 10.4889 | 10.0014 | 4.2041 | 16.4908 | 0.60648 | [11 empty] | 74 | 68 | 48 | 3.8 | 9.2 | 13 | 13 | 0.28103 | 0.29231 | 10.1333 | 9.6624 | 3.6667 | 19.3333 | 0.49978 | [10 empty] | 68 | 52 | 32 | 2.1 | 7.1 | 9.2 | 9.2 | 0.41269 | 0.22826 | 11.2 | 10.6795 | 4.144 | 23.856 | 0.44766
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
Note on N9: TSC_ADM: Verified by Consultant
Note on AJ40: C. Rice: Consultant verified the pressure and flow for the low MTCw on 2/18/91. No explanation was given but the consultant stated that since it was one of five sampling events for the day (occurring at 4:00 am) it could be considered an outlier.
Note on CW14: C. Rice: Consultant verified low permeate pH values. Consultant stated that the feed sample point was immediately prior to the sulfuric acid addition and consequently the pH, alkalinity and sulfate values do not represent this. To make the pH more representative of the actual pH going through the membrane system, the first stage pH was substituted for the system and stage 1 feed pH.
Note on CW38: C. Rice: Consultant verified value. No explanation was given.
Note on CX33: C. Rice: Consultant verified value; no explanation was given.
Note on DH14: C. Rice: Consultant verified low permeate pH values. Consultant stated that the feed sample point was immediately prior to the sulfuric acid addition and consequently the pH, alkalinity and sulfate values do not represent this. To make the pH more representative of the actual pH going through the membrane system, the first stage pH was substituted for the system and stage 1 feed pH.
Note on DH36: C. Rice: Consultant verified low permeate pH values. Consultant stated that the feed sample point was immediately prior to the sulfuric acid addition and consequently the pH, alkalinity and sulfate values do not represent this. To make the pH more representative of the actual pH going through the membrane system, the first stage pH was substituted for the system and stage 1 feed pH.
Note on DQ14: C. Rice: Consultant verified low permeate pH values. Consultant stated that the feed sample point was immediately prior to the sulfuric acid addition and consequently the pH, alkalinity and sulfate values do not represent this. To make the pH more representative of the actual pH going through the membrane system, the first stage pH was substituted for the system and stage 1 feed pH.
Note on DQ38: C. Rice: Consultant verified value. No explanation was given.
Note on EB14: C. Rice: Consultant verified low permeate pH values. Consultant stated that the feed sample point was immediately prior to the sulfuric acid addition and consequently the pH, alkalinity and sulfate values do not represent this. To make the pH more representative of the actual pH going through the membrane system, the first stage pH was substituted for the system and stage 1 feed pH.
Note on EB36: C. Rice: Consultant verified low permeate pH values. Consultant stated that the feed sample point was immediately prior to the sulfuric acid addition and consequently the pH, alkalinity and sulfate values do not represent this. To make the pH more representative of the actual pH going through the membrane system, the first stage pH was substituted for the system and stage 1 feed pH.
Note on EK14: C. Rice: Consultant verified low permeate pH values. Consultant stated that the feed sample point was immediately prior to the sulfuric acid addition and consequently the pH, alkalinity and sulfate values do not represent this. To make the pH more representative of the actual pH going through the membrane system, the first stage pH was substituted for the system and stage 1 feed pH.
Note on EV14: C. Rice: Consultant verified low permeate pH values. Consultant stated that the feed sample point was immediately prior to the sulfuric acid addition and consequently the pH, alkalinity and sulfate values do not represent this. To make the pH more representative of the actual pH going through the membrane system, the first stage pH was substituted for the system and stage 1 feed pH.
Note on EV36: C. Rice: Consultant verified low permeate pH values. Consultant stated that the feed sample point was immediately prior to the sulfuric acid addition and consequently the pH, alkalinity and sulfate values do not represent this. To make the pH more representative of the actual pH going through the membrane system, the first stage pH was substituted for the system and stage 1 feed pH.
Note on FE11: Reviewer added dates and times necessary for the review process.
Note on FY14: C. Rice: Consultant verified low permeate pH values. Consultant stated that the feed sample point was immediately prior to the sulfuric acid addition and consequently the pH, alkalinity and sulfate values do not represent this. To make the pH more representative of the actual pH going through the membrane system, the first stage pH was substituted for the system and stage 1 feed pH.
Note on GJ14: C. Rice: Consultant verified low permeate pH values. Consultant stated that the feed sample point was immediately prior to the sulfuric acid addition and consequently the pH, alkalinity and sulfate values do not represent this. To make the pH more representative of the actual pH going through the membrane system, the first stage pH was substituted for the system and stage 1 feed pH.
Note on GJ36: C. Rice: Consultant verified low permeate pH values. Consultant stated that the feed sample point was immediately prior to the sulfuric acid addition and consequently the pH, alkalinity and sulfate values do not represent this. To make the pH more representative of the actual pH going through the membrane system, the first stage pH was substituted for the system and stage 1 feed pH.

## Sheet2. Weeks 11-20
FIELD-SET 2: PILOT-SCALE MEMBRANE RESULTS: WEEKS 11-20 (FILE: mempilot.xls)
Field 2-1: PWS And Treatment Plant Data |  | Field 2-2: Manufacturer Reported Membrane Characteristics1 |  | Field 2-3: 2-Stage Membrane Pilot System Design Parameters |  | Field 2-4: Foulants And Fouling Indices1 |  | Field 2-5: Pretreatment Used Prior To Membranes1 |  |  | Field 2-6: Membrane Performance Data During Operation With The Test Water | [18 empty] | Field 2-6: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 2-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 2-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 2-8: System And Stage Water Quality For Week 14 | [9 empty] | Field 2-8: System And Stage Water Quality For Week 14 (continued) | [7 empty] | Field 2-9: System And Stage Water Quality For Week 16 | [9 empty] | Field 2-9: System And Stage Water Quality For Week 16 (continued) | [7 empty] | Field 2-10: System And Stage Water Quality For Week 18 | [9 empty] | Field 2-10: System And Stage Water Quality For Week 18 (continued) | [7 empty] | Field 2-11: System And Stage Water Quality For Week 20 | [9 empty] | Field 2-11: System And Stage Water Quality For Week 20 (continued) | [7 empty] | Field 2-12: Duplicate Analysis Of System And Stage Water Quality For Week 20 | [9 empty] | Field 2-12: Duplicate Analysis Of System And Stage Water Quality For Week 20 (continued) | [7 empty] | Field 2-13: Membrane Cost Parameters
|  | General Information |  | Calculate Temperature Normalized MTCW |  | Parameters Evaluated Prior to Pretreatment |  |  |  |  | System Operating Parameters | [30 empty] | Stage 1 Operating Parameters | [23 empty] | Stage 2 Operating Parameters | [23 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | General Cost Parameters
PWS Name | City of Melbourne Water System | Membrane manufacturer | Osmonics Desal | Average yearly temperature of feed water, TavgoC (oC) | 24.49 | Alkalinity (mg/L as CaCO3) | 92 | Process | Description | Scale | Date | Time | Operation |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  |  |  | System recovery during sample collection (decimal) | 0.44 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.3 | [6 empty] | System recovery during sample collection (decimal) | [9 empty] | Stage 1 recovery during sample collection (decimal) | [7 empty] | System recovery during sample collection (decimal) | [9 empty] | Stage 1 recovery during sample collection (decimal) | [7 empty] | System recovery during sample collection (decimal) | [9 empty] | Stage 1 recovery during sample collection (decimal) | [7 empty] | System recovery during sample collection (decimal) | [9 empty] | Stage 1 recovery during sample collection (decimal) | [5 empty] | Cost Parameter | Parameter value
Public Water System Identification Number | FL3051447 | Membrane trade name | DS5 | Temperature normalized MTCW (gfd/psi) | 0.19701 | Calcium Hardness (mg/L as CaCO3) | 100 | Alum Coagulation | Aluminum sulfate dose: 151.4 mg/L | Full-scale |  |  | time | Influent | PI | PC | PP | QR | Qp | QW | Cleaning Event | QF | QI | Recovery | Recycle | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) |  |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) | [6 empty] | System feed flow rate during sample collection (gpm) | 17.5 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 5.2 | [6 empty] | System feed flow rate during sample collection (gpm) | [9 empty] | Stage 1 permeate flow rate during sample collection (gpm) | [7 empty] | System feed flow rate during sample collection (gpm) | [9 empty] | Stage 1 permeate flow rate during sample collection (gpm) | [7 empty] | System feed flow rate during sample collection (gpm) | [9 empty] | Stage 1 permeate flow rate during sample collection (gpm) | [7 empty] | System feed flow rate during sample collection (gpm) | [9 empty] | Stage 1 permeate flow rate during sample collection (gpm) | [5 empty] | Capital Recovery Interest Rate (%) | 6
Water Industry Data Base Number (optional) |  | Membrane element model number | DK4040F |  |  | LSI |  | Sedimentation | Circular clarifier | Full-scale | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | Indicate with "X" | (gpm) | (gpm) | (decimal) | ratio | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHF (before acid) | pHF (after acid) | TDSp | TDSF (before acid) | TDSF (after acid) | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) |  |  | System influent flow rate during sample collection (gpm) | 17.5 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 17.5 | [6 empty] | System influent flow rate during sample collection (gpm) | [9 empty] | Stage 1 influent flow rate during sample collection (gpm) | [7 empty] | System influent flow rate during sample collection (gpm) | [9 empty] | Stage 1 influent flow rate during sample collection (gpm) | [7 empty] | System influent flow rate during sample collection (gpm) | [9 empty] | Stage 1 influent flow rate during sample collection (gpm) | [7 empty] | System influent flow rate during sample collection (gpm) | [9 empty] | Stage 1 influent flow rate during sample collection (gpm) | [5 empty] | Capital Recovery Period (years) | 20
|  | Molecular weight cutoff (Daltons) | 150 - 300 | Calculate System Permeate, Feed and Waste Flow Rates |  | Dissolved iron (mg/L) |  | Dual Media Filtration | Sand/anthracite | Full-scale | 1991-04-15 | 7:00 | 1421.5 | 26.7 | 80 | 50 | 44.5932 | 0 | 5.9 | 7.3 |  | 13.2 | 13.2 | 0.44697 | 0 | 10.4889 | 9.8256 | 4.2041 | 16.2027 | 0.60642 | [11 empty] | 80 | 70 | 51 | 3.8 | 9.4 | 13.2 | 13.2 | 0.2861 | 0.28788 | 10.1333 | 9.4925 | 3.6667 | 20.3333 | 0.46685 | [10 empty] | 70 | 50 | 33 | 2.1 | 7.3 | 9.4 | 9.4 | 0.42282 | 0.2234 | 11.2 | 10.4917 | 4.144 | 22.856 | 0.45904 | [100 empty] | Overhead & Profit Factor (% of construction costs) | 10
Official ICR Contact Person |  | Membrane material (e.g., PVD, polyamide, etc.) | Proprietary | Design system recovery, R (decimal) | 0.65 | Total iron (mg/L) | 0.28 | Sulfuric Acid Feed | Approx. 85 mg/L to pH 3.5 to 4.5 | Pilot-scale | 1991-04-15 | 11:10 | 1425.7 | 26.7 | 78 | 51 | 44.3333 | 0 | 5.7 | 7.3 |  | 13 | 13 | 0.43846 | 0 | 10.1333 | 9.4925 | 4.2041 | 15.9626 | 0.59467 | [11 empty] | 78 | 68 | 50 | 3.8 | 9.2 | 13 | 13 | 0.28103 | 0.29231 | 10.1333 | 9.4925 | 3.6667 | 19.3333 | 0.49099 | [10 empty] | 68 | 51 | 33 | 1.9 | 7.3 | 9.2 | 9.2 | 0.41775 | 0.20652 | 10.1333 | 9.4925 | 4.144 | 22.356 | 0.42461 | [10 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | Special Sitework Factor (% of construction costs) | 6.5
Mailing Address |  | Membrane construction (e.g., thin-film composite) | Thin-Film Composite | Design average system flux, FW (gfd) | 15 | Dissolved aluminum (mg/L) |  | Microfiltration | 5um filter Filter Specialists Bag Filter | Pilot-scale | 1991-04-15 | 21:00 | 1434.5 | 26.7 | 76 | 50 | 43.5254 | 0 | 5.9 | 7.3 |  | 13.2 | 13.2 | 0.44697 | 0 | 10.4889 | 9.8256 | 4.2041 | 15.2705 | 0.64344 | [11 empty] | 76 | 68 | 51 | 3.8 | 9.4 | 13.2 | 13.2 | 0.2861 | 0.28788 | 10.1333 | 9.4925 | 3.6667 | 17.3333 | 0.54765 | [10 empty] | 68 | 50 | 30 | 2.1 | 7.3 | 9.4 | 9.4 | 0.42282 | 0.2234 | 11.2 | 10.4917 | 4.144 | 24.856 | 0.4221 | [10 empty] | Parameter | Units | Cp-sys-14 | CF-sys-14 | CC-sys-14 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-14 | CI-s1-14 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-16 | CF-sys-16 | CC-sys-16 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-16 | CI-s1-16 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-18 | CF-sys-18 | CC-sys-18 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-18 | CI-s1-18 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-20 | CF-sys-20 | CC-sys-20 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-20 | CI-s1-20 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-20 (dup) | CF-sys-20 (dup) | CC-sys-20 (dup) | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-20 (dup) | CI-s1-20 (dup) | CC(calc) | RF (%) | CB | RB (%) | Construction Contingencies (% of construction costs) | 10
|  | Membrane hydrophobicity | Hydrophilic | Number of elements per pressure vessel, Ne | 3 | Total aluminum (mg/L) |  |  |  |  | 1991-04-16 | 4:00 | 1441.5 | 26.1 | 80 | 50 | 44.5932 | 0 | 5.9 | 7.2 |  | 13.1 | 13.1 | 0.45038 | 0 | 10.4889 | 10.0014 | 4.2041 | 16.2027 | 0.61727 | [11 empty] | 80 | 70 | 51 | 3.8 | 9.3 | 13.1 | 13.1 | 0.28356 | 0.29008 | 10.1333 | 9.6624 | 3.6667 | 20.3333 | 0.4752 | [10 empty] | 70 | 50 | 33 | 2.1 | 7.2 | 9.3 | 9.3 | 0.41775 | 0.22581 | 11.2 | 10.6795 | 4.144 | 22.856 | 0.46725 | [10 empty] | Sampling date | MM/DD/YY | 1991-05-06 | 1991-05-06 | 1991-05-06 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1991-05-06 | 1991-05-06 | --- | --- | --- | --- | Sampling date | MM/DD/YY |  |  |  | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY |  |  | --- | --- | --- | --- | Sampling date | MM/DD/YY |  |  |  | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY |  |  | --- | --- | --- | --- | Sampling date | MM/DD/YY |  |  |  | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY |  |  | --- | --- | --- | --- | Sampling date | MM/DD/YY |  |  |  | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY |  |  | --- | --- | --- | --- | Engineering Fee Factor (% of construction costs) | 10
Phone Number |  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Negative | Number of parallel pressure vessels in stage 1, Nv-s(1) | 2 | Fluoride (mg/L) |  |  |  |  | 1991-04-16 | 11:00 | 1448.5 | 26.1 | 78 | 52 | 44.1273 | 0 | 5.5 | 7.3 |  | 12.8 | 12.8 | 0.42969 | 0 | 9.7778 | 9.3234 | 4.2041 | 16.6686 | 0.55934 | [11 empty] | 78 | 68 | 50 | 3.6 | 9.2 | 12.8 | 12.8 | 0.2785 | 0.28125 | 9.6 | 9.1538 | 3.6667 | 19.3333 | 0.47347 | [10 empty] | 68 | 52 | 33 | 1.9 | 7.3 | 9.2 | 9.2 | 0.41775 | 0.20652 | 10.1333 | 9.6624 | 4.144 | 22.856 | 0.42275 | [10 empty] | Sampling time | hh:mm | 14:00 | 14:00 | 14:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 14:00 | 14:00 | --- | --- | --- | --- | Sampling time | hh:mm |  |  |  | --- | --- | --- | --- | --- | Sampling time | hh:mm |  |  | --- | --- | --- | --- | Sampling time | hh:mm |  |  |  | --- | --- | --- | --- | --- | Sampling time | hh:mm |  |  | --- | --- | --- | --- | Sampling time | hh:mm |  |  |  | --- | --- | --- | --- | --- | Sampling time | hh:mm |  |  | --- | --- | --- | --- | Sampling time | hh:mm |  |  |  | --- | --- | --- | --- | --- | Sampling time | hh:mm |  |  | --- | --- | --- | --- | 1998 ENR Construction Cost Index (CCI base year 1913) | 5881.41
FAX Number |  |  |  | Number of parallel pressure vessels in stage 2, Nv-s(2) | 1 | Phosphate (mg/L) |  |  |  |  | 1991-04-16 | 21:00 | 1458.5 | 26.1 | 78 | 52 | 43.7368 | 0 | 5.7 | 7.3 |  | 13 | 13 | 0.43846 | 0 | 10.1333 | 9.6624 | 4.2041 | 17.059 | 0.56641 | [11 empty] | 78 | 68 | 50 | 3.6 | 9.4 | 13 | 13 | 0.28356 | 0.27692 | 9.6 | 9.1538 | 3.6667 | 19.3333 | 0.47347 | [10 empty] | 68 | 52 | 33 | 2.1 | 7.3 | 9.4 | 9.4 | 0.42282 | 0.2234 | 11.2 | 10.6795 | 4.144 | 22.856 | 0.46725 | [10 empty] | Operation time | hh.hh | 1898.5 | 1898.5 | 1898.5 | --- | --- | --- | --- | --- | Operation time | hh.hh | 1898.5 | 1898.5 | --- | --- | --- | --- | Operation time | hh.hh |  |  |  | --- | --- | --- | --- | --- | Operation time | hh.hh |  |  | --- | --- | --- | --- | Operation time | hh.hh |  |  |  | --- | --- | --- | --- | --- | Operation time | hh.hh |  |  | --- | --- | --- | --- | Operation time | hh.hh |  |  |  | --- | --- | --- | --- | --- | Operation time | hh.hh |  |  | --- | --- | --- | --- | Operation time | hh.hh |  |  |  | --- | --- | --- | --- | --- | Operation time | hh.hh |  |  | --- | --- | --- | --- | 1998 Producers Price Index (PPI base year 1967 = 100) | NR
E-Mail Address (optional) |  | Design Parameters |  | Permeate flow rate per element, Qp-e (gpm) | 0.9375 | Sulfate (mg/L) | BDL |  |  |  | 1991-04-17 | 6:00 | 1467.5 | 26.7 | 78 | 52 | 44.4828 | 0 | 5.8 | 7.3 |  | 13.1 | 13.1 | 0.44275 | 0 | 10.3111 | 9.6591 | 4.2041 | 16.3131 | 0.5921 | [11 empty] | 78 | 68 | 51 | 3.7 | 9.4 | 13.1 | 13.1 | 0.28483 | 0.28244 | 9.8667 | 9.2427 | 3.6667 | 18.3333 | 0.50415 | [10 empty] | 68 | 52 | 33 | 2.1 | 7.3 | 9.4 | 9.4 | 0.42282 | 0.2234 | 11.2 | 10.4917 | 4.144 | 22.856 | 0.45904 | [10 empty] | pH | --- | 4.4 | 7.3 | 4.4 | --- | --- | --- | --- | --- | pH | --- | 4.5 | 7.3 | --- | --- | --- | --- | pH | --- |  |  |  | --- | --- | --- | --- | --- | pH | --- |  |  | --- | --- | --- | --- | pH | --- |  |  |  | --- | --- | --- | --- | --- | pH | --- |  |  | --- | --- | --- | --- | pH | --- |  |  |  | --- | --- | --- | --- | --- | pH | --- |  |  | --- | --- | --- | --- | pH | --- |  |  |  | --- | --- | --- | --- | --- | pH | --- |  |  | --- | --- | --- | --- | Labor Rate + Fringe ($/work-hour) | 40.03
|  | Element size (e.g., 2.5" x 40", 4" x 40", etc.) | 4" X 40" | Permeate flow rate per pressure vessel, Qp-v (gpm) | 2.8125 | Calcium (mg/L) |  |  |  |  | 1991-04-17 | 14:00 | 1475.5 | 26.7 | 78 | 50 | 41.9057 | 0 | 5.3 | 7.3 |  | 12.6 | 12.6 | 0.42063 | 0 | 9.4222 | 8.8264 | 4.2041 | 17.8902 | 0.49336 | [11 empty] | 78 | 68 | 48 | 3.4 | 9.2 | 12.6 | 12.6 | 0.27597 | 0.26984 | 9.0667 | 8.4933 | 3.6667 | 21.3333 | 0.39812 | [10 empty] | 68 | 50 | 31 | 1.9 | 7.3 | 9.2 | 9.2 | 0.41775 | 0.20652 | 10.1333 | 9.4925 | 4.144 | 23.856 | 0.39791 | [10 empty] | Temperature | oC | 27.8 | 27.8 | 27.8 | --- | --- | --- | --- | --- | Temperature | oC | 27.8 | 27.8 | --- | --- | --- | --- | Temperature | oC |  |  |  | --- | --- | --- | --- | --- | Temperature | oC |  |  | --- | --- | --- | --- | Temperature | oC |  |  |  | --- | --- | --- | --- | --- | Temperature | oC |  |  | --- | --- | --- | --- | Temperature | oC |  |  |  | --- | --- | --- | --- | --- | Temperature | oC |  |  | --- | --- | --- | --- | Temperature | oC |  |  |  | --- | --- | --- | --- | --- | Temperature | oC |  |  | --- | --- | --- | --- | Labor Overhead Factor (% of labor) | 35
Technical ICR Contact Person |  | Active membrane area of membrane element used, A (ft2) | 90 | Permeate flow rate from stage 1, Qp-s(1) (gpm) | 5.625 | Barium (mg/L) |  |  |  |  | 1991-04-17 | 21:00 | 1482.5 | 26.7 | 80 | 50 | 43.5932 | 0 | 5.9 | 7.3 |  | 13.2 | 13.2 | 0.44697 | 0 | 10.4889 | 9.8256 | 4.2041 | 17.2027 | 0.57117 | [11 empty] | 80 | 70 | 50 | 3.8 | 9.4 | 13.2 | 13.2 | 0.2861 | 0.28788 | 10.1333 | 9.4925 | 3.6667 | 21.3333 | 0.44496 | [10 empty] | 70 | 50 | 32 | 2.1 | 7.3 | 9.4 | 9.4 | 0.42282 | 0.2234 | 11.2 | 10.4917 | 4.144 | 23.856 | 0.43979 | [10 empty] | Alkalinity | mg/L as CaCO3 | BMRL | NR | BMRL | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | BMRL | NR | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Electric Rate ($/kW-h) | 0.09
Mailing Address |  | Design flux, FW (gfd) | 20 | Permeate flow rate from stage 2, Qp-s(2) (gpm) | 2.8125 | Strontium (mg/L) |  |  |  |  | 1991-04-18 | 6:00 | 1491.5 | 23.3 | 80 | 50 | 42 | 0 | 5.6 | 7.2 |  | 12.8 | 12.8 | 0.4375 | 0 | 9.9556 | 10.312 | 4.2041 | 18.7959 | 0.54863 | [11 empty] | 80 | 70 | 48 | 3.5 | 9.3 | 12.8 | 12.8 | 0.27977 | 0.27344 | 9.3333 | 9.6675 | 3.6667 | 23.3333 | 0.41432 | [10 empty] | 70 | 50 | 32 | 2.1 | 7.2 | 9.3 | 9.3 | 0.41775 | 0.22581 | 11.2 | 11.601 | 4.144 | 23.856 | 0.48629 | [10 empty] | Total dissolved solids | mg/L | 220 | 410 | 590 | 559.2857 | 5.2058 | 46.3415 | 484.6429 | 54.6057 | Total dissolved solids | mg/L | 200 | 410 | 498.7805 | 51.2195 | 454.3902 | 55.985 | Total dissolved solids | mg/L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Fuel Oil Rate ($/gal) | 0.911
|  | Net driving pressure at the design flux, NDP (psi) | 100 | Permeate flow rate from system, Qp-sys (gpm) | 8.4375 | Reactive silica (mg/L as SiO2) |  |  |  |  | 1991-04-18 | 11:00 | 1496.5 | 23.3 | 78 | 52 | 43.5472 | 0 | 5.3 | 7.3 |  | 12.6 | 12.6 | 0.42063 | 0 | 9.4222 | 9.7595 | 4.2041 | 17.2487 | 0.56581 | [11 empty] | 78 | 70 | 50 | 3.4 | 9.2 | 12.6 | 12.6 | 0.27597 | 0.26984 | 9.0667 | 9.3913 | 3.6667 | 20.3333 | 0.46187 | [10 empty] | 70 | 52 | 32 | 1.9 | 7.3 | 9.2 | 9.2 | 0.41775 | 0.20652 | 10.1333 | 10.4961 | 4.144 | 24.856 | 0.42228 | [10 empty] | Total hardness | mg/L as CaCO3 | 44 | 180 | 280 | 286.8571 | -2.449 | 75.5556 | 233.4286 | 81.1506 | Total hardness | mg/L as CaCO3 | 36 | 180 | 240.878 | 80 | 210.439 | 82.8929 | Total hardness | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Natural Gas Rate ($/ft3) | NR
Phone Number |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.2 | Feed flow rate to system, QF-sys (gpm) | 12.9808 | Turbidity (ntu) | 12 |  |  |  | 1991-04-18 | 21:00 | 1506.5 | 23.3 | 78 | 50 | 43.25 | 0 | 5.6 | 7.3 |  | 12.9 | 12.9 | 0.43411 | 0 | 9.9556 | 10.312 | 4.2041 | 16.5459 | 0.62323 | [11 empty] | 78 | 70 | 50 | 3.5 | 9.4 | 12.9 | 12.9 | 0.2823 | 0.27132 | 9.3333 | 9.6675 | 3.6667 | 20.3333 | 0.47545 | [10 empty] | 70 | 50 | 32 | 2.1 | 7.3 | 9.4 | 9.4 | 0.42282 | 0.2234 | 11.2 | 11.601 | 4.144 | 23.856 | 0.48629 | [10 empty] | Calcium hardness | mg/L as CaCO3 | 34 | 130 | 210 | 205.4286 | 2.1769 | 73.8462 | 167.7143 | 79.7274 | Calcium hardness | mg/L as CaCO3 | 29 | 130 | 172.6992 | 77.6923 | 151.3496 | 80.8391 | Calcium hardness | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Current Process Water Rate ($/1000 gal) | 1.882
FAX Number |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | Concentrate-waste flow rate from system, QW-sys (gpm) | 4.5433 | SDI |  |  |  |  | 1991-04-19 | 6:00 | 1515.5 | 23.3 | 78 | 50 | 44.1887 | 0 | 5.3 | 7.3 |  | 12.6 | 12.6 | 0.42063 | 0 | 9.4222 | 9.7595 | 4.2041 | 15.6072 | 0.62532 | [11 empty] | 78 | 70 | 51 | 3.4 | 9.2 | 12.6 | 12.6 | 0.27597 | 0.26984 | 9.0667 | 9.3913 | 3.6667 | 19.3333 | 0.48575 | [10 empty] | 70 | 50 | 32 | 1.9 | 7.3 | 9.2 | 9.2 | 0.41775 | 0.20652 | 10.1333 | 10.4961 | 4.144 | 23.856 | 0.43998 | [10 empty] | Turbidity | ntu | BMRL | 0.2 | 0.2 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | 0.2 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Modifications to Existing Plant (% of construction costs) | NR
E-Mail Address (optional) |  | Maximum flow rate to the element, QI, max (gpm) | 12 |  |  | MFI |  |  |  |  | 1991-04-19 | 15:00 | 1524.5 | 23.3 | 78 | 51 | 44.963 | 0 | 5.4 | 7 |  | 12.4 | 12.4 | 0.43548 | 0 | 9.6 | 9.9437 | 4.2041 | 15.3329 | 0.64852 | [11 empty] | 78 | 69 | 52 | 3.5 | 8.9 | 12.4 | 12.4 | 0.26964 | 0.28226 | 9.3333 | 9.6675 | 3.6667 | 17.8333 | 0.5421 | [10 empty] | 69 | 51 | 32 | 1.9 | 7 | 8.9 | 8.9 | 0.40256 | 0.21348 | 10.1333 | 10.4961 | 4.144 | 23.856 | 0.43998 | [10 empty] | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.5 | 9 | 12.5935 | 94.4444 | 10.7967 | 95.369 | Ammonia | mg NH3-N / L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Minimum flow rate to the element, QI, min (gpm) | 6.25 | Calculate the Feed Flow Rates at the End of Each Stage |  | MPFI |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | 1991-04-19 | 22:00 | 1531.5 | 23.3 | 78 | 51 | 44.3148 | 0 | 5.4 | 7 |  | 12.4 | 12.4 | 0.43548 | 0 | 9.6 | 9.9437 | 4.2041 | 15.9811 | 0.62222 | [11 empty] | 78 | 70 | 51 | 3.5 | 8.9 | 12.4 | 12.4 | 0.26964 | 0.28226 | 9.3333 | 9.6675 | 3.6667 | 19.3333 | 0.50004 | [10 empty] | 70 | 51 | 32 | 1.9 | 7 | 8.9 | 8.9 | 0.40256 | 0.21348 | 10.1333 | 10.4961 | 4.144 | 24.356 | 0.43095 | [10 empty] | Total organic carbon | mg/L | 0.6 | 9 | 15 | 15.6 | -4 | 93.3333 | 12.3 | 95.122 | UV254 | cm-1 | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | UV254 | cm-1 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | UV254 | cm-1 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | UV254 | cm-1 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | UV254 | cm-1 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Plant Name | South WTP | Total width of all membrane envelopes in the element, w (ft) | 16 | Feed flow rate at the end of stage 1, (QF-s(1))end (gpm) | 9.2308 | Color | 240 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | 1991-04-20 | 6:00 | 1539.5 | 25 | 78 | 50 | 43.7455 | 0 | 5.5 | 7 |  | 12.5 | 12.5 | 0.44 | 0 | 9.7778 | 9.6315 | 4.2041 | 16.0504 | 0.60008 | [11 empty] | 78 | 70 | 51 | 3.4 | 9.1 | 12.5 | 12.5 | 0.27344 | 0.272 | 9.0667 | 8.931 | 3.6667 | 19.3333 | 0.46195 | [10 empty] | 70 | 50 | 32 | 2.1 | 7 | 9.1 | 9.1 | 0.40762 | 0.23077 | 11.2 | 11.0324 | 4.144 | 23.856 | 0.46246 | [10 empty] | UV254 | cm-1 | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | NR | --- | --- | --- | --- | UV254 | cm-1 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | --- | --- | --- | --- | UV254 | cm-1 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | --- | --- | --- | --- | UV254 | cm-1 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | --- | --- | --- | --- | UV254 | cm-1 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | --- | --- | --- | ---
Treatment Plant Category | Full Treatment | Feed spacer thickness, T (ft) | 0.00275 | Feed flow rate at the end of stage 2, (QF-s(2))end (gpm) | 5.4808 | TDS | 430 | is to list the pretreatment processes used in this particular pilot-scale run. |  |  | 1991-04-20 | 11:00 | 1544.5 | 25 | 72 | 43 | 39.7551 | 0 | 4.9 | 6.4 |  | 11.3 | 11.3 | 0.43363 | 0 | 8.7111 | 8.5808 | 4.2041 | 13.5408 | 0.6337 | [11 empty] | 72 | 61 | 46 | 3.2 | 8.1 | 11.3 | 11.3 | 0.24559 | 0.28319 | 8.5333 | 8.4057 | 3.6667 | 16.8333 | 0.49935 | [10 empty] | 61 | 43 | 28 | 1.7 | 6.4 | 8.1 | 8.1 | 0.36712 | 0.20988 | 9.0667 | 8.931 | 4.144 | 19.856 | 0.44979 | [10 empty] | SUVA | L/(mg*m) | NR | NR | NR | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | #DIV/0! | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | #DIV/0! | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | #DIV/0! | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | #DIV/0! | --- | --- | --- | --- | ---
Process Train Name |  | Active membrane area of an equivalent 8" x 40" element (ft2) | 350 |  |  | NPDOC | 47 |  |  |  | 1991-04-20 | 22:00 | 1555.5 | 25 | 90 | 61 | 53.7049 | 0 | 6.1 | 7.9 |  | 14 | 14 | 0.43571 | 0 | 10.8444 | 10.6822 | 4.2041 | 17.591 | 0.60725 | [11 empty] | 90 | 82 | 62 | 3.9 | 10.1 | 14 | 14 | 0.30509 | 0.27857 | 10.4 | 10.2444 | 3.6667 | 20.3333 | 0.50382 | [10 empty] | 82 | 61 | 39 | 2.2 | 7.9 | 10.1 | 10.1 | 0.45573 | 0.21782 | 11.7333 | 11.5578 | 4.144 | 28.356 | 0.4076 | [10 empty] | Bromide | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | [8 empty] | Bromide | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | [8 empty] | Bromide | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | [8 empty] | Bromide | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0!
ICR Treatment Plant Identification Number | 283 | Purchase price for an equivalent 8" x 40 " element ($) | 1500 | Calculate the Minimum Recycle Flow Rates for Each Stage1 |  | Chloride | 98 |  |  |  | 1991-04-21 | 5:10 | 1562.7 | 25.6 | 92 | 60 | 52.9231 | 0 | 6.5 | 8 |  | 14.5 | 14.5 | 0.44828 | 0 | 11.5556 | 11.1826 | 4.2041 | 18.8728 | 0.59252 | [11 empty] | 92 | 82 | 60 | 4.2 | 10.3 | 14.5 | 14.5 | 0.31395 | 0.28966 | 11.2 | 10.8385 | 3.6667 | 23.3333 | 0.46451 | [10 empty] | 82 | 60 | 40 | 2.3 | 8 | 10.3 | 10.3 | 0.46332 | 0.2233 | 12.2667 | 11.8707 | 4.144 | 26.856 | 0.44201 | [10 empty] | SDS-Cl2 dose | mg/L | 5 | 25 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L |  |  | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L |  |  | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L |  |  | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L |  |  | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection
PWSID Number of Plant (if assigned) | FL 3051447 |  |  | Minimum recycle flow rate for stage 1, (QR-s(1))min (gpm) | 3.2692 | Total Hardness | 150 |  |  |  | 1991-04-21 | 12:00 | 1569.5 | 25.6 | 92 | 61 | 53.0938 | 0 | 6.4 | 7.9 |  | 14.3 | 14.3 | 0.44755 | 0 | 11.3778 | 11.0105 | 4.2041 | 19.2021 | 0.5734 | [11 empty] | 92 | 82 | 61 | 4.1 | 10.2 | 14.3 | 14.3 | 0.31015 | 0.28671 | 10.9333 | 10.5804 | 3.6667 | 22.3333 | 0.47375 | [10 empty] | 82 | 61 | 39 | 2.3 | 7.9 | 10.2 | 10.2 | 0.45826 | 0.22549 | 12.2667 | 11.8707 | 4.144 | 28.356 | 0.41863 | [10 empty] | SDS-Free Cl2 residual | mg/L | 0.2 | 0.2 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.21 |  |  |  |  | SDS-Free Cl2 residual | mg/L |  |  | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | [5 empty] | SDS-Free Cl2 residual | mg/L |  |  | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | [5 empty] | SDS-Free Cl2 residual | mg/L |  |  | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | [5 empty] | SDS-Free Cl2 residual | mg/L |  |  | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal)
Historical Minimum Water Temperature (oC) | 13.3 | Additional Information |  | Minimum recycle flow rate for stage 2, (QR-s(2))min (gpm) | 0.76923 | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | 1991-04-21 | 21:45 | 1579.3 | 25.6 | 92 | 61 | 52.4531 | 0 | 6.4 | 7.9 |  | 14.3 | 14.3 | 0.44755 | 0 | 11.3778 | 11.0105 | 4.2041 | 19.8428 | 0.55489 | [11 empty] | 92 | 81 | 60 | 4.1 | 10.2 | 14.3 | 14.3 | 0.31015 | 0.28671 | 10.9333 | 10.5804 | 3.6667 | 22.8333 | 0.46338 | [10 empty] | 81 | 61 | 39 | 2.3 | 7.9 | 10.2 | 10.2 | 0.45826 | 0.22549 | 12.2667 | 11.8707 | 4.144 | 27.856 | 0.42615 | [10 empty] | SDS-Cl2 demand | mg/L | 4.8 | 24.8 | --- | 40.5143 | --- | 80.6452 | 32.6571 | 85.3018 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 2.6 |  |  |  |  | SDS-Cl2 demand | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! |  |  | Stage 2 permeate flow rate during sample collection (gpm) | [5 empty] | SDS-Cl2 demand | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! |  |  | Stage 2 permeate flow rate during sample collection (gpm) | [5 empty] | SDS-Cl2 demand | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! |  |  | Stage 2 permeate flow rate during sample collection (gpm) | [5 empty] | SDS-Cl2 demand | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! |  |  | Stage 2 permeate flow rate during sample collection (gpm)
Historical Average Water Temperature (oC) | 24.5 | Design cross-flow velocity (fps) | 0.001 | 1: A negative minimum recycle flow rate indicates that recycle is not required to |  | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | 1991-04-22 | 4:00 | 1585.5 | 24.4 | 92 | 61 | 52.4531 | 0 | 6.4 | 7.9 |  | 14.3 | 14.3 | 0.44755 | 0 | 11.3778 | 11.4081 | 4.2041 | 19.8428 | 0.57492 | [11 empty] | 92 | 82 | 60 | 4.1 | 10.2 | 14.3 | 14.3 | 0.31015 | 0.28671 | 10.9333 | 10.9625 | 3.6667 | 23.3333 | 0.46982 | [10 empty] | 82 | 61 | 39 | 2.3 | 7.9 | 10.2 | 10.2 | 0.45826 | 0.22549 | 12.2667 | 12.2993 | 4.144 | 28.356 | 0.43375 | [10 empty] | SDS-Chlorination temp. | oC | 22 | 22 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 12.3 |  |  |  |  | SDS-Chlorination temp. | oC |  |  | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | [5 empty] | SDS-Chlorination temp. | oC |  |  | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | [5 empty] | SDS-Chlorination temp. | oC |  |  | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | [5 empty] | SDS-Chlorination temp. | oC |  |  | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm)
State Approved Plant Capacity (MGD) | 16.5 | Required influent flow to permeate flow rate ratio, QI:Qp | 5 | meet the manufacturer's minimum flow requirement. | [6 empty] | 1991-04-22 | 11:00 | 1592.5 | 24.4 | 92 | 60 | 50.5484 | 0 | 6.2 | 8 |  | 14.2 | 14.2 | 0.43662 | 0 | 11.0222 | 11.0516 | 4.2041 | 21.2475 | 0.52014 | [11 empty] | 92 | 82 | 58 | 4 | 10.2 | 14.2 | 14.2 | 0.30888 | 0.28169 | 10.6667 | 10.6951 | 3.6667 | 25.3333 | 0.42217 | [10 empty] | 82 | 60 | 37 | 2.2 | 8 | 10.2 | 10.2 | 0.46079 | 0.21569 | 11.7333 | 11.7646 | 4.144 | 29.856 | 0.39404 | [10 empty] | SDS-Chlorination pH | --- | 7.6 | 7.6 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- |  |  | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- |  |  | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- |  |  | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- |  |  | --- | --- | --- | --- | --- | ---
|  | Maximum element recovery (%) | 20 | [7 empty] | 1991-04-23 | 3:15 | 1608.7 | 24.4 | 92 | 58 | 51.0656 | 0 | 6.1 | 7.6 |  | 13.7 | 13.7 | 0.44526 | 0 | 10.8444 | 10.8733 | 4.2041 | 19.7303 | 0.5511 | [11 empty] | 92 | 80 | 59 | 3.9 | 9.8 | 13.7 | 13.7 | 0.29749 | 0.28467 | 10.4 | 10.4277 | 3.6667 | 23.3333 | 0.4469 | [10 empty] | 80 | 58 | 37 | 2.2 | 7.6 | 9.8 | 9.8 | 0.44054 | 0.22449 | 11.7333 | 11.7646 | 4.144 | 27.856 | 0.42234 | [10 empty] | SDS-Incubation time | hours | 96 | 96 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours |  |  | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours |  |  | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours |  |  | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours |  |  | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters
|  | Variability of design flux (%) | 15 | Calculate the Maximum Recycle Flow Rates for Each Stage | [6 empty] | 1991-04-24 | 10:00 | 1639.5 | 25 | 92 | 58 | 50.4262 | 0 | 6.1 | 7.6 |  | 13.7 | 13.7 | 0.44526 | 0 | 10.8444 | 10.6822 | 4.2041 | 20.3697 | 0.52442 | [11 empty] | 92 | 80 | 58 | 3.9 | 9.8 | 13.7 | 13.7 | 0.29749 | 0.28467 | 10.4 | 10.2444 | 3.6667 | 24.3333 | 0.421 | [10 empty] | 80 | 58 | 37 | 2.2 | 7.6 | 9.8 | 9.8 | 0.44054 | 0.22449 | 11.7333 | 11.5578 | 4.144 | 27.856 | 0.41491 | [10 empty] | SDS-TOX | mg Cl- /L | 77 | 1200 | --- | 2082.3571 | --- | 93.5833 | 1641.1786 | 95.3082 | Parameter | Units | Cp-s2-14 | CI-s2-14 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Parameter | Units | Cp-s2-16 | CI-s2-16 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Parameter | Units | Cp-s2-18 | CI-s2-18 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Parameter | Units | Cp-s2-20 | CI-s2-20 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Parameter | Units | Cp-s2-20 (dup) | CI-s2-20 (dup) | CC(calc) | RF (%) | CB | RB (%)
|  | Rejection of reference solute and conditions of test | 98% of 2000 mg/L MgSO4 at 100 psig | Maximum recycle flow rate for stage 1, (QR-s(1))max (gpm) | 11.0192 | [5 empty] | 1991-04-24 | 21:00 | 1650.5 | 25 | 82 | 50 | 44.9057 | 0 | 5.3 | 6.8 |  | 12.1 | 12.1 | 0.43802 | 0 | 9.4222 | 9.2812 | 4.2041 | 16.8902 | 0.5495 | [11 empty] | 72 | 70 | 51 | 3.4 | 8.7 | 12.1 | 12.1 | 0.26331 | 0.28099 | 9.0667 | 8.931 | 3.6667 | 16.3333 | 0.5468 | [10 empty] | 70 | 50 | 34 | 1.9 | 6.8 | 8.7 | 8.7 | 0.39243 | 0.21839 | 10.1333 | 9.9817 | 4.144 | 21.856 | 0.4567 | [10 empty] | SDS-CHCl3 | mg/L | 4 | 210 | --- | 371.8571 | --- | 98.0952 | 290.9286 | 98.6251 | Sampling date | MM/DD/YY | 1991-05-06 | 1991-05-06 | --- | --- | --- | --- | SDS-CHCl3 | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Sampling date | MM/DD/YY |  |  | --- | --- | --- | --- | SDS-CHCl3 | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Sampling date | MM/DD/YY |  |  | --- | --- | --- | --- | SDS-CHCl3 | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Sampling date | MM/DD/YY |  |  | --- | --- | --- | --- | SDS-CHCl3 | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Sampling date | MM/DD/YY |  |  | --- | --- | --- | ---
|  | (e.g., solute type and concentration) |  | Maximum recycle flow rate for stage 2, (QR-s(2))max (gpm) | 4.6442 | [5 empty] | 1991-04-25 | 6:00 | 1659.5 | 25.6 | 82 | 50 | 44.0769 | 0 | 5.2 | 7 |  | 12.2 | 12.2 | 0.42623 | 0 | 9.2444 | 8.9461 | 4.2041 | 17.719 | 0.50489 | [11 empty] | 82 | 70 | 51 | 3.4 | 8.8 | 12.2 | 12.2 | 0.26584 | 0.27869 | 9.0667 | 8.774 | 3.6667 | 21.3333 | 0.41128 | [10 empty] | 70 | 50 | 31 | 1.8 | 7 | 8.8 | 8.8 | 0.40003 | 0.20455 | 9.6 | 9.2901 | 4.144 | 24.856 | 0.37376 | [10 empty] | SDS-BDCM | mg/L | 12 | 77 | --- | 128.0714 | --- | 84.4156 | 102.5357 | 88.2968 | Sampling time | hh:mm | 14:00 | 14:00 | --- | --- | --- | --- | SDS-BDCM | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Sampling time | hh:mm |  |  | --- | --- | --- | --- | SDS-BDCM | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Sampling time | hh:mm |  |  | --- | --- | --- | --- | SDS-BDCM | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Sampling time | hh:mm |  |  | --- | --- | --- | --- | SDS-BDCM | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Sampling time | hh:mm |  |  | --- | --- | --- | ---
|  | Variability of rejection of reference solute (%) | [8 empty] | 1991-04-25 | 11:00 | 1664.5 | 25.6 | 80 | 50 | 42.963 | 0 | 5.4 | 7.1 |  | 12.5 | 12.5 | 0.432 | 0 | 9.6 | 9.2901 | 4.2041 | 17.8329 | 0.52095 | [11 empty] | 80 | 68 | 50 | 3.5 | 9 | 12.5 | 12.5 | 0.27217 | 0.28 | 9.3333 | 9.0321 | 3.6667 | 20.3333 | 0.4442 | [10 empty] | 68 | 50 | 30 | 1.9 | 7.1 | 9 | 9 | 0.40762 | 0.21111 | 10.1333 | 9.8063 | 4.144 | 24.856 | 0.39452 | [10 empty] | SDS-DBCM | mg/L | 21 | 26 | --- | 29.9286 | --- | 19.2308 | 27.9643 | 24.9042 | Operation time | hh.hh | 1898.5 | 1898.5 | --- | --- | --- | --- | SDS-DBCM | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Operation time | hh.hh |  |  | --- | --- | --- | --- | SDS-DBCM | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Operation time | hh.hh |  |  | --- | --- | --- | --- | SDS-DBCM | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Operation time | hh.hh |  |  | --- | --- | --- | --- | SDS-DBCM | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Operation time | hh.hh |  |  | --- | --- | --- | ---
|  | Standard testing recovery (%) | 10 | Select the Design System Recycle Flow Rate2 | [6 empty] | 1991-04-26 | 22:00 | 1697.5 | 25 | 88 | 60 | 50.5424 | 0 | 5.9 | 7.6 |  | 13.5 | 13.5 | 0.43704 | 0 | 10.4889 | 10.332 | 4.2041 | 19.2535 | 0.53663 | [11 empty] | 88 | 79 | 58 | 3.7 | 9.8 | 13.5 | 13.5 | 0.29496 | 0.27407 | 9.8667 | 9.719 | 3.6667 | 21.8333 | 0.44515 | [10 empty] | 79 | 60 | 38 | 2.2 | 7.6 | 9.8 | 9.8 | 0.44054 | 0.22449 | 11.7333 | 11.5578 | 4.144 | 27.356 | 0.4225 | [10 empty] | SDS-CHBr3 | mg/L | 12 | 10 | --- | 8.4286 | --- | -20 | 9.2143 | -30.2326 | pH | --- | 4.7 | 4.4 | --- | --- | --- | --- | SDS-CHBr3 | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | pH | --- |  |  | --- | --- | --- | --- | SDS-CHBr3 | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | pH | --- |  |  | --- | --- | --- | --- | SDS-CHBr3 | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | pH | --- |  |  | --- | --- | --- | --- | SDS-CHBr3 | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | pH | --- |  |  | --- | --- | --- | ---
|  | Standard testing pH | 7 | Minimum system recycle flow rate, (QR-sys)min (gpm) | 3.2692 | [5 empty] | 1991-04-27 | 12:00 | 1709.5 | 25.6 | 71 | 50 | 38.3953 | 0 | 4.3 | 6.3 |  | 10.6 | 10.6 | 0.40566 | 0 | 7.6444 | 7.3977 | 4.2041 | 17.9005 | 0.41327 | [11 empty] | 71 | 65 | 41 | 2.9 | 7.7 | 10.6 | 10.6 | 0.23166 | 0.27358 | 7.7333 | 7.4837 | 3.6667 | 23.3333 | 0.32073 | [10 empty] | 65 | 50 | 33 | 1.4 | 6.3 | 7.7 | 7.7 | 0.35446 | 0.18182 | 7.4667 | 7.2257 | 4.144 | 20.356 | 0.35496 | [10 empty] | SDS-THM4 | mg/L | 49 | 323 | --- | 538.2857 | --- | 84.8297 | 430.6429 | 88.6217 | Temperature | oC | 27.8 | 27.8 | --- | --- | --- | --- | SDS-THM4 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Temperature | oC |  |  | --- | --- | --- | --- | SDS-THM4 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Temperature | oC |  |  | --- | --- | --- | --- | SDS-THM4 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Temperature | oC |  |  | --- | --- | --- | --- | SDS-THM4 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Temperature | oC |  |  | --- | --- | --- | ---
|  | Acceptable range of operating pressures | 70 - 500 psig | Maximum system recycle flow rate, (QR-sys)max (gpm) | 4.6442 | [5 empty] | 1991-04-28 | 17:30 | 1733 | 27.2 | 83 | 57 | 51.4717 | 0 | 5.3 | 7.6 |  | 12.9 | 12.9 | 0.41085 | 0 | 9.4222 | 8.6969 | 4.2041 | 14.3242 | 0.60715 | [11 empty] | 83 | 74 | 59 | 3.4 | 9.5 | 12.9 | 12.9 | 0.28356 | 0.26357 | 9.0667 | 8.3687 | 3.6667 | 15.8333 | 0.52855 | [10 empty] | 74 | 57 | 38 | 1.9 | 7.6 | 9.5 | 9.5 | 0.43294 | 0.2 | 10.1333 | 9.3533 | 4.144 | 23.356 | 0.40047 | [10 empty] | SDS-MCAA* | mg/L | 3 | 8 | --- | 11.9286 | --- | 62.5 | 9.9643 | 69.8925 | Alkalinity | mg/L as CaCO3 | BMRL | BMRL | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Acceptable range of operating pH values | 2 - 11 | Design system recycle flow rate, QR-sys (gpm) | [6 empty] | 1991-04-29 | 21:00 | 1747.5 | 27.7 | 85 | 51 | 50.8302 | 0 | 5.3 | 7.5 |  | 12.8 | 12.8 | 0.41406 | 0 | 9.4222 | 8.5693 | 4.2041 | 12.9657 | 0.66092 | [11 empty] | 85 | 75 | 58 | 3.4 | 9.4 | 12.8 | 12.8 | 0.28103 | 0.26562 | 9.0667 | 8.2459 | 3.6667 | 18.3333 | 0.44978 | [10 empty] | 75 | 51 | 38 | 1.9 | 7.5 | 9.4 | 9.4 | 0.42788 | 0.20213 | 10.1333 | 9.2161 | 4.144 | 20.856 | 0.44189 | [10 empty] | SDS-DCAA* | mg/L | 5 | 98 | --- | 171.0714 | --- | 94.898 | 134.5357 | 96.2835 | Total dissolved solids | mg/L | 270 | 520 | 587.0103 | 34.1463 | 553.5052 | 51.22 | SDS-DCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Typical pressure drop across a single element (psi) | <10 | System influent flow rate, QI-sys (gpm) | 12.9808 | [5 empty] | 1991-04-30 | 6:00 | 1756.5 | 27.7 | 85 | 52 | 49.2807 | 0 | 5.7 | 7.3 |  | 13 | 13 | 0.43846 | 0 | 10.1333 | 9.2161 | 4.2041 | 15.0152 | 0.61378 | [11 empty] | 85 | 75 | 57 | 3.5 | 9.5 | 13 | 13 | 0.28483 | 0.26923 | 9.3333 | 8.4885 | 3.6667 | 19.3333 | 0.43906 | [10 empty] | 75 | 52 | 37 | 2.2 | 7.3 | 9.5 | 9.5 | 0.42535 | 0.23158 | 11.7333 | 10.6712 | 4.144 | 22.356 | 0.47733 | [10 empty] | SDS-TCAA* | mg/L | 1 | 140 | --- | 249.2143 | --- | 99.2857 | 194.6071 | 99.4861 | Total hardness | mg/L as CaCO3 | 61 | 220 | 262.6186 | 66.1111 | 241.3093 | 74.7212 | SDS-TCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Maximum permissible SDI | 5 | Recycle ratio, r | 0 | [5 empty] | 1991-04-30 | 11:00 | 1761.5 | 27.7 | 80 | 55 | 48.8302 | 0 | 5.3 | 7.5 |  | 12.8 | 12.8 | 0.41406 | 0 | 9.4222 | 8.5693 | 4.2041 | 14.4657 | 0.59239 | [11 empty] | 80 | 72 | 56 | 3.4 | 9.4 | 12.8 | 12.8 | 0.28103 | 0.26562 | 9.0667 | 8.2459 | 3.6667 | 16.3333 | 0.50485 | [10 empty] | 72 | 55 | 36 | 1.9 | 7.5 | 9.4 | 9.4 | 0.42788 | 0.20213 | 10.1333 | 9.2161 | 4.144 | 23.356 | 0.39459 | [10 empty] | SDS-MBAA* | mg/L | BMRL | 3 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 50 | 170 | 202.1649 | 61.5385 | 186.0825 | 73.1302 | SDS-MBAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Maximum permissible turbidity (ntu) | 1 | 2: The design system recycle flow rate must fall between the minimum and | [6 empty] | 1991-04-30 | 22:00 | 1772.5 | 27.7 | 85 | 52 | 49.8302 | 0 | 5.3 | 7.5 |  | 12.8 | 12.8 | 0.41406 | 0 | 9.4222 | 8.5693 | 4.2041 | 14.4657 | 0.59239 | [11 empty] | 85 | 75 | 57 | 3.4 | 9.4 | 12.8 | 12.8 | 0.28103 | 0.26562 | 9.0667 | 8.2459 | 3.6667 | 19.3333 | 0.42651 | [10 empty] | 75 | 52 | 37 | 1.9 | 7.5 | 9.4 | 9.4 | 0.42788 | 0.20213 | 10.1333 | 9.2161 | 4.144 | 22.356 | 0.41224 | [10 empty] | SDS-DBAA* | mg/L | 8 | 9 | --- | 9.7857 | --- | 11.1111 | 9.3929 | 14.8289 | Turbidity | ntu | BMRL | 0.3 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DBAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DBAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DBAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | 1000 ppm - hours | maximum system recycle flow rates. | [6 empty] | 1991-05-01 | 14:00 | 1788.5 | 27.7 | 84 | 52 | 49.0769 | 0 | 5.2 | 7.5 |  | 12.7 | 12.7 | 0.40945 | 0 | 9.2444 | 8.4076 | 4.2041 | 14.719 | 0.57121 | [11 empty] | 84 | 73 | 56 | 3.4 | 9.3 | 12.7 | 12.7 | 0.2785 | 0.26772 | 9.0667 | 8.2459 | 3.6667 | 18.8333 | 0.43784 | [10 empty] | 73 | 52 | 36 | 1.8 | 7.5 | 9.3 | 9.3 | 0.42535 | 0.19355 | 9.6 | 8.731 | 4.144 | 22.356 | 0.39054 | [10 empty] | SDS-BCAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.8 | 12 | 15.0021 | 91.1111 | 13.501 | 94.0745 | SDS-BCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-BCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-BCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-BCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | 1: All of the information requested in this field may not be available, but values for all of the Design | [8 empty] | 1991-05-01 | 21:00 | 1795.5 | 27.7 | 84 | 52 | 48.1887 | 0 | 5.3 | 7.5 |  | 12.8 | 12.8 | 0.41406 | 0 | 9.4222 | 8.5693 | 4.2041 | 15.6072 | 0.54906 | [11 empty] | 84 | 73 | 55 | 3.4 | 9.4 | 12.8 | 12.8 | 0.28103 | 0.26562 | 9.0667 | 8.2459 | 3.6667 | 19.8333 | 0.41576 | [10 empty] | 73 | 52 | 36 | 1.9 | 7.5 | 9.4 | 9.4 | 0.42788 | 0.20213 | 10.1333 | 9.2161 | 4.144 | 22.356 | 0.41224 | [10 empty] | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | UV254 | cm-1 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | UV254 | cm-1 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | UV254 | cm-1 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | UV254 | cm-1 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Parameters must be entered in cells E15:E26, since these parameters are used in calculations. |  | Summary of the Stage and System Flow Rates | [6 empty] | 1991-05-02 | 6:00 | 1804.5 | 28.3 | 84 | 52 | 48.7692 | 0 | 5.2 | 7.5 |  | 12.7 | 12.7 | 0.40945 | 0 | 9.2444 | 8.2598 | 4.2041 | 15.0267 | 0.54968 | [11 empty] | 84 | 75 | 55 | 3.4 | 9.3 | 12.7 | 12.7 | 0.2785 | 0.26772 | 9.0667 | 8.101 | 3.6667 | 20.8333 | 0.38885 | [10 empty] | 75 | 52 | 37 | 1.8 | 7.5 | 9.3 | 9.3 | 0.42535 | 0.19355 | 9.6 | 8.5775 | 4.144 | 22.356 | 0.38368 | [10 empty] | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | NR | --- | --- | --- | --- | SDS-CDBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | --- | --- | --- | --- | SDS-CDBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | --- | --- | --- | --- | SDS-CDBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | --- | --- | --- | --- | SDS-CDBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | --- | --- | --- | ---
|  |  |  | Influent flow rate to stage 1, QI-s(1) (gpm) | 12.9808 | [5 empty] | 1991-05-02 | 9:00 | 1807.5 | 28.305 | 82 | 54 | 48.5472 | 0 | 5.3 | 7.5 |  | 12.8 | 12.8 | 0.41406 | 0 | 9.4222 | 8.4174 | 4.2041 | 15.2487 | 0.55201 | [11 empty] | 82 | 73 | 55 | 3.4 | 9.4 | 12.8 | 12.8 | 0.28103 | 0.26562 | 9.0667 | 8.0998 | 3.6667 | 18.8333 | 0.43008 | [10 empty] | 73 | 54 | 37 | 1.9 | 7.5 | 9.4 | 9.4 | 0.42788 | 0.20213 | 10.1333 | 9.0527 | 4.144 | 22.356 | 0.40493 | [10 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | [8 empty] | SDS-DCBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | [8 empty] | SDS-DCBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | [8 empty] | SDS-DCBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  |  |  | Permeate flow rate from stage 1, Qp-s(1) (gpm) | 5.625 | [5 empty] | 1991-05-02 | 17:00 | 1807.5 | 28.3 | 89 | 40 | 35.0345 | 0 | 8.7 | 10.7 | X | 19.4 | 19.4 | 0.44845 | 0 | 15.4667 | 13.8193 | 4.2041 | 25.2614 | 0.54705 | [11 empty] | 89 | 72 | 44 | 5.7 | 13.7 | 19.4 | 19.4 | 0.41902 | 0.29381 | 15.2 | 13.5811 | 3.6667 | 32.8333 | 0.41364 | [10 empty] | 72 | 40 | 18 | 3 | 10.7 | 13.7 | 13.7 | 0.61777 | 0.21898 | 16 | 14.2959 | 4.144 | 33.856 | 0.42225 | [10 empty] | SDS-HAA5 | mg/L | 17 | 258 | --- | 447.3571 | --- | 93.4109 | 352.6786 | 95.1797 | [8 empty] | SDS-HAA5 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | [8 empty] | SDS-HAA5 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | [8 empty] | SDS-HAA5 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | [8 empty] | SDS-HAA5 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  |  |  | Concentrate flow rate from stage 1, QC-s(1) (gpm) | 7.3558 | [5 empty] | 1991-05-03 | 6:00 | 1820.5 | 27.7 | 90 | 40 | 34.4773 | 0 | 8.8 | 10.2 |  | 19 | 19 | 0.46316 | 0 | 15.6444 | 14.2283 | 2.6451 | 27.8776 | 0.51038 | [11 empty] | 90 | 72 | 43 | 5.8 | 13.2 | 19 | 19 | 0.40762 | 0.30526 | 15.4667 | 14.0666 | 2.5439 | 35.4561 | 0.39673 | [10 empty] | 72 | 40 | 18 | 3 | 10.2 | 13.2 | 13.2 | 0.59245 | 0.22727 | 16 | 14.5517 | 2.8351 | 35.1649 | 0.41381 | [10 empty] | SDS-HAA6 | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-HAA6 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | [8 empty] | SDS-HAA6 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | [8 empty] | SDS-HAA6 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | [8 empty] | SDS-HAA6 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  |  |  | Influent flow rate to stage 2, QI-s(2) (gpm) | 7.3558 | [5 empty] | 1991-05-03 | 9:30 | 1824 | 27.7 | 90 | 40 | 36.4706 | 0 | 8.5 | 10.5 |  | 19 | 19 | 0.44737 | 0 | 15.1111 | 13.7432 | 2.6451 | 25.8843 | 0.53095 | [11 empty] | 90 | 72 | 46 | 5.5 | 13.5 | 19 | 19 | 0.41142 | 0.28947 | 14.6667 | 13.339 | 2.5439 | 32.4561 | 0.41099 | [10 empty] | 72 | 40 | 19 | 3 | 10.5 | 13.5 | 13.5 | 0.60764 | 0.22222 | 16 | 14.5517 | 2.8351 | 34.1649 | 0.42592 | [10 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
|  |  |  | Permeate flow rate from stage 2, Qp-s(2) (gpm) | 2.8125 | [5 empty] | 1991-05-03 | 19:00 | 1831.5 | 27.7 | 91 | 44 | 39.1176 | 0 | 8.5 | 10.5 |  | 19 | 19 | 0.44737 | 0 | 15.1111 | 13.7432 | 2.6451 | 25.7373 | 0.53398 | [11 empty] | 91 | 76 | 49 | 5.5 | 13.5 | 19 | 19 | 0.41142 | 0.28947 | 14.6667 | 13.339 | 2.5439 | 31.9561 | 0.41742 | [10 empty] | 76 | 44 | 21 | 3 | 10.5 | 13.5 | 13.5 | 0.60764 | 0.22222 | 16 | 14.5517 | 2.8351 | 36.1649 | 0.40237 | [10 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
|  |  |  | Concentrate flow rate from stage 2, QC-s(2) (gpm) | 4.5433 | [5 empty] | 1991-05-04 | 11:00 | 1847.5 | 28.3 | 90 | 42 | 37.4706 | 0 | 8.5 | 10.5 |  | 19 | 19 | 0.44737 | 0 | 15.1111 | 13.5016 | 2.6451 | 25.8843 | 0.52161 | [11 empty] | 90 | 75 | 47 | 5.5 | 13.5 | 19 | 19 | 0.41142 | 0.28947 | 14.6667 | 13.1045 | 2.5439 | 32.9561 | 0.39764 | [10 empty] | 75 | 42 | 20 | 3 | 10.5 | 13.5 | 13.5 | 0.60764 | 0.22222 | 16 | 14.2959 | 2.8351 | 35.6649 | 0.40084
|  |  |  | System concentrate recycle flow rate, QR-sys (gpm) | 0 | [5 empty] | 1991-05-04 | 22:00 | 1858.5 | 28.3 | 90 | 42 | 35.1765 | 0 | 8.5 | 10.4 |  | 18.9 | 18.9 | 0.44974 | 0 | 15.1111 | 13.5016 | 2.6451 | 28.1784 | 0.47915 | [11 empty] | 90 | 74 | 44 | 5.5 | 13.4 | 18.9 | 18.9 | 0.40889 | 0.29101 | 14.6667 | 13.1045 | 2.5439 | 35.4561 | 0.3696 | [10 empty] | 74 | 42 | 19 | 3 | 10.4 | 13.4 | 13.4 | 0.60258 | 0.22388 | 16 | 14.2959 | 2.8351 | 36.1649 | 0.3953 | [10 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs
|  |  |  | System concentrate waste flow rate, QW-sys (gpm) | 4.5433 | [5 empty] | 1991-05-05 | 7:00 | 1867.5 | 27.2 | 92 | 40 | 39.7284 | 0 | 8.1 | 9.1 |  | 17.2 | 17.2 | 0.47093 | 0 | 14.4 | 13.2915 | 2.6451 | 23.6265 | 0.56257 | [11 empty] | 92 | 70 | 50 | 5.5 | 11.7 | 17.2 | 17.2 | 0.36585 | 0.31977 | 14.6667 | 13.5376 | 2.5439 | 28.4561 | 0.47574 | [10 empty] | 70 | 40 | 18 | 2.6 | 9.1 | 11.7 | 11.7 | 0.52662 | 0.22222 | 13.8667 | 12.7992 | 2.8351 | 34.1649 | 0.37463 | [11 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls
|  |  |  | System permeate flow rate, Qp-sys (gpm) | 8.4375 | [5 empty] | 1991-05-05 | 11:00 | 1871.5 | 27.2 | 92 | 38 | 34.2208 | 0 | 7.7 | 9.7 |  | 17.4 | 17.4 | 0.44253 | 0 | 13.6889 | 12.6351 | 2.6451 | 28.1341 | 0.4491 | [11 empty] | 92 | 69 | 43 | 5.1 | 12.3 | 17.4 | 17.4 | 0.37598 | 0.2931 | 13.6 | 12.5531 | 2.5439 | 34.9561 | 0.35911 | [10 empty] | 69 | 38 | 17 | 2.6 | 9.7 | 12.3 | 12.3 | 0.557 | 0.21138 | 13.8667 | 12.7992 | 2.8351 | 33.6649 | 0.38019 | [11 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2
|  |  |  | System feed flow rate, QF-sys (gpm) | 12.9808 | [5 empty] | 1991-05-05 | 22:00 | 1882.5 | 27.2 | 99 | 32 | 33.5375 | 0 | 8 | 9.2 |  | 17.2 | 17.2 | 0.46512 | 0 | 14.2222 | 13.1274 | 2.6451 | 29.3174 | 0.44777 | [11 empty] | 99 | 68 | 44 | 5.3 | 11.9 | 17.2 | 17.2 | 0.36838 | 0.30814 | 14.1333 | 13.0453 | 2.5439 | 36.9561 | 0.353 | [10 empty] | 68 | 32 | 13 | 2.7 | 9.2 | 11.9 | 11.9 | 0.53422 | 0.22689 | 14.4 | 13.2915 | 2.8351 | 34.1649 | 0.38904 | [10 empty] | Qp/QT (THM4), % | 91.6058 | 104.7445 |  | Qp/QT (HAA5), % | 84.6473 | 95.8506 | [11 empty] | Qp/QT (THM4), % | #DIV/0! | #DIV/0! |  | Qp/QT (HAA5), % | #DIV/0! | #DIV/0! | [11 empty] | Qp/QT (THM4), % | #DIV/0! | #DIV/0! |  | Qp/QT (HAA5), % | #DIV/0! | #DIV/0! | [11 empty] | Qp/QT (THM4), % | #DIV/0! | #DIV/0! |  | Qp/QT (HAA5), % | #DIV/0! | #DIV/0! | [11 empty] | Qp/QT (THM4), % | #DIV/0! | #DIV/0! |  | Qp/QT (HAA5), % | #DIV/0! | #DIV/0!
[11 empty] | 1991-05-06 | 4:00 | 1888.5 | 27.7 | 99 | 32 | 33.875 | 0 | 8 | 9.2 |  | 17.2 | 17.2 | 0.46512 | 0 | 14.2222 | 12.9348 | 2.6451 | 28.9799 | 0.44634 | [11 empty] | 99 | 68 | 44 | 5.3 | 11.9 | 17.2 | 17.2 | 0.36838 | 0.30814 | 14.1333 | 12.854 | 2.5439 | 36.9561 | 0.34782 | [10 empty] | 68 | 32 | 14 | 2.7 | 9.2 | 11.9 | 11.9 | 0.53422 | 0.22689 | 14.4 | 13.0965 | 2.8351 | 33.1649 | 0.39489 | [10 empty] | SDS-THM4b, mg/L | 72 | NA |  | SDS-THM4b, mg/L | 91.0664 | 60.3693 | [11 empty] | SDS-THM4b, mg/L | #DIV/0! | #DIV/0! |  | SDS-THM4b, mg/L | #DIV/0! | #DIV/0! | [11 empty] | SDS-THM4b, mg/L | #DIV/0! | #DIV/0! |  | SDS-THM4b, mg/L | #DIV/0! | #DIV/0! | [11 empty] | SDS-THM4b, mg/L | #DIV/0! | #DIV/0! |  | SDS-THM4b, mg/L | #DIV/0! | #DIV/0! | [11 empty] | SDS-THM4b, mg/L | #DIV/0! | #DIV/0! |  | SDS-THM4b, mg/L | #DIV/0! | #DIV/0!
|  |  |  | Calculate the Required System Influent Pressure | [6 empty] | 1991-05-06 | 14:00 | 1898.5 | 27.7 | 98 | 37 | 35.6667 | 0 | 7.8 | 9.7 |  | 17.5 | 17.5 | 0.44571 | 0 | 13.8667 | 12.6114 | 2.6639 | 29.1694 | 0.43235 | 7.6 | 4.5 | 220 | 340 | 410 | 590 | 562.7835 | 4.613 | 46.3415 | 486.3918 | 54.769 | 98 | 69 | 45 | 5.2 | 12.3 | 17.5 | 17.5 | 0.37724 | 0.29714 | 13.8667 | 12.6114 | 2.5439 | 35.9561 | 0.35075 | 4.5 | 4.4 | 200 | 410 | 520 | 498.7805 | 4.0807 | 51.2195 | 454.3902 | 55.985 | 69 | 37 | 17 | 2.6 | 9.7 | 12.3 | 12.3 | 0.557 | 0.21138 | 13.8667 | 12.6114 | 2.8351 | 33.1649 | 0.38026 | 4.4 | 4.4 | 270 | 520 | 590 | 587.0103 | 0.50673 | 34.1463 | 553.5052 | 51.22 | SDS-HAA5b, mg/L | 37.2299 | NA |  | SDS-HAA5b, mg/L | 54 | 27 | [11 empty] | SDS-HAA5b, mg/L | #DIV/0! | #DIV/0! |  | SDS-HAA5b, mg/L | #DIV/0! | #DIV/0! | [11 empty] | SDS-HAA5b, mg/L | #DIV/0! | #DIV/0! |  | SDS-HAA5b, mg/L | #DIV/0! | #DIV/0! | [11 empty] | SDS-HAA5b, mg/L | #DIV/0! | #DIV/0! |  | SDS-HAA5b, mg/L | #DIV/0! | #DIV/0! | [11 empty] | SDS-HAA5b, mg/L | #DIV/0! | #DIV/0! |  | SDS-HAA5b, mg/L | #DIV/0! | #DIV/0!
|  |  |  | Osmotic pressure for stage 13, Dp1 (psi) | 3 | [5 empty] | 1991-05-06 | 22:00 | 1906.5 | 27.7 | 100 | 40 | 39.4118 | 0 | 8.5 | 10.2 |  | 18.7 | 18.7 | 0.45455 | 0 | 15.1111 | 13.7432 | 2.6451 | 27.9431 | 0.49183 | [11 empty] | 100 | 75 | 50 | 5.5 | 13.2 | 18.7 | 18.7 | 0.40383 | 0.29412 | 14.6667 | 13.339 | 2.5439 | 34.9561 | 0.38159 | [10 empty] | 75 | 40 | 20 | 3 | 10.2 | 13.2 | 13.2 | 0.59245 | 0.22727 | 16 | 14.5517 | 2.8351 | 34.6649 | 0.41978 | [10 empty] | SDS-TOXb, mg Cl- /L | 171.2664 | NA |  | SDS-TOXb, mg Cl- /L | 249.4108 | 123.5975 | [11 empty] | SDS-TOXb, mg Cl- /L | #DIV/0! | #DIV/0! |  | SDS-TOXb, mg Cl- /L | #DIV/0! | #DIV/0! | [11 empty] | SDS-TOXb, mg Cl- /L | #DIV/0! | #DIV/0! |  | SDS-TOXb, mg Cl- /L | #DIV/0! | #DIV/0! | [11 empty] | SDS-TOXb, mg Cl- /L | #DIV/0! | #DIV/0! |  | SDS-TOXb, mg Cl- /L | #DIV/0! | #DIV/0! | [11 empty] | SDS-TOXb, mg Cl- /L | #DIV/0! | #DIV/0! |  | SDS-TOXb, mg Cl- /L | #DIV/0! | #DIV/0!
|  |  |  | Osmotic pressure for stage 23, Dp2 (psi) | 6 | [5 empty] | 1991-05-07 | 4:15 | 1912.8 | 27.7 | 95 | 41 | 37.85 | 0 | 8 | 10.2 |  | 18.2 | 18.2 | 0.43956 | 0 | 14.2222 | 12.9348 | 2.6451 | 27.5049 | 0.47027 | [11 empty] | 95 | 73 | 48 | 5.2 | 13 | 18.2 | 18.2 | 0.39497 | 0.28571 | 13.8667 | 12.6114 | 2.5439 | 33.4561 | 0.37695 | [10 empty] | 73 | 41 | 19 | 2.8 | 10.2 | 13 | 13 | 0.58738 | 0.21538 | 14.9333 | 13.5815 | 2.8351 | 35.1649 | 0.38622 | [10 empty] | SDS-CDb, mg/L | 6.4788 | NA |  | SDS-CDb, mg/L | 7.8705 | 5.6299 | [11 empty] | SDS-CDb, mg/L | #DIV/0! | #DIV/0! |  | SDS-CDb, mg/L | #DIV/0! | #DIV/0! | [11 empty] | SDS-CDb, mg/L | #DIV/0! | #DIV/0! |  | SDS-CDb, mg/L | #DIV/0! | #DIV/0! | [11 empty] | SDS-CDb, mg/L | #DIV/0! | #DIV/0! |  | SDS-CDb, mg/L | #DIV/0! | #DIV/0! | [11 empty] | SDS-CDb, mg/L | #DIV/0! | #DIV/0! |  | SDS-CDb, mg/L | #DIV/0! | #DIV/0!
|  |  |  | Pressure losses due to stage hardware, DPs (psi) | 3 | [5 empty] | 1991-05-07 | 11:00 | 1919.5 | 27.7 | 99 | 41 | 39.4118 | 0 | 8.5 | 10.2 |  | 18.7 | 18.7 | 0.45455 | 0 | 15.1111 | 13.7432 | 2.6451 | 27.9431 | 0.49183 | [11 empty] | 99 | 75 | 50 | 5.5 | 13.2 | 18.7 | 18.7 | 0.40383 | 0.29412 | 14.6667 | 13.339 | 2.5439 | 34.4561 | 0.38713 | [10 empty] | 75 | 41 | 20 | 3 | 10.2 | 13.2 | 13.2 | 0.59245 | 0.22727 | 16 | 14.5517 | 2.8351 | 35.1649 | 0.41381 | [10 empty] | TOCb, mg/L | 1.3051 | NA |  | TOCb, mg/L | 1.8896 | 0.94855 | [11 empty] | TOCb, mg/L | #DIV/0! | #DIV/0! |  | TOCb, mg/L | #DIV/0! | #DIV/0! | [11 empty] | TOCb, mg/L | #DIV/0! | #DIV/0! |  | TOCb, mg/L | #DIV/0! | #DIV/0! | [11 empty] | TOCb, mg/L | #DIV/0! | #DIV/0! |  | TOCb, mg/L | #DIV/0! | #DIV/0! | [11 empty] | TOCb, mg/L | #DIV/0! | #DIV/0! |  | TOCb, mg/L | #DIV/0! | #DIV/0!
|  |  |  | Pressure losses in a single element, DPe (psi) | 3 | [5 empty] | 1991-05-07 | 21:00 | 1929.5 | 27.7 | 99 | 41 | 39.4118 | 0 | 8.5 | 10.2 |  | 18.7 | 18.7 | 0.45455 | 0 | 15.1111 | 13.7432 | 2.6451 | 27.9431 | 0.49183 | [11 empty] | 99 | 75 | 50 | 5.5 | 13.2 | 18.7 | 18.7 | 0.40383 | 0.29412 | 14.6667 | 13.339 | 2.5439 | 34.4561 | 0.38713 | [10 empty] | 75 | 41 | 20 | 3 | 10.2 | 13.2 | 13.2 | 0.59245 | 0.22727 | 16 | 14.5517 | 2.8351 | 35.1649 | 0.41381 | [10 empty] | UV254 b, cm-1 | #VALUE! | NA |  | UV254 b, cm-1 | #VALUE! | #VALUE! | [11 empty] | UV254 b, cm-1 | #DIV/0! | #DIV/0! |  | UV254 b, cm-1 | #DIV/0! | #DIV/0! | [11 empty] | UV254 b, cm-1 | #DIV/0! | #DIV/0! |  | UV254 b, cm-1 | #DIV/0! | #DIV/0! | [11 empty] | UV254 b, cm-1 | #DIV/0! | #DIV/0! |  | UV254 b, cm-1 | #DIV/0! | #DIV/0! | [11 empty] | UV254 b, cm-1 | #DIV/0! | #DIV/0! |  | UV254 b, cm-1 | #DIV/0! | #DIV/0!
|  |  |  | Design permeate pressure, Pp (psi) | 45 | [5 empty] | 1991-05-08 | 5:45 | 1938.3 | 27.2 | 92 | 40 | 36.3077 | 0 | 7.8 | 10.2 |  | 18 | 18 | 0.43333 | 0 | 13.8667 | 12.7992 | 2.6451 | 27.0472 | 0.47322 | [11 empty] | 92 | 72 | 46 | 5.1 | 12.9 | 18 | 18 | 0.39117 | 0.28333 | 13.6 | 12.5531 | 2.5439 | 33.4561 | 0.37521 | [10 empty] | 72 | 40 | 18 | 2.7 | 10.2 | 12.9 | 12.9 | 0.58485 | 0.2093 | 14.4 | 13.2915 | 2.8351 | 35.1649 | 0.37798 | [10 empty] | Bromideb, mg/L | #VALUE! | NA |  | Bromideb, mg/L | #VALUE! | #VALUE! | [11 empty] | Bromideb, mg/L | #DIV/0! | #DIV/0! |  | Bromideb, mg/L | #DIV/0! | #DIV/0! | [11 empty] | Bromideb, mg/L | #DIV/0! | #DIV/0! |  | Bromideb, mg/L | #DIV/0! | #DIV/0! | [11 empty] | Bromideb, mg/L | #DIV/0! | #DIV/0! |  | Bromideb, mg/L | #DIV/0! | #DIV/0! | [11 empty] | Bromideb, mg/L | #DIV/0! | #DIV/0! |  | Bromideb, mg/L | #DIV/0! | #DIV/0!
|  |  |  | Mechanical pressure losses per stage, Ls (psi) | 12 | [5 empty] | 1991-05-08 | 10:30 | 1943 | 27.2 | 90 | 40 | 35.6667 | 0 | 8.1 | 10.2 |  | 18.3 | 18.3 | 0.44262 | 0 | 14.4 | 13.2915 | 2.6451 | 26.6882 | 0.49803 | [11 empty] | 90 | 72 | 45 | 5.3 | 13 | 18.3 | 18.3 | 0.39623 | 0.28962 | 14.1333 | 13.0453 | 2.5439 | 33.4561 | 0.38992 | [10 empty] | 72 | 40 | 18 | 2.8 | 10.2 | 13 | 13 | 0.58738 | 0.21538 | 14.9333 | 13.7838 | 2.8351 | 35.1649 | 0.39197 | [10 empty] | Alkb, mg/L CaCO3 | #VALUE! | NA |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! | [11 empty] | Alkb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | Alkb, mg/L CaCO3 | #DIV/0! | #DIV/0! | [11 empty] | Alkb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | Alkb, mg/L CaCO3 | #DIV/0! | #DIV/0! | [11 empty] | Alkb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | Alkb, mg/L CaCO3 | #DIV/0! | #DIV/0! | [11 empty] | Alkb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | Alkb, mg/L CaCO3 | #DIV/0! | #DIV/0!
|  |  |  | Net driving pressure required for permeation, NDP (psi) | 76.1392 | [5 empty] | 1991-05-08 | 12:00 | 1944.5 | 27.2 | 91 | 41 | 36.55 | 0 | 8 | 10.2 |  | 18.2 | 18.2 | 0.43956 | 0 | 14.2222 | 13.1274 | 2.6451 | 26.8049 | 0.48974 | [11 empty] | 91 | 72 | 46 | 5.2 | 13 | 18.2 | 18.2 | 0.39497 | 0.28571 | 13.8667 | 12.7992 | 2.5439 | 32.9561 | 0.38837 | [10 empty] | 72 | 41 | 19 | 2.8 | 10.2 | 13 | 13 | 0.58738 | 0.21538 | 14.9333 | 13.7838 | 2.8351 | 34.6649 | 0.39763 | [10 empty] | T-Hdb, mg/L CaCO3 | 55.4161 | NA |  | T-Hdb, mg/L CaCO3 | 64.8797 | 49.6432 | [11 empty] | T-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | T-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! | [11 empty] | T-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | T-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! | [11 empty] | T-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | T-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! | [11 empty] | T-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | T-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0!
|  |  |  | Flow weighted system pressure losses, Lsys (psi) | 18 | [5 empty] | 1991-05-08 | 21:00 | 1953.5 | 27.2 | 92 | 41 | 36.55 | 0 | 8 | 10.2 |  | 18.2 | 18.2 | 0.43956 | 0 | 14.2222 | 13.1274 | 2.6451 | 27.3049 | 0.48077 | [11 empty] | 92 | 72 | 46 | 5.2 | 13 | 18.2 | 18.2 | 0.39497 | 0.28571 | 13.8667 | 12.7992 | 2.5439 | 33.4561 | 0.38257 | [10 empty] | 72 | 41 | 19 | 2.8 | 10.2 | 13 | 13 | 0.58738 | 0.21538 | 14.9333 | 13.7838 | 2.8351 | 34.6649 | 0.39763 | [10 empty] | Ca-Hdb, mg/L CaCO3 | 42.0584 | NA |  | Ca-Hdb, mg/L CaCO3 | 48.7386 | 37.9834 | [11 empty] | Ca-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | Ca-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! | [11 empty] | Ca-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | Ca-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! | [11 empty] | Ca-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | Ca-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! | [11 empty] | Ca-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | Ca-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0!
|  |  |  | Required influent pressure to the system, PI (psi) | 139.1392 | [5 empty] | 1991-05-09 | 1:00 | 1957.5 | 27.2 | 92 | 40 | 35.8831 | 0 | 7.7 | 10.2 |  | 17.9 | 17.9 | 0.43017 | 0 | 13.6889 | 12.6351 | 2.6451 | 27.4718 | 0.45993 | [11 empty] | 92 | 72 | 45 | 5.1 | 12.8 | 17.9 | 17.9 | 0.38864 | 0.28492 | 13.6 | 12.5531 | 2.5439 | 34.4561 | 0.36432 | [10 empty] | 72 | 40 | 18 | 2.6 | 10.2 | 12.8 | 12.8 | 0.58232 | 0.20312 | 13.8667 | 12.7992 | 2.8351 | 35.1649 | 0.36398 | [10 empty] | Notes: | [17 empty] | Notes: | [17 empty] | Notes: | [17 empty] | Notes: | [17 empty] | Notes:
|  |  |  | 3: The osmotic pressure can be estimated from Table 6-5 in Part 3 of the | [6 empty] | 1991-05-09 | 13:00 | 1969.5 | 27.2 | 92 | 40 | 35.8831 | 0 | 7.7 | 10.2 |  | 17.9 | 17.9 | 0.43017 | 0 | 13.6889 | 12.6351 | 2.6451 | 27.4718 | 0.45993 | [11 empty] | 92 | 72 | 45 | 5.1 | 12.8 | 17.9 | 17.9 | 0.38864 | 0.28492 | 13.6 | 12.5531 | 2.5439 | 34.4561 | 0.36432 | [10 empty] | 72 | 40 | 18 | 2.6 | 10.2 | 12.8 | 12.8 | 0.58232 | 0.20312 | 13.8667 | 12.7992 | 2.8351 | 35.1649 | 0.36398 | [10 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be
|  |  |  | "ICR Manual for Bench- and Pilot-Scale Treatment Studies." | [6 empty] | 1991-05-10 | 0:15 | 1980.7 | 27.7 | 95 | 40 | 37.2 | 0 | 8 | 10.3 |  | 18.3 | 18.3 | 0.43716 | 0 | 14.2222 | 12.9348 | 2.6451 | 27.6549 | 0.46772 | [11 empty] | 95 | 73 | 47 | 5.2 | 13.1 | 18.3 | 18.3 | 0.3975 | 0.28415 | 13.8667 | 12.6114 | 2.5439 | 34.4561 | 0.36601 | [10 empty] | 73 | 40 | 19 | 2.8 | 10.3 | 13.1 | 13.1 | 0.59245 | 0.21374 | 14.9333 | 13.5815 | 2.8351 | 34.6649 | 0.39179 | [10 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs.
[11 empty] | 1991-05-10 | 16:00 | 1996.5 | 27.7 | 93 | 42 | 37.2 | 0 | 8 | 10.2 |  | 18.2 | 18.2 | 0.43956 | 0 | 14.2222 | 12.9348 | 2.6451 | 27.6549 | 0.46772 | [11 empty] | 93 | 73 | 47 | 5.2 | 13 | 18.2 | 18.2 | 0.39497 | 0.28571 | 13.8667 | 12.6114 | 2.5439 | 33.4561 | 0.37695 | [10 empty] | 73 | 42 | 19 | 2.8 | 10.2 | 13 | 13 | 0.58738 | 0.21538 | 14.9333 | 13.5815 | 2.8351 | 35.6649 | 0.38081 | [10 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5.
[11 empty] | 1991-05-10 | 22:00 | 2002.5 | 27.7 | 93 | 41 | 37.0759 | 0 | 7.9 | 10.2 |  | 18.1 | 18.1 | 0.43646 | 0 | 14.0444 | 12.7731 | 2.6451 | 27.279 | 0.46824 | [11 empty] | 93 | 73 | 47 | 5.1 | 13 | 18.1 | 18.1 | 0.3937 | 0.28177 | 13.6 | 12.3689 | 2.5439 | 33.4561 | 0.36971 | [10 empty] | 73 | 41 | 19 | 2.8 | 10.2 | 13 | 13 | 0.58738 | 0.21538 | 14.9333 | 13.5815 | 2.8351 | 35.1649 | 0.38622 | [10 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters.
[11 empty] | 1991-05-11 | 5:00 | 2009.5 | 27.2 | 92 | 42 | 37.5455 | 0 | 7.7 | 10.1 |  | 17.8 | 17.8 | 0.43258 | 0 | 13.6889 | 12.6351 | 2.6451 | 26.8094 | 0.47129 | [11 empty] | 92 | 72 | 47 | 5.1 | 12.7 | 17.8 | 17.8 | 0.3861 | 0.28652 | 13.6 | 12.5531 | 2.5439 | 32.4561 | 0.38677 | [10 empty] | 72 | 42 | 19 | 2.6 | 10.1 | 12.7 | 12.7 | 0.57726 | 0.20472 | 13.8667 | 12.7992 | 2.8351 | 35.1649 | 0.36398 | [10 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design.
[11 empty] | 1991-05-11 | 10:00 | 2014.5 | 27.2 | 93 | 42 | 37.0759 | 0 | 7.9 | 10.1 |  | 18 | 18 | 0.43889 | 0 | 14.0444 | 12.9633 | 2.6451 | 27.779 | 0.46666 | [11 empty] | 93 | 72 | 47 | 5.1 | 12.9 | 18 | 18 | 0.39117 | 0.28333 | 13.6 | 12.5531 | 2.5439 | 32.9561 | 0.3809 | [10 empty] | 72 | 42 | 19 | 2.8 | 10.1 | 12.9 | 12.9 | 0.58232 | 0.21705 | 14.9333 | 13.7838 | 2.8351 | 35.1649 | 0.39197 | [10 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[11 empty] | 1991-05-11 | 22:00 | 2026.5 | 27.2 | 93 | 42 | 37.0759 | 0 | 7.9 | 10.2 |  | 18.1 | 18.1 | 0.43646 | 0 | 14.0444 | 12.9633 | 2.6451 | 27.779 | 0.46666 | [11 empty] | 93 | 72 | 47 | 5.1 | 13 | 18.1 | 18.1 | 0.3937 | 0.28177 | 13.6 | 12.5531 | 2.5439 | 32.9561 | 0.3809 | [10 empty] | 72 | 42 | 19 | 2.8 | 10.2 | 13 | 13 | 0.58738 | 0.21538 | 14.9333 | 13.7838 | 2.8351 | 35.1649 | 0.39197 | [10 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[11 empty] | 1991-05-12 | 6:00 | 2034.5 | 27.2 | 90 | 40 | 35.2208 | 0 | 7.7 | 9 |  | 16.7 | 16.7 | 0.46108 | 0 | 13.6889 | 12.6351 | 2.6451 | 27.1341 | 0.46565 | [11 empty] | 90 | 70 | 44 | 5.1 | 11.6 | 16.7 | 16.7 | 0.35825 | 0.30539 | 13.6 | 12.5531 | 2.5439 | 33.4561 | 0.37521 | [10 empty] | 70 | 40 | 18 | 2.6 | 9 | 11.6 | 11.6 | 0.52156 | 0.22414 | 13.8667 | 12.7992 | 2.8351 | 34.1649 | 0.37463 | [10 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio.
[11 empty] | 1991-05-12 | 12:15 | 2040.7 | 27.2 | 92 | 41 | 36.7722 | 0 | 7.9 | 10.2 |  | 18.1 | 18.1 | 0.43646 | 0 | 14.0444 | 12.9633 | 2.6451 | 27.0828 | 0.47866 | [11 empty] | 92 | 72 | 46 | 5.2 | 12.9 | 18.1 | 18.1 | 0.39243 | 0.28729 | 13.8667 | 12.7992 | 2.5439 | 33.4561 | 0.38257 | [10 empty] | 72 | 41 | 19 | 2.7 | 10.2 | 12.9 | 12.9 | 0.58485 | 0.2093 | 14.4 | 13.2915 | 2.8351 | 34.6649 | 0.38343 | [10 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL.
[11 empty] | 1991-05-12 | 21:00 | 2049.5 | 27.2 | 98 | 41 | 39.0886 | 0 | 7.9 | 10.2 | X | 18.1 | 18.1 | 0.43646 | 0 | 14.0444 | 12.9633 | 2.6451 | 27.7663 | 0.46687 | [11 empty] | 98 | 72 | 49 | 5.2 | 12.9 | 18.1 | 18.1 | 0.39243 | 0.28729 | 13.8667 | 12.7992 | 2.5439 | 33.4561 | 0.38257 | [10 empty] | 72 | 41 | 20 | 2.7 | 10.2 | 12.9 | 12.9 | 0.58485 | 0.2093 | 14.4 | 13.2915 | 2.8351 | 33.6649 | 0.39482 | [10 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[11 empty] | 1991-05-13 | 6:00 | 2058.5 | 27.2 | 98 | 41 | 38.7468 | 0 | 7.9 | 10.2 |  | 18.1 | 18.1 | 0.43646 | 0 | 14.0444 | 12.9633 | 2.6451 | 28.1081 | 0.4612 | [11 empty] | 98 | 72 | 49 | 5.2 | 12.9 | 18.1 | 18.1 | 0.39243 | 0.28729 | 13.8667 | 12.7992 | 2.5439 | 33.4561 | 0.38257 | [10 empty] | 72 | 41 | 19 | 2.7 | 10.2 | 12.9 | 12.9 | 0.58485 | 0.2093 | 14.4 | 13.2915 | 2.8351 | 34.6649 | 0.38343
[11 empty] | 1991-05-13 | 11:00 | 2063.5 | 27.2 | 92 | 41 | 36.4304 | 0 | 7.9 | 10.2 |  | 18.1 | 18.1 | 0.43646 | 0 | 14.0444 | 12.9633 | 2.6451 | 27.4245 | 0.47269 | [11 empty] | 92 | 72 | 46 | 5.2 | 12.9 | 18.1 | 18.1 | 0.39243 | 0.28729 | 13.8667 | 12.7992 | 2.5439 | 33.4561 | 0.38257 | [10 empty] | 72 | 41 | 18 | 2.7 | 10.2 | 12.9 | 12.9 | 0.58485 | 0.2093 | 14.4 | 13.2915 | 2.8351 | 35.6649 | 0.37268
[11 empty] | 1991-05-13 | 21:00 | 2073.5 | 27.2 | 92 | 41 | 36.4304 | 0 | 7.9 | 10.2 |  | 18.1 | 18.1 | 0.43646 | 0 | 14.0444 | 12.9633 | 2.6451 | 27.4245 | 0.47269 | [11 empty] | 92 | 72 | 46 | 5.2 | 12.9 | 18.1 | 18.1 | 0.39243 | 0.28729 | 13.8667 | 12.7992 | 2.5439 | 33.4561 | 0.38257 | [10 empty] | 72 | 41 | 18 | 2.7 | 10.2 | 12.9 | 12.9 | 0.58485 | 0.2093 | 14.4 | 13.2915 | 2.8351 | 35.6649 | 0.37268
[11 empty] | 1991-05-14 | 6:00 | 2082.5 | 26.7 | 98 | 40 | 35.6296 | 0 | 8.1 | 10.1 |  | 18.2 | 18.2 | 0.44505 | 0 | 14.4 | 13.4894 | 2.6451 | 30.7253 | 0.43903 | [11 empty] | 98 | 73 | 46 | 5.3 | 12.9 | 18.2 | 18.2 | 0.3937 | 0.29121 | 14.1333 | 13.2396 | 2.5439 | 36.9561 | 0.35825 | [10 empty] | 73 | 40 | 16 | 2.8 | 10.1 | 12.9 | 12.9 | 0.58232 | 0.21705 | 14.9333 | 13.989 | 2.8351 | 37.6649 | 0.37141
[11 empty] | 1991-05-14 | 11:00 | 2087.5 | 26.7 | 90 | 40 | 34.7848 | 0 | 7.9 | 10.1 |  | 18 | 18 | 0.43889 | 0 | 14.0444 | 13.1563 | 2.6451 | 27.5701 | 0.4772 | [11 empty] | 90 | 72 | 44 | 5.1 | 12.9 | 18 | 18 | 0.39117 | 0.28333 | 13.6 | 12.74 | 2.5439 | 34.4561 | 0.36975 | [10 empty] | 72 | 40 | 18 | 2.8 | 10.1 | 12.9 | 12.9 | 0.58232 | 0.21705 | 14.9333 | 13.989 | 2.8351 | 35.1649 | 0.39781
[11 empty] | 1991-05-14 | 21:00 | 2097.5 | 26.7 | 92 | 40 | 34.7848 | 0 | 7.9 | 10.1 |  | 18 | 18 | 0.43889 | 0 | 14.0444 | 13.1563 | 2.6451 | 28.5701 | 0.46049 | [11 empty] | 92 | 72 | 44 | 5.1 | 12.9 | 18 | 18 | 0.39117 | 0.28333 | 13.6 | 12.74 | 2.5439 | 35.4561 | 0.35932 | [10 empty] | 72 | 40 | 18 | 2.8 | 10.1 | 12.9 | 12.9 | 0.58232 | 0.21705 | 14.9333 | 13.989 | 2.8351 | 35.1649 | 0.39781
[11 empty] | 1991-05-15 | 11:15 | 2111.8 | 26.7 | 92 | 40 | 34.7848 | 0 | 7.9 | 10.1 |  | 18 | 18 | 0.43889 | 0 | 14.0444 | 13.1563 | 2.6451 | 28.5701 | 0.46049 | [11 empty] | 92 | 72 | 44 | 5.1 | 12.9 | 18 | 18 | 0.39117 | 0.28333 | 13.6 | 12.74 | 2.5439 | 35.4561 | 0.35932 | [10 empty] | 72 | 40 | 18 | 2.8 | 10.1 | 12.9 | 12.9 | 0.58232 | 0.21705 | 14.9333 | 13.989 | 2.8351 | 35.1649 | 0.39781
[11 empty] | 1991-05-15 | 21:00 | 2121.5 | 26.7 | 92 | 40 | 34.7848 | 0 | 7.9 | 10.1 |  | 18 | 18 | 0.43889 | 0 | 14.0444 | 13.1563 | 2.6451 | 28.5701 | 0.46049 | [11 empty] | 92 | 72 | 44 | 5.1 | 12.9 | 18 | 18 | 0.39117 | 0.28333 | 13.6 | 12.74 | 2.5439 | 35.4561 | 0.35932 | [10 empty] | 72 | 40 | 18 | 2.8 | 10.1 | 12.9 | 12.9 | 0.58232 | 0.21705 | 14.9333 | 13.989 | 2.8351 | 35.1649 | 0.39781
[11 empty] | 1991-05-16 | 7:00 | 2131.5 | 27.2 | 92 | 40 | 34.7848 | 0 | 7.9 | 10.1 |  | 18 | 18 | 0.43889 | 0 | 14.0444 | 12.9633 | 2.6451 | 28.5701 | 0.45374 | [11 empty] | 92 | 72 | 44 | 5.1 | 12.9 | 18 | 18 | 0.39117 | 0.28333 | 13.6 | 12.5531 | 2.5439 | 35.4561 | 0.35405 | [10 empty] | 72 | 40 | 18 | 2.8 | 10.1 | 12.9 | 12.9 | 0.58232 | 0.21705 | 14.9333 | 13.7838 | 2.8351 | 35.1649 | 0.39197
[11 empty] | 1991-05-16 | 16:00 | 2140.5 | 27.2 | 91 | 48 | 38.7059 | 0 | 8.5 | 10.1 |  | 18.6 | 18.6 | 0.45699 | 0 | 15.1111 | 13.9479 | 2.6451 | 28.149 | 0.4955 | [11 empty] | 91 | 76 | 50 | 5.3 | 13.3 | 18.6 | 18.6 | 0.40383 | 0.28495 | 14.1333 | 13.0453 | 2.5439 | 30.9561 | 0.42141 | [10 empty] | 76 | 48 | 20 | 3.2 | 10.1 | 13.3 | 13.3 | 0.59245 | 0.2406 | 17.0667 | 15.7529 | 2.8351 | 39.1649 | 0.40222
[11 empty] | 1991-05-17 | 12:30 | 2161 | 26.7 | 90 | 45 | 37.5181 | 0 | 8.3 | 10 |  | 18.3 | 18.3 | 0.45355 | 0 | 14.7556 | 13.8225 | 2.6451 | 27.3368 | 0.50564 | [11 empty] | 90 | 72 | 48 | 5.3 | 13 | 18.3 | 18.3 | 0.39623 | 0.28962 | 14.1333 | 13.2396 | 2.5439 | 30.4561 | 0.43471 | [10 empty] | 72 | 45 | 19 | 3 | 10 | 13 | 13 | 0.58232 | 0.23077 | 16 | 14.9882 | 2.8351 | 36.6649 | 0.40879
[11 empty] | 1991-05-17 | 17:00 | 2165.5 | 26.7 | 88 | 46 | 36.3902 | 0 | 8.2 | 9.9 |  | 18.1 | 18.1 | 0.45304 | 0 | 14.5778 | 13.6559 | 2.6451 | 27.9647 | 0.48833 | [11 empty] | 88 | 72 | 47 | 5.2 | 12.9 | 18.1 | 18.1 | 0.39243 | 0.28729 | 13.8667 | 12.9898 | 2.5439 | 30.4561 | 0.42651 | [10 empty] | 72 | 46 | 18 | 3 | 9.9 | 12.9 | 12.9 | 0.57726 | 0.23256 | 16 | 14.9882 | 2.8351 | 38.1649 | 0.39272
[11 empty] | 1991-05-18 | 6:00 | 2178.5 | 26.7 | 89 | 46 | 36.5181 | 0 | 8.3 | 10 |  | 18.3 | 18.3 | 0.45355 | 0 | 14.7556 | 13.8225 | 2.6451 | 28.3368 | 0.48779 | [11 empty] | 89 | 72 | 47 | 5.3 | 13 | 18.3 | 18.3 | 0.39623 | 0.28962 | 14.1333 | 13.2396 | 2.5439 | 30.9561 | 0.42769 | [10 empty] | 72 | 46 | 18 | 3 | 10 | 13 | 13 | 0.58232 | 0.23077 | 16 | 14.9882 | 2.8351 | 38.1649 | 0.39272
[11 empty] | 1991-05-18 | 11:00 | 2183.5 | 26.7 | 88 | 45 | 36.122 | 0 | 8.2 | 10 |  | 18.2 | 18.2 | 0.45055 | 0 | 14.5778 | 13.6559 | 2.6451 | 27.733 | 0.49241 | [11 empty] | 88 | 72 | 46 | 5.2 | 13 | 18.2 | 18.2 | 0.39497 | 0.28571 | 13.8667 | 12.9898 | 2.5439 | 31.4561 | 0.41295 | [10 empty] | 72 | 45 | 19 | 3 | 10 | 13 | 13 | 0.58232 | 0.23077 | 16 | 14.9882 | 2.8351 | 36.6649 | 0.40879
[11 empty] | 1991-05-18 | 22:00 | 2194.5 | 26.7 | 88 | 45 | 35.122 | 0 | 8.2 | 10 |  | 18.2 | 18.2 | 0.45055 | 0 | 14.5778 | 13.6559 | 2.6451 | 28.733 | 0.47527 | [11 empty] | 88 | 72 | 45 | 5.2 | 13 | 18.2 | 18.2 | 0.39497 | 0.28571 | 13.8667 | 12.9898 | 2.5439 | 32.4561 | 0.40023 | [10 empty] | 72 | 45 | 18 | 3 | 10 | 13 | 13 | 0.58232 | 0.23077 | 16 | 14.9882 | 2.8351 | 37.6649 | 0.39794
[11 empty] | 1991-05-19 | 5:00 | 2201.5 | 27.2 | 85 | 42 | 34.1818 | 0 | 7.7 | 9.7 |  | 17.4 | 17.4 | 0.44253 | 0 | 13.6889 | 12.6351 | 2.6451 | 26.6731 | 0.4737 | [11 empty] | 85 | 71 | 44 | 4.9 | 12.5 | 17.4 | 17.4 | 0.37851 | 0.28161 | 13.0667 | 12.0608 | 2.5439 | 31.4561 | 0.38342 | [10 empty] | 71 | 42 | 17 | 2.8 | 9.7 | 12.5 | 12.5 | 0.56207 | 0.224 | 14.9333 | 13.7838 | 2.8351 | 36.6649 | 0.37594
[11 empty] | 1991-05-19 | 14:30 | 2208 | 27.2 | 90 | 45 | 38.4235 | 0 | 8.5 | 10.1 |  | 18.6 | 18.6 | 0.45699 | 0 | 15.1111 | 13.9479 | 2.6451 | 26.4314 | 0.5277 | [11 empty] | 90 | 75 | 49 | 5.4 | 13.2 | 18.6 | 18.6 | 0.40256 | 0.29032 | 14.4 | 13.2915 | 2.5439 | 30.9561 | 0.42937 | [10 empty] | 75 | 45 | 20 | 3.1 | 10.1 | 13.2 | 13.2 | 0.58992 | 0.23485 | 16.5333 | 15.2606 | 2.8351 | 37.1649 | 0.41062
[11 empty] | 1991-05-19 | 20:30 | 2214 | 27.2 | 85 | 45 | 36.9753 | 0 | 8.1 | 10.1 |  | 18.2 | 18.2 | 0.44505 | 0 | 14.4 | 13.2915 | 2.6451 | 25.3796 | 0.52371 | [11 empty] | 85 | 72 | 47 | 5.3 | 12.9 | 18.2 | 18.2 | 0.3937 | 0.29121 | 14.1333 | 13.0453 | 2.5439 | 28.9561 | 0.45052 | [10 empty] | 72 | 45 | 18 | 2.8 | 10.1 | 12.9 | 12.9 | 0.58232 | 0.21705 | 14.9333 | 13.7838 | 2.8351 | 37.6649 | 0.36596
[11 empty] | 1991-05-20 | 7:30 | 2225 | 27.2 | 90 | 42 | 36.4588 | 0 | 8.5 | 8.9 |  | 17.4 | 17.4 | 0.48851 | 0 | 15.1111 | 13.9479 | 2.6451 | 26.8961 | 0.51858 | [11 empty] | 90 | 75 | 47 | 5.3 | 12.1 | 17.4 | 17.4 | 0.37344 | 0.3046 | 14.1333 | 13.0453 | 2.5439 | 32.9561 | 0.39584 | [10 empty] | 75 | 42 | 19 | 3.2 | 8.9 | 12.1 | 12.1 | 0.53168 | 0.26446 | 17.0667 | 15.7529 | 2.8351 | 36.6649 | 0.42964
[11 empty] | 1991-05-20 | 13:00 | 2230.5 | 27.2 | 90 | 45 | 36.7561 | 0 | 8.2 | 10 |  | 18.2 | 18.2 | 0.45055 | 0 | 14.5778 | 13.4556 | 2.6451 | 28.0988 | 0.47887 | [11 empty] | 90 | 75 | 47 | 5.2 | 13 | 18.2 | 18.2 | 0.39497 | 0.28571 | 13.8667 | 12.7992 | 2.5439 | 32.9561 | 0.38837 | [10 empty] | 75 | 45 | 19 | 3 | 10 | 13 | 13 | 0.58232 | 0.23077 | 16 | 14.7683 | 2.8351 | 38.1649 | 0.38696
[11 empty] | 1991-05-20 | 21:00 | 2238.5 | 27.2 | 90 | 45 | 36.2308 | 0 | 7.8 | 10 |  | 17.8 | 17.8 | 0.4382 | 0 | 13.8667 | 12.7992 | 2.6451 | 28.6241 | 0.44715 | [11 empty] | 90 | 75 | 47 | 4.8 | 13 | 17.8 | 17.8 | 0.3899 | 0.26966 | 12.8 | 11.8147 | 2.5439 | 32.9561 | 0.3585 | [10 empty] | 75 | 45 | 19 | 3 | 10 | 13 | 13 | 0.58232 | 0.23077 | 16 | 14.7683 | 2.8351 | 38.1649 | 0.38696
[11 empty] | 1991-05-21 | 4:00 | 2245.5 | 26.1 | 91 | 45 | 36.6296 | 0 | 8.1 | 10 |  | 18.1 | 18.1 | 0.44751 | 0 | 14.4 | 13.7308 | 2.6451 | 28.7253 | 0.478 | [11 empty] | 91 | 76 | 47 | 5.1 | 13 | 18.1 | 18.1 | 0.3937 | 0.28177 | 13.6 | 12.9679 | 2.5439 | 33.9561 | 0.3819 | [10 empty] | 76 | 45 | 19 | 3 | 10 | 13 | 13 | 0.58232 | 0.23077 | 16 | 15.2564 | 2.8351 | 38.6649 | 0.39458
[11 empty] | 1991-05-21 | 21:00 | 2262.5 | 26.1 | 91 | 45 | 36.6296 | 0 | 8.1 | 10 |  | 18.1 | 18.1 | 0.44751 | 0 | 14.4 | 13.7308 | 2.6451 | 28.7253 | 0.478 | [11 empty] | 91 | 76 | 47 | 5.1 | 13 | 18.1 | 18.1 | 0.3937 | 0.28177 | 13.6 | 12.9679 | 2.5439 | 33.9561 | 0.3819 | [10 empty] | 76 | 45 | 19 | 3 | 10 | 13 | 13 | 0.58232 | 0.23077 | 16 | 15.2564 | 2.8351 | 38.6649 | 0.39458
[11 empty] | 1991-05-22 | 5:00 | 2270.5 | 26.1 | 91 | 47 | 36.0759 | 0 | 7.9 | 10 |  | 17.9 | 17.9 | 0.44134 | 0 | 14.0444 | 13.3917 | 2.6451 | 30.279 | 0.44228 | [11 empty] | 91 | 77 | 46 | 5.1 | 12.8 | 17.9 | 17.9 | 0.38864 | 0.28492 | 13.6 | 12.9679 | 2.5439 | 35.4561 | 0.36575 | [10 empty] | 77 | 47 | 18 | 2.8 | 10 | 12.8 | 12.8 | 0.57726 | 0.21875 | 14.9333 | 14.2393 | 2.8351 | 41.1649 | 0.34591
[11 empty] | 1991-05-22 | 11:00 | 2276.5 | 26.1 | 90 | 48 | 35.8795 | 0 | 8.3 | 10 |  | 18.3 | 18.3 | 0.45355 | 0 | 14.7556 | 14.0698 | 2.6451 | 30.4754 | 0.46168 | [11 empty] | 90 | 75 | 46 | 5.3 | 13 | 18.3 | 18.3 | 0.39623 | 0.28962 | 14.1333 | 13.4765 | 2.5439 | 33.9561 | 0.39688 | [10 empty] | 75 | 48 | 18 | 3 | 10 | 13 | 13 | 0.58232 | 0.23077 | 16 | 15.2564 | 2.8351 | 40.6649 | 0.37517
[11 empty] | 1991-05-22 | 21:00 | 2286.5 | 26.1 | 90 | 48 | 36.321 | 0 | 8.1 | 10 |  | 18.1 | 18.1 | 0.44751 | 0 | 14.4 | 13.7308 | 2.6451 | 30.0339 | 0.45718 | [11 empty] | 90 | 75 | 46 | 5.3 | 12.8 | 18.1 | 18.1 | 0.39117 | 0.29282 | 14.1333 | 13.4765 | 2.5439 | 33.9561 | 0.39688 | [10 empty] | 75 | 48 | 18 | 2.8 | 10 | 12.8 | 12.8 | 0.57726 | 0.21875 | 14.9333 | 14.2393 | 2.8351 | 40.6649 | 0.35016
[11 empty] | 1991-05-23 | 5:15 | 2294.8 | 26.1 | 90 | 42 | 34.4304 | 0 | 7.9 | 9.5 |  | 17.4 | 17.4 | 0.45402 | 0 | 14.0444 | 13.3917 | 2.6451 | 28.9245 | 0.46299 | [11 empty] | 90 | 72 | 44 | 5.1 | 12.3 | 17.4 | 17.4 | 0.37598 | 0.2931 | 13.6 | 12.9679 | 2.5439 | 34.4561 | 0.37636 | [10 empty] | 72 | 42 | 17 | 2.8 | 9.5 | 12.3 | 12.3 | 0.55194 | 0.22764 | 14.9333 | 14.2393 | 2.8351 | 37.1649 | 0.38314
[11 empty] | 1991-05-23 | 13:00 | 2302.5 | 26.1 | 89 | 42 | 33.8831 | 0 | 7.7 | 9.4 |  | 17.1 | 17.1 | 0.45029 | 0 | 13.6889 | 13.0527 | 2.6451 | 28.9718 | 0.45053 | [11 empty] | 89 | 70 | 43 | 5.1 | 12 | 17.1 | 17.1 | 0.36838 | 0.29825 | 13.6 | 12.9679 | 2.5439 | 33.9561 | 0.3819 | [10 empty] | 70 | 42 | 16 | 2.6 | 9.4 | 12 | 12 | 0.54181 | 0.21667 | 13.8667 | 13.2222 | 2.8351 | 37.1649 | 0.35577
[11 empty] | 1991-05-23 | 21:00 | 2310.5 | 26.1 | 89 | 35 | 33.2078 | 0 | 7.7 | 10.2 |  | 17.9 | 17.9 | 0.43017 | 0 | 13.6889 | 13.0527 | 2.6451 | 26.1471 | 0.4992 | [11 empty] | 89 | 69 | 43 | 5.1 | 12.8 | 17.9 | 17.9 | 0.38864 | 0.28492 | 13.6 | 12.9679 | 2.5439 | 33.4561 | 0.38761 | [10 empty] | 69 | 35 | 14 | 2.6 | 10.2 | 12.8 | 12.8 | 0.58232 | 0.20312 | 13.8667 | 13.2222 | 2.8351 | 35.1649 | 0.37601
[11 empty] | 1991-05-24 | 11:10 | 2324.7 | 26.1 | 88 | 37 | 33.2432 | 0 | 7.4 | 10.2 |  | 17.6 | 17.6 | 0.42045 | 0 | 13.1556 | 12.5442 | 2.6451 | 26.6117 | 0.47138 | [11 empty] | 88 | 69 | 42 | 5 | 12.6 | 17.6 | 17.6 | 0.38231 | 0.28409 | 13.3333 | 12.7137 | 2.5439 | 33.9561 | 0.37441 | [10 empty] | 69 | 37 | 15 | 2.4 | 10.2 | 12.6 | 12.6 | 0.57726 | 0.19048 | 12.8 | 12.2051 | 2.8351 | 35.1649 | 0.34708
[11 empty] | 1991-05-24 | 20:00 | 2333.5 | 26.1 | 88 | 36 | 32.9189 | 0 | 7.4 | 10.2 |  | 17.6 | 17.6 | 0.42045 | 0 | 13.1556 | 12.5442 | 2.6451 | 26.436 | 0.47451 | [11 empty] | 88 | 69 | 42 | 5 | 12.6 | 17.6 | 17.6 | 0.38231 | 0.28409 | 13.3333 | 12.7137 | 2.5439 | 33.9561 | 0.37441 | [10 empty] | 69 | 36 | 14 | 2.4 | 10.2 | 12.6 | 12.6 | 0.57726 | 0.19048 | 12.8 | 12.2051 | 2.8351 | 35.6649 | 0.34222
[11 empty] | 1991-05-25 | 3:00 | 2340.5 | 26.7 | 89 | 40 | 34.1818 | 0 | 7.7 | 10.6 |  | 18.3 | 18.3 | 0.42077 | 0 | 13.6889 | 12.8232 | 2.6451 | 27.6731 | 0.46338 | [11 empty] | 89 | 71 | 44 | 5 | 13.3 | 18.3 | 18.3 | 0.40003 | 0.27322 | 13.3333 | 12.4902 | 2.5439 | 33.4561 | 0.37333 | [10 empty] | 71 | 40 | 16 | 2.7 | 10.6 | 13.3 | 13.3 | 0.60511 | 0.20301 | 14.4 | 13.4894 | 2.8351 | 36.6649 | 0.36791
[11 empty] | 1991-05-26 | 6:15 | 2367.7 | 27.195 | 89 | 35 | 33.5455 | 0 | 7.7 | 10.2 |  | 17.9 | 17.9 | 0.43017 | 0 | 13.6889 | 12.637 | 2.6451 | 25.8094 | 0.48963 | [11 empty] | 89 | 70 | 43 | 5.1 | 12.8 | 17.9 | 17.9 | 0.38864 | 0.28492 | 13.6 | 12.5549 | 2.5439 | 33.9561 | 0.36974 | [10 empty] | 70 | 35 | 15 | 2.6 | 10.2 | 12.8 | 12.8 | 0.58232 | 0.20312 | 13.8667 | 12.8011 | 2.8351 | 34.6649 | 0.36928
[11 empty] | 1991-05-26 | 10:00 | 2371.5 | 27.195 | 85 | 38 | 33.5455 | 0 | 7.7 | 10.4 |  | 18.1 | 18.1 | 0.42541 | 0 | 13.6889 | 12.637 | 2.6451 | 25.3094 | 0.4993 | [11 empty] | 85 | 70 | 43 | 5.1 | 13 | 18.1 | 18.1 | 0.3937 | 0.28177 | 13.6 | 12.5549 | 2.5439 | 31.9561 | 0.39288 | [10 empty] | 70 | 38 | 15 | 2.6 | 10.4 | 13 | 13 | 0.59245 | 0.2 | 13.8667 | 12.8011 | 2.8351 | 36.1649 | 0.35396
[11 empty] | 1991-05-26 | 21:00 | 2382.5 | 27.195 | 87 | 35 | 33.9296 | 0 | 7.1 | 10.2 |  | 17.3 | 17.3 | 0.4104 | 0 | 12.6222 | 11.6523 | 2.6451 | 24.4253 | 0.47706 | [11 empty] | 87 | 69 | 43 | 4.8 | 12.5 | 17.3 | 17.3 | 0.37724 | 0.27746 | 12.8 | 11.8164 | 2.5439 | 32.4561 | 0.36407 | [10 empty] | 69 | 35 | 15 | 2.3 | 10.2 | 12.5 | 12.5 | 0.57473 | 0.184 | 12.2667 | 11.3241 | 2.8351 | 34.1649 | 0.33145
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
Note on N9: TSC_ADM: Verified by Consultant
Note on Q84: C. Rice: The consultant addressed the low flux and MTCw values for 5/15/91 and 5/16/91. The consultant stated that the original study reported 0.0 gpm for stage 2 and had missing data for 5/16/91. Since these data were considered outliers, the consultant verified that the spreadsheet was modified by replacing the 5/15/91 and 5/16/91 flow and pressure data with the data set recorded immediately before at 11:15 on 5/15/91.
Note on Q85: C. Rice: The consultant addressed the low flux and MTCw values for 5/15/91 and 5/16/91. The consultant stated that the original study reported 0.0 gpm for stage 2 and had missing data for 5/16/91. Since these data were considered outliers, the consultant verified that the spreadsheet was modified by replacing the 5/15/91 and 5/16/91 flow and pressure data with the data set recorded immediately before at 11:15 on 5/15/91.
Note on AJ6: C. Rice: The consultant addressed the low flux and MTCw values for 5/15/91 and 5/16/91. The consultant stated that the original study reported 0.0 gpm for stage 2 and had missing data for 5/16/91. Since these data were considered outliers, the consultant verified that the spreadsheet was modified by replacing the 5/15/91 and 5/16/91 flow and pressure data with the data set recorded immediately before at 11:15 on 5/15/91.
Note on CW14: C. Rice: Consultant verified low permeate pH values. Consultant stated that the feed sample point was immediately prior to the sulfuric acid addition and consequently the pH, alkalinity and sulfate values do not represent this. To make the pH more representative of the actual pH going through the membrane system, the first stage pH was substituted for the system and stage 1 feed pH.
Note on CX22: C. Rice: Consultant stated that the original feed TOC concentration was verified (19 mg/L C). However, since all feed samples other than this event were between 7 and 10 mg/L C, the data point was considered an outlier and was subsequently changed to 9 mg/L C for the system and stage 1 feed concentration.
Note on DA22: C. Rice: Consultant stated that the original feed TOC concentration was verified (19 mg/L C). However, since all feed samples other than this event were between 7 and 10 mg/L C, the data point was considered an outlier and was subsequently changed to 9 mg/L C for the system and stage 1 feed concentration. Changing the feed concentration from 19 mg/L C to 9 mg/L C (which was more representative of the feed concentration) significantly reduced the MB closure error for TOC.
Note on DH14: C. Rice: Consultant verified low permeate pH values. Consultant stated that the feed sample point was immediately prior to the sulfuric acid addition and consequently the pH, alkalinity and sulfate values do not represent this. To make the pH more representative of the actual pH going through the membrane system, the first stage pH was substituted for the system and stage 1 feed pH.
Note on DH36: C. Rice: Consultant verified low permeate pH values. Consultant stated that the feed sample point was immediately prior to the sulfuric acid addition and consequently the pH, alkalinity and sulfate values do not represent this. To make the pH more representative of the actual pH going through the membrane system, the first stage pH was substituted for the system and stage 1 feed pH.
Note on DI21: C. Rice: Consultant stated that the original feed TOC concentration was verified (19 mg/L C). However, since all feed samples other than this event were between 7 and 10 mg/L C, the data point was considered an outlier and was subsequently changed to 9 mg/L C for the system and stage 1 feed concentration.