## Sheet1. 1st Pilot Study
FIELD-SET 1: RESULTS FROM 1st PILOT-SCALE STUDY (FILE: gacpilot.xls)
Field 1-1: PWS And Treatment Plant Data |  | Field 1-2: Pilot-Scale GAC Design Parameters |  |  |  | Field 1-3: Pretreatment Used Prior To GAC1 |  |  | Field 1-4: Influent Water Quality For The 10- And 20-Minute, Pilot-Scale GAC Contactors1 | [14 empty] | Field 1-4: Influent Water Quality For The 10- And 20-Minute, Pilot-Scale GAC Contactors (continued) | [15 empty] | Field 1-4: Influent Water Quality For The 10- And 20-Minute, Pilot-Scale GAC Contactors (continued) | [9 empty] | Field 1-5: Effluent Water Quality For The 10-Minute, Pilot-Scale GAC Contactor1 | [16 empty] | Field 1-5: Effluent Water Quality For The 10-Minute, Pilot-Scale GAC Contactor (continued) | [18 empty] | Field 1-6: Effluent Water Quality For The 20-Minute, Pilot-Scale GAC Contactor1 | [16 empty] | Field 1-6: Effluent Water Quality For The 20-Minute, Pilot-Scale GAC Contactor (continued) | [18 empty] | Field 1-7: GAC Cost Parameters
|  | Input Design Parameters |  | US Standard Mesh Sizes |  |  |  |  | Group A, 15 influent samples per run | [40 empty] | Group B, 15 effluent samples per run | [35 empty] | Group C, 15 effluent samples per run
PWS Name | City of Durham, NC | Carbon manufacturer | Calgon | US standard | Opening | Process | Description | Scale | Sample | Was sample | Sampling | Sampling | Operation | Bed | Bed | pH | Turbidity | Alkalinity | Temp. | Total | Calcium | Ammonia | Bromide | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Cost Parameter | Parameter value
Public Water System Identification Number | NC 0332010 | Carbon trade name | Filtrasorb 400 | mesh size | (mm) | Coagulation | 20-40 mg/L Alum (Al2(SO4)3+ 5-15 mg/L Alkalinity | Full-Scale | ID | duplicated? | date | time | time | volumes | volumes |  |  |  |  | Hardness | Hardness | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | Capital Recovery Interest Rate (%) | 8
Water Industry Data Base Number (optional) | NA | Carbon type | Bituminous coal based | 4 | 4.75 | Flocculation | 3-Stage | Full-Scale |  | Y/N | MM/DD/YY | hh:mm | hh.hh | ( 20 minute) | ( 10 minute) | --- | ntu | mg/L as CaCO3 | oC | mg/L as CaCO3 | mg/L as CaCO3 | mg NH3-N / L | mg/L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | Capital Recovery Period (years) | 20
|  | Pilot GAC influent TOC (mg/L) | 2.3 | 6 | 3.35 | Sedimentation | Conv. Settling/ Continuous Sludge Removal | Full-Scale | START | --- | 1998-04-28 | 16:00 | 0 | 0 | 0 | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | START | --- | 1998-04-28 | 16:00 | 0 | 0 | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | START | --- | 1998-04-28 | 16:00 | 0 | 0 | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | Overhead & Profit Factor (% of construction costs) | 20
Official ICR Contact Person |  | Inner diameter of the pilot GAC column, D (mm) | 76.2 | 8 | 2.36 | Dual Media Filtration | Sand/Anthracite | Pilot | A1 | N | 1998-04-29 | 13:30 | 21.5 | 64.5 | 129 | 6.26 | 0.137 | 6 | 19.3 | 20 | 6.4 | BMRL | BMRL | 2.855 | 0.042 | 1.4711 | 2.5 | 0.85 | 1.65 | 22 | 7 | 24 | 131 | 24.6 | 4.01 | BMRL | BMRL | 28.61 | 1.53 | 6.322 | 1.46 | 1.23 | 1.49 | 1.4 | NA | NA | NA | 12.032 | 13.432 | B1 | N | 1998-04-29 | 13:30 | 21.5 | 129 | 5.69 | 0.127 | 19.3 | NR | BMRL | 0 | #VALUE! | 1 | 0.69 | 0.31 | 22 | 7 | 24 | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | C1 | N | 1998-04-29 | 13:30 | 21.5 | 64.5 | 5.75 | 0.15 | 19.3 | BMRL | BMRL | BMRL | #VALUE! | 1 | 0.63 | 0.37 | 22 | 7 | 24 | BMRL | 0.85 | BMRL | BMRL | BMRL | 0.85 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | Special Sitework Factor (% of construction costs) | 20
Mailing Address |  | Manufacturer reported dry bed density, r (kg/m3) | 448.56 | 10 | 2 |  |  |  | A2 | N | 1998-05-07 | 9:30 | 209.5 | 628.5 | 1257 | 6 | 0.1 | 5 | 20 | 19 | 22.5 | BMRL | BMRL | 2.855 | 0.042 | 1.4711 | 2.5 | 0.78 | 1.72 | 22 | 7 | 24 | 169 | 22.5 | 3.83 | BMRL | BMRL | 26.33 | 1.73 | 43.5 | 23.3 | 1.41 | 1.6 | 1.53 | NA | NA | NA | 71.54 | 73.07 | B2 | N | 1998-05-03 | 9:30 | 113.5 | 681 | 6.1 | 0.1 | 19 | BMRL | BMRL | NA | #VALUE! | 1.5 | 0.5 | 1 | 22 | 7 | 24 | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | C2 | N | 1998-05-07 | 9:30 | 209.5 | 628.5 | 6.1 | 0.1 | 19 | BMRL | BMRL | NA | #VALUE! | 1.5 | 1.09 | 0.41 | 22 | 7 | 24 | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | Construction Contingencies (% of construction costs) | 20
|  | Pilot GAC mesh size, upper (US standard mesh) | 12 | 12 | 1.68 |  |  |  | A3 | N | 1998-05-15 | 10:30 | 402.5 | 1207.5 | 2415 | 6 | 0.15 | 5 | 19 | 17 | 21.9 | BMRL | BMRL | 2.3 | 0.052 | 2.2609 | 2.5 | 0.97 | 1.53 | 22 | 7 | 24 | 150 | 24.65 | 4.06 | BMRL | BMRL | 28.71 | BMRL | 7.3 | 10.5 | 0.69 | BMRL | 0.7 | NA | NA | NA | 18.49 | 19.19 | B3 | N | 1998-05-07 | 9:30 | 209.5 | 1257 | 6 | 0.1 | 20 | BMRL | BMRL | 0.016 | #VALUE! | 1.5 | 0.89 | 0.61 | 22 | 7 | 24 | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | C3 | N | 1998-05-15 | 10:30 | 402.5 | 1207.5 | 6 | 0.15 | 19 | BMRL | BMRL | BMRL | #VALUE! | 1.5 | 1.03 | 0.47 | 22 | 7 | 24 | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | Engineering Fee Factor (% of construction costs) | 10
Phone Number |  | Pilot GAC mesh size, lower (US standard mesh) | 40 | 16 | 1.18 |  |  |  | Avg-A4 | Y | 1998-05-24 | 11:00 | 619 | 1857 | 3714 | 6 | 0.1 | 6 | 21 | 21 | NA | BMRL | BMRL | 2.27 | 0.049 | 2.1586 | 2.5 | 0.78 | 1.72 | 22 | 7 | 24 | 154.75 | 22.65 | 4.43 | BMRL | BMRL | 27.08 | 3.55 | 20.1 | 16.75 | 1.85 | BMRL | 1.45 | NA | NA | NA | 42.25 | 43.7 | B4 | N | 1998-05-11 | 9:00 | 305 | 1830 | 6.2 | 0.1 | 19 | BMRL | BMRL | 0.008 | #VALUE! | 1.5 | 0.71 | 0.79 | 22 | 7 | 24 | BMRL | 1.31 | BMRL | BMRL | BMRL | 1.31 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | C4-AVG | Y | 1998-05-24 | 11:00 | 619 | 1857 | 5.9 | 0.15 | 20 | BMRL | BMRL | BMRL | #VALUE! | 1.5 | 0.83 | 0.67 | 22 | 7 | 24 | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | BMRL | BMRL | BMRL | 1.35 | BMRL | BMRL | NA | NA | NA | 1.35 | 1.35 | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920
FAX Number |  | Flow rate, Q (L/hr) | 44.5 | 20 | 0.85 |  |  |  | A5 | N | 1998-06-01 | 9:00 | 809 | 2427 | 4854 | 5.9 | 0.2 | 5 | 23.5 | 25 | 21 | NA | BMRL | 2.845 | 0.042 | 1.4763 | 2.5 | 0.88 | 1.62 | 22 | 7 | 24 | 173.5 | 23.6 | 5.7 | BMRL | BMRL | 29.3 | 2.96 | 19.9 | 12.9 | 1.25 | BMRL | 1.35 | NA | NA | NA | 37.01 | 38.36 | B5-AVG | Y | 1998-05-15 | 10:30 | 402.5 | 2415 | 6 | 0.15 | 19 | BMRL | BMRL | 0.003 | #VALUE! | 1.5 | 1.05 | 0.45 | 22 | 7 | 24 | BMRL | 1.43 | BMRL | BMRL | BMRL | 1.43 | 4.73 | 10.88 | BMRL | 2.565 | BMRL | 6.95 | NA | NA | NA | 18.175 | 25.125 | C5 | N | 1998-06-01 | 9:00 | 809 | 2427 | 5.4 | 0.15 | 24 | BMRL | BMRL | 0.008 | #VALUE! | 1.5 | 0.95 | 0.55 | 22 | 7 | 24 | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | 1998 Producers Price Index (PPI base year 1967 = 100) | 367
E-Mail Address (optional) |  |  |  | 30 | 0.6 |  |  |  | A6 | N | 1998-06-09 | 10:30 | 1002.5 | 3007.5 | 6015 | 6.17 | 0.2 | 5 | 22.7 | 21 | NA | BMRL | BMRL | 2.847 | 0.054 | 1.8967 | 2.5 | 0.91 | 1.59 | 22 | 7 | 24 | 127 | 24.1 | 5.7 | BMRL | BMRL | 29.8 | 2.65 | 18.2 | 11 | 1.95 | BMRL | 1.4 | NA | NA | NA | 33.8 | 35.2 | B6 | N | 1998-05-20 | 8:45 | 520.75 | 3124.5 | 6.3 | 0.15 | 23 | BMRL | BMRL | 0.015 | #VALUE! | 1.5 | 1.02 | 0.48 | 22 | 7 | 24 | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | C6 | N | 1998-06-09 | 10:30 | 1002.5 | 3007.5 | 5.1 | 0.2 | 22.6 | BMRL | BMRL | BMRL | #VALUE! | 1.5 | 0.91 | 0.59 | 22 | 7 | 24 | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | Labor Rate + Fringe ($/work-hour) | 14.4
|  | Estimated Run Length |  | 40 | 0.425 |  |  |  | A7 | N | 1998-06-17 | 7:45 | 1191.75 | 3575.25 | 7150.5 | 6 | 0.15 | 8 | 25 | 22 | NA | BMRL | BMRL | 2.49 | 0.042 | 1.6867 | 2.5 | 0.77 | 1.73 | 22 | 7 | 24 | 139 | 22.85 | 4.19 | BMRL | BMRL | 27.04 | 2.5 | 22.8 | 11.5 | 1.5 | BMRL | 1.8 | NA | NA | NA | 38.3 | 40.1 | B7 | N | 1998-05-24 | 11:00 | 619 | 3714 | 6.2 | 0.1 | 20 | BMRL | BMRL | 0.011 | #VALUE! | 1.5 | 1.02 | 0.48 | 22 | 7 | 24 | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | BMRL | 1.2 | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 1.2 | 1.2 | C7 | N | 1998-06-17 | 7:45 | 1191.75 | 3575.25 | 5.1 | 0.1 | 25 | BMRL | BMRL | BMRL | #VALUE! | 1.5 | 0.72 | 0.78 | 22 | 7 | 24 | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | Labor Overhead Factor (% of labor) | 1.6
Technical ICR Contact Person |  | Bed volumes to 50% TOC breakthrough, BV50 | 7348.7512 | 50 | 0.3 |  |  |  | Avg-A8 | Y | 1998-06-25 | 10:00 | 1386 | 4158 | 8316 | 6.1 | 0.2 | 10 | 27 | 35 | NA | NA | 21 | 2.63 | 0.036 | 1.3688 | 2.5 | 0.58 | 1.92 | 22 | 7 | 24 | 179 | 28.505 | 5.77 | BMRL | BMRL | 34.275 | 2.58 | 8.4 | 18.04 | 1.82 | BMRL | 1.89 | NA | NA | NA | 30.84 | 32.73 | B8-AVG | Y | 1998-05-28 | 7:45 | 711.75 | 4270.5 | 5.5 | 0.15 | 23 | BMRL | 0.522 | BMRL | #VALUE! | 1.5 | 1.04 | 0.46 | 22 | 7 | 24 | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | C8-AVG | Y | 1998-06-25 | 10:00 | 1386 | 4158 | 5.3 | 0.1 | 27 | NA | BMRL | BMRL | #VALUE! | 1.5 | 0.49 | 1.01 | 22 | 7 | 24 | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | Electric Rate ($/kW-h) | 11.61
Mailing Address |  | Estimated run length, BVT (= 2 x BV50) | 14697.5025 | 60 | 0.25 |  |  |  | A9 | N | 1998-07-03 | 10:40 | 1578.6667 | 4736 | 9472 | 6.7 | 0.2 | 14 | 25.4 | 15 | NA | NA | 22 | 1.72 | 0.042 | 2.4419 | 2 | 0.49 | 1.51 | 22 | 7 | 18.5 | 149.5 | 31.75 | 6.25 | BMRL | BMRL | 38 | 4.21 | 12.15 | 19.64 | 1.75 | BMRL | 2.21 | NA | NA | NA | 37.75 | 39.96 | B9 | N | 1998-06-01 | 9:00 | 809 | 4854 | 5 | 0.15 | 24 | BMRL | BMRL | 0.004 | #VALUE! | 1.5 | 0.895 | 0.605 | 22 | 7 | 24 | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | C9 | N | 1998-07-03 | 10:40 | 1578.6667 | 4736 | 6.2 | 0.1 | 24.3 | NA | BMRL | BMRL | #VALUE! | 2.5 | 0.58 | 1.92 | 22 | 7 | 18.5 | BMRL | 1.63 | BMRL | BMRL | BMRL | 1.63 | BMRL | BMRL | BMRL | 1.52 | BMRL | BMRL | NA | NA | NA | 1.52 | 1.52 | Fuel Oil Rate ($/gal) | 0.58
|  |  |  | 70 | 0.21 |  |  |  | A10 | N | 1998-07-11 | 8:45 | 1768.75 | 5306.25 | 10612.5 | 6.2 | 0.1 | 9 | 25 | 21 | 6 | NA | BMRL | NA | 0.031 | #VALUE! | 3 | 1.07 | 1.93 | 22 | 7 | 24 | 196 | 30.5 | 5.67 | BMRL | BMRL | 36.17 | 4.87 | 11.98 | 20.92 | 1.92 | BMRL | 2.34 | NA | NA | NA | 39.69 | 42.03 | B10 | N | 1998-06-05 | 7:45 | 903.75 | 5422.5 | 5.2 | 0.15 | 24 | BMRL | BMRL | BMRL | #VALUE! | 1.5 | 0.89 | 0.61 | 22 | 7 | 24 | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | C10 | N | 1998-07-11 | 8:45 | 1768.75 | 5306.25 | 5.7 | 0.1 | 25 | NA | BMRL | BMRL | #VALUE! | 2 | 0.9 | 1.1 | 22 | 7 | 24 | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | 3.62 | 1.71 | 1.32 | 1.59 | BMRL | BMRL | NA | NA | NA | 8.24 | 8.24 | Natural Gas Rate ($/ft3) | NA
Phone Number |  | General Pilot Design Parameters |  | 80 | 0.18 |  |  |  | A11 | N | 1998-07-23 | 9:30 | 2057.5 | 6172.5 | 12345 | 6.1 | 0.2 | 9 | 25 | 16 | NA | NA | 24 | 2.846 | 0.042 | 1.4758 | 4.5 | 2.2 | 2.3 | 22 | 7 | 24 | 206 | 32.9 | 7.1 | BMRL | BMRL | 40 | 4.45 | 27.8 | 40 | 2.57 | BMRL | 1.71 | NA | NA | NA | 74.82 | 76.53 | B11 | N | 1998-06-10 | 10:30 | 1026.5 | 6159 | 6 | 0.2 | 23 | BMRL | BMRL | BMRL | #VALUE! | 1.5 | 0.77 | 0.73 | 22 | 7 | 24 | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | C11 | N | 1998-07-23 | 9:30 | 2057.5 | 6172.5 | 5.4 | 0.2 | 28 | NA | BMRL | BMRL | #VALUE! | 2 | 1.16 | 0.84 | 22 | 7 | 24 | BMRL | 1.12 | BMRL | BMRL | BMRL | 1.12 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | Current Process Water Rate ($/1000 gal) | 12.5
FAX Number |  | Carbon particle diameter, d (mm) | 1.0525 | [5 empty] | Avg-A12 | Y | 1998-08-04 | 9:15 | 2345.25 | 7035.75 | 14071.5 | 5.8 | 0.2 | 8 | 25 | 18 | 7.1 | NA | 26 | 2.97 | 0.035 | 1.1785 | 4.5 | 2.1 | 2.4 | 22 | 7 | 24 | 203.5 | 23.725 | 4.5 | BMRL | BMRL | 28.225 | 4.685 | 25.405 | 42.4 | 3.36 | BMRL | 2.055 | NA | NA | NA | 75.85 | 77.905 | B12-AVG | Y | 1998-06-16 | 7:30 | 1167.5 | 7005 | 5.7 | 0.15 | 25 | 0.07 | BMRL | BMRL | #VALUE! | 1.5 | 0.94 | 0.56 | 22 | 7 | 24 | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | C12-AVG | Y | 1998-08-04 | 9:15 | 2345.25 | 7035.75 | 5.8 | 0.2 | 25 | NA | BMRL | BMRL | #VALUE! | 1.5 | 1.24 | 0.26 | 22 | 7 | 24 | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | BMRL | 0.605 | 1.11 | BMRL | BMRL | BMRL | NA | NA | NA | 1.715 | 1.715 | Modifications to Existing Plant (% of construction costs) | 15
E-Mail Address (optional) |  | Column cross-sectional area, A (m2) | 0.0045604 | [5 empty] | A13 | N | 1998-08-16 | 12:10 | 2636.1667 | 7908.5 | 15817 | 6 | 0.2 | 7 | 27 | 23 | 9.1 | NA | 32 | 1.4335 | 0.032 | 2.2323 | 4.5 | 4 | 0.5 | 22 | 7 | 24 | 102.5 | 21.18 | 5.64 | 1.38 | BMRL | 28.2 | BMRL | 7.41 | 16.97 | 3.12 | BMRL | 1.61 | NA | NA | NA | 27.5 | 29.11 | B13 | N | 1998-06-22 | 9:30 | 1313.5 | 7881 | 5.6 | 0.2 | 28 | NA | BMRL | 0.012 | #VALUE! | 1.5 | 0.46 | 1.04 | 22 | 7 | 24 | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | C13 | N | 1998-08-16 | 12:10 | 2636.1667 | 7908.5 | 5.9 | 0.15 | 27 | NA | BMRL | BMRL | #VALUE! | 1 | 0.8 | 0.2 | 22 | 7 | 24 | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | BMRL | BMRL | BMRL | 1.3 | BMRL | BMRL | NA | NA | NA | 1.3 | 1.3
|  | Hydraulic loading rate1, v (m/hr) | 9.758 |  |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | A14 | N | 1998-08-27 | 9:00 | 2897 | 8691 | 17382 | 5.7 | 0.2 | 8 | 28 | 29 | 5.9 | NA | 50 | 3.3465 | 0.045 | 1.3447 | 4.5 | 1.21 | 3.29 | 22 | 7 | 24 | 190 | 27.29 | 6.27 | 1.13 | BMRL | 34.69 | 2.1 | 19.77 | 29.64 | 1.74 | BMRL | 2.36 | NA | NA | NA | 53.25 | 55.61 | B14 | Y | 1998-06-28 | 12:00 | 1460 | 8760 | 5.6 | 0.2 | 29 | NA | BMRL | BMRL | #VALUE! | 2 | 0.91 | 1.09 | 22 | 7 | 24 | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | C14 | N | 1998-08-27 | 9:00 | 2897 | 8691 | 5.6 | 0.125 | 28 | NA | BMRL | BMRL | #VALUE! | 1.5 | 0.95 | 0.55 | 22 | 7 | 24 | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | BMRL | 1.06 | 1.01 | BMRL | BMRL | BMRL | NA | NA | NA | 2.07 | 2.07
Plant Name | Brown Water Treatment Plant | 1: If v is not in the range from 5 to 15 m/hr (2 to 6 gpm/ft2) then either Q or D must be adjusted. |  |  |  | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | A15 | N | 1998-09-09 | 9:50 | 3209.8333 | 9629.5 | 19259 | 5.7 | 0.15 | 6 | 23 | 27 | NA | NA | BMRL | 3.672 | 0.05 | 1.3617 | 4.5 | 0.91 | 3.59 | 22 | 7 | 24 | 167 | 19.25 | 4.27 | BMRL | BMRL | 23.52 | 4.94 | 24.5 | 32.74 | 7.51 | BMRL | 2.48 | NA | NA | NA | 69.69 | 72.17 | B15 | N | 1998-08-25 | 9:15 | 2849.25 | 17095.5 | 5.5 | 0.25 | 28 | NA | BMRL | NR | #VALUE! | 1.5 | 0.76 | 0.74 | 22 | 7 | 24 | BMRL | 1.04 | BMRL | BMRL | BMRL | 1.04 | NR | NR | NR | NR | NR | NR | NA | NA | NA | NR | NR | C15 | N | 1998-09-06 | 9:50 | 3137.8333 | 9413.5 | NA | NA | NA | NA | BMRL | NA | #VALUE! | 1.5 | 0.2 | 1.3 | 22 | 7 | 24 | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | BMRL | BMRL | 1.16 | BMRL | BMRL | BMRL | NA | NA | NA | 1.16 | 1.16
Treatment Plant Category | CONV |  |  |  |  | is to list the pretreatment processes used in this particular pilot GAC run. |  |  | A16 | N | 1998-09-21 | 9:30 | 3497.5 | 10492.5 | 20985 | 6.1 | 0.1 | 11 | 25 | 24 | NA | NA | BMRL | NR | 0.05 | #VALUE! | 4.5 | 1.21 | 3.29 | 22 | 7 | 24 | 168 | 24.21 | 4.57 | BMRL | BMRL | 28.78 | 6.61 | 20.6 | 29.27 | 3.55 | BMRL | 2.07 | NA | NA | NA | 60.03 | 62.1 | B16 | N | 1998-08-31 | 9:30 | 2993.5 | 17961 | 5.3 | 0.1 | 28 | NA | BMRL | 0.013 | #VALUE! | 1.5 | 0.94 | 0.56 | 22 | 7 | 24 | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | BMRL | 1.37 | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 1.37 | 1.37 | C16 | N | 1998-09-21 | 9:30 | 3497.5 | 10492.5 | 5.9 | 0.1 | 24.5 | NA | BMRL | BMRL | #VALUE! | 2 | 0.85 | 1.15 | 22 | 7 | 24 | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | BMRL | 1.46 | 1.56 | BMRL | BMRL | BMRL | NA | NA | NA | 3.02 | 3.02
Process Train Name | Conventional | 10-Minute EBCT Run | [6 empty] | A17 | N | 1998-09-28 | 10:00 | 3666 | 10998 | 21996 | NA | NA | NA | NA | NA | NA | NA | NA | 2.41 | NA | #VALUE! | NA | NA | #VALUE! | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | B17 | N | 1998-09-08 | 12:15 | 3188.25 | 19129.5 | 6 | 0.1 | 28 | NA | NR | BMRL | #VALUE! | 1.5 | 1.17 | 0.33 | 22 | 7 | 24 | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | BMRL | BMRL | 1.16 | BMRL | BMRL | BMRL | NA | NA | NA | 1.16 | 1.16 | C17 | N | 1998-09-28 | 10:00 | 3666 | 10998 | NA | NA | NA | NA | BMRL | NA | #VALUE! | NA | NA | #VALUE! | NA | NA | NA | NA | NA | NA | NA | NA | 0 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
ICR Treatment Plant Identification Number | 450 | Empty bed contact time, EBCT (min) | 10 | [5 empty] | A18 | N | 1998-10-05 | 10:00 | 3834 | 11502 | 23004 | 6 | 0.2 | 9 | 21 | 29 | NA | NA | NA | 3.1 | 0.029 | 0.93548 | 4.5 | 1.46 | 3.04 | 22 | 7 | 24 | 182 | 22.39 | 4.03 | BMRL | BMRL | 26.42 | 5.99 | 14.56 | 32.48 | BMRL | BMRL | BMRL | NA | NA | NA | 53.03 | 53.03 | B18 | N | 1998-09-12 | 9:45 | 3281.75 | 19690.5 | 5.9 | 0.1 | 25 | NA | NR | BMRL | #VALUE! | 2.5 | 0.87 | 1.63 | 22 | 7 | 24 | BMRL | 5.09 | 2.16 | BMRL | BMRL | 7.25 | BMRL | 3.64 | 4.82 | BMRL | BMRL | BMRL | NA | NA | NA | 8.46 | 8.46 | C18 | N | 1998-10-05 | 9:30 | 3833.5 | 11500.5 | 5.6 | 0.05 | 21 | NA | 1.05 | BMRL | #VALUE! | 2 | 0.83 | 1.17 | 22 | 7 | 24 | BMRL | 2.09 | BMRL | BMRL | BMRL | 2.09 | BMRL | BMRL | BMRL | 1.43 | BMRL | BMRL | NA | NA | NA | 1.43 | 1.43
PWSID Number of Plant (if assigned) | NC 0332010 | Estimated run time, t (days) | 102.066 | [5 empty] | A19 | N | 1998-10-08 | 10:00 | 3906 | 11718 | 23436 | NA | NA | NA | NA | NA | NA | NA | BMRL | 3.17 | NA | #VALUE! | NA | NA | #VALUE! | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | B19 | N | 1998-09-21 | 9:30 | 3497.5 | 20985 | 5.9 | 0.15 | 25 | NA | NR | BMRL | #VALUE! | 2 | 0.97 | 1.03 | 22 | 7 | 24 | BMRL | 2.93 | 1.68 | BMRL | BMRL | 4.61 | BMRL | 4.98 | 3.22 | 1.42 | BMRL | BMRL | NA | NA | NA | 9.62 | 9.62 | C19 | N | 1998-10-08 | 10:00 | 3906 | 11718 | NA | NA | NA | NA | 1.15 | NA | #VALUE! | NA | NA | #VALUE! | NA | NA | NA | NA | NA | NA | NA | NA | 0 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Historical Minimum Water Temperature (oC) | 4 | Pilot column bed length, l (m) | 1.6263 | [5 empty] | A20 | N | 1998-10-13 | 13:30 | 4029.5 | 12088.5 | 24177 | 6.1 | 0.1 | 9 | 25 | 24 | NA | NA | BMRL | 3.25 | 0.045 | 1.3846 | 4.5 | 1.25 | 3.25 | 22 | 7 | 24 | 210 | 27.76 | 5 | BMRL | 1.55 | 34.31 | BMRL | 10.97 | 15.84 | 2.01 | BMRL | 1.44 | NA | NA | NA | 28.82 | 30.26 | B20 | N | 1998-09-24 | 9:30 | 3569.5 | 21417 | 5.7 | 0.1 | 23.5 | NA | 1.175 | BMRL | #VALUE! | 2 | 1.13 | 0.87 | 22 | 7 | 24 | BMRL | 5.13 | 2.24 | 1.09 | BMRL | 8.46 | BMRL | 2.28 | 2.88 | BMRL | BMRL | BMRL | NA | NA | NA | 5.16 | 5.16 | C20 | N | 1998-10-13 | 13:30 | 4029.5 | 12088.5 | 6 | 0.1 | 25 | NA | NR | BMRL | #VALUE! | 2 | 0.59 | 1.41 | 22 | 7 | 24 | BMRL | BMRL | BMRL | BMRL | 1.52 | 1.52 | BMRL | 2.5 | 1.56 | BMRL | BMRL | BMRL | NA | NA | NA | 4.06 | 4.06
Historical Average Water Temperature (oC) | 15 | Mass GAC required, m (kg) | 3.3268 | [5 empty] | A21 | N | 1998-10-21 | 10:10 | 4218.1667 | 12654.5 | 25309 | NA | NA | NA | NA | NA | NA | NA | BMRL | 2.3 | NA | #VALUE! | NA | NA | #VALUE! | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | B21 | N | 1998-09-30 | 9:30 | 3713.5 | 22281 | 5.9 | 0.1 | 25 | NA | 1.58 | BMRL | #VALUE! | 2 | 0.86 | 1.14 | 22 | 7 | 24 | BMRL | 5.54 | 2.57 | 1.3 | BMRL | 9.41 | BMRL | 2.72 | 3.53 | 1.05 | BMRL | BMRL | NA | NA | NA | 7.3 | 7.3 | C21 | N | 1998-10-21 | 10:10 | 4218.1667 | 12654.5 | NA | NA | NA | NA | 0.58 | NA | #VALUE! | NA | NA | #VALUE! | NA | NA | NA | NA | NA | NA | NA | NA | 0 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
State Approved Plant Capacity (MGD) | 30 | [7 empty] | A22 | N | 1998-11-03 | 9:00 | 4529 | 13587 | 27174 | 6.2 | 0.1 | 10 | 17 | 24 | NA | NA | 30 | 2.53 | 0.039 | 1.5415 | 4.5 | 1.69 | 2.81 | 22 | 7 | 24 | 180 | 22.6 | 5.34 | BMRL | BMRL | 27.94 | 1.95 | 12.6 | 24.7 | 1.33 | BMRL | 1.64 | NA | NA | NA | 40.58 | 42.22 | B22 | N | 1998-10-05 | 9:30 | 3833.5 | 23001 | 5.5 | 0.1 | 21 | NA | 1.7 | BMRL | #VALUE! | 2 | 0.7 | 1.3 | 22 | 7 | 24 | BMRL | 6.11 | 1.85 | BMRL | BMRL | 7.96 | BMRL | 4.42 | 5.64 | BMRL | BMRL | BMRL | NA | NA | NA | 10.06 | 10.06 | C22 | N | 1998-11-03 | 9:00 | 4529 | 13587 | 6.2 | 0.1 | 18 | NA | 0.69 | BMRL | #VALUE! | 2 | 0.51 | 1.49 | 22 | 7 | 24 | BMRL | 3.3 | 1.33 | BMRL | BMRL | 4.63 | BMRL | 2.27 | 3.54 | 1.07 | BMRL | BMRL | NA | NA | NA | 6.88 | 6.88
|  | 20-Minute EBCT Run | [6 empty] | A23 | N | 1998-11-10 | 9:30 | 4697.5 | 14092.5 | 28185 | 6.3 | 0.15 | 10 | 17 | 25 | NA | NA | 30 | 2.24 | 0.039 | 1.7411 | NA | NA | #VALUE! | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | B23 | N | 1998-10-13 | 13:30 | 4029.5 | 24177 | 6.1 | 0.1 | 25 | NA | 1.35 | 0.019 | 1.4074 | 2 | 0.4 | 1.6 | 22 | 7 | 24 | 50.5 | 10.09 | 3.45 | BMRL | BMRL | 13.54 | BMRL | 4.26 | 4.27 | 1.86 | BMRL | BMRL | NA | NA | NA | 10.39 | 10.39 | C23 | N | 1998-11-10 | 9:30 | 4697.5 | 14092.5 | 6.3 | 0.1 | 17 | NA | 0.657 | BMRL | #VALUE! | NA | NA | #VALUE! | NA | NA | NA | NA | NA | NA | NA | NA | 0 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
|  | Empty bed contact time, EBCT (min) | 20 | [5 empty] | A24 | N | 1998-11-17 | 9:30 | 4865.5 | 14596.5 | 29193 | 6.2 | 0.1 | 9 | 18 | 24 | 21.2 | NA | 20 | 2.505 | 0.021 | 0.83832 | 4.5 | 2.34 | 2.16 | 22 | 7 | 24 | 188.5 | 22.16 | 4.49 | BMRL | BMRL | 26.65 | 16.68 | 22.4 | 38.84 | 5.64 | BMRL | 1.51 | NA | NA | NA | 83.56 | 85.07 | B24 | N | 1998-10-20 | 10:00 | 4194 | 25164 | 6.2 | 0.1 | 21.5 | NA | 1.34 | NA | #VALUE! | NA | NA | #VALUE! | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | C24 | N | 1998-11-17 | 9:30 | 4865.5 | 14596.5 | 6.1 | 0.1 | 18 | NA | 0.825 | BMRL | #VALUE! | 2 | 1.42 | 0.58 | 22 | 7 | 24 | 65 | 3.01 | 1.62 | 1.21 | BMRL | 5.84 | BMRL | BMRL | 1.51 | 1.28 | BMRL | BMRL | NA | NA | NA | 2.79 | 2.79
|  | Estimated run time, t (days) | 204.132 | [5 empty] | A25 | N | 1998-11-24 | 11:30 | 5035.5 | 15106.5 | 30213 | 6.1 | 0.1 | 10 | 21 | 24 | 20 | NA | NA | 2.35 | 0.027 | 1.1489 | NA | NA | #VALUE! | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | B25 | N | 1998-11-03 | 9:00 | 4529 | 27174 | 6.2 | 0.1 | 18 | NA | 1.49 | 0.01 | 0.67114 | NA | NA | #VALUE! | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | C25 | N | 1998-11-24 | 11:30 | 5035.5 | 15106.5 | 6.2 | 0.05 | 20.5 | NA | 0.82 | BMRL | #VALUE! | NA | NA | #VALUE! | NA | NA | NA | NA | NA | NA | NA | NA | 0 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
|  | Pilot column bed length, l (m) | 3.2527 | [5 empty] | A26 | N | 1998-12-01 | 8:40 | 5200.6667 | 15602 | 31204 | 6 | 0.05 | 9 | 17.5 | 24 | 16.9 | NA | 30 | 2.2 | 0.027 | 1.2273 | 4.5 | 1.28 | 3.22 | 22 | 7 | 24 | 118.5 | 17.4 | 5.04 | BMRL | BMRL | 22.44 | 1.18 | 10.7 | 22.67 | 1.53 | BMRL | 1.49 | NA | NA | NA | 36.08 | 37.57 | B26 | N | 1998-11-10 | 9:30 | 4697.5 | 28185 | 6.3 | 0.15 | 17 | NA | 1.386 | 0.016 | 1.1544 | NA | NA | #VALUE! | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | C26 | N | 1998-12-01 | 8:40 | 5200.6667 | 15602 | 6.1 | 0.05 | 17 | NA | 1.46 | BMRL | #VALUE! | 2 | 1.14 | 0.86 | 22 | 7 | 24 | 49.5 | 6.54 | 3.2 | 1.09 | BMRL | 10.83 | BMRL | 5.23 | 7.03 | 1.23 | BMRL | BMRL | NA | NA | NA | 13.49 | 13.49
|  | Mass GAC required, m (kg) | 6.6536 | [5 empty] | A27 | N | 1998-12-08 | 10:00 | 5370 | 16110 | 32220 | 5.9 | 0.1 | 10 | 19 | 24 | 6.2 | NA | 40 | 2.545 | 0.042 | 1.6503 | 4.5 | 2.4 | 2.1 | 22 | 7 | 24 | 165 | 23.82 | 6.01 | BMRL | BMRL | 29.83 | 1.88 | 14.57 | 24.44 | 1.76 | BMRL | 1.77 | NA | NA | NA | 42.65 | 44.42 | B27 | N | 1998-11-17 | 9:30 | 4865.5 | 29193 | 6.1 | 0.1 | 18 | NA | 1.64 | BMRL | #VALUE! | 2 | 1.07 | 0.93 | 22 | 7 | 24 | 65 | 10.93 | 3.88 | 1.3 | BMRL | 16.11 | 6.08 | 5.52 | 2.89 | 1.98 | BMRL | 1.14 | NA | NA | NA | 16.47 | 17.61 | C27 | N | 1998-12-08 | 10:00 | 5370 | 16110 | 6 | 0.1 | 18 | NA | 1.415 | BMRL | #VALUE! | NA | NA | #VALUE! | NA | NA | NA | NA | NA | NA | NA | NA | 0 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
[9 empty] | A28 | N | 1998-12-17 | 9:30 | 5585.5 | 16756.5 | 33513 | 6.2 | 0.05 | 11 | 14 | 22 | 19.7 | NA | NA | 2.305 | NA | #VALUE! | NA | NA | #VALUE! | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | B28 | N | 1998-11-24 | 11:30 | 5035.5 | 30213 | 6.2 | 0.05 | 21 | NA | 1.61 | 0.011 | 0.68323 | NA | NA | #VALUE! | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | C28 | N | 1998-12-17 | 9:30 | 5585.5 | 16756.5 | 6.2 | 0.05 | 14 | NA | 1.195 | NA | #VALUE! | NA | NA | #VALUE! | NA | NA | NA | NA | NA | NA | NA | NA | 0 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
[9 empty] | A29 | N | 1998-12-22 | 10:00 | 5706 | 17118 | 34236 | 6.1 | 0.1 | 10 | 17 | 25 | 19.9 | NA | NA | 2.17 | 0.034 | 1.5668 | NA | NA | #VALUE! | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | B29 | N | 1998-12-01 | 8:40 | 5200.6667 | 31204 | 6.1 | 0.05 | 17.5 | NA | 1.73 | 0.016 | 0.92486 | NA | NA | #VALUE! | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | C29 | N | 1998-12-22 | 10:00 | 5706 | 17118 | 6.2 | 0.05 | 17.5 | NA | 1.135 | 0.012 | 1.0573 | NA | NA | #VALUE! | NA | NA | NA | NA | NA | NA | NA | NA | 0 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
[9 empty] | A30 | N | 1998-12-29 | 10:15 | 5874.25 | 17622.75 | 35245.5 | 6.3 | 0.05 | 10 | 11.5 | 25 | NA | NA | 30 | 2.58 | 0.035 | 1.3566 | 4.5 | 2.3 | 2.2 | 22 | 7 | 24 | 192 | 18.77 | 3.97 | BMRL | BMRL | 22.74 | 3.06 | 25.9 | 30.39 | 1.66 | BMRL | 1.29 | NA | NA | NA | 61.01 | 62.3 | B30 | N | 1998-12-08 | 10:00 | 5370 | 32220 | 6 | 0.1 | 18 | NA | 2.025 | BMRL | #VALUE! | 2 | 0.74 | 1.26 | 22 | 7 | 24 | 91 | 14.86 | 5.6 | 1.09 | BMRL | 21.55 | BMRL | 8.47 | 11.46 | BMRL | BMRL | 1.31 | NA | NA | NA | 19.93 | 21.24 | C30 | N | 1998-12-29 | 10:15 | 5874.25 | 17622.75 | 6.2 | 0.05 | 12 | NA | 1.49 | 0.01 | 0.67114 | 2 | 1.02 | 0.98 | 22 | 7 | 24 | 62 | 8.55 | 3.14 | 1.17 | BMRL | 12.86 | 1.89 | 8.1 | 5.38 | 1.03 | BMRL | 1.21 | NA | NA | NA | 16.4 | 17.61
[9 empty] | A31 | N | 1999-01-14 | 10:00 | 6258 | 18774 | 37548 | 6 | 1.9 | 8 | 10 | 22 | 16.4 | NA | 20 | 2.9 | 0.048 | 1.6552 | 4.5 | 1.71 | 2.79 | 22 | 7 | 24 | 223 | 33.89 | 3.75 | BMRL | BMRL | 37.64 | 4.53 | 53.58 | 30.39 | 2.26 | BMRL | 2.03 | NA | NA | NA | 90.76 | 92.79 | B31 | N | 1998-12-17 | 9:30 | 5585.5 | 33513 | 6.2 | 0.1 | 14 | NA | 1.69 | NA | #VALUE! | NA | NA | #VALUE! | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | C31 | N | 1999-01-12 | 10:00 | 6210 | 18630 | 6 | 0.1 | 10.5 | NA | 2.1 | 0.029 | 1.381 | 2 | 0.26 | 1.74 | 22 | 7 | 24 | 89 | 14.92 | 3.71 | BMRL | BMRL | 18.63 | 13.07 | 14.4 | 8.88 | 1.21 | BMRL | 1.21 | NA | NA | NA | 37.56 | 38.77
[9 empty] | A32 | N | 1999-01-20 | 9:30 | 6401.5 | 19204.5 | 38409 | 5.7 | 8.8 | 5 | 10 | 23 | 10.9 | NA | BMRL | 3.3 | NR | #VALUE! | 4.5 | 1.09 | 3.41 | 22 | 7 | 24 | 234 | 17.62 | 1.31 | BMRL | BMRL | 18.93 | 6.72 | 51.32 | 37.98 | BMRL | BMRL | 2.08 | NA | NA | NA | 96.02 | 98.1 | B32 | N | 1998-12-22 | 10:00 | 5706 | 34236 | 6.1 | 0.1 | 17.5 | NA | 1.68 | 0.02 | 1.1905 | NA | NA | #VALUE! | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | C32 | N | 1999-01-20 | 9:30 | 6401.5 | 19204.5 | 5.8 | 0.1 | 10.5 | NA | 2.42 | 0.027 | 1.1157 | 2 | 0.28 | 1.72 | 22 | 7 | 24 | 115 | 12.54 | 2.55 | BMRL | 1.5 | 16.59 | 3.01 | 15.54 | 8.91 | BMRL | BMRL | BMRL | NA | NA | NA | 27.46 | 27.46
[9 empty] | A33 | N | 1999-01-26 | 10:30 | 6546.5 | 19639.5 | 39279 | 6 | 2.5 | 5 | 11 | 21 | 12.5 | NA | NA | 3.21 | NR | #VALUE! | NA | NA | #VALUE! | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | B33 | N | 1998-12-29 | 10:15 | 5874.25 | 35245.5 | 6.2 | 0.05 | 11.5 | NA | 1.96 | 0.02 | 1.0204 | 2 | 1.14 | 0.86 | 22 | 7 | 24 | 105 | 14.28 | 4.48 | 1.13 | BMRL | 19.89 | 2.24 | 14.6 | 9.5 | BMRL | BMRL | 1.21 | NA | NA | NA | 26.34 | 27.55 | C33 | N | 1999-01-26 | 10:30 | 6546.5 | 19639.5 | 6 | 0.1 | 11.5 | NA | 2.37 | 0.033 | 1.3924 | NA | NA | #VALUE! | NA | NA | NA | NA | NA | NA | NA | NA | 0 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
[50 empty] | B34 | N | 1999-01-14 | 10:00 | 6258 | 37548 | 6 | 0.15 | 10 | NA | 2.74 | 0.033 | 1.2044 | 2 | 0.31 | 1.69 | 22 | 7 | 24 | 120.5 | 18.27 | 3.54 | BMRL | BMRL | 21.81 | 3.2 | 19.16 | 11.53 | 1.5 | BMRL | 1.49 | NA | NA | NA | 35.39 | 36.88
[50 empty] | B35 | N | 1999-01-20 | 9:30 | 6401.5 | 38409 | 5.8 | 0.1 | 10.5 | NA | 2.72 | 0.037 | 1.3603 | NA | NA | #VALUE! | NA | NA | NA | NA | NA | NA | NA | NA | 0 | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0 | 0
[50 empty] | B36 | N | 1999-01-26 | 10:30 | 6546.5 | 39279 | 6 | 0.1 | 11.5 | NA | 2.84 | 0.037 | 1.3028 | NA | NA | #VALUE! | NA | NA | NA | NA | NA | NA | NA | NA | 0 | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0 | 0
[9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [18 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [18 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
[9 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below. | [40 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below. | [35 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below.
[9 empty] | Group D, 3 duplicate influent samples per run | [40 empty] | Group D, 3 duplicate effluent samples per run | [35 empty] | Group D, 3 duplicate effluent samples per run
[9 empty] | Sample | Sample | Sampling | Sampling | Operation | Bed | Bed | pH | Turbidity | Alkalinity | Temp. | Total | Calcium | Ammonia | Bromide | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS
[9 empty] | ID | Type | date | time | time | volumes | volumes | [5 empty] | Hardness | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6
[11 empty] | MM/DD/YY | hh:mm | hh.hh | ( 20 minute) | ( 10 minute) | --- | ntu | mg/L as CaCO3 | oC | mg/L as CaCO3 | mg/L as CaCO3 | mg NH3-N / L | mg/L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L
[9 empty] | A4-1 | Primary | 1998-05-24 | 11:00 | 619 | 1857 | 3714 | 6 | 0.1 | 6 | 21 | 21 | NA | BMRL | BMRL | 2.261 | 0.049 | 2.1672 | 2.5 | 0.78 | 1.72 | 22 | 7 | 24 | 163 | 22.8 | 4.5 | BMRL | BMRL | 27.3 | 3.2 | 11.3 | 15.9 | 1.5 | BMRL | 1.4 | NA | NA | NA | 31.9 | 33.3 | B5-1 | Primary | 1998-05-15 | 10:30 | 402.5 | 2415 | 6 | 0.15 | 19 | BMRL | BMRL | BMRL | #VALUE! | 1.5 | 1.02 | 0.48 | 22 | 7 | 24 | BMRL | 1.3 | BMRL | BMRL | BMRL | 1.3 | 7.19 | 15.9 | BMRL | 2.84 | BMRL | 13.9 | NA | NA | NA | 25.93 | 39.83 | C4-1 | Primary | 1998-05-24 | 11:00 | 619 | 1857 | 5.9 | 0.15 | 20 | BMRL | BMRL | BMRL | #VALUE! | 1.5 | 0.83 | 0.67 | 22 | 7 | 24 | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | BMRL | BMRL | BMRL | 1.4 | BMRL | BMRL | NA | NA | NA | 1.4 | 1.4
[9 empty] | A4-2 | Duplicate | 1998-05-24 | 11:00 | 619 | 1857 | 3714 | 6 | 0.1 | 6 | 21 | 21 | NA | BMRL | BMRL | 2.281 | 0.049 | 2.1482 | 2.5 | NR | #VALUE! | 22 | 7 | 24 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | B5-2 | Duplicate | 1998-05-15 | 10:30 | 402.5 | 2415 | 6 | 0.15 | 19 | BMRL | BMRL | BMRL | #VALUE! | 1.5 | NA | #VALUE! | 22 | 7 | 24 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | C4-2 | Duplicate | 1998-05-24 | 11:00 | 619 | 1857 | 5.9 | 0.15 | 20 | BMRL | BMRL | BMRL | #VALUE! | 1.5 | NA | #VALUE! | 22 | 7 | 24 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR
[10 empty] | Average | --- | --- | --- | --- | --- | 6 | 0.1 | 6 | 21 | 21 | #DIV/0! | #DIV/0! | #DIV/0! | 2.271 | 0.049 | 2.1577 | 2.5 | 0.78 | #VALUE! | 22 | 7 | 24 | 163 | 22.8 | 4.5 | #DIV/0! | #DIV/0! | 27.3 | 3.2 | 11.3 | 15.9 | 1.5 | #DIV/0! | 1.4 | #DIV/0! | #DIV/0! | #DIV/0! | 31.9 | 33.3 |  | Average | --- | --- | --- | --- | 6 | 0.15 | 19 | #DIV/0! | #DIV/0! | #DIV/0! | #VALUE! | 1.5 | 1.02 | #VALUE! | 22 | 7 | 24 | #DIV/0! | 1.3 | #DIV/0! | #DIV/0! | #DIV/0! | 1.3 | 7.19 | 15.9 | #DIV/0! | 2.84 | #DIV/0! | 13.9 | #DIV/0! | #DIV/0! | #DIV/0! | 25.93 | 39.83 |  | Average | --- | --- | --- | --- | 5.9 | 0.15 | 20 | #DIV/0! | #DIV/0! | #DIV/0! | #VALUE! | 1.5 | 0.83 | #VALUE! | 22 | 7 | 24 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | 1.4 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1.4 | 1.4
[10 empty] | RPD | --- | --- | --- | --- | --- | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | 0.88067 | 0 | 0.88067 | 0 | #VALUE! | #VALUE! | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | RPD | --- | --- | --- | --- | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | RPD | --- | --- | --- | --- | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[9 empty] | A8-1 | Primary | 1998-06-25 | 10:00 | 1386 | 4158 | 8316 | 6.1 | 0.2 | 10 | 27 | 35 | NA | NA | 21 | 2.53 | 0.036 | 1.4229 | 2.5 | 0.58 | 1.92 | 22 | 7 | 24 | 173 | 27.59 | BMRL | BMRL | BMRL | 27.59 | 1.41 | 3.75 | 17.32 | 1.86 | BMRL | 1.75 | NA | NA | NA | 24.34 | 26.09 | B8-1 | Primary | 1998-05-28 | 7:45 | 711.75 | 4270.5 | 5.5 | 0.15 | 23 | BMRL | 0.522 | BMRL | #VALUE! | 1.5 | 1.04 | 0.46 | 22 | 7 | 24 | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | C8-1 | Primary | 1998-06-25 | 10:00 | 1386 | 4158 | 5.3 | 0.1 | 27 | NA | BMRL | BMRL | #VALUE! | 1.5 | 0.49 | 1.01 | 22 | 7 | 24 | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0
[9 empty] | A8-2 | Duplicate | 1998-06-25 | 10:00 | 1386 | 4158 | 8316 | 6.1 | 0.2 | 10 | 27 | 35 | NA | NA | 21 | 2.73 | 0.036 | 1.3187 | 2.5 | 0.58 | 1.92 | 22 | 7 | 24 | 185 | 29.42 | 5.77 | BMRL | BMRL | 35.19 | 3.75 | 13.05 | 18.75 | 1.78 | BMRL | 1.99 | NA | NA | NA | 37.33 | 39.32 | B8-2 | Duplicate | 1998-05-28 | 7:45 | 711.75 | 4270.5 | 5.5 | 0.15 | 23 | BMRL | 0.522 | BMRL | #VALUE! | 1.5 | NA | #VALUE! | 22 | 7 | 24 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | C8-2 | Duplicate | 1998-06-25 | 10:00 | 1386 | 4158 | 5.3 | 0.1 | 27 | NA | BMRL | BMRL | #VALUE! | 1.5 | 0.49 | 1.01 | 22 | 7 | 24 | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0
[10 empty] | Average | --- | --- | --- | --- | --- | 6.1 | 0.2 | 10 | 27 | 35 | #DIV/0! | #DIV/0! | 21 | 2.63 | 0.036 | 1.3708 | 2.5 | 0.58 | 1.92 | 22 | 7 | 24 | 179 | 28.505 | 5.77 | #DIV/0! | #DIV/0! | 31.39 | 2.58 | 8.4 | 18.035 | 1.82 | #DIV/0! | 1.87 | #DIV/0! | #DIV/0! | #DIV/0! | 30.835 | 32.705 |  | Average | --- | --- | --- | --- | 5.5 | 0.15 | 23 | #DIV/0! | 0.522 | #DIV/0! | #VALUE! | 1.5 | 1.04 | #VALUE! | 22 | 7 | 24 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 |  | Average | --- | --- | --- | --- | 5.3 | 0.1 | 27 | #DIV/0! | #DIV/0! | #DIV/0! | #VALUE! | 1.5 | 0.49 | 1.01 | 22 | 7 | 24 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0
[10 empty] | RPD | --- | --- | --- | --- | --- | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | 0 | 7.6046 | 0 | 7.6046 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7039 | 6.4199 | #VALUE! | #VALUE! | #VALUE! | 24.2115 | NR | NR | 7.929 | 4.3956 | #VALUE! | 12.8342 | #VALUE! | #VALUE! | #VALUE! | 42.1275 | 40.4525 |  | RPD | --- | --- | --- | --- | 0 | 0 | 0 | #VALUE! | 0 | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | RPD | --- | --- | --- | --- | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #DIV/0! | #DIV/0!
[9 empty] | A12-1 | Primary | 1998-08-04 | 9:15 | 2345.25 | 7035.75 | 14071.5 | 5.8 | 0.2 | 6 | 25 | 18 | NA | NA | 26 | 3.055 | 0.029 | 0.94926 | 2.5 | 1.19 | 1.31 | 22 | 7 | 24 | 200 | 25.04 | 5.27 | 0.88 | BMRL | 31.19 | 5.18 | 27.68 | 44.91 | 3.99 | BMRL | 2.07 | NA | NA | NA | 81.76 | 83.83 | B12-1 | Primary | 1998-06-16 | 7:30 | 1167.5 | 7005 | 5.7 | 0.15 | 25 | 0.07 | BMRL | BMRL | #VALUE! | 1.5 | 0.94 | 0.56 | 22 | 7 | 24 | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | C12-1 | Primary | 1998-08-04 | 9:15 | 2345.25 | 7035.75 | 5.8 | 0.2 | 25 | NA | BMRL | BMRL | #VALUE! | 1.5 | 1.29 | 0.21 | 22 | 7 | 24 | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | BMRL | 1.21 | 1.13 | BMRL | BMRL | BMRL | NA | NA | NA | 2.34 | 2.34
[9 empty] | A12-2 | Duplicate | 1998-08-04 | 9:15 | 2345.25 | 7035.75 | 14071.5 | 5.8 | 0.2 | 6 | 25 | 18 | NA | NA | NA | 2.89 | 0.029 | 1.0035 | 2.5 | 1.19 | 1.31 | 22 | 7 | 24 | 207 | 22.41 | 3.73 | BMRL | BMRL | 26.14 | 4.19 | 23.13 | 39.89 | 2.73 | BMRL | 2.04 | NA | NA | NA | 69.94 | 71.98 | B12-2 | Duplicate | 1998-06-16 | 7:30 | 1167.5 | 7005 | 5.7 | 0.15 | 25 | NA | BMRL | BMRL | #VALUE! | 1.5 | NA | #VALUE! | 22 | 7 | 24 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | C12-2 | Duplicate | 1998-08-04 | 9:15 | 2345.25 | 7035.75 | 5.8 | 0.2 | 25 | NA | BMRL | BMRL | #VALUE! | 1.5 | 1.19 | 0.31 | 22 | 7 | 24 | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | BMRL | BMRL | 1.09 | BMRL | BMRL | BMRL | NA | NA | NA | 1.09 | 1.09
[10 empty] | Average | --- | --- | --- | --- | --- | 5.8 | 0.2 | 6 | 25 | 18 | #DIV/0! | #DIV/0! | 26 | 2.9725 | 0.029 | 0.97636 | 2.5 | 1.19 | 1.31 | 22 | 7 | 24 | 203.5 | 23.725 | 4.5 | 0.88 | #DIV/0! | 28.665 | 4.685 | 25.405 | 42.4 | 3.36 | #DIV/0! | 2.055 | #DIV/0! | #DIV/0! | #DIV/0! | 75.85 | 77.905 |  | Average | --- | --- | --- | --- | 5.7 | 0.15 | 25 | 0.07 | #DIV/0! | #DIV/0! | #VALUE! | 1.5 | 0.94 | #VALUE! | 22 | 7 | 24 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 |  | Average | --- | --- | --- | --- | 5.8 | 0.2 | 25 | #DIV/0! | #DIV/0! | #DIV/0! | #VALUE! | 1.5 | 1.24 | 0.26 | 22 | 7 | 24 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 1.21 | 1.11 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1.715 | 1.715
[10 empty] | RPD | --- | --- | --- | --- | --- | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | 5.5509 | 0 | 5.5509 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4398 | 11.0854 | 34.2222 | #VALUE! | #VALUE! | 17.6173 | 21.1313 | 17.9099 | 11.8396 | 37.5 | #VALUE! | 1.4599 | #VALUE! | #VALUE! | #VALUE! | 15.5834 | 15.2108 |  | RPD | --- | --- | --- | --- | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | RPD | --- | --- | --- | --- | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 8.0645 | 38.4615 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #DIV/0! | #VALUE! | #VALUE! | 3.6036 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 72.8863 | 72.8863
[9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [18 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [18 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
Note on AD30: Value was verified by lab.
Note on AD31: Value was verified by lab.
Note on AD40: cahughes: Value reported as 0.125 cm-1. Questionable date so it was changed to NR.
Note on AD41: cahughes: cahughes: Value reported as 0.075 cm-1. Questionable date so it was changed to NR.
Note on AH21: Value verified. No reason for low chlorine demand available.
Note on AI9: All SDS temperatures reported were measured values.
Note on AJ9: cahughes: Reflects measured values, not target values
Note on AK9: cahughes: Incubation time reflects measured results, not target results.
Note on AR63: cahughes: Original RPD was 90.7. Value verified by lab. No apparent reason for high relative percent difference. Because result was quesitonable, changed to NR
Note on AS59: Value verified by lab. No reason for high relative percent difference was available.
Note on AS63: Original RPD was 110.7. Value verified by lab. No apparent reason for high relative percent difference. Because result was quesitonable, changed to NR
Note on CL13: Lab verified concentration
Note on DO19: Lab verified this concentration. Typo in original submittal.