## Sheet1. 1st Pilot Study
FIELD-SET 1: RESULTS FROM 1st PILOT-SCALE STUDY (FILE: gacpilot.xls)
Field 1-1: PWS And Treatment Plant Data |  | Field 1-2: Pilot-Scale GAC Design Parameters |  |  |  | Field 1-3: Pretreatment Used Prior To GAC1 |  |  | Field 1-4: Influent Water Quality For The 10- And 20-Minute, Pilot-Scale GAC Contactors1 | [14 empty] | Field 1-4: Influent Water Quality For The 10- And 20-Minute, Pilot-Scale GAC Contactors (continued) | [15 empty] | Field 1-4: Influent Water Quality For The 10- And 20-Minute, Pilot-Scale GAC Contactors (continued) | [9 empty] | Field 1-5: Effluent Water Quality For The 10-Minute, Pilot-Scale GAC Contactor1 | [16 empty] | Field 1-5: Effluent Water Quality For The 10-Minute, Pilot-Scale GAC Contactor (continued) | [18 empty] | Field 1-6: Effluent Water Quality For The 20-Minute, Pilot-Scale GAC Contactor1 | [16 empty] | Field 1-6: Effluent Water Quality For The 20-Minute, Pilot-Scale GAC Contactor (continued) | [18 empty] | Field 1-7: GAC Cost Parameters
|  | Input Design Parameters |  | US Standard Mesh Sizes |  |  |  |  | Group A, 15 influent samples per run | [40 empty] | Group B, 15 effluent samples per run | [35 empty] | Group C, 15 effluent samples per run
PWS Name | Fort Worth Water Department | Carbon manufacturer | Calgon Corporation | US standard | Opening | Process | Description | Scale | Sample | Was sample | Sampling | Sampling | Operation | Bed | Bed | pH | Turbidity | Alkalinity | Temp. | Total | Calcium | Ammonia | Bromide | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Cost Parameter | Parameter value
Public Water System Identification Number | TX2200012 | Carbon trade name | Filtrasorb - F820 | mesh size | (mm) | Coagulation | 50% Ferric Sulfate solution - Avg. Dose = 31.6 mg/L; Std. Deviation = 8.4 / CATFLOC Polymer - Avg. Dose = 2.1 mg/L; Std. Deviation = 0.2 | Pilot-scale | ID | duplicated? | date | time | time | volumes | volumes |  |  |  |  | Hardness | Hardness | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | Capital Recovery Interest Rate (%) | 7
Water Industry Data Base Number (optional) | 1503 | Carbon type | Bituminous | 4 | 4.75 | Rapid Mixing | 3/4"x7" In-line static mixers (6 mixing elements) | Pilot-scale |  | Y/N | MM/DD/YY | hh:mm | hh.hh | ( 20 minute) | ( 10 minute) | --- | ntu | mg/L as CaCO3 | oC | mg/L as CaCO3 | mg/L as CaCO3 | mg NH3-N / L | mg/L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | Capital Recovery Period (years) | 20
|  | Pilot GAC influent TOC (mg/L) | 3.3 | 6 | 3.35 | Flocculation | 3-flocculation stages with floc paddles operating at 65, 50, and 30 rpm (detention time is 8 min./stage) | Pilot-scale | START | --- | 1998-04-14 | 14:00 | 0 | 0 | 0 | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | START | --- | 1998-04-14 | 14:00 | 0 | 0 | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | START | --- | 1998-04-14 | 14:00 | 0 | 0 | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | Overhead & Profit Factor (% of construction costs) | 57.1
Official ICR Contact Person |  | Inner diameter of the pilot GAC column, D (mm) | 76.2 | 8 | 2.36 | Sedimentation | Basin includes a tube settler and has a detention time of 1 1/2 hours | Pilot-scale | Avg-A1 | Y | 1998-04-15 | 15:45 | 25.75 | 77.25 | 154.5 | 7.86 | 0.21 | 132.5 | 25.2 | 139 | 127 | BMRL | 220 | 3.45 | 0.062 | 1.7971 | 3.5 | 0.35 | 3.15 | 21 | 7.95 | 23.8 | 217.5 | 28.5 | 38 | 39 | 8.4 | 113.9 | BMRL | 11 | 7.6 | 2.4 | 10.45 | 14.5 | NR | NR | 12.5 | 31.45 | 45.95 | Avg-A1 | Y | 1998-04-15 | 15:45 | 25.75 | 154.5 | 8.39 | 0.22 | 24.7 | BMRL | BMRL | 0 | -- | 1 | 0.45 | 0.55 | 21 | 8.25 | 23.8 | BMRL | BMRL | BMRL | 1.45 | 2.85 | 4.3 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NR | NR | BMRL | 0 | 0 | Avg-A1 | Y | 1998-04-15 | 15:45 | 25.75 | 77.25 | 8.3 | 0.27 | 24.5 | BMRL | BMRL | 0.001 | -- | 1 | 0.38 | 0.62 | 21 | 8.1 | 23.8 | BMRL | BMRL | BMRL | 1 | 1.7 | 2.7 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NR | NR | BMRL | 0 | 0 | Special Sitework Factor (% of construction costs) | 10
Mailing Address |  | Manufacturer reported dry bed density, r (kg/m3) | 505.7 | 10 | 2 | Filtration | 3"-dia. dual media (sand/anthracite with gravel support), declining rate columns | Pilot-scale | A2 | N | 1998-04-29 | 12:30 | 348.5 | 1045.5 | 2091 | 7.64 | 0.41 | 135 | 21.4 | 173 | 132 | BMRL | 220 | 3.3 | 0.072 | 2.1818 | 4 | 0.75 | 3.25 | 23.3 | 8 | 24.8 | 280 | 34 | 41 | 46 | 10 | 131 | 3.6 | 15 | 9.8 | 2.4 | 12 | 14 | 6.1 | 11 | 14 | 42.8 | 56.8 | A2 | N | 1998-04-28 | 18:30 | 330.5 | 1983 | 7.43 | 0.28 | 23.1 | BMRL | 0.8 | 0.01 | 1.25 | 1.4 | 0.6 | 0.8 | 21.4 | 8.2 | 24 | 44 | BMRL | 2.5 | 11 | 21 | 34.5 | BMRL | 1.2 | BMRL | 1 | 5.5 | 2 | 6.3 | 2.6 | 1.1 | 7.7 | 9.7 | A2 | N | 1998-04-29 | 12:30 | 348.5 | 1045.5 | 7.6 | 0.25 | 22 | BMRL | BMRL | 0.002 | -- | 1.1 | 0.85 | 0.25 | 23.4 | 8.2 | 24.5 | NR | BMRL | BMRL | 1.9 | 4.2 | 6.1 | BMRL | BMRL | BMRL | BMRL | 1.4 | BMRL | BMRL | BMRL | BMRL | 1.4 | 1.4 | Construction Contingencies (% of construction costs) | 25
|  | Pilot GAC mesh size, upper (US standard mesh) | 8 | 12 | 1.68 |  |  |  | A3 | N | 1998-05-11 | 18:30 | 639.75 | 1919.25 | 3838.5 | 7.76 | 0.22 | 130 | 24.7 | 178 | 132 | BMRL | 220 | 3.2 | 0.07 | 2.1875 | 3.5 | 0.6 | 2.9 | 23.5 | 8.1 | 24 | 265 | 30 | 42 | 50 | 15 | 137 | 2.1 | 13 | 7.5 | 2 | 12 | 16 | BMRL | 10 | 12 | 36.6 | 52.6 | A3 | N | 1998-04-30 | 17:30 | 377.5 | 2265 | 7.51 | 0.29 | 24.1 | BMRL | 1.1 | 0.012 | 1.0909 | 1.7 | 0.8 | 0.9 | 22.8 | 8.1 | 24.8 | 53 | 1.5 | 4.5 | 17 | 26 | 49 | BMRL | 1.4 | BMRL | 1.6 | 7.5 | 2.8 | 8.5 | 3.6 | 1.5 | 10.5 | 13.3 | A3 | N | 1998-05-11 | 18:45 | 640 | 1920 | 7.64 | 0.21 | 24.2 | BMRL | 0.6 | 0.008 | 1.3333 | 1.1 | 0.45 | 0.65 | 23.4 | 8.1 | 24 | 25 | BMRL | 1.3 | 7.2 | 17 | 25.5 | BMRL | BMRL | BMRL | 1.9 | 3.5 | 1.4 | BMRL | 2.2 | BMRL | 5.4 | 6.8 | Engineering Fee Factor (% of construction costs) | 15
Phone Number |  | Pilot GAC mesh size, lower (US standard mesh) | 20 | 16 | 1.18 |  |  |  | A4 | N | 1998-05-19 | 17:00 | 827.25 | 2481.75 | 4963.5 | 7.87 | 0.33 | 125 | 30.2 | 175 | 130 | BMRL | 210 | 3.1 | 0.064 | 2.0645 | 3 | 0.6 | 2.4 | 27.8 | 8.1 | 24 | 230 | 28 | 41 | 48 | 15 | 132 | 2 | 11 | 6.2 | 2.1 | 12 | 14 | BMRL | 8.4 | 11 | 33.3 | 47.3 | A4 | N | 1998-05-04 | 18:15 | 472.25 | 2833.5 | 7.61 | 0.19 | 24.4 | BMRL | 1.2 | 0.017 | 1.4167 | 1.8 | 0.4 | 1.4 | 23.9 | 8.5 | 24 | 80 | 1.7 | 5.8 | 21 | 27 | 55.5 | BMRL | 1.5 | BMRL | 2.1 | 9.5 | 3.8 | NR | 4.3 | 1.7 | 13.1 | 16.9 | A4 | N | 1998-05-19 | 16:45 | 827 | 2481 | 7.56 | 0.2 | 29.9 | BMRL | 1 | 0.011 | 1.1 | 1.3 | 0.3 | 1 | 26.5 | 8.3 | 24 | 49 | BMRL | 2.2 | 12 | 31 | 45.2 | BMRL | 1.2 | BMRL | 1.5 | 8.8 | 1.9 | 5.4 | 2.2 | BMRL | 11.5 | 13.4 | 1998 ENR Construction Cost Index (CCI base year 1913) | 6095.24
FAX Number |  | Flow rate, Q (L/hr) | 30 | 20 | 0.85 |  |  |  | A5 | N | 1998-05-29 | 13:45 | 1064 | 3192 | 6384 | 7.84 | 0.33 | 115 | 27.9 | 163 | 122 | BMRL | 220 | 3.5 | 0.065 | 1.8571 | 3.3 | 0.5 | 2.8 | 26.5 | 8.2 | 24 | 240 | 30 | 43 | 50 | 17 | 140 | 2.2 | 9.5 | 4.7 | 1.5 | 11 | 11 | 4.8 | 8.1 | 8.4 | 28.9 | 39.9 | A5 | N | 1998-05-08 | 11:45 | 561.75 | 3370.5 | 7.62 | 0.17 | 23.3 | BMRL | 1.6 | 0.025 | 1.5625 | 1.9 | 0.1 | 1.8 | 23.6 | 8.1 | 24.3 | 94 | 2.6 | 9.3 | 29 | 29 | 69.9 | BMRL | 2.1 | 1 | 2.2 | 12 | 5.8 | NR | 5.8 | 2.4 | 17.3 | 23.1 | A5 | N | 1998-05-29 | 13:45 | 1064 | 3192 | 7.59 | 0.28 | 27.9 | 0.07 | 1.2 | 0.016 | 1.3333 | 1.5 | 0.5 | 1 | 26.6 | 8.2 | 24 | 56 | 1.2 | 4.9 | 25 | 42 | 73.1 | BMRL | 1.3 | BMRL | 1.5 | 8.8 | 2.8 | 6.8 | 3.5 | 1.6 | 11.6 | 14.4 | 1998 Producers Price Index (PPI base year 1967 = 100) | NA
E-Mail Address (optional) |  |  |  | 30 | 0.6 |  |  |  | A6 | N | 1998-06-03 | 17:45 | 1188 | 3564 | 7128 | 7.85 | 0.6 | 125 | 27.7 | 163 | 117 | 0.05 | NA | 3.3 | 0.064 | 1.9394 | 3.5 | 0.6 | 2.9 | 22.6 | 7.9 | 24 | 240 | 25 | 35 | 42 | 14 | 116 | 2.2 | 12 | 7.8 | 2.2 | 12 | 14 | 5.3 | 10 | 12 | 36.2 | 50.2 | A6 | N | 1998-05-11 | 18:15 | 640.25 | 3841.5 | 7.7 | 0.18 | 24.6 | 0.06 | 1.6 | 0.028 | 1.75 | 2.1 | 0.4 | 1.7 | 23.5 | 8.1 | 24 | 110 | 3.9 | 14 | 42 | 38 | 97.9 | BMRL | 2.7 | 1.2 | 2.6 | 12 | 6.7 | 6.2 | 6.7 | 3.3 | 18.5 | 25.2 | A6 | N | 1998-06-03 | 17:45 | 1188 | 3564 | 7.6 | 0.33 | 27.7 | 0.07 | 1.4 | 0.019 | 1.3571 | 2 | 0.8 | 1.2 | 22.6 | NA | 24 | 75 | 1.5 | 6.1 | 22 | 27 | 56.6 | BMRL | 2.3 | 1.4 | 1.8 | 10 | 2.4 | 7.7 | 5.1 | 2.4 | 15.5 | 17.9 | Labor Rate + Fringe ($/work-hour) | 27.2
|  | Estimated Run Length |  | 40 | 0.425 |  |  |  | A7 | N | 1998-06-09 | 13:45 | 1326 | 3978 | 7956 | 7.9 | 0.5 | 125 | 29.5 | 161 | 120 | 0.06 | 220 | 3.1 | 0.064 | 2.0645 | 3.5 | 0.75 | 2.75 | 23.9 | 8.2 | 24 | 250 | 33 | 43 | 50 | 17 | 143 | 2.5 | 12 | 5.5 | 2.4 | 14 | 16 | 7 | 8.8 | 10 | 36.4 | 52.4 | A7 | N | 1998-05-13 | 18:00 | 688 | 4128 | 7.73 | 0.22 | 23.2 | BMRL | 1.7 | 0.033 | 1.9412 | 2.1 | 0.65 | 1.45 | 23.3 | 8.1 | 24 | 115 | 4.4 | 16 | 46 | 38 | 104.4 | BMRL | 3 | 1 | 2.6 | 13 | 7.4 | 6.4 | 7.2 | 3.6 | 19.6 | 27 | A7 | N | 1998-06-09 | 13:45 | 1326 | 3978 | 7.42 | 0.25 | 29.5 | BMRL | 1.5 | 0.022 | 1.4667 | 2.2 | 0.7 | 1.5 | 23.9 | 8.3 | 24 | 94 | 2.5 | 10 | 32 | 38 | 82.5 | BMRL | 1.8 | BMRL | 2.1 | 12 | 5.6 | 9.2 | 5.1 | 2.9 | 15.9 | 21.5 | Labor Overhead Factor (% of labor) | 33
Technical ICR Contact Person |  | Bed volumes to 50% TOC breakthrough, BV50 | 4596.1227 | 50 | 0.3 |  |  |  | Avg-A8 | Y | 1998-06-17 | 12:30 | 1516.75 | 4550.25 | 9100.5 | 7.9 | 0.45 | 120 | 28.7 | 161.5 | 118.5 | 0.13 | 230 | 3.45 | 0.062 | 1.7971 | 3.5 | 0.2 | 3.3 | 25.9 | 8.05 | 24 | 250 | 37 | 48 | 51 | 16 | 152 | 3.05 | 11.5 | 6.6 | 2.65 | 13 | 15 | BMRL | 8.55 | 10.5 | 36.8 | 51.8 | Avg-A8 | Y | 1998-05-21 | 17:15 | 876.25 | 5257.5 | 7.66 | 0.27 | 29.2 | BMRL | 2.05 | 0.032 | 1.561 | 2.3 | 0.6 | 1.7 | 24 | 8.2 | 24.5 | 147.5 | 6.75 | 18.5 | 42.5 | 30.5 | 98.25 | BMRL | 4.1 | 1.7 | 2 | 13.5 | 8.25 | 7.5 | 7.65 | 4.8 | 21.3 | 29.55 | Avg-A8 | Y | 1998-06-17 | 12:45 | 1517 | 4551 | 7.75 | 0.25 | 28 | BMRL | 1.9 | 0.025 | 1.3158 | 2.3 | 0.48 | 1.82 | 26.2 | 8.15 | 24 | 125 | 6.5 | 18 | 49 | 39.5 | 113 | BMRL | 3 | 1.6 | 2.2 | 14 | 7.5 | 6.2 | 5.95 | 3.5 | 20.8 | 28.3 | Electric Rate ($/kW-h) | 0.06
Mailing Address |  | Estimated run length, BVT (= 2 x BV50) | 9192.2454 | 60 | 0.25 |  |  |  | A9 | N | 1998-06-26 | 12:00 | 1729.25 | 5187.75 | 10375.5 | 8.05 | 0.49 | 120 | 24.3 | 156 | 115 | BMRL | 230 | 3.1 | 0.053 | 1.7097 | 4 | 0.65 | 3.35 | 21.2 | 8.2 | 24.3 | 255 | 33 | 44 | 47 | 15 | 139 | 2.2 | 13 | 8.1 | 2.9 | 14 | 16 | NR | 10 | 12 | 40.2 | 56.2 | A9 | N | 1998-05-29 | 13:45 | 1064.75 | 6388.5 | 7.62 | 0.22 | 27.9 | BMRL | 2.2 | 0.035 | 1.5909 | 2.5 | 0.6 | 1.9 | 26.5 | 8.2 | 24 | 140 | 8.2 | 23 | 50 | 34 | 115.2 | BMRL | 4.4 | 2 | 1.7 | 13 | 8.2 | 7.7 | 7.9 | 5.1 | 21.1 | 29.3 | A9 | N | 1998-06-26 | 12:00 | 1729.25 | 5187.75 | 7.9 | 0.26 | 23.9 | BMRL | 1.8 | 0.018 | 1 | 2.5 | 0.45 | 2.05 | 21.3 | 8.1 | 24.3 | 120 | 5.1 | 16 | 40 | 35 | 96.1 | BMRL | 3.4 | 2.2 | 2 | 13 | 7.7 | NR | 6.8 | 4.2 | 20.6 | 28.3 | Fuel Oil Rate ($/gal) | NA
|  |  |  | 70 | 0.21 |  |  |  | A10 | N | 1998-07-03 | 11:15 | 1896.5 | 5689.5 | 11379 | 7.79 | 0.35 | 115 | 23.8 | 160 | 115 | 0.09 | 240 | 3.5 | 0.07 | 2 | 4.1 | 0.4 | 3.7 | 23.6 | 8 | 24 | 265 | 41 | 55 | 58 | 19 | 173 | 2.6 | 14 | 7.5 | 2.6 | 13 | 15 | BMRL | 9 | 9.7 | 39.7 | 54.7 | A10 | N | 1998-06-03 | 17:45 | 1188.75 | 7132.5 | 7.65 | 0.27 | 27.7 | 0.07 | 2.4 | 0.036 | 1.5 | 2.5 | 0.6 | 1.9 | 22.6 | 8 | 24 | 140 | 6.8 | 19 | 42 | 29 | 96.8 | BMRL | 5.3 | 2.6 | 2 | 14 | 9.4 | 6.9 | 7.3 | 4.4 | 23.9 | 33.3 | A10 | N | 1998-07-03 | 11:15 | 1896.5 | 5689.5 | 7.67 | 0.26 | 23.8 | 0.08 | 1.8 | 0.035 | 1.9444 | 2.8 | 0.6 | 2.2 | 24 | 8 | 24 | 135 | 7 | 21 | 50 | 42 | 120 | BMRL | 4 | 2.3 | 2.3 | 14 | 8.1 | 9.9 | 6.3 | 4.1 | 22.6 | 30.7 | Natural Gas Rate ($/ft3) | 5.3
Phone Number |  | General Pilot Design Parameters |  | 80 | 0.18 |  |  |  | A11 | N | 1998-07-10 | 18:00 | 2068.25 | 6204.75 | 12409.5 | 7.81 | 0.42 | 110 | 23.7 | 148 | 102 | BMRL | 280 | 3.8 | 0.074 | 1.9474 | 4.3 | 0.3 | 4 | 24.2 | 8.1 | 23.8 | 290 | 58 | 57 | 61 | 20 | 196 | 3.2 | 15 | 8.6 | 2.4 | 14 | 16 | 7.7 | 9.8 | 11 | 43.2 | 59.2 | A11 | N | 1998-06-09 | 13:45 | 1326.75 | 7960.5 | 7.54 | 0.25 | 29.5 | BMRL | 2.3 | 0.04 | 1.7391 | 2.8 | 0.8 | 2 | 23.9 | 8.3 | 24 | 165 | 10 | 26 | 51 | 30 | 117 | 2 | 5 | 2.1 | 1.9 | 15 | 11 | 8.9 | 8.1 | 6.1 | 26 | 37 | A11 | N | 1998-07-10 | 18:00 | 2068.25 | 6204.75 | 7.72 | 0.27 | 25 | BMRL | 2.1 | 0.039 | 1.8571 | 3.1 | 0.6 | 2.5 | 24.9 | 8.1 | 23.8 | NR | 12 | 30 | 56 | 39 | 137 | BMRL | 5.3 | 3.1 | 2.4 | 16 | 10 | 15 | 8.2 | 5.3 | 26.8 | 36.8 | Current Process Water Rate ($/1000 gal) | 0.2
FAX Number |  | Carbon particle diameter, d (mm) | 1.605 | [5 empty] | A12 | N | 1998-08-27 | 9:30 | 2878.5 | 8635.5 | 17271 | 7.72 | 0.5 | 99 | 21.5 | 144 | 95 | BMRL | 290 | 3.5 | 0.061 | 1.7429 | 4.5 | 0.2 | 4.3 | 21.3 | 8.2 | 24 | 295 | 57 | 61 | 67 | 25 | 210 | 3 | 13 | 7.6 | 2.9 | 13 | 12 | 8.8 | 12 | 12 | 39.5 | 51.5 | A12 | N | 1998-06-17 | 12:15 | 1517.25 | 9103.5 | 7.78 | 0.23 | 27.5 | BMRL | 2.6 | 0.042 | 1.6154 | 3 | 0.5 | 2.5 | 26.4 | 8.2 | 24 | 185 | 20 | 34 | 56 | 27 | 137 | 2.3 | 6.8 | 4.6 | 2.4 | 15 | 12 | 4.6 | 7.9 | 6.5 | 31.1 | 43.1 | A12 | N | 1998-08-27 | 9:30 | 2878.5 | 8635.5 | 7.58 | 0.38 | 21 | BMRL | 2.3 | 0.031 | 1.3478 | 3.3 | 0.6 | 2.7 | 21.7 | 8.2 | 24 | 160 | 14 | 28 | 61 | 43 | 146 | BMRL | 4.1 | 1.8 | 2.1 | 13 | 8.9 | 13 | 9.6 | 5.8 | 21 | 29.9 | Modifications to Existing Plant (% of construction costs) | 33
E-Mail Address (optional) |  | Column cross-sectional area, A (m2) | 0.0045604 | [5 empty] | A13 | N | 1998-09-19 | 12:45 | 3433.75 | 10301.25 | 20602.5 | 7.81 | 0.52 | 92 | 20.8 | 128 | 82 | BMRL | 310 | 3.8 | 0.059 | 1.5526 | 5 | 0.55 | 4.45 | 19.5 | 8.3 | 24 | 300 | 44 | 49 | 62 | NR | 155 | BMRL | 14 | 7.6 | 2.6 | 15 | 16 | NR | NR | 11 | 39.2 | 55.2 | Avg-A13 | Y | 1998-06-26 | 12:00 | 1730 | 10380 | 7.99 | 0.27 | 24.1 | BMRL | 2.3 | 0.031 | 1.3478 | 3 | 0.4 | 2.6 | 24.3 | 8.1 | 24.3 | 187.5 | 15 | 31 | 54.5 | 29.5 | 130 | BMRL | 6.95 | 3.8 | 2.6 | 15.5 | 12 | NR | 8.5 | 7.05 | 28.85 | 40.85 | A13 | N | 1998-09-19 | 12:45 | 3433.75 | 10301.25 | 7.46 | 0.33 | 20.3 | BMRL | 2.6 | 0.03 | 1.1538 | 3.7 | 1.1 | 2.6 | 19.8 | 8.3 | 24 | 155 | 10 | 22 | 55 | 41 | 128 | BMRL | 3.8 | 1.4 | 2.2 | 15 | 8.8 | NR | NR | 4.6 | 22.4 | 31.2
|  | Hydraulic loading rate1, v (m/hr) | 6.5784 |  |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | Avg-A14 | Y | 1998-10-16 | 10:00 | 4031 | 12093 | 24186 | 7.74 | 0.55 | 88.5 | 19.3 | 114.5 | 77 | 0.07 | NA | 3.15 | 0.046 | 1.4603 | 5 | 1.23 | 3.77 | 14.7 | 8.2 | 24 | 232.5 | 23.5 | 32.5 | 46.5 | 20 | 122.5 | BMRL | 8.35 | 6.3 | 2.4 | 10.5 | 12.5 | 8.05 | 13.5 | 14 | 27.55 | 40.05 | A14 | N | 1998-07-10 | 18:00 | 2069 | 12414 | 7.59 | 0.37 | 24.1 | BMRL | 2.8 | 0.051 | 1.8214 | 3.5 | 0.45 | 3.05 | 24 | 8.1 | 23.8 | 210 | 29 | 49 | 64 | 31 | 173 | BMRL | 8.4 | 4.6 | 2.3 | 15 | 12 | 11 | 8.3 | 6.7 | 30.3 | 42.3 | Avg-A14 | Y | 1998-10-16 | 10:00 | 4031 | 12093 | 7.58 | 0.28 | 18.9 | 0.06 | 2.1 | 0.026 | 1.2381 | 3.5 | 1.28 | 2.22 | 14.5 | 8.2 | 24.3 | 135 | 8.5 | 16 | 36.5 | 27 | 88 | BMRL | 2.95 | 1.85 | 2 | 9.95 | 7.25 | 9.4 | 9.95 | 6.4 | 16.75 | 24
Plant Name | South Holly WTP | 1: If v is not in the range from 5 to 15 m/hr (2 to 6 gpm/ft2) then either Q or D must be adjusted. |  |  |  | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | A15 | N | 1998-11-14 | 10:00 | 4703 | 14109 | 28218 | 7.5 | 1.02 | 91 | 12.1 | 116 | 80 | BMRL | 290 | 2.8 | 0.049 | 1.75 | 4 | 0.9 | 3.1 | 10.7 | 8.3 | 23.5 | 190 | 16 | 25 | 40 | 20 | 101 | BMRL | 7.1 | 5 | 2.2 | 11 | 12 | 6.2 | 11 | 9.8 | 25.3 | 37.3 | A15 | N | 1998-09-04 | 10:00 | 3072.75 | 18436.5 | 7.39 | 0.26 | 20.3 | BMRL | 3 | 0.043 | 1.4333 | 3.9 | 0.7 | 3.2 | 21.6 | 8.1 | 24 | 205 | 19 | 33 | 64 | 30 | 146 | BMRL | 6.6 | 3.3 | 2.7 | 14 | 12 | 6.9 | 9.1 | 7.7 | 26.6 | 38.6 | A15 | N | 1998-11-14 | 10:00 | 4703 | 14109 | 7.38 | 0.37 | 12.4 | 0.09 | 2.2 | 0.028 | 1.2727 | 3 | 0.75 | 2.25 | 10.5 | 8.2 | 23.5 | 125 | 6.3 | 13 | 31 | 26 | 76.3 | BMRL | 2.4 | 1.2 | 1.8 | 10 | 7 | 7.3 | 8.3 | 4.9 | 15.4 | 22.4
Treatment Plant Category | CONV |  |  |  |  | is to list the pretreatment processes used in this particular pilot GAC run.
Process Train Name | Conventional Train | 10-Minute EBCT Run
ICR Treatment Plant Identification Number | 647 | Empty bed contact time, EBCT (min) | 10
PWSID Number of Plant (if assigned) | TX2200012960920162238 | Estimated run time, t (days) | 63.835
Historical Minimum Water Temperature (oC) | 5 | Pilot column bed length, l (m) | 1.0964
Historical Average Water Temperature (oC) | NA | Mass GAC required, m (kg) | 2.5285
State Approved Plant Capacity (MGD) | 100
20-Minute EBCT Run
|  | Empty bed contact time, EBCT (min) | 20
|  | Estimated run time, t (days) | 127.6701
|  | Pilot column bed length, l (m) | 2.1928 | [5 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [18 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
|  | Mass GAC required, m (kg) | 5.057 | [5 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [18 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
[9 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below. | [40 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below. | [35 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below.
[9 empty] | Group D, 3 duplicate influent samples per run | [40 empty] | Group D, 3 duplicate effluent samples per run | [35 empty] | Group D, 3 duplicate effluent samples per run
[9 empty] | Sample | Sample | Sampling | Sampling | Operation | Bed | Bed | pH | Turbidity | Alkalinity | Temp. | Total | Calcium | Ammonia | Bromide | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS
[9 empty] | ID | Type | date | time | time | volumes | volumes |  |  |  |  | Hardness | Hardness | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6
[11 empty] | MM/DD/YY | hh:mm | hh.hh | ( 20 minute) | ( 10 minute) | --- | ntu | mg/L as CaCO3 | oC | mg/L as CaCO3 | mg/L as CaCO3 | mg NH3-N / L | mg/L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L
[9 empty] | A1 | Primary | 1998-04-15 | 15:45 | 25.75 | 77.25 | 154.5 | 7.86 | 0.21 | 135 | 25.2 | 160 | 127 | BMRL | 220 | 3.5 | 0.062 | 1.7714 | 3.5 | 0.5 | 3 | 21 | 7.9 | 23.5 | 220 | 30 | 39 | 40 | 8.4 | 117.4 | BMRL | 12 | 8.3 | 2.8 | 11 | 15 | NR | NR | 13 | 34.1 | 49.1 | A1 | Primary | 1998-04-15 | 15:45 | 25.75 | 154.5 | 8.39 | 0.22 | 24.7 | BMRL | BMRL | 0 | -- | 1 | 0.5 | 0.5 | 21 | 8.3 | 23.5 | BMRL | BMRL | BMRL | 1.9 | 3.9 | 5.8 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NR | NR | BMRL | 0 | 0 | A1 | Primary | 1998-04-15 | 15:45 | 25.75 | 77.25 | 8.3 | 0.27 | 24.5 | BMRL | BMRL | 0.001 | -- | 1 | 0.35 | 0.65 | 21 | 8 | 23.5 | BMRL | BMRL | BMRL | 1 | 1.9 | 2.9 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NR | NR | BMRL | 0 | 0
[9 empty] | D-A1 | Duplicate | 1998-04-15 | 15:45 | 25.75 | 77.25 | 154.5 | 7.86 | 0.21 | 130 | 25.2 | 118 | NA | BMRL | 220 | 3.4 | 0.062 | 1.8235 | 3.5 | 0.2 | 3.3 | 21 | 8 | 24 | 215 | 27 | 37 | 38 | 8.4 | 110.4 | BMRL | 10 | 6.9 | 2 | 9.9 | 14 | NR | NR | 12 | 28.8 | 42.8 | D-A1 | Duplicate | 1998-04-15 | 15:45 | 25.75 | 154.5 | 8.39 | 0.22 | 24.7 | BMRL | BMRL | 0 | -- | 1 | 0.4 | 0.6 | 21 | 8.2 | 24 | BMRL | BMRL | BMRL | 1 | 1.8 | 2.8 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NR | NR | BMRL | 0 | 0 | D-A1 | Duplicate | 1998-04-15 | 15:45 | 25.75 | 77.25 | 8.3 | 0.27 | 24.5 | BMRL | BMRL | 0.001 | -- | 1 | 0.4 | 0.6 | 21 | 8.2 | 24 | BMRL | BMRL | BMRL | BMRL | 1.5 | 1.5 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NR | NR | BMRL | 0 | 0
[9 empty] | Avg-A1 | Average | --- | --- | --- | --- | --- | 7.86 | 0.21 | 132.5 | 25.2 | 139 | 127 | BMRL | 220 | 3.45 | 0.062 | 1.7975 | 3.5 | 0.35 | 3.15 | 21 | 7.95 | 23.75 | 217.5 | 28.5 | 38 | 39 | 8.4 | 113.9 | BMRL | 11 | 7.6 | 2.4 | 10.45 | 14.5 | -- | -- | 12.5 | 31.45 | 45.95 | Avg-A1 | Average | --- | --- | --- | --- | 8.39 | 0.22 | 24.7 | BMRL | BMRL | 0 | -- | 1 | 0.45 | 0.55 | 21 | 8.25 | 23.75 | BMRL | BMRL | BMRL | 1.45 | 2.85 | 4.3 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | -- | -- | BMRL | 0 | 0 | Avg-A1 | Average | --- | --- | --- | --- | 8.3 | 0.27 | 24.5 | BMRL | BMRL | 0.001 | -- | 1 | 0.375 | 0.625 | 21 | 8.1 | 23.75 | BMRL | BMRL | BMRL | 1 | 1.7 | 2.2 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | -- | -- | -- | 0 | 0
[9 empty] | RPD-A1 | RPD | --- | --- | --- | --- | --- | 0 | 0 | 3.7736 | 0 | 30.2158 | -- | -- | 0 | 2.8986 | 0 | 2.8986 | 0 | 85.7143 | 9.5238 | 0 | 1.2579 | 2.1053 | 2.2989 | 10.5263 | 5.2632 | 5.1282 | 0 | 6.1457 | -- | 18.1818 | 18.4211 | 33.3333 | 10.5263 | 6.8966 | -- | -- | 8 | 16.8521 | 13.7106 | RPD-A1 | RPD | --- | --- | --- | --- | 0 | 0 | 0 | -- | -- | -- | -- | 0 | 22.2222 | 18.1818 | 0 | 1.2121 | 2.1053 | -- | -- | -- | 62.069 | 73.6842 | 69.7674 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | RPD-A1 | RPD | --- | --- | --- | --- | 0 | 0 | 0 | -- | -- | 0 | -- | 0 | 13.3333 | 8 | 0 | 2.4691 | 2.1053 | -- | -- | -- | -- | 23.5294 | 63.6364 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[9 empty] | A8 | Primary | 1998-06-17 | 12:30 | 1516.75 | 4550.25 | 9100.5 | 7.9 | 0.45 | 120 | 28.7 | 158 | 117 | BMRL | 230 | 3.3 | 0.062 | 1.8788 | 3.5 | 0.2 | 3.3 | 25.7 | 8.1 | 24 | 245 | 38 | 49 | 52 | 16 | 155 | 3 | 12 | 6.7 | 2.7 | 13 | 15 | BMRL | 8.7 | 11 | 37.4 | 52.4 | A8 | Primary | 1998-05-21 | 17:15 | 876.25 | 5257.5 | 7.66 | 0.27 | 29.2 | BMRL | 2.1 | 0.032 | 1.5238 | 2.3 | 0.6 | 1.7 | 24 | 8.2 | 24.5 | 145 | 6.6 | 18 | 42 | 31 | 97.6 | BMRL | 4.1 | 1.7 | 2 | 13 | 8.2 | 7.4 | 7.5 | 4.7 | 20.8 | 29 | A8 | Primary | 1998-06-17 | 12:45 | 1517 | 4551 | 7.75 | 0.25 | 28 | BMRL | 2 | 0.025 | 1.25 | 2.3 | 0.5 | 1.8 | 26.2 | 8.1 | 24 | 120 | 6.5 | 18 | 48 | 39 | 111.5 | BMRL | 3.1 | 1.6 | 2.5 | 14 | 7.6 | 6.2 | 5.9 | 3.5 | 21.2 | 28.8
[9 empty] | D-A8 | Duplicate | 1998-06-17 | 12:30 | 1516.75 | 4550.25 | 9100.5 | 7.9 | 0.45 | 120 | 28.7 | 165 | 120 | 0.13 | 230 | 3.6 | 0.062 | 1.7222 | 3.5 | 0.2 | 3.3 | 26.1 | 8 | 24 | 255 | 36 | 47 | 50 | 16 | 149 | 3.1 | 11 | 6.5 | 2.6 | 13 | 15 | BMRL | 8.4 | 10 | 36.2 | 51.2 | D-A8 | Duplicate | 1998-05-21 | 17:15 | 876.25 | 5257.5 | 7.66 | 0.27 | 29.2 | BMRL | 2 | 0.032 | 1.6 | 2.3 | 0.6 | 1.7 | 24 | 8.2 | 24.5 | 150 | 6.9 | 19 | 43 | 30 | 98.9 | BMRL | 4.1 | 1.7 | 2 | 14 | 8.3 | 7.6 | 7.8 | 4.9 | 21.8 | 30.1 | D-A8 | Duplicate | 1998-06-17 | 12:45 | 1517 | 4551 | 7.75 | 0.25 | 28 | BMRL | 1.8 | 0.025 | 1.3889 | 2.3 | 0.45 | 1.85 | 26.1 | 8.2 | 24 | 130 | 6.5 | 18 | 50 | 40 | 114.5 | BMRL | 2.9 | 1.6 | 1.9 | 14 | 7.4 | 6.2 | 6 | 3.5 | 20.4 | 27.8
[9 empty] | Avg-A8 | Average | --- | --- | --- | --- | --- | 7.9 | 0.45 | 120 | 28.7 | 161.5 | 118.5 | 0.13 | 230 | 3.45 | 0.062 | 1.8005 | 3.5 | 0.2 | 3.3 | 25.9 | 8.05 | 24 | 250 | 37 | 48 | 51 | 16 | 152 | 3.05 | 11.5 | 6.6 | 2.65 | 13 | 15 | BMRL | 8.55 | 10.5 | 36.8 | 51.8 | Avg-A8 | Average | --- | --- | --- | --- | 7.66 | 0.27 | 29.2 | BMRL | 2.05 | 0.032 | 1.5619 | 2.3 | 0.6 | 1.7 | 24 | 8.2 | 24.5 | 147.5 | 6.75 | 18.5 | 42.5 | 30.5 | 98.25 | BMRL | 4.1 | 1.7 | 2 | 13.5 | 8.25 | 7.5 | 7.65 | 4.8 | 21.3 | 29.55 | Avg-A8 | Average | --- | --- | --- | --- | 7.75 | 0.25 | 28 | BMRL | 1.9 | 0.025 | 1.3194 | 2.3 | 0.475 | 1.825 | 26.15 | 8.15 | 24 | 125 | 6.5 | 18 | 49 | 39.5 | 113 | BMRL | 3 | 1.6 | 2.2 | 14 | 7.5 | 6.2 | 5.95 | 3.5 | 20.8 | 28.3
[9 empty] | RPD-A8 | RPD | --- | --- | --- | --- | --- | 0 | 0 | 0 | 0 | 4.3344 | 2.5316 | -- | 0 | 8.6957 | 0 | 8.6957 | 0 | 0 | 0 | 1.5444 | 1.2422 | 0 | 4 | 5.4054 | 4.1667 | 3.9216 | 0 | 3.9474 | 3.2787 | 8.6957 | 3.0303 | 3.7736 | 0 | 0 | -- | 3.5088 | 9.5238 | 3.2609 | 2.3166 | RPD-A8 | RPD | --- | --- | --- | --- | 0 | 0 | 0 | -- | 4.878 | 0 | 4.878 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3898 | 4.4444 | 5.4054 | 2.3529 | 3.2787 | 1.3232 | -- | 0 | 0 | 0 | 7.4074 | 1.2121 | 2.6667 | 3.9216 | 4.1667 | 4.6948 | 3.7225 | RPD-A8 | RPD | --- | --- | --- | --- | 0 | 0 | 0 | -- | 10.5263 | 0 | 10.5263 | 0 | 10.5263 | 2.7397 | 0.38241 | 1.227 | 0 | 8 | 0 | 0 | 4.0816 | 2.5316 | 2.6549 | -- | 6.6667 | 0 | 27.2727 | 0 | 2.6667 | 0 | 1.6807 | 0 | 3.8462 | 3.5336
[9 empty] | A14 | Primary | 1998-10-16 | 10:00 | 4031 | 12093 | 24186 | 7.74 | 0.55 | 89 | 19.3 | 116 | 78 | 0.07 | -- | 3.3 | 0.046 | 1.3939 | 5 | 1.25 | 3.75 | 14.9 | 8.3 | 24 | 225 | 21 | 31 | 46 | 20 | 118 | BMRL | 7.6 | 5.4 | 2.5 | 10 | 12 | 8.1 | 14 | 14 | 25.5 | 37.5 | A13 | Primary | 1998-06-26 | 12:00 | 1730 | 10380 | 7.99 | 0.27 | 24.1 | BMRL | 2.3 | 0.031 | 1.3478 | 3 | 0.4 | 2.6 | 24.3 | 8.1 | 24.3 | 185 | 14 | 28 | 52 | 29 | 123 | BMRL | 7.1 | 3.9 | 2.5 | 16 | 12 | NR | 8.6 | 7.1 | 29.5 | 41.5 | A14 | Primary | 1998-10-16 | 10:00 | 4031 | 12093 | 7.58 | 0.28 | 18.9 | 0.06 | 2.1 | 0.026 | 1.2381 | 3.5 | 1.25 | 2.25 | 14.5 | 8.2 | 24.25 | 130 | 8.7 | 16 | 37 | 27 | 88.7 | BMRL | 2.9 | 1.9 | 2 | 10 | 7.3 | 9.5 | 10 | 6.3 | 16.8 | 24.1
[9 empty] | D-A14 | Duplicate | 1998-10-16 | 10:00 | 4031 | 12093 | 24186 | 7.74 | 0.55 | 88 | 19.3 | 113 | 76 | 0.07 | -- | 3 | 0.046 | 1.5333 | 5 | 1.2 | 3.8 | 14.5 | 8.3 | 24 | 240 | 26 | 34 | 47 | 20 | 127 | BMRL | 9.1 | 7.2 | 2.3 | 11 | 13 | 8 | 13 | 14 | 29.6 | 42.6 | D-A13 | Duplicate | 1998-06-26 | 12:00 | 1730 | 10380 | 7.99 | 0.27 | 24.1 | BMRL | 2.3 | 0.031 | 1.3478 | 3 | 0.35 | 2.65 | 24.2 | 8.1 | 24.3 | 190 | 16 | 34 | 57 | 30 | 137 | BMRL | 6.8 | 3.7 | 2.7 | 15 | 12 | NR | 8.4 | 7 | 28.2 | 40.2 | D-A14 | Duplicate | 1998-10-16 | 10:00 | 4031 | 12093 | 7.58 | 0.28 | 18.9 | BMRL | 2.1 | 0.026 | 1.2381 | 3.5 | 1.3 | 2.2 | 14.5 | 8.2 | 24.25 | 140 | 8.3 | 16 | 36 | 27 | 87.3 | BMRL | 3 | 1.8 | 2 | 9.9 | 7.2 | 9.3 | 9.9 | 6.5 | 16.7 | 23.9
[9 empty] | Avg-A14 | Average | --- | --- | --- | --- | --- | 7.74 | 0.55 | 88.5 | 19.3 | 114.5 | 77 | 0.07 | -- | 3.15 | 0.046 | 1.4636 | 5 | 1.225 | 3.775 | 14.7 | 8.3 | 24 | 232.5 | 23.5 | 32.5 | 46.5 | 20 | 122.5 | BMRL | 8.35 | 6.3 | 2.4 | 10.5 | 12.5 | 8.05 | 13.5 | 14 | 27.55 | 40.05 | Avg-A13 | Average | --- | --- | --- | --- | 7.99 | 0.27 | 24.1 | BMRL | 2.3 | 0.031 | 1.3478 | 3 | 0.375 | 2.625 | 24.25 | 8.1 | 24.3 | 187.5 | 15 | 31 | 54.5 | 29.5 | 130 | BMRL | 6.95 | 3.8 | 2.6 | 15.5 | 12 | -- | 8.5 | 7.05 | 28.85 | 40.85 | Avg-A14 | Average | --- | --- | --- | --- | 7.58 | 0.28 | 18.9 | 0.06 | 2.1 | 0.026 | 1.2381 | 3.5 | 1.275 | 2.225 | 14.5 | 8.2 | 24.25 | 135 | 8.5 | 16 | 36.5 | 27 | 88 | BMRL | 2.95 | 1.85 | 2 | 9.95 | 7.25 | 9.4 | 9.95 | 6.4 | 16.75 | 24
[9 empty] | RPD-A14 | RPD | --- | --- | --- | --- | --- | 0 | 0 | 1.1299 | 0 | 2.6201 | 2.5974 | 0 | -- | 9.5238 | 0 | 9.5238 | 0 | 4.0816 | 1.3245 | 2.7211 | 0 | 0 | 6.4516 | 21.2766 | 9.2308 | 2.1505 | 0 | 7.3469 | -- | 17.9641 | 28.5714 | 8.3333 | 9.5238 | 8 | 1.2422 | 7.4074 | 0 | 14.882 | 12.7341 | RPD-A13 | RPD | --- | --- | --- | --- | 0 | 0 | 0 | -- | 0 | 0 | 0 | 0 | 13.3333 | 1.9048 | 0.41237 | 0 | 0 | 2.6667 | 13.3333 | 19.3548 | 9.1743 | 3.3898 | 10.7692 | -- | 4.3165 | 5.2632 | 7.6923 | 6.4516 | 0 | -- | 2.3529 | 1.4184 | 4.5061 | 3.1824 | RPD-A14 | RPD | --- | --- | --- | --- | 0 | 0 | 0 | -- | 0 | 0 | 0 | 0 | 3.9216 | 2.2472 | 0 | 0 | 0 | 7.4074 | 4.7059 | 0 | 2.7397 | 0 | 1.5909 | -- | 3.3898 | 5.4054 | 0 | 1.005 | 1.3793 | 2.1277 | 1.005 | 3.125 | 0.59701 | 0.83333
[9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [18 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [18 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.