## Sheet1. 1st Quarter
FIELD-SET 1: 1st QUARTER RSSCT RESULTS (FILE: ICR448.xls)
Field 1-1: PWS And Treatment Plant Data |  | Field 1-2: Full-Scale GAC Characteristics1 |  | Field 1-3: RSSCT Design Parameters |  |  |  | Field 1-4: Pretreatment Used Prior To GAC1 |  |  |  | Field 1-5: GAC Influent Water Quality For The 10-Minute EBCT Run | [7 empty] | Field 1-6: GAC Influent Water Quality For The 20-Minute EBCT Run1 | [6 empty] | Field 1-7: GAC Effluent Water Quality For The 10-Minute EBCT Run1 | [15 empty] | Field 1-7: GAC Effluent Water Quality For The 10-Minute EBCT Run (continued) | [17 empty] | Field 1-8: GAC Effluent Water Quality For The 20-Minute EBCT Run1 | [14 empty] | Field 1-8: GAC Effluent Water Quality For The 20-Minute EBCT Run (continued) | [18 empty] | Field 1-9: GAC Cost Parameters
|  |  |  | Input Design Parameters |  | US Standard Mesh Sizes | [20 empty] | Group C, 12 effluent samples per run | [33 empty] | Group C, 12 effluent samples per run
PWS Name | Public Works Commision of the City of Fayettville | Carbon manufacturer | Calgon Corp. | RSSCT influent TOC (mg/L) | 2.75 | US standard | Opening | Process | Description | Scale |  | 10-min. EBCT Start Date | 1998-03-26 | [6 empty] | 20-min. EBCT Start Date | 1998-03-26 | [5 empty] | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Cost Parameter | Parameter value
Public Water System Identification Number | NC 0326010 | Carbon trade name | Filtrasorb-400 | Inner diameter of the RSSCT column, DSC (mm) | 15 | mesh size | (mm) | Coagulation | 30 - 60 mg/L alum as Al2(SO4)3*14H2O | Full-Scale |  | 10-min. EBCT Start Time | 8:00 | [6 empty] | 20-min. EBCT Start Time | 8:00 | [5 empty] | ID | duplicated? | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | Capital Recovery Interest Rate (%) | 5.3
Water Industry Data Base Number (optional) | 1244 | Carbon type | Bituminous | Minimum RSSCT Reynolds number, ReSC, min | 0.2 | 4 | 4.75 | Flocculation | 1-stage | Full-Scale | [17 empty] | Y/N | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | Capital Recovery Period (years) | 45
|  | Original GAC mesh size, upper (US standard mesh) | 12 | Full-scale operating temperature, ToC (oC) | 11.1 | 6 | 3.35 | Sedimentation | 3.1 hours conventional | Full-Scale |  | Group A, 2 samples per batch | [7 empty] | Group A, 2 samples per batch | [6 empty] | C1 | N | 1998-03-26 | 9:00 | 1 | 38.2727 | 6.38 | 18 | BMRL | BMRL | BMRL | 3 | 2.19 | 0.81 | 14 | 7.34 | 48 | BMRL | BMRL | 0.6 | 1 | 0.6 | 2.2 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | 0 | C1 | N | 1998-03-26 | 9:00 | 1 | 19.1364 | 6.45 | 18 | BMRL | BMRL | BMRL | 3 | 1.97 | 1.03 | 14 | 7.38 | 48 | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | 0 | Overhead & Profit Factor (% of construction costs) | 10
Official ICR Contact Person |  | Original GAC mesh size, lower (US standard mesh) | 40 | Full-scale bed porosity, eLC | 0.45 | 8 | 2.36 | Cartridge filtration | 1um exclusion size | Bench-scale |  | Parameter | Units | Sample A1-10 | Sample A2-10 | Sample A3-10 | Average | RPD |  | Parameter | Units | Sample A1-20 | Sample A2-20 | Sample A3-20 | Average | RPD | C2 | N | 1998-03-27 | 16:00 | 32 | 1224.7273 | 6.28 | 18 | 1.041 | 0.005 | 0.48031 | 3 | 2.12 | 0.88 | 14 | 7.29 | 48 | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | 0 | C2 | N | 1998-03-27 | 16:00 | 32 | 612.3636 | 6.41 | 18 | BMRL | BMRL | BMRL | 3 | 2.2 | 0.8 | 14 | 7.41 | 48 | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | 0 | Special Sitework Factor (% of construction costs) | 5
Mailing Address |  | Original carbon particle diameter, dLC (mm) | 1.0525 | Measured RSSCT dry bed density, rSC (g/cm3) | 0.463 | 10 | 2 |  |  |  |  | Sampling date | MM/DD/YY | 1998-03-26 | 1998-04-07 | 1998-04-24 | --- | --- |  | Sampling date | MM/DD/YY | 1998-03-26 | 1998-04-07 | 1998-04-24 | --- | --- | C3 | N | 1998-03-28 | 16:00 | 56 | 2143.2727 | 6.25 | 19 | 0.97 | BMRL | BMRL | 3 | 1.85 | 1.15 | 14 | 7.28 | 48 | BMRL | BMRL | BMRL | 1 | 2.6 | 3.6 | BMRL | BMRL | BMRL | BMRL | 1.5 | BMRL | BMRL | BMRL | BMRL | 1.5 | 1.5 | C3 | N | 1998-03-28 | 16:00 | 56 | 1071.6364 | 6.35 | 19 | BMRL | BMRL | BMRL | 3 | 1.9 | 1.1 | 14 | 7.27 | 48 | BMRL | BMRL | BMRL | BMRL | 1.2 | 1.2 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | 0 | Construction Contingencies (% of construction costs) | 10
|  | 1: These are the characteristics before the carbon is ground for RSSCT experiments. |  | RSSCT GAC mesh size, upper (US standard mesh) | 80 | 12 | 1.68 |  |  |  |  | Sampling time | hh:mm | 9:00 | 16:00 | 14:00 | --- | --- |  | Sampling time | hh:mm | 9:00 | 16:00 | 14:00 | --- | --- | C4 | N | 1998-03-29 | 17:00 | 81 | 3100.0909 | 6.4 | 19 | 1.158 | BMRL | BMRL | 3 | 1.64 | 1.36 | 14 | 7.03 | 48 | BMRL | BMRL | BMRL | 1.7 | 9.7 | 11.4 | BMRL | BMRL | BMRL | 1 | 4.1 | BMRL | 8.8 | BMRL | BMRL | 5.1 | 5.1 | C4 | N | 1998-03-29 | 17:00 | 81 | 1550.0455 | 6.45 | 19 | BMRL | BMRL | BMRL | 3 | 1.5 | 1.5 | 14 | 7.29 | 48 | NR | NR | NR | NR | NR | 0 | NR | NR | NR | NR | NR | NR | NR | NR | NR | 0 | 0 | Engineering Fee Factor (% of construction costs) | 10
Phone Number |  |  |  | RSSCT GAC mesh size, lower (US standard mesh) | 100 | 16 | 1.18 |  |  |  |  | Operation time | hh.hh | 1 | 296 | 702 | --- | --- |  | Operation time | hh.hh | 1 | 296 | 702 | --- | --- | Avg-C5 | Y | 1998-03-30 | 2:30 | 90.5 | 3463.6818 | 6.22 | 19 | 0.973 | BMRL | BMRL | 3 | 1.565 | 1.435 | 14 | 7.275 | 48 | 36 | BMRL | BMRL | 1.6 | 17.5 | 19.1 | BMRL | BMRL | BMRL | BMRL | 2.05 | BMRL | 9.3 | 2.2 | BMRL | 2.05 | 2.05 | Avg-C5 | Y | 1998-03-30 | 14:30 | 102.5 | 1961.4773 | 6.41 | 19 | BMRL | BMRL | BMRL | 3 | 1.92 | 1.08 | 14 | 7.375 | 48 | 32 | BMRL | BMRL | 2.6 | 5.1 | 7.7 | BMRL | BMRL | 1 | BMRL | 1.6 | BMRL | 7.3 | 2.5 | 1.8 | 2.6 | 2.6 | 1998 ENR Construction Cost Index (CCI base year 1913) | 77.8
FAX Number | [5 empty] | 20 | 0.85 |  |  |  |  | Bed volumes | (10 minutes) | 38.2727 | 11328.7273 | 26867.4545 | --- | --- |  | Bed volumes | (20 minutes) | 19.1364 | 5664.3636 | 26867.4545 | --- | --- | C6 | N | 1998-03-31 | 16:00 | 128 | 4898.9091 | 6.21 | 20 | 1.31 | BMRL | BMRL | 3 | 2.15 | 0.85 | 14 | 7.17 | 48 | BMRL | BMRL | BMRL | 1.6 | 6.1 | 7.7 | BMRL | BMRL | BMRL | BMRL | 1.6 | BMRL | 4.9 | BMRL | BMRL | 1.6 | 1.6 | C6 | N | 1998-03-31 | 16:00 | 128 | 2449.4545 | 6.34 | 20 | BMRL | BMRL | BMRL | 3 | 2.1 | 0.9 | 14 | 7.45 | 48 | BMRL | BMRL | BMRL | 1.3 | 1.5 | 2.8 | BMRL | BMRL | BMRL | BMRL | 1 | BMRL | BMRL | BMRL | 1.5 | 1 | 1 | 1998 Producers Price Index (PPI base year 1982 = 100) | 131.3
E-Mail Address (optional) |  |  |  | Estimated Run Length |  | 30 | 0.6 |  |  |  |  | Alkalinity | mg/L as CaCO3 | 7.9 | 7.3 | NA | 7.6 | 7.8947 |  | Alkalinity | mg/L as CaCO3 | 7.9 | 7.3 | NA | 7.6 | 7.8947 | C7 | N | 1998-04-03 | 16:00 | 200 | 7654.5455 | 6.33 | 19 | 1.547 | 0.0094 | 0.60763 | 3 | 1.7 | 1.3 | 14 | 7.37 | 48 | 45 | BMRL | 2.4 | 8.4 | 20 | 30.8 | BMRL | BMRL | 1.1 | 1.4 | 5.3 | 2.2 | 12 | 4.4 | 3 | 7.8 | 10 | C7 | N | 1998-04-03 | 16:00 | 200 | 3827.2727 | 6.17 | 19 | 1.396 | BMRL | BMRL | 3 | 1.72 | 1.28 | 14 | 7.35 | 48 | BMRL | BMRL | BMRL | 0.7 | 2.3 | 3 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | 0 | Labor Rate + Fringe ($/work-hour) | 21
|  |  |  | Bed volumes to 50% TOC breakthrough, BV50 | 5825.4199 | 40 | 0.425 |  |  |  |  | Total hardness | mg/L as CaCO3 | 18.9 | 19.4 | NA | 19.15 | 2.611 |  | Total hardness | mg/L as CaCO3 | 18.9 | 19.4 | NA | 19.15 | 2.611 | C8 | N | 1998-04-04 | 16:00 | 224 | 8573.0909 | 6.41 | 20 | 1.48 | 0.0148 | 1 | 3 | 1.68 | 1.32 | 14 | 7.38 | 48 | 62 | 0.6 | 3.3 | 11 | 24 | 38.9 | BMRL | BMRL | 1.1 | BMRL | 6.6 | 2.7 | 14 | 5.4 | 3.5 | 7.7 | 10.4 | C8 | N | 1998-04-04 | 16:00 | 224 | 4286.5455 | 6.28 | 20 | 1.17 | BMRL | BMRL | 3 | 1.28 | 1.72 | 14 | 7.4 | 48 | BMRL | BMRL | 0.7 | 2 | 5.8 | 8.5 | BMRL | BMRL | BMRL | BMRL | 1.6 | BMRL | 6.6 | 2.5 | 1.8 | 1.6 | 1.6 | Labor Overhead Factor (% of labor) | 4.1
Technical ICR Contact Person |  |  |  | Estimated run length, BVT ( = 2 x BV50) | 11650.8397 | 50 | 0.3 |  |  |  |  | Calcium hardness | mg/L as CaCO3 | 11.7 | 11.7 | NA | 11.7 | 0 |  | Calcium hardness | mg/L as CaCO3 | 11.7 | 11.7 | NA | 11.7 | 0 | C9 | N | 1998-04-05 | 16:00 | 248 | 9491.6364 | 6.33 | 19 | 1.498 | 0.0146 | 0.97463 | 3 | 1.46 | 1.54 | 14 | 7.38 | 48 | 66 | 0.6 | 3.6 | 13 | 31 | 48.2 | BMRL | BMRL | 1.2 | 1.7 | 8.2 | 3 | 16 | 6.3 | 3.8 | 11.1 | 14.1 | C9 | N | 1998-04-05 | 16:00 | 248 | 4745.8182 | 6.25 | 19 | 1.28 | BMRL | BMRL | 3 | 1.58 | 1.42 | 14 | 7.41 | 48 | BMRL | BMRL | 0.9 | 3.1 | 10 | 14 | BMRL | BMRL | BMRL | BMRL | 2.5 | BMRL | 7.7 | 2.7 | 1.8 | 2.5 | 2.5 | Electric Rate ($/kW-h) | 0.035
Mailing Address |  |  |  | BVT + 30% safety factor, BVT+30% ( = 2.6 x BV50) | 15146.0916 | 60 | 0.25 |  |  |  |  | Ammonia | mg NH3-N / L | 0.02 | 0.03 | NA | 0.025 | 40 |  | Ammonia | mg NH3-N / L | 0.02 | 0.03 | NA | 0.025 | 40 | Avg-C10 | Y | 1998-04-06 | 16:00 | 272 | 10410.1818 | 6.23 | 20 | 1.7265 | 0.016 | 0.92673 | 3 | 1.335 | 1.665 | 14 | 7.36 | 48 | 74.75 | BMRL | 4.25 | 15 | 37 | 56.25 | BMRL | 1.6 | BMRL | 1.9 | 6.55 | 3.1 | 11.3 | 3.6 | 2.6 | 10.05 | 13.15 | Avg-C10 | Y | 1998-04-06 | 16:00 | 272 | 5205.0909 | 6.31 | 20 | 1.3685 | BMRL | BMRL | 3 | 1.15 | 1.85 | 14 | 7.3255 | 48 | 38.5 | BMRL | BMRL | 2.25 | 16 | 18.25 | BMRL | 2.1 | 1 | 3.1 | 7.15 | 3.4 | 11.35 | 6.2 | 2.65 | 13.35 | 16.75 | Fuel Oil Rate ($/gal) | 0.55
[6 empty] | 70 | 0.21 |  |  |  |  | Bromide | mg/L | 740 | 1500 | 24 | 754.6667 | 97.806 |  | Bromide | mg/L | 740 | 1500 | 24 | 754.6667 | 97.806 | C11 | N | 1998-04-07 | 10:00 | 290 | 11099.0909 | 6.21 | 19 | 1.754 | 0.0168 | 0.95781 | 3 | 0.91 | 2.09 | 14 | 7.36 | 48 | 85 | 1 | 4.3 | 15 | 41 | 61.3 | BMRL | 2.7 | BMRL | 1.7 | 9.6 | 3.5 | 9.8 | 5.6 | 3.3 | 14 | 17.5 | C11 | N | 1998-04-07 | 10:00 | 290 | 5549.5455 | 6.33 | 19 | 1.309 | 0.005 | 0.38197 | 3 | 1.52 | 1.48 | 14 | 7.3277 | 48 | 33 | BMRL | 1 | 3.8 | 16 | 20.8 | BMRL | BMRL | BMRL | 1.5 | 3.6 | BMRL | 9.9 | 2.9 | 2.1 | 5.1 | 5.1 | Natural Gas Rate ($/ft3) | 0.007
Phone Number |  |  |  | General RSSCT Design Parameters |  | 80 | 0.18 | [19 empty] | Avg-C12 | Y | 1998-04-07 | 16:00 | 296 | 11328.7273 | 6.21 | 20 | 1.8385 | 0.0169 | 0.91923 | 3 | 1.05 | 1.95 | 14 | 7.365 | 48 | 84.25 | 1 | 3.95 | 15.5 | 43.5 | 63.45 | BMRL | BMRL | 1.15 | 2.95 | 10.5 | 3.5 | 17 | 6.1 | 3.55 | 14.6 | 18.1 | Avg-C12 | Y | 1998-04-07 | 16:00 | 296 | 5664.3636 | 6.33 | 20 | 1.5 | 0.0092 | 0.61333 | 3 | 1.535 | 1.465 | 14 | 7.345 | 48 | 32.25 | BMRL | 1 | 4 | 18.5 | 23.5 | BMRL | BMRL | BMRL | 2.7 | 4.5 | BMRL | 9.65 | 2.7 | 1.9 | 7.2 | 7.2 | Current Process Water Rate ($/1000 gal) | 0.35
FAX Number |  |  |  | Kinematic viscosity at ToC, nLC (m2/s) | 1.2848e-06 | 100 | 0.15 |  |  |  |  | Group B, 3 samples per batch | [7 empty] | Group B, 3 samples per batch | [6 empty] | C13 | N | 1998-04-08 | 11:00 | 315 | 12055.9091 | 6.5 | 20 | 2.21 | 0.0232 | 1.0498 | 3 | 1.05 | 1.95 | 14 | 7.42 | 48 | 73 | 1.7 | 7.4 | 19 | 20 | 48.1 | BMRL | 1.6 | 1 | 1.3 | 6.8 | 5 | 7.3 | 6.7 | 4.2 | 10.7 | 15.7 | C13 | N | 1998-04-08 | 11:00 | 315 | 6027.9545 | 6.25 | 20 | 1.494 | 0.006 | 0.40161 | 3 | 1.275 | 1.725 | 14 | 7.33 | 48 | 31 | BMRL | 2 | 6.5 | 12 | 20.5 | BMRL | 3.5 | BMRL | 1.6 | 3.4 | 1.8 | 5.1 | 3.6 | 2.2 | 8.5 | 10.3 | Modifications to Existing Plant (% of construction costs) | 20
E-Mail Address (optional) |  |  |  | RSSCT carbon particle diameter, dSC (mm) | 0.165 | 120 | 0.125 |  |  |  |  | Parameter | Units | Sample B1-10 | Sample B2-10 | Sample B3-10 | Average | %SD |  | Parameter | Units | Sample B1-20 | Sample B2-20 | Sample B3-20 | Average | %SD | [34 empty] | C14 | N | 1998-04-16 | 16:00 | 512 | 9797.8182 | 6.31 | 18 | 1.571 | 0.014 | 0.89115 | 3 | 1.1 | 1.9 | 14 | 7.32 | 48 | 81 | 9.3 | 7.3 | 4.8 | BMRL | 21.4 | BMRL | 6.5 | 6.7 | BMRL | 1.5 | 4.7 | BMRL | 3.6 | 6.9 | 14.7 | 19.4
|  |  |  | Scaling factor, SF | 6.3788 | 140 | 0.106 | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  |  | Sampling date | MM/DD/YY | 1998-03-26 | 1998-04-07 | 1998-04-24 | --- | --- |  | Sampling date | MM/DD/YY | 1998-03-26 | 1998-04-07 | 1998-04-24 | --- | --- | [34 empty] | C15 | N | 1998-04-21 | 16:00 | 632 | 12094.1818 | 6.38 | 19 | 1.831 | 0.022 | 1.2015 | 3 | 0.85 | 2.15 | 14 | 7.29 | 48 | 100 | 14 | 8.8 | 3.9 | BMRL | 26.7 | BMRL | 6.4 | 7 | BMRL | BMRL | 3 | NR | NR | 4.1 | 13.4 | 16.4
Plant Name | P.O. Hoffer Water Treatment Plant |  |  | RSSCT hydraulic loading rate, vSC (m/hr) | 2.5228 | 170 | 0.088 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  |  | Sampling time | hh:mm | 9:00 | 16:00 | 14:00 | --- | --- |  | Sampling time | hh:mm | 9:00 | 16:00 | 14:00 | --- | ---
Treatment Plant Category | CONV |  |  | RSSCT flow rate, QSC (mL/min) | 7.4302 | 200 | 0.075 | is to list the pretreatment processes used in this particular RSSCT run. |  |  |  | Operation time | hh.hh | 1 | 296 | 702 | --- | --- |  | Operation time | hh.hh | 1 | 296 | 702 | --- | ---
Process Train Name | Conventional train |  |  | Estimated total influent volume required, VSCT (L) | 529.2812 | 230 | 0.062 |  |  |  |  | Bed volumes | (10 minute) | 38.2727 | 11328.7273 | 26867.4545 | --- | --- |  | Bed volumes | (20 minute) | 19.1364 | 5664.3636 | 13433.7273 | --- | --- | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
ICR Treatment Plant Identification Number | 448 |  |  |  |  | 270 | 0.053 |  |  |  |  | pH | --- | 6.26 | 6.29 | 6.3 | 6.2833 | 0.3313 |  | pH | --- | 6.26 | 6.29 | 6.3 | 6.2833 | 0.3313 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
PWSID Number of Plant (if assigned) | NC 0326010 |  |  | 10-Minute EBCT Run |  | 325 | 0.044 |  |  |  |  | Turbidity | ntu | 0.79 | 0.59 | 0.57 | 0.65 | 18.7162 |  | Turbidity | ntu | 0.79 | 0.59 | 0.57 | 0.65 | 18.7162 | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for | [15 empty] | the primary and duplicate analyses below. | [17 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for | [14 empty] | the primary and duplicate analyses below.
Historical Minimum Water Temperature (oC) | 4 |  |  | Full-scale empty bed contact time, EBCTLC (min) | 10 | 400 | 0.037 |  |  |  |  | Temperature | oC | 20 | 19 | 20 | 19.6667 | 2.9357 |  | Temperature | oC | 20 | 19 | 20 | 19.6667 | 2.9357
Historical Average Water Temperature (oC) | 34 |  |  | Estimated full-scale run time, tLCT (days) | 105.1812 | [6 empty] | Total organic carbon | mg/L | 2.842 | 2.828 | NR | 2.835 | 0.34919 |  | Total organic carbon | mg/L | 2.842 | 2.828 | NR | 2.835 | 0.34919 | Group D, 3 duplicate effluent samples per run (results from primary and duplicate analyses) | [33 empty] | Group D, 3 duplicate effluent samples per run (results from primary and duplicate analyses)
State Approved Plant Capacity (MGD) | 32 |  |  | RSSCT empty bed contact time, EBCTSC (min) | 1.5677 | [6 empty] | UV254 | cm-1 | 0.0472 | 0.0446 | 0.0534 | 0.0484 | 9.341 |  | UV254 | cm-1 | 0.0472 | 0.0446 | 0.0534 | 0.0484 | 9.341 | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS
|  |  |  | Estimated RSSCT run time, tSCT (days) | 16.4892 | [6 empty] | SUVA | L/(mg*m) | 1.6608 | 1.5771 | NR | 1.6189 | 3.6565 |  | SUVA | L/(mg*m) | 1.6608 | 1.5771 | NR | 1.6189 | 3.6565 | ID | Type | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6
|  |  |  | RSSCT bed length, lSC (cm) | 6.5916 | [6 empty] | SDS-Cl2 dose | mg/L | 3 | 3 | 3 | 3 | 0 |  | SDS-Cl2 dose | mg/L | 3 | 3 | 3 | 3 | 0 |  |  | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L
|  |  |  | Estimated volume required for 10-minute EBCT, VSC (L) | 176.4271 | [6 empty] | SDS-Free Cl2 residual | mg/L | 0.38 | 0.3 | 0.45 | 0.37667 | 19.9262 |  | SDS-Free Cl2 residual | mg/L | 0.38 | 0.3 | 0.45 | 0.37667 | 19.9262 | D5 | Primary | 1998-03-30 | 2:30 | 90.5 | 3463.6818 | 6.22 | 19 | 1.066 | BMRL | BMRL | 3 | 1.54 | 1.46 | 14 | 7.31 | 48 | BMRL | BMRL | BMRL | 1.1 | 12 | 13.1 | BMRL | BMRL | BMRL | BMRL | 1.5 | BMRL | 4.6 | BMRL | BMRL | 1.5 | 1.5 | D5 | Primary | 1998-03-30 | 14:30 | 102.5 | 1961.4773 | 6.38 | 19 | BMRL | BMRL | BMRL | 3 | 1.98 | 1.02 | 14 | 7.35 | 48 | BMRL | BMRL | BMRL | 1.3 | 1.7 | 3 | BMRL | BMRL | 1 | BMRL | 1.1 | BMRL | BMRL | BMRL | BMRL | 2.1 | 2.1
|  |  |  | Mass GAC required, mSC (g) | 5.3932 | [6 empty] | SDS-Cl2 demand | mg/L | 2.62 | 2.7 | 2.55 | 2.6233 | 2.8611 |  | SDS-Cl2 demand | mg/L | 2.62 | 2.7 | 2.55 | 2.6233 | 2.8611 | D-D5 | Duplicate | 1998-03-30 | 2:30 | 90.5 | 3463.6818 | 6.22 | 19 | 0.88 | BMRL | BMRL | 3 | 1.59 | 1.41 | 14 | 7.24 | 48 | 36 | BMRL | BMRL | 2.1 | 23 | 25.1 | BMRL | BMRL | BMRL | BMRL | 2.6 | BMRL | 14 | 2.2 | BMRL | 2.6 | 2.6 | D-D5 | Duplicate | 1998-03-30 | 14:30 | 102.5 | 1961.4773 | 6.44 | 19 | BMRL | BMRL | BMRL | 3 | 1.86 | 1.14 | 14 | 7.4 | 48 | 32 | BMRL | BMRL | 3.9 | 8.5 | 12.4 | BMRL | BMRL | 1 | BMRL | 2.1 | BMRL | 7.3 | 2.5 | 1.8 | 3.1 | 3.1
[12 empty] | SDS-Chlorination temp. | oC | 14 | 14 | 14 | 14 | 0 |  | SDS-Chlorination temp. | oC | 14 | 14 | 14 | 14 | 0 | Avg-D5 | Average | --- | --- | --- | --- | 6.22 | 19 | 0.973 | BMRL | BMRL | 3 | 1.565 | 1.435 | 14 | 7.275 | 48 | 36 | BMRL | BMRL | 1.6 | 17.5 | 19.1 | BMRL | BMRL | BMRL | BMRL | 2.05 | BMRL | 9.3 | 2.2 | BMRL | 2.05 | 2.05 | Avg-D5 | Average | --- | --- | --- | --- | 6.41 | 19 | BMRL | BMRL | BMRL | 3 | 1.92 | 1.08 | 14 | 7.375 | 48 | 32 | BMRL | BMRL | 2.6 | 5.1 | 7.7 | BMRL | BMRL | 1 | BMRL | 1.6 | BMRL | 7.3 | 2.5 | 1.8 | 2.6 | 2.6
|  |  |  | 20-Minute EBCT Run | [7 empty] | SDS-Chlorination pH | --- | 7.27 | 7.3 | 7.35 | 7.3067 | 0.55312 |  | SDS-Chlorination pH | --- | 7.27 | 7.3 | 7.35 | 7.3067 | 0.55312 | RPD-D5 | RPD | --- | --- | --- | --- | 0 | 0 | 19.1161 | BMRL | BMRL | 0 | 3.1949 | 3.4843 | 0 | 0.9622 | 0 | #VALUE! | #VALUE! | #VALUE! | 62.5 | 62.8571 | 62.8272 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 53.6585 | #VALUE! | 101.0753 | #VALUE! | #VALUE! | 53.6585 | 53.6585 | RPD-D5 | RPD | --- | --- | --- | --- | 0.93604 | 0 | BMRL | BMRL | BMRL | 0 | 6.25 | 11.1111 | 0 | 0.67797 | 0 | #VALUE! | #VALUE! | #VALUE! | 100 | 133.3333 | 122.0779 | #VALUE! | #VALUE! | 0 | #VALUE! | 62.5 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 38.4615 | 38.4615
|  |  |  | Full-scale empty bed contact time, EBCTLC (min) | 20 | [6 empty] | SDS-Incubation time | hours | 48 | 48 | 48 | 48 | 0 |  | SDS-Incubation time | hours | 48 | 48 | 48 | 48 | 0 | D10 | Primary | 1998-04-06 | 16:00 | 272 | 10410.1818 | 6.23 | 20 | 1.762 | 0.016 | 0.90806 | 3 | 1.35 | 1.65 | 14 | 7.33 | 48 | 77 | BMRL | 4.2 | 15 | 38 | 57.2 | BMRL | 1.3 | BMRL | 1.5 | 8.7 | 3.1 | 14 | 5.2 | 2.6 | 11.5 | 14.6 | D10 | Primary | 1998-04-06 | 16:00 | 272 | 5205.0909 | 6.3 | 20 | 1.396 | BMRL | BMRL | 3 | 1.1 | 1.9 | 14 | 7.321 | 48 | 34 | BMRL | BMRL | 2.1 | 17 | 19.1 | BMRL | BMRL | BMRL | BMRL | 4.3 | BMRL | 6.7 | BMRL | 1 | 4.3 | 4.3
|  |  |  | Estimated full-scale run time, tLCT (days) | 210.3624 | [6 empty] | SDS-TOX | mg Cl- /L | 185 | 202.5 | 205 | 197.5 | 5.5176 |  | SDS-TOX | mg Cl- /L | 185 | 202.5 | 205 | 197.5 | 5.5176 | D-D10 | Duplicate | 1998-04-06 | 16:00 | 272 | 10410.1818 | 6.23 | 20 | 1.691 | 0.016 | 0.94619 | 3 | 1.32 | 1.68 | 14 | 7.39 | 48 | 72.5 | BMRL | 4.3 | 15 | 36 | 55.3 | BMRL | 1.9 | BMRL | 2.3 | 4.4 | BMRL | 8.6 | 2 | BMRL | 8.6 | 8.6 | D-D10 | Duplicate | 1998-04-06 | 16:00 | 272 | 5205.0909 | 6.32 | 20 | 1.341 | BMRL | BMRL | 3 | 1.2 | 1.8 | 14 | 7.33 | 48 | 43 | BMRL | BMRL | 2.4 | 15 | 17.4 | BMRL | 2.1 | 1 | 3.1 | 10 | 3.4 | 16 | 6.2 | 4.3 | 16.2 | 19.6
|  |  |  | RSSCT empty bed contact time, EBCTSC (min) | 3.1354 | [6 empty] | SDS-CHCl3 | mg/L | 5.4 | 2.4 | 36 | 14.6 | 127.3531 |  | SDS-CHCl3 | mg/L | 5.4 | 2.4 | 36 | 14.6 | 127.3531 | Avg-D10 | Average | --- | --- | --- | --- | 6.23 | 20 | 1.7265 | 0.016 | 0.92712 | 3 | 1.335 | 1.665 | 14 | 7.36 | 48 | 74.75 | BMRL | 4.25 | 15 | 37 | 56.25 | BMRL | 1.6 | BMRL | 1.9 | 6.55 | 3.1 | 11.3 | 3.6 | 2.6 | 10.05 | 13.15 | Avg-D10 | Average | --- | --- | --- | --- | 6.31 | 20 | 1.3685 | BMRL | BMRL | 3 | 1.15 | 1.85 | 14 | 7.3255 | 48 | 38.5 | BMRL | BMRL | 2.25 | 16 | 18.25 | BMRL | 2.1 | 1 | 3.1 | 7.15 | 3.4 | 11.35 | 6.2 | 2.65 | 13.35 | 16.75
|  |  |  | Estimated RSSCT run time, tSCT (days) | 32.9784 | [6 empty] | SDS-BDCM | mg/L | 19 | 10 | 11 | 13.3333 | 36.9966 |  | SDS-BDCM | mg/L | 19 | 10 | 11 | 13.3333 | 36.9966 | RPD-D10 | RPD | --- | --- | --- | --- | 0 | 0 | 4.1124 | 0 | 4.1124 | 0 | 2.2472 | 1.8018 | 0 | 0.81522 | 0 | 6.0201 | #VALUE! | 2.3529 | 0 | 5.4054 | 3.3778 | #VALUE! | 37.5 | #VALUE! | 42.1053 | 65.6489 | #VALUE! | 47.7876 | 88.8889 | #VALUE! | 28.8557 | 45.6274 | RPD-D10 | RPD | --- | --- | --- | --- | 0.31696 | 0 | 4.019 | BMRL | BMRL | 0 | 8.6957 | 5.4054 | 0 | 0.12286 | 0 | 23.3766 | #VALUE! | #VALUE! | 13.3333 | 12.5 | 9.3151 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 79.7203 | #VALUE! | 81.9383 | #VALUE! | 124.5283 | 89.1386 | 91.3433
|  |  |  | RSSCT bed length, lSC (cm) | 13.1832 | [6 empty] | SDS-DBCM | mg/L | 43 | 32 | 2.1 | 25.7 | 82.3553 |  | SDS-DBCM | mg/L | 43 | 32 | 2.1 | 25.7 | 82.3553 | D12 | Primary | 1998-04-07 | 16:00 | 296 | 11328.7273 | 6.21 | 20 | 1.896 | 0.0168 | 0.88608 | 3 | 1.01 | 1.99 | 14 | 7.38 | 48 | 85.5 | 1 | 4.1 | 16 | 43 | 64.1 | BMRL | BMRL | 1.2 | 2.3 | 10 | 3.6 | 17 | 6.3 | 3.7 | 13.5 | 17.1 | D12 | Primary | 1998-04-07 | 16:00 | 296 | 5664.3636 | 6.33 | 20 | 1.545 | 0.0092 | 0.59547 | 3 | 1.42 | 1.58 | 14 | 7.35 | 48 | 34.5 | BMRL | 1 | 4.1 | 20 | 25.1 | BMRL | BMRL | BMRL | BMRL | 3.6 | BMRL | 9.3 | 2.7 | 1.9 | 3.6 | 3.6
|  |  |  | Estimated volume required for 20-minute EBCT, VSC (L) | 352.8541 | [6 empty] | SDS-CHBr3 | mg/L | 37 | 98 | BMRL | 67.5 | 63.9015 |  | SDS-CHBr3 | mg/L | 37 | 98 | BMRL | 67.5 | 63.9015 | D-D12 | Duplicate | 1998-04-07 | 16:00 | 296 | 11328.7273 | 6.21 | 20 | 1.781 | 0.017 | 0.95452 | 3 | 1.09 | 1.91 | 14 | 7.35 | 48 | 83 | BMRL | 3.8 | 15 | 44 | 62.8 | BMRL | BMRL | 1.1 | 3.6 | 11 | 3.4 | 17 | 5.9 | 3.4 | 15.7 | 19.1 | D-D12 | Duplicate | 1998-04-07 | 16:00 | 296 | 5664.3636 | 6.33 | 20 | 1.455 | 0.0092 | 0.6323 | 3 | 1.65 | 1.35 | 14 | 7.34 | 48 | 30 | BMRL | 1 | 3.9 | 17 | 21.9 | BMRL | BMRL | BMRL | 2.7 | 5.4 | BMRL | 10 | 2.7 | 1.9 | 8.1 | 8.1
|  |  |  | Mass GAC required, mSC (g) | 10.7864 | [6 empty] | SDS-THM4 | mg/L | 104.4 | 142.4 | 49.1 | 98.6333 | 47.5666 |  | SDS-THM4 | mg/L | 104.4 | 142.4 | 49.1 | 98.6333 | 47.5666 | Avg-D12 | Average | --- | --- | --- | --- | 6.21 | 20 | 1.8385 | 0.0169 | 0.9203 | 3 | 1.05 | 1.95 | 14 | 7.365 | 48 | 84.25 | 1 | 3.95 | 15.5 | 43.5 | 63.95 | BMRL | BMRL | 1.15 | 2.95 | 10.5 | 3.5 | 17 | 6.1 | 3.55 | 14.6 | 18.1 | Avg-D12 | Average | --- | --- | --- | --- | 6.33 | 20 | 1.5 | 0.0092 | 0.61389 | 3 | 1.535 | 1.465 | 14 | 7.345 | 48 | 32.25 | BMRL | 1 | 4 | 18.5 | 23.5 | BMRL | BMRL | BMRL | 2.7 | 4.5 | BMRL | 9.65 | 2.7 | 1.9 | 7.2 | 7.2
[12 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | 2.3 | 2.3 | NR |  | SDS-MCAA* | mg/L | BMRL | BMRL | 2.3 | 2.3 | NR | RPD-D12 | RPD | --- | --- | --- | --- | 0 | 0 | 6.2551 | 1.1834 | 7.4372 | 0 | 7.619 | 4.1026 | 0 | 0.40733 | 0 | 2.9674 | #VALUE! | 7.5949 | 6.4516 | 2.2989 | 2.0328 | #VALUE! | #VALUE! | 8.6957 | 44.0678 | 9.5238 | 5.7143 | 0 | 6.5574 | 8.4507 | 15.0685 | 11.0497 | RPD-D12 | RPD | --- | --- | --- | --- | 0 | 0 | 6 | 0 | 6 | 0 | 14.9837 | 15.6997 | 0 | 0.13615 | 0 | 13.9535 | #VALUE! | 0 | 5 | 16.2162 | 13.617 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 40 | #VALUE! | 7.2539 | 0 | 0 | 62.5 | 62.5
[12 empty] | SDS-DCAA* | mg/L | 4 | 3 | 15 | 7.3333 | 90.7954 |  | SDS-DCAA* | mg/L | 4 | 3 | 15 | 7.3333 | 90.7954 | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[12 empty] | SDS-TCAA* | mg/L | 2.8 | 2 | 20 | 8.2667 | 123.0149 |  | SDS-TCAA* | mg/L | 2.8 | 2 | 20 | 8.2667 | 123.0149 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
[12 empty] | SDS-MBAA* | mg/L | 2.3 | 4 | BMRL | 3.15 | 38.1613 |  | SDS-MBAA* | mg/L | 2.3 | 4 | ND | 3.15 | 38.1613
[12 empty] | SDS-DBAA* | mg/L | 16 | 20 | BMRL | 18 | 15.7135 |  | SDS-DBAA* | mg/L | 16 | 20 | ND | 18 | 15.7135
[12 empty] | SDS-BCAA* | mg/L | 11 | 6.7 | 3.5 | 7.0667 | 53.2559 |  | SDS-BCAA* | mg/L | 11 | 6.7 | 3.5 | 7.0667 | 53.2559
[12 empty] | SDS-TBAA | mg/L | 15 | 24 | NR | 19.5 | 32.6357 |  | SDS-TBAA | mg/L | 15 | 24 | NR | 19.5 | 32.6357
[12 empty] | SDS-CDBAA | mg/L | 12 | 11 | NR | 11.5 | 6.1488 |  | SDS-CDBAA | mg/L | 12 | 11 | NR | 11.5 | 6.1488
[12 empty] | SDS-DCBAA | mg/L | 8.6 | 7.2 | NR | 7.9 | 12.531 |  | SDS-DCBAA | mg/L | 8.6 | 7.2 | NR | 7.9 | 12.531
[12 empty] | SDS-HAA5 | mg/L | 25.1 | 29 | 37.3 | 30.4667 | 20.4513 |  | SDS-HAA5 | mg/L | 25.1 | 29 | 37.3 | 30.4667 | 20.4513
[12 empty] | SDS-HAA6 | mg/L | 36.1 | 35.7 | 40.8 | 37.5333 | 7.5562 |  | SDS-HAA6 | mg/L | 36.1 | 35.7 | 40.8 | 37.5333 | 7.5562
[12 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [7 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
*: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
*: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
Note on S18: CDM: See Section 4 of the report for description of bromide contamination that led to variability in influent values.
Note on T18: CDM: Empirical relations for predicting DBP formation indicate that an increase in bromide concentration will result in higher levels of DBP's with a shift in speciation towards a higher percentage of bromanated species.
Note on AR8: CDM:At the start of the first quarter of testing the laboratory staff was under the belief that the chlorine dose for the SDS testing could be held constant as long as the residual remained above 0.2 mg/L. After discussions with the USEPA staff, it became clear that it was desirable to hold the chlorine residual constant. Thus, in subsequent quarters the chlorine dose was adjusted to try to obtain a constant chlorine residual.
Note on AU8: CDM: SDS Conditions: pH values are measured values Temperature values are the temperature of the fridgerator used for sample incubation.
Note on AX5: CDM: DO NOT USE THESE DBP VALUES, THE RESULTS ARE SKEWED DUE TO BROMIDE CONTAMINATION IN INFLUENT. PLEASE DIRECT QUESTIONS TO STEVE ALLGEIER
Note on AX33: CDM: D5 sample and duplicate DBP values were double checked. The sample analyses met all laboratory QA/QC standards. There is no explanation for the high RPD for these analytes.
Note on BD37: CDM: D10 sample and duplicate HAA values were double checked. The sample analyses met all laboratory QA/QC standards. There is no explanation for the high RPD for these analytes.
Note on BX22: CDM: The 20 minute column run was stopped by the UNC laboratory personel when 70% TOC breakthrough was reached according to their on-site TOC analyses. The TOC values reported for this study are from ICR certified laboratory NC016. The TOC value reported from NC016 was slightly lower than the value from the UNC lab. Thus, while the UNC lab showed 70% breakthrough, the NC016 lab did not.
Note on CA8: CDM:At the start of the first quarter of testing the laboratory staff was under the belief that the chlorine dose for the SDS testing could be held constant as long as the residual remained above 0.2 mg/L. After discussions with the USEPA staff, it became clear that it was desirable to hold the chlorine residual constant. Thus, in subsequent quarters the chlorine dose was adjusted to try to obtain a constant chlorine residual.
Note on CG5: CDM: DO NOT USE THESE DBP VALUES, THE RESULTS ARE SKEWED DUE TO BROMIDE CONTAMINATION IN INFLUENT. PLEASE DIRECT QUESTIONS TO STEVE ALLGEIER
Note on CG11: CDM: Laboratory reported TOX of 96ug/L. All DBP's for D-4 EBCT20 are abnorally high and felt to be outliers.
Note on CG33: CDM: D5 sample and duplicate DBP values were double checked. The sample analyses met all laboratory QA/QC standards. There is no explanation for the high RPD for these analytes.
Note on CG37: CDM: D10 sample and duplicate DBP values were double checked. The sample analyses met all laboratory QA/QC standards. There is no explanation for the high RPD for these analytes.
Note on CH11: CDM: Laboratory reported CHCl3 of 1.2ug/L. All DBP's for D-4 EBCT20 are abnorally high and felt to be outliers.
Note on CI11: CDM: Laboratory reported BDCM of 7.3ug/L. All DBP's for D-4 EBCT20 are abnorally high and felt to be outliers.
Note on CJ11: CDM: Laboratory reported DBCM of 34.0ug/L. All DBP's for D-4 EBCT20 are abnorally high and felt to be outliers.
Note on CK11: CDM: Laboratory reported CHBr3 of 50.0ug/L. All DBP's for D-4 EBCT20 are abnorally high and felt to be outliers.
Note on CM11: CDM: Laboratory reported MCAA of 3.7ug/L. All DBP's for D-4 EBCT20 are abnorally high and felt to be outliers.
Note on CN11: CDM: Laboratory reported DCAA of 2.9ug/L. All DBP's for D-4 EBCT20 are abnorally high and felt to be outliers.
Note on CO11: CDM: Laboratory reported TCAA of BMRL. All DBP's for D-4 EBCT20 are abnorally high and felt to be outliers.
Note on CP11: CDM: Laboratory reported MBAA of 7.0ug/L. All DBP's for D-4 EBCT20 are abnorally high and felt to be outliers.
Note on CQ11: CDM: Laboratory reported DBAA of 25.0ug/L. All DBP's for D-4 EBCT20 are abnorally high and felt to be outliers.
Note on CR11: CDM: Laboratory reported BCAA of 11.0ug/L. All DBP's for D-4 EBCT20 are abnorally high and felt to be outliers.
Note on CS11: CDM: Laboratory reported TBAA of 4.1ug/L. All DBP's for D-4 EBCT20 are abnorally high and felt to be outliers.
Note on CT11: CDM: Laboratory reported CDBAA of BMRL. All DBP's for D-4 EBCT20 are abnorally high and felt to be outliers.
Note on CU11: CDM: Laboratory reported DCBAA of BMRL. All DBP's for D-4 EBCT20 are abnorally high and felt to be outliers.

## Sheet2. 2nd Quarter
FIELD-SET 2: 2nd QUARTER RSSCT RESULTS (FILE: ICR448.xls)
Field 2-1: PWS And Treatment Plant Data |  | Field 2-2: Full-Scale GAC Characteristics1 |  | Field 2-3: RSSCT Design Parameters |  |  |  | Field 2-4: Pretreatment Used Prior To GAC1 |  |  |  | Field 2-5: GAC Influent Water Quality For The 10-Minute EBCT Run | [7 empty] | Field 2-6: GAC Influent Water Quality For The 20-Minute EBCT Run1 | [6 empty] | Field 2-7: GAC Effluent Water Quality For The 10-Minute EBCT Run1 | [14 empty] | Field 2-7: GAC Effluent Water Quality For The 10-Minute EBCT Run (continued) | [11 empty] | Field 2-7: GAC Effluent Water Quality For The 10-Minute EBCT Run (continued) | [6 empty] | Field 2-8: GAC Effluent Water Quality For The 20-Minute EBCT Run1 | [13 empty] | Field 2-8: GAC Effluent Water Quality For The 20-Minute EBCT Run (continued) | [13 empty] | Field 2-8: GAC Effluent Water Quality For The 20-Minute EBCT Run | [5 empty] | Field 2-9: GAC Cost Parameters
|  |  |  | Input Design Parameters |  | US Standard Mesh Sizes | [20 empty] | Group C, 12 effluent samples per run | [33 empty] | Group C, 12 effluent samples per run
PWS Name | Public Works Commision of the City of Fayettville | Carbon manufacturer | Calgon Corp. | RSSCT influent TOC (mg/L) | 2.75 | US standard | Opening | Process | Description | Scale |  | 10-min. EBCT Start Date | 1998-06-03 | [6 empty] | 20-min. EBCT Start Date | 1998-05-26 | [5 empty] | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS Free | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Cost Parameter | Parameter value
Public Water System Identification Number | NC 0326010 | Carbon trade name | Filtrasorb-400 | Inner diameter of the RSSCT column, DSC (mm) | 15 | mesh size | (mm) | Coagulation | 30 - 60 mg/L alum as Al2(SO4)3*14H2O | Full-Scale |  | 10-min. EBCT Start Time | 13:00 | [6 empty] | 20-min. EBCT Start Time | 18:00 | [5 empty] | ID | duplicated? | date | time | time | volumes | [5 empty] | Cl2 dose | Cl2 residual | Cl2 demand | Chlorin. temp. | Chlorin. pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | Capital Recovery Interest Rate (%) | 5.3
Water Industry Data Base Number (optional) | 1244 | Carbon type | Bituminous | Minimum RSSCT Reynolds number, ReSC, min | 0.2 | 4 | 4.75 | Flocculation | 1-stage | Full-Scale | [17 empty] | Y/N | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | Capital Recovery Period (years) | 45
|  | Original GAC mesh size, upper (US standard mesh) | 12 | Full-scale operating temperature, ToC (oC) | 23.5 | 6 | 3.35 | Sedimentation | 3.1 hours conventional | Full-Scale |  | Group A, 2 samples per batch | [7 empty] | Group A, 2 samples per batch | [6 empty] | C1 | N | 1998-06-03 | 14:00 | 1 | 38.2727 | 7.1 | 24 | 0.413 | BMRL | BMRL | 2.65 | 1.06 | 1.59 | 20 | 7.26 | 48 | BMRL | BMRL | BMRL | BMRL | 17 | 17 | BMRL | BMRL | BMRL | 1 | 3.4 | BMRL | 5 | BMRL | BMRL | 4.4 | 4.4 | C1 | N | 1998-05-26 | 19:00 | 1 | 19.1364 | 6.8 | 22 | BMRL | BMRL | BMRL | 2.65 | 1.23 | 1.42 | 20 | 7.19 | 48 | BMRL | 2 | 1.5 | 0.8 | BMRL | 4.3 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | 0 | Overhead & Profit Factor (% of construction costs) | 10
Official ICR Contact Person |  | Original GAC mesh size, lower (US standard mesh) | 40 | Full-scale bed porosity, eLC | 0.45 | 8 | 2.36 | Cartridge filtration | 1um exclusion size | Bench-scale |  | Parameter | Units | Sample A1-10 | Sample A2-10 | Average | RPD |  |  | Parameter | Units | Sample A1-20 | Sample A2-20 | Average | RPD |  | C2 | N | 1998-06-04 | 13:00 | 24 | 918.5455 | 6.95 | 23 | 0.477 | 0.005 | 1.0482 | 2.65 | 1.03 | 1.62 | 20 | 7.24 | 48 | BMRL | BMRL | BMRL | BMRL | 16 | 16 | BMRL | BMRL | BMRL | BMRL | 3 | BMRL | 4.2 | BMRL | BMRL | 3 | 3 | C2 | N | 1998-05-27 | 17:30 | 23.5 | 449.7045 | 7.14 | 22 | 0.131 | BMRL | BMRL | 2.65 | 1.15 | 1.5 | 20 | 7.15 | 48 | 27 | 2.2 | 2.1 | 1.4 | BMRL | 5.7 | BMRL | 1.4 | 1.1 | BMRL | BMRL | BMRL | BMRL | BMRL | 1.2 | 2.5 | 2.5 | Special Sitework Factor (% of construction costs) | 5
Mailing Address |  | Original carbon particle diameter, dLC (mm) | 1.0525 | Measured RSSCT dry bed density, rSC (g/cm3) | 0.463 | 10 | 2 |  |  |  |  | Sampling date | MM/DD/YY | 1998-06-03 | 1998-06-25 | --- | --- |  |  | Sampling date | MM/DD/YY | 1998-05-26 | 1998-06-03 | --- | --- |  | C3 | N | 1998-06-05 | 14:00 | 49 | 1875.3636 | 5.78 | 22 | 0.748 | BMRL | BMRL | 2.65 | 1 | 1.65 | 20 | 7.15 | 48 | BMRL | BMRL | BMRL | BMRL | 25 | 25 | BMRL | BMRL | BMRL | BMRL | 2.8 | BMRL | 4 | BMRL | BMRL | 2.8 | 2.8 | C3 | N | 1998-05-28 | 18:30 | 48.5 | 928.1136 | 6.8 | 24 | 0.213 | BMRL | BMRL | 2.65 | 1.75 | 0.9 | 20 | 7.14 | 48 | BMRL | 1.6 | 2 | 3 | 0.8 | 7.4 | BMRL | 1.4 | 1 | BMRL | BMRL | 1.2 | BMRL | BMRL | 1 | 2.4 | 3.6 | Construction Contingencies (% of construction costs) | 10
|  | 1: These are the characteristics before the carbon is ground for RSSCT experiments. |  | RSSCT GAC mesh size, upper (US standard mesh) | 80 | 12 | 1.68 |  |  |  |  | Sampling time | hh:mm | 14:00 | 13:00 | --- | --- |  |  | Sampling time | hh:mm | 18:00 | 14:00 | --- | --- |  | C4 | N | 1998-06-06 | 16:00 | 75 | 2870.4545 | 6.8 | 23 | 0.746 | 0.007 | 0.93834 | 2.7 | 1.27 | 1.43 | 20 | 7.22 | 48 | BMRL | BMRL | BMRL | BMRL | 16 | 16 | BMRL | BMRL | BMRL | BMRL | 3.3 | BMRL | BMRL | BMRL | BMRL | 3.3 | 3.3 | C4 | N | 1998-05-29 | 14:00 | 68 | 1301.2727 | 6.3 | 23 | 0.35 | 0.008 | 2.2857 | 2.7 | 1.56 | 1.14 | 20 | 7.17 | 48 | 29 | 3.3 | 3.8 | 5.2 | 1.4 | 13.7 | BMRL | 3.3 | 2.4 | BMRL | 1.1 | 2.4 | BMRL | BMRL | 2.1 | 6.8 | 9.2 | Engineering Fee Factor (% of construction costs) | 10
Phone Number |  |  |  | RSSCT GAC mesh size, lower (US standard mesh) | 100 | 16 | 1.18 |  |  |  |  | Operation time | hh.hh | 1 | 528 | --- | --- |  |  | Operation time | hh.hh | 0 | 188 | --- | --- |  | C5 | N | 1998-06-07 | 15:30 | 98.5 | 3769.8636 | 6.5 | 23 | 1.185 | 0.014 | 1.1814 | 2.7 | 1.7 | 1 | 20 | 7.31 | 48 | 37 | BMRL | BMRL | 2.7 | 32 | 34.7 | BMRL | BMRL | BMRL | 1.2 | 6.9 | BMRL | 5.5 | BMRL | BMRL | 8.1 | 8.1 | C5 | N | 1998-05-30 | 15:00 | 93 | 1779.6818 | 6.5 | 22 | 0.178 | 0.009 | 5.0562 | 2.7 | 1.33 | 1.37 | 20 | 7.22 | 48 | 35 | 4 | 4.8 | 5.2 | 1.6 | 15.6 | BMRL | 2.4 | 1.9 | BMRL | 1 | 2.5 | BMRL | BMRL | 1.7 | 5.3 | 7.8 | 1998 ENR Construction Cost Index (CCI base year 1913) | 131.3
FAX Number | [5 empty] | 20 | 0.85 |  |  |  |  | Bed volumes | (10 minutes) | 38.2727 | 20208 | --- | --- |  |  | Bed volumes | (20 minutes) | 0 | 3597.6364 | --- | --- |  | C6 | N | 1998-06-08 | 10:00 | 117 | 4477.9091 | 6.45 | 22 | 1.417 | 0.008 | 0.56457 | 2.7 | 1.26 | 1.44 | 20 | 7.22 | 48 | 41 | BMRL | BMRL | 2.5 | 44 | 46.5 | BMRL | 5.3 | BMRL | 1.1 | 7.8 | BMRL | 8.3 | BMRL | 1.4 | 14.2 | 14.2 | C6 | N | 1998-05-31 | 15:00 | 117 | 2238.9545 | 6.6 | 23 | 0.446 | 0.01 | 2.2422 | 2.75 | 1.39 | 1.36 | 20 | 7.23 | 48 | BMRL | BMRL | BMRL | BMRL | 24 | 24 | BMRL | BMRL | BMRL | BMRL | 4.8 | BMRL | BMRL | BMRL | BMRL | 4.8 | 4.8 | 1998 Producers Price Index (PPI base year 1982 = 100) | 78.8
E-Mail Address (optional) |  |  |  | Estimated Run Length |  | 30 | 0.6 |  |  |  |  | Alkalinity | mg/L as CaCO3 | 8.4 | 10.4 | 9.4 | 21.2766 |  |  | Alkalinity | mg/L as CaCO3 | 9.4 | 8.4 | 8.9 | 11.236 |  | C7 | N | 1998-06-09 | 14:00 | 145 | 5549.5455 | 6.3 | 23 | 1.324 | 0.0156 | 1.1782 | 2.87 | 0.45 | 2.42 | 20 | 7.35 | 48 | 71 | BMRL | 1.2 | 4.6 | 51 | 56.8 | BMRL | BMRL | BMRL | 1.3 | 9.6 | 1.1 | 9.9 | 2 | 1 | 10.9 | 12 | Avg-C7 | Y | 1998-06-01 | 15:00 | 141 | 2698.2273 | 6.4 | 24 | 0.581 | 0.012 | 2.0654 | 2.8 | 0.71 | 2.09 | 20 | 7.345 | 48 | BMRL | BMRL | BMRL | BMRL | 19.5 | 19.5 | BMRL | BMRL | BMRL | 1.1 | 2.6 | BMRL | NR | NR | BMRL | 3.7 | 3.7 | Labor Rate + Fringe ($/work-hour) | 21
|  |  |  | Bed volumes to 50% TOC breakthrough, BV50 | 5825.4199 | 40 | 0.425 |  |  |  |  | Total hardness | mg/L as CaCO3 | 23.2 | 22.1 | 22.65 | 4.8565 |  |  | Total hardness | mg/L as CaCO3 | 21.6 | 23.2 | 22.4 | 7.1429 |  | C8 | N | 1998-06-10 | 13:30 | 168.5 | 6448.9545 | 6.1 | 24 | 1.514 | 0.018 | 1.1889 | 2.9 | 0.35 | 2.55 | 20 | 7.39 | 48 | 80 | BMRL | 1.2 | 4.4 | 62 | 67.6 | BMRL | 2.7 | BMRL | 2.4 | 12 | 1.4 | 6.5 | 2 | 1.2 | 17.1 | 18.5 | C8 | N | 1998-06-02 | 16:00 | 166 | 3176.6364 | 6.45 | 24 | 0.56 | 0.0086 | 1.5357 | 2.8 | 0.58 | 2.22 | 20 | 7.27 | 48 | 30 | BMRL | BMRL | 1 | 33 | 34 | BMRL | BMRL | BMRL | 1.1 | 6.4 | BMRL | 5.3 | BMRL | BMRL | 7.5 | 7.5 | Labor Overhead Factor (% of labor) | 4.1
Technical ICR Contact Person |  |  |  | Estimated run length, BVT ( = 2 x BV50) | 11650.8397 | 50 | 0.3 |  |  |  |  | Calcium hardness | mg/L as CaCO3 | 13.6 | 13.4 | 13.5 | 1.4815 |  |  | Calcium hardness | mg/L as CaCO3 | 13.2 | 13.6 | 13.4 | 2.9851 |  | C9 | N | 1998-06-11 | 15:00 | 194 | 7424.9091 | 6.03 | 24 | 1.877 | 0.0208 | 1.1082 | 3 | 0.3 | 2.7 | 20 | 7.28 | 48 | 93 | BMRL | 1.9 | 7.5 | 83 | 92.4 | BMRL | 1.9 | BMRL | 2.4 | 14 | 1.4 | 16 | 3 | 1.6 | 18.3 | 19.7 | C9 | N | 1998-06-03 | 14:00 | 188 | 3597.6364 | 6.4 | 24 | 0.505 | 0.007 | 1.3861 | 2.7 | 1.27 | 1.43 | 20 | NR | 48 | BMRL | BMRL | BMRL | BMRL | 16 | 16 | BMRL | BMRL | BMRL | BMRL | 2.3 | BMRL | 4.1 | BMRL | BMRL | 2.3 | 2.3 | Electric Rate ($/kW-h) | 0.035
Mailing Address |  |  |  | BVT + 30% safety factor, BVT+30% ( = 2.6 x BV50) | 15146.0916 | 60 | 0.25 |  |  |  |  | Ammonia | mg NH3-N / L | 0.05 | 0.02 | 0.035 | 85.7143 |  |  | Ammonia | mg NH3-N / L | 0.05 | 0.05 | 0.05 | 0 |  | Avg-C10 | Y | 1998-06-12 | 15:00 | 218 | 8343.4545 | 6.3 | 24 | 1.9105 | 0.021 | 1.0992 | 3 | 1.1 | 1.9 | 20 | 7.235 | 48 | 115 | BMRL | 3.4 | 14 | 98.5 | 115.9 | BMRL | BMRL | BMRL | 3.15 | 16.5 | 2.6 | 17 | 5 | 19.65 | 19.65 | 22.25 | C10 | N | 1998-06-04 | 13:00 | 211 | 4037.7727 | 6.53 | 23 | 1.069 | 0.0074 | 0.69224 | 2.8 | 1.32 | 1.48 | 20 | 7.43 | 48 | BMRL | BMRL | BMRL | 1 | 24 | 25 | BMRL | BMRL | BMRL | BMRL | 4.7 | BMRL | BMRL | BMRL | BMRL | 4.7 | 4.7 | Fuel Oil Rate ($/gal) | 0.55
[6 empty] | 70 | 0.21 |  |  |  |  | Bromide | mg/L | 349 | 30 | 189.5 | 168.3377 |  |  | Bromide | mg/L | 51 | 349 | 200 | 149 |  | C11 | N | 1998-06-13 | 11:00 | 238 | 9108.9091 | 6.4 | 23 | 2.023 | 0.021 | 1.0381 | 3 | 1.13 | 1.87 | 20 | 7.36 | 48 | 122.5 | BMRL | 3.4 | 15 | 105 | 123.4 | BMRL | BMRL | BMRL | 3.15 | 17.5 | 2.65 | 24 | 7.4 | 3 | 20.65 | 23.3 | C11 | N | 1998-06-05 | 13:00 | 235 | 4497.0455 | 6.36 | 22 | NA | 0.011 | NA | 2.8 | 1.53 | 1.27 | 20 | 7.26 | 48 | BMRL | BMRL | BMRL | 1.4 | 26 | 27.4 | BMRL | BMRL | BMRL | 1.3 | 3.2 | BMRL | 5.1 | BMRL | 1.2 | 4.5 | 4.5 | Natural Gas Rate ($/ft3) | 0.007
Phone Number |  |  |  | General RSSCT Design Parameters |  | 80 | 0.18 | [19 empty] | Avg-C12 | Y | 1998-06-13 | 23:00 | 250 | 9568.1818 | 6.35 | 23 | 2.1485 | 0.028 | 1.3032 | 3.1 | 1.09 | 2.01 | 20 | 7.29 | 48 | 130 | BMRL | 3.6 | 15.5 | 110 | 129.1 | BMRL | BMRL | BMRL | 2.85 | 18 | 2.7 | 24 | 7.5 | 20.85 | 20.85 | 23.55 | Avg-C12 | Y | 1998-06-07 | 13:00 | 283 | 5415.5909 | 6.21 | 23 | 0.793 | 0.009 | 1.1349 | 2.7 | 1.26 | 1.44 | 20 | 7.24 | 48 | 34 | BMRL | BMRL | 1.45 | 29 | 30.45 | BMRL | BMRL | BMRL | 1.45 | 5.95 | BMRL | 6.1 | BMRL | 1.1 | 7.4 | 7.4 | Current Process Water Rate ($/1000 gal) | 0.35
FAX Number |  |  |  | Kinematic viscosity at ToC, nLC (m2/s) | 9.4342e-07 | 100 | 0.15 |  |  |  |  | Group B, 3 samples per batch | [7 empty] | Group B, 3 samples per batch | [6 empty] | C13 | N | 1998-06-14 | 14:00 | 265 | 10142.2727 | 6.31 | 24 | 1.646 | 0.024 | 1.4581 | 3 | 1.05 | 1.95 | 20 | 7.3 | 48 | 130 | BMRL | 4.1 | 16 | 120 | 140.1 | BMRL | BMRL | BMRL | 3.8 | 19 | 3.1 | 24 | 8 | 3.5 | 22.8 | 25.9 | Avg-C13 | Y | 1998-06-12 | 2:00 | 392 | 7501.4545 | 6.27 | 23 | 1.2565 | 0.0145 | 1.154 | 2.9 | 1.45 | 1.45 | 20 | 7.33 | 48 | 87 | BMRL | 2.6 | 12.5 | 70 | 85.1 | BMRL | BMRL | BMRL | 2.75 | 14.5 | 2.6 | 14.5 | 4.5 | 3.2 | 17.25 | 19.85 | Modifications to Existing Plant (% of construction costs) | 20
E-Mail Address (optional) |  |  |  | RSSCT carbon particle diameter, dSC (mm) | 0.165 | 120 | 0.125 |  |  |  |  | Parameter | Units | Sample B1-10 | Sample B2-10 | Sample B3-10 | Average | %SD |  | Parameter | Units | Sample B1-10 | Sample B2-10 | Sample B3-10 | Average | %SD | Avg-C14 | Y | 1998-06-15 | 13:00 | 288 | 11022.5455 | 6.36 | 24 | 1.7425 | 0.026 | 1.4921 | 3 | 0.97 | 2.03 | 20 | 7.29 | 48 | 147.5 | BMRL | 3.55 | 15 | 130 | 148.55 | BMRL | BMRL | BMRL | 3.9 | 23 | 2.9 | 17 | 5.15 | 2.65 | 26.9 | 29.8 | C14 | N | 1998-06-25 | 13:00 | 715 | 13682.5 | 6.2 | 24 | 2.472 | 0.025 | 1.0113 | 2.8 | 0.67 | 2.13 | 20 | 7.24 | 48 | 145 | 1.7 | 5.8 | 22 | 100 | 129.5 | BMRL | 2.2 | BMRL | 3.4 | 18 | 5.1 | NR | 6.9 | 4.1 | 23.6 | 28.7
|  |  |  | Scaling factor, SF | 6.3788 | 140 | 0.106 | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  |  | Sampling date | MM/DD/YY | 1998-06-03 | 1998-06-25 | NA | --- | --- |  | Sampling date | MM/DD/YY | 1998-05-26 | 1998-06-03 | 1998-06-25 | --- | --- | C15 | N | 1998-06-16 | 11:00 | 310 | 11864.5455 | 6.34 | 23 | 2.771 | 0.024 | 0.86611 | 3 | 0.74 | 2.26 | 20 | 7.36 | 48 | 150 | BMRL | 2.6 | 10 | 140 | 152.6 | BMRL | BMRL | BMRL | 3 | 22 | 1.8 | 20 | 4.2 | 2.5 | 25 | 26.8 | C15 | N | 1998-06-29 | 14:00 | 812 | 15538.7273 | 6.3 | 24 | NA | 0.02 | NA | 3 | 0.79 | 2.21 | 20 | 7.35 | 48 | 135 | NA | NA | NA | NA | 0 | BMRL | 2.8 | BMRL | 2.8 | 17 | 3.6 | 19 | 5.7 | 3.1 | 22.6 | 26.2
Plant Name | P.O. Hoffer Water Treatment Plant |  |  | RSSCT hydraulic loading rate, vSC (m/hr) | 1.8525 | 170 | 0.088 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  |  | Sampling time | hh:mm | 14:00 | 13:00 | NA | --- | --- |  | Sampling time | hh:mm | 18:00 | 14:00 | 13:00 | --- | --- | C16 | N | 1998-06-25 | 13:00 | 528 | 20208 | 6.23 | 24 | 2.538 | 0.036 | 1.4184 | 3.1 | 0.65 | 2.45 | 20 | 7.25 | 48 | 190 | 1.4 | 6.2 | 29 | 130 | 166.6 | BMRL | 2.1 | 1 | 4.1 | 25 | 6 | NR | 8.3 | 4.8 | 32.2 | 38.2
Treatment Plant Category | CONV |  |  | RSSCT flow rate, QSC (mL/min) | 5.4562 | 200 | 0.075 | is to list the pretreatment processes used in this particular RSSCT run. |  |  |  | Operation time | hh.hh | 1 | 528 | NA | --- | --- |  | Operation time | hh.hh | 0 | 188 | 715 | --- | --- | C17 | N | 1998-06-29 | 14:00 | 625 | 23920.4545 | 6.27 | 23 | NA | 0.028 | NA | 3.5 | 0.82 | 2.68 | 20 | 7.22 | 48 | 135 | 1.4 | 8.5 | 38 | 130 | 177.9 | BMRL | 3.2 | 1 | 3.8 | 22 | 6.8 | 24 | 10 | 5.3 | 30 | 36.8
Process Train Name | Conventional train |  |  | Estimated total influent volume required, VSCT (L) | 388.6606 | 230 | 0.062 |  |  |  |  | Bed volumes | (10 minute) | 38.2727 | 20208 | NA | --- | --- |  | Bed volumes | (20 minute) | 0 | 3597.6364 | 13682.5 | --- | --- | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [6 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [13 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [13 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
ICR Treatment Plant Identification Number | 448 |  |  |  |  | 270 | 0.053 |  |  |  |  | pH | --- | 6.23 | 6.15 | NA | 6.19 | 0.91387 |  | pH | --- | 6.05 | 6.23 | 6.15 | 6.1433 | 1.468 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [6 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [13 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [13 empty] | *: These six species make up HAA6, but the other three HAA species,
PWSID Number of Plant (if assigned) | NC 0326010 |  |  | 10-Minute EBCT Run |  | 325 | 0.044 |  |  |  |  | Turbidity | ntu | 0.59 | NR | NA | 0.59 | NA |  | Turbidity | ntu | 0.66 | 0.59 | NR | 0.625 | 7.9196 | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results | [14 empty] | for the primary and duplicate analyses below. | [11 empty] | for the primary and duplicate analyses below. | [6 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below. | [27 empty] | TBAA, CDBAA and DCBAA, should be reported if measured.
Historical Minimum Water Temperature (oC) | 4 |  |  | Full-scale empty bed contact time, EBCTLC (min) | 10 | 400 | 0.037 |  |  |  |  | Temperature | oC | 24 | 24 | NA | 24 | 0 |  | Temperature | oC | 22 | 24 | 24 | 23.3333 | 4.9487
Historical Average Water Temperature (oC) | 34 |  |  | Estimated full-scale run time, tLCT (days) | 105.1812 | [6 empty] | Total organic carbon | mg/L | 3.275 | 3.015 | NA | 3.145 | 5.8457 |  | Total organic carbon | mg/L | 2.269 | 3.275 | 3.015 | 2.853 | 18.3035 | Group D, 3 duplicate effluent samples per run (results from primary and duplicate analyses) | [33 empty] | Group D, 3 duplicate effluent samples per run (results from primary and duplicate analyses)
State Approved Plant Capacity (MGD) | 32 |  |  | RSSCT empty bed contact time, EBCTSC (min) | 1.5677 | [6 empty] | UV254 | cm-1 | 0.06 | 0.054 | NA | 0.057 | 7.4432 |  | UV254 | cm-1 | 0.0556 | 0.06 | 0.054 | 0.056533 | 5.4958 | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS
|  |  |  | Estimated RSSCT run time, tSCT (days) | 16.4892 | [6 empty] | SUVA | L/(mg*m) | 1.8321 | 1.791 | NA | 1.8116 | 1.601 |  | SUVA | L/(mg*m) | 2.4504 | 1.8321 | 1.791 | 2.0245 | 18.2473 | ID | Type | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6
|  |  |  | RSSCT bed length, lSC (cm) | 4.8403 | [6 empty] | SDS-Cl2 dose | mg/L | 3.6 | 4 | NA | 3.8 | 7.4432 |  | SDS-Cl2 dose | mg/L | 3.4 | 3.6 | 4 | 3.6667 | 8.332 |  |  | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L
|  |  |  | Estimated volume required for 10-minute EBCT, VSC (L) | 129.5535 | [6 empty] | SDS-Free Cl2 residual | mg/L | 0.22 | 0.45 | NA | 0.335 | 48.5476 |  | SDS-Free Cl2 residual | mg/L | 0.2 | 0.22 | 0.45 | 0.29 | 47.905 | D10 | Primary | 1998-06-12 | 15:00 | 218 | 8343.4545 | 6.3 | 24 | 1.843 | 0.021 | 1.1394 | 3 | 1.1 | 1.9 | 20 | 7.26 | 48 | 115 | BMRL | 3.4 | 14 | 97 | 114.4 | BMRL | BMRL | BMRL | 3.5 | 18 | 2.5 | 19 | 5.4 | 21.5 | 21.5 | 24 | D7 | Primary | 1998-06-01 | 15:00 | 141 | 2698.2273 | 6.4 | 24 | 0.581 | 0.012 | 2.0654 | 2.8 | 0.71 | 2.09 | 20 | 7.36 | 48 | BMRL | BMRL | BMRL | BMRL | 17 | 17 | BMRL | BMRL | BMRL | BMRL | 2.1 | BMRL | NR | NR | BMRL | 2.1 | 2.1
|  |  |  | Mass GAC required, mSC (g) | 3.9603 | [6 empty] | SDS-Cl2 demand | mg/L | 3.38 | 3.55 | NA | 3.465 | 3.4692 |  | SDS-Cl2 demand | mg/L | 3.2 | 3.38 | 3.55 | 3.3767 | 5.1833 | D-D10 | Duplicate | 1998-06-12 | 15:00 | 218 | 8343.4545 | 6.3 | 24 | 1.978 | 0.021 | 1.0617 | 3 | 1.1 | 1.9 | 20 | 7.21 | 48 | 115 | BMRL | 3.4 | 14 | 100 | 117.4 | BMRL | BMRL | BMRL | 2.8 | 15 | 2.7 | 15 | 4.6 | 17.8 | 17.8 | 20.5 | D-D7 | Duplicate | 1998-06-01 | 15:00 | 141 | 2698.2273 | 6.4 | 24 | NR | NR | NR | 2.8 | 0.71 | 2.09 | 20 | 7.33 | 48 | BMRL | BMRL | BMRL | BMRL | 22 | 22 | BMRL | BMRL | BMRL | 1.1 | 3.1 | BMRL | NR | NR | BMRL | 4.2 | 4.2
[12 empty] | SDS-Chlorination temp. | oC | 20 | 20 | NA | 20 | 0 |  | SDS-Chlorination temp. | oC | 20 | 20 | 20 | 20 | 0 | Avg-D10 | Average | --- | --- | --- | --- | 6.3 | 24 | 1.9105 | 0.021 | 1.1006 | 3 | 1.1 | 1.9 | 20 | 7.235 | 48 | 115 | BMRL | 3.4 | 14 | 98.5 | 115.9 | BMRL | BMRL | BMRL | 3.15 | 16.5 | 2.6 | 17 | 5 | 19.65 | 19.65 | 22.25 | Avg-D7 | Average | --- | --- | --- | --- | 6.4 | 24 | 0.581 | 0.012 | 2.0654 | 2.8 | 0.71 | 2.09 | 20 | 7.345 | 48 | BMRL | BMRL | BMRL | BMRL | 19.5 | 19.5 | BMRL | BMRL | BMRL | 1.1 | 2.6 | BMRL | NR | NR | BMRL | 3.7 | 3.7
|  |  |  | 20-Minute EBCT Run | [7 empty] | SDS-Chlorination pH | --- | 7.31 | 7.33 | NA | 7.32 | 0.1932 |  | SDS-Chlorination pH | --- | 7.26 | 7.31 | 7.33 | 7.3 | 0.49391 | RPD-D10 | RPD | --- | --- | --- | --- | 0 | 0 | 7.0662 | 0 | 7.0662 | 0 | 0 | 0 | 0 | 0.69109 | 0 | 0 | #VALUE! | 0 | 0 | 3.0457 | 2.5884 | #VALUE! | #VALUE! | #VALUE! | 22.2222 | 18.1818 | 7.6923 | 23.5294 | 16 | 18.8295 | 18.8295 | 15.7303 | RPD-D7 | RPD | --- | --- | --- | --- | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | 0 | 0 | 0.40844 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 25.641 | 25.641 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 38.4615 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 56.7568 | 56.7568
|  |  |  | Full-scale empty bed contact time, EBCTLC (min) | 20 | [6 empty] | SDS-Incubation time | hours | 48 | 48 | NA | 48 | 0 |  | SDS-Incubation time | hours | 48 | 48 | 48 | 48 | 0 | D12 | Primary | 1998-06-13 | 23:00 | 250 | 9568.1818 | 6.35 | 23 | 2.159 | 0.028 | 1.2969 | 3.1 | 1.08 | 2.02 | 20 | 7.29 | 48 | 125 | BMRL | 3.8 | 15 | 110 | 128.8 | BMRL | BMRL | BMRL | 2.6 | 18 | 2.7 | 24 | 7.2 | 20.6 | 20.6 | 23.3 | D12 | Primary | 1998-06-07 | 13:00 | 283 | 5415.5909 | 6.21 | 23 | 0.795 | 0.009 | 1.1321 | 2.7 | 1.26 | 1.44 | 20 | 7.27 | 48 | 31 | BMRL | BMRL | 1.4 | 32 | 33.4 | BMRL | BMRL | BMRL | 1.7 | 6.4 | BMRL | 6.2 | BMRL | 1.1 | 8.1 | 8.1
|  |  |  | Estimated full-scale run time, tLCT (days) | 210.3624 | [6 empty] | SDS-TOX | mg Cl- /L | 240 | 240 | NA | 240 | 0 |  | SDS-TOX | mg Cl- /L | 170 | 240 | 240 | 216.6667 | 18.6529 | D-D12 | Duplicate | 1998-06-13 | 23:00 | 250 | 9568.1818 | 6.35 | 23 | 2.138 | 0.028 | 1.3096 | 3.1 | 1.1 | 2 | 20 | NA | 48 | 135 | BMRL | 3.4 | 16 | 110 | 129.4 | BMRL | BMRL | BMRL | 3.1 | 18 | 2.7 | 24 | 7.8 | 21.1 | 21.1 | 23.8 | D-D12 | Duplicate | 1998-06-07 | 13:00 | 283 | 5415.5909 | 6.21 | 23 | 0.791 | 0.009 | 1.1378 | 2.7 | 1.26 | 1.44 | 20 | 7.21 | 48 | 37 | BMRL | BMRL | 1.5 | 26 | 27.5 | BMRL | BMRL | BMRL | 1.2 | 5.5 | BMRL | 6 | BMRL | BMRL | 6.7 | 6.7
|  |  |  | RSSCT empty bed contact time, EBCTSC (min) | 3.1354 | [6 empty] | SDS-CHCl3 | mg/L | BMRL | 3.2 | NA | 3.2 | NA |  | SDS-CHCl3 | mg/L | 31 | BMRL | 3.2 | 17.1 | 114.9565 | Avg-D12 | Average | --- | --- | --- | --- | 6.35 | 23 | 2.1485 | 0.028 | 1.3033 | 3.1 | 1.09 | 2.01 | 20 | 7.29 | 48 | 130 | BMRL | 3.6 | 15.5 | 110 | 129.1 | BMRL | BMRL | BMRL | 2.85 | 18 | 2.7 | 24 | 7.5 | 20.85 | 20.85 | 23.55 | Avg-D12 | Average | --- | --- | --- | --- | 6.21 | 23 | 0.793 | 0.009 | 1.1349 | 2.7 | 1.26 | 1.44 | 20 | 7.24 | 48 | 34 | BMRL | BMRL | 1.45 | 29 | 30.45 | BMRL | BMRL | BMRL | 1.45 | 5.95 | BMRL | 6.1 | BMRL | 1.1 | 7.4 | 7.4
|  |  |  | Estimated RSSCT run time, tSCT (days) | 32.9784 | [6 empty] | SDS-BDCM | mg/L | 4.7 | 15 | NA | 9.85 | 73.9411 |  | SDS-BDCM | mg/L | 16 | 4.7 | 15 | 11.9 | 52.5664 | RPD-D12 | RPD | --- | --- | --- | --- | 0 | 0 | 0.97743 | 0 | 0.97743 | 0 | 1.8349 | 0.99502 | 0 | NA | 0 | 7.6923 | #VALUE! | 11.1111 | 6.4516 | 0 | 0.46476 | #VALUE! | #VALUE! | #VALUE! | 17.5439 | 0 | 0 | 0 | 8 | 2.3981 | 2.3981 | 2.1231 | RPD-D12 | RPD | --- | --- | --- | --- | 0 | 0 | 0.50441 | 0 | 0.50441 | 0 | 0 | 0 | 0 | 0.82873 | 0 | 17.6471 | #VALUE! | #VALUE! | 6.8966 | 20.6897 | 19.376 | #VALUE! | #VALUE! | #VALUE! | 34.4828 | 15.1261 | #VALUE! | 3.2787 | #VALUE! | #VALUE! | 18.9189 | 18.9189
|  |  |  | RSSCT bed length, lSC (cm) | 9.6807 | [6 empty] | SDS-DBCM | mg/L | 21 | 68 | NA | 44.5 | 74.6832 |  | SDS-DBCM | mg/L | 5.7 | 21 | 68 | 31.5667 | 102.8501 | D14 | Primary | 1998-06-15 | 13:00 | 288 | 11022.5455 | 6.36 | 24 | 1.737 | 0.026 | 1.4968 | 3 | 0.97 | 2.03 | 20 | 7.3 | 48 | 145 | BMRL | 3 | 14 | 140 | 157 | BMRL | BMRL | BMRL | 4.1 | 24 | 2.6 | 17 | 4.3 | 2.4 | 28.1 | 30.7 | D13 | Primary | 1998-06-12 | 2:00 | 392 | 7501.4545 | 6.27 | 23 | 1.362 | 0.015 | 1.1013 | 2.9 | 1.45 | 1.45 | 20 | 7.36 | 48 | 88 | BMRL | 2.4 | 12 | 70 | 84.4 | BMRL | BMRL | BMRL | 2.8 | 15 | 2.7 | 15 | 4.6 | 4.6 | 17.8 | 20.5
|  |  |  | Estimated volume required for 20-minute EBCT, VSC (L) | 259.107 | [6 empty] | SDS-CHBr3 | mg/L | 260 | 150 | NA | 205 | 37.9423 |  | SDS-CHBr3 | mg/L | BMRL | 260 | 150 | 205 | 37.9423 | D-D14 | Duplicate | 1998-06-15 | 13:00 | 288 | 11022.5455 | 6.36 | 24 | 1.748 | 0.026 | 1.4874 | 3 | 0.97 | 2.03 | 20 | 7.28 | 48 | 150 | BMRL | 4.1 | 16 | 120 | 140.1 | BMRL | BMRL | BMRL | 3.7 | 22 | 3.2 | 17 | 6 | 2.9 | 25.7 | 28.9 | D-D13 | Duplicate | 1998-06-12 | 2:00 | 392 | 7501.4545 | 6.27 | 23 | 1.151 | 0.014 | 1.2163 | 2.9 | 1.45 | 1.45 | 20 | 7.3 | 48 | 86 | BMRL | 2.8 | 13 | 70 | 85.8 | BMRL | BMRL | BMRL | 2.7 | 14 | 2.5 | 14 | 4.4 | 1.8 | 16.7 | 19.2
|  |  |  | Mass GAC required, mSC (g) | 7.9206 | [6 empty] | SDS-THM4 | mg/L | 285.7 | 236.2 | 0 | 173.9667 | 87.7633 |  | SDS-THM4 | mg/L | 52.7 | 285.7 | 236.2 | 191.5333 | 64.0902 | Avg-D14 | Average | --- | --- | --- | --- | 6.36 | 24 | 1.7425 | 0.026 | 1.4921 | 3 | 0.97 | 2.03 | 20 | 7.29 | 48 | 147.5 | BMRL | 3.55 | 15 | 130 | 148.55 | BMRL | BMRL | BMRL | 3.9 | 23 | 2.9 | 17 | 5.15 | 2.65 | 26.9 | 29.8 | Avg-D13 | Average | --- | --- | --- | --- | 6.27 | 23 | 1.2565 | 0.0145 | 1.1588 | 2.9 | 1.45 | 1.45 | 20 | 7.33 | 48 | 87 | BMRL | 2.6 | 12.5 | 70 | 85.1 | BMRL | BMRL | BMRL | 2.75 | 14.5 | 2.6 | 14.5 | 4.5 | 3.2 | 17.25 | 19.85
[12 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | NA | NA | NA |  | SDS-MCAA* | mg/L | BMRL | BMRL | BMRL | BMRL | BMRL | RPD-D14 | RPD | --- | --- | --- | --- | 0 | 0 | 0.63128 | 0 | 0.63128 | 0 | 0 | 0 | 0 | 0.27435 | 0 | 3.3898 | #VALUE! | 30.9859 | 13.3333 | 15.3846 | 11.3766 | #VALUE! | #VALUE! | #VALUE! | 10.2564 | 8.6957 | 20.6897 | 0 | 33.0097 | 18.8679 | 8.9219 | 6.0403 | RPD-D13 | RPD | --- | --- | --- | --- | 0 | 0 | 16.7927 | 6.8966 | 9.9249 | 0 | 0 | 0 | 0 | 0.81855 | 0 | 2.2989 | #VALUE! | 15.3846 | 8 | 0 | 1.6451 | #VALUE! | #VALUE! | #VALUE! | 3.6364 | 6.8966 | 7.6923 | 6.8966 | 4.4444 | 87.5 | 6.3768 | 6.5491
[12 empty] | SDS-DCAA* | mg/L | 2 | 3.9 | NA | 2.95 | 45.5425 |  | SDS-DCAA* | mg/L | 10 | 2 | 3.9 | 5.3 | 78.8625 | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [6 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [13 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[12 empty] | SDS-TCAA* | mg/L | BMRL | 2.8 | NA | 2.8 | NA |  | SDS-TCAA* | mg/L | 9.7 | BMRL | 2.8 | 6.25 | 78.0646 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [6 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [13 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
[12 empty] | SDS-MBAA* | mg/L | 4.1 | 4.6 | NA | 4.35 | 8.1277 |  | SDS-MBAA* | mg/L | BMRL | 4.1 | 4.6 | 4.35 | 8.1277
[12 empty] | SDS-DBAA* | mg/L | 33 | 28 | NA | 30.5 | 11.5919 |  | SDS-DBAA* | mg/L | 1.1 | 33 | 28 | 20.7 | 82.8851
[12 empty] | SDS-BCAA* | mg/L | 3.8 | 11 | NA | 7.4 | 68.7996 |  | SDS-BCAA* | mg/L | 4.7 | 3.8 | 11 | 6.5 | 60.354
[12 empty] | SDS-TBAA | mg/L | 35 | NR | NA | 35 | NA |  | SDS-TBAA | mg/L | BMRL | 35 | NR | 35 | #DIV/0!
[12 empty] | SDS-CDBAA | mg/L | 9.8 | 15 | NA | 12.4 | 29.6529 |  | SDS-CDBAA | mg/L | BMRL | 9.8 | 15 | 12.4 | 29.6529
[12 empty] | SDS-DCBAA | mg/L | 4.9 | 4.4 | NA | 4.65 | 7.6033 |  | SDS-DCBAA | mg/L | 4.9 | 4.4 | 10 | 6.4333 | 48.1698
[12 empty] | SDS-HAA5 | mg/L | 39.1 | 39.3 | 0 | 26.1333 | 86.6034 |  | SDS-HAA5 | mg/L | 20.8 | 39.1 | 39.3 | 33.0667 | 32.1282
[12 empty] | SDS-HAA6 | mg/L | 42.9 | 50.3 | 0 | 31.0667 | 87.4176 |  | SDS-HAA6 | mg/L | 25.5 | 42.9 | 50.3 | 39.5667 | 32.1776
BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[12 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [6 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
*: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
Note on R5: 10MIN COLUMN BROKE AND HAD TO BE RESTARTED A WEEK INTO THE RUN
Note on S18: CDM: Empirical relations for predicting DBP formation indicate that an increase in bromide concentration will result in higher levels of DBP's with a shift in speciation towards a higher percentage of bromanated species.
Note on U21: CDM: Both the EBCT10 and EBCT20 minute columns used the same batch influent water. Three complete influent samples were take of the batch water (on May 26, June 3 and June 25). Samples for bromide analyses were taken on May 26 and June3. Approximately one week into the experimental run, the EBCT10 minutes column broke. A new EBCT10 minute column was started on June 3. The UNC laboratory did not adjust their planned influent sampling schedule to account for three complete influent samples for the new EBCT10 minute column.
Note on AA18: CDM: See Section 4 of the report for description of bromide contamination that led to variability in influent values.
Note on AB18: CDM: Empirical relations for predicting DBP formation indicate that an increase in bromide concentration will result in higher levels of DBP's with a shift in speciation towards a higher percentage of bromanated species.
Note on AO8: Parameswarc: UNC data, where are dupes?
Note on AR5: CDM: A calibration curve of UV254 absorbance versus chlorine dose to obtain a constant chlorine residual was produced and was used to try to maintain a constant chlorine residual.
Note on AU8: CDM: SDS Conditions: pH values are measured values Temperature values are the temperature of the fridgerator used for sample incubation.
Note on AX5: CDM: DO NOT USE THESE DBP VALUES, THE RESULTS ARE SKEWED DUE TO BROMIDE CONTAMINATION IN INFLUENT. PLEASE DIRECT QUESTIONS TO STEVE ALLGEIER
Note on CA5: CDM: A calibration curve of UV254 absorbance versus chlorine dose to obtain a constant chlorine residual was produced and was used to try to maintain a constant chlorine residual.
Note on CG5: CDM: DO NOT USE THESE DBP VALUES, THE RESULTS ARE SKEWED DUE TO BROMIDE CONTAMINATION IN INFLUENT. PLEASE DIRECT QUESTIONS TO STEVE ALLGEIER
Note on CH22: Parameswarc: Lab did not rec any THM bottles

## Sheet3. 3rd Quarter
FIELD-SET 3: 3rd QUARTER RSSCT RESULTS (FILE: ICR448.xls)
Field 3-1: PWS And Treatment Plant Data |  | Field 3-2: Full-Scale GAC Characteristics1 |  | Field 3-3: RSSCT Design Parameters |  |  |  | Field 3-4: Pretreatment Used Prior To GAC1 |  |  | Field 3-5: GAC Influent Water Quality For The 10-Minute EBCT Run | [7 empty] | Field 3-6: GAC Influent Water Quality For The 20-Minute EBCT Run1 | [6 empty] | Field 3-7: GAC Effluent Water Quality For The 10-Minute EBCT Run1 | [14 empty] | Field 3-7: GAC Effluent Water Quality For The 10-Minute EBCT Run (continued) | [9 empty] | Field 3-7: GAC Effluent Water Quality For The 10-Minute EBCT Run (continued) | [8 empty] | Field 3-8: GAC Effluent Water Quality For The 20-Minute EBCT Run1 | [13 empty] | Field 3-8: GAC Effluent Water Quality For The 20-Minute EBCT Run (continued) | [10 empty] | Field 3-8: GAC Effluent Water Quality For The 20-Minute EBCT Run (continued) | [8 empty] | Field 3-9: GAC Cost Parameters
|  |  |  | Input Design Parameters |  | US Standard Mesh Sizes | [19 empty] | Group C, 12 effluent samples per run | [33 empty] | Group C, 12 effluent samples per run
PWS Name | Public Works Commision of the City of Fayettville | Carbon manufacturer | Calgon Corp. | RSSCT influent TOC (mg/L) | 2.75 | US standard | Opening | Process | Description | Scale | 10-min. EBCT Start Date | 1998-08-25 | [6 empty] | 20-min. EBCT Start Date | 1998-08-25 | [5 empty] | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Cost Parameter | Parameter value
Public Water System Identification Number | NC 0326010 | Carbon trade name | Filtrasorb-400 | Inner diameter of the RSSCT column, DSC (mm) | 15 | mesh size | (mm) | Coagulation | 30 - 60 mg/L alum as Al2(SO4)3*14H2O | Full-Scale | 10-min. EBCT Start Time | 17:30 | [6 empty] | 20-min. EBCT Start Time | 17:30 | [5 empty] | ID | duplicated? | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorin. temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | Capital Recovery Interest Rate (%) | 5.3
Water Industry Data Base Number (optional) | 1244 | Carbon type | Bituminous | Minimum RSSCT Reynolds number, ReSC, min | 0.2 | 4 | 4.75 | Flocculation | 3-stage | Full-Scale | [16 empty] | Y/N | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | Capital Recovery Period (years) | 45
|  | Original GAC mesh size, upper (US standard mesh) | 12 | Full-scale operating temperature, ToC (oC) | 29.8 | 6 | 3.35 | Sedimentation | 3.1 hours conventional | Full-Scale | Group A, 2 samples per batch | [7 empty] | Group A, 2 samples per batch | [6 empty] | C1 | N | 1998-08-25 | 18:30 | 1 | 38.2727 | 7.53 | 20 | 0.258 | 0.007 | 2.7132 | 2.3 | 2 | 0.3 | 27 | 7.19 | 48 | BMRL | 1.5 | 1.6 | 1.2 | BMRL | 4.3 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | 1 | 0 | 0 | C1 | N | 1998-08-25 | 18:30 | 1 | 19.1364 | 7.4 | 20 | 0.235 | 0.007 | 2.9787 | 2.3 | 1.83 | 0.47 | 27 | 7.15 | 48 | BMRL | 2.2 | 2.8 | 2.2 | BMRL | 7.2 | BMRL | 1 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | 1.2 | 1 | 1 | Overhead & Profit Factor (% of construction costs) | 10
Official ICR Contact Person |  | Original GAC mesh size, lower (US standard mesh) | 40 | Full-scale bed porosity, eLC | 0.45 | 8 | 2.36 | Cartridge filtration | 1um exclusion size | Bench-scale | Parameter | Units | Sample A1-10 | Sample A2-10 | Average | RPD |  |  | Parameter | Units | Sample A1-20 | Sample A2-20 | Average | RPD |  | C2 | N | 1998-08-26 | 11:00 | 17.5 | 669.7727 | 7.2 | 20 | 0.386 | 0.006 | 1.5544 | 2.3 | 1.95 | 0.35 | 27 | 7.22 | 48 | BMRL | BMRL | 1 | 1 | BMRL | 2 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | 0 | C2 | N | 1998-08-26 | 11:00 | 17.5 | 334.8864 | 7.3 | 20 | 0.21 | 0.008 | 3.8095 | 2.3 | 1.7 | 0.6 | 27 | 7.22 | 48 | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | 0 | Special Sitework Factor (% of construction costs) | 5
Mailing Address |  | Original carbon particle diameter, dLC (mm) | 1.0525 | Measured RSSCT dry bed density, rSC (g/cm3) | 0.463 | 10 | 2 |  |  |  | Sampling date | MM/DD/YY | 1998-08-25 | 1998-09-02 | --- | --- |  |  | Sampling date | MM/DD/YY | 1998-08-25 | 1998-09-02 | --- | --- |  | C3 | N | 1998-08-27 | 12:00 | 42.5 | 1626.5909 | 7.2 | 20 | 0.349 | 0.009 | 2.5788 | 2.3 | 2.13 | 0.17 | 27 | 7.29 | 48 | BMRL | 1 | 1.3 | 1.3 | BMRL | 3.6 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | 0 | C3 | N | 1998-08-28 | 14:00 | 68.5 | 1310.8409 | 7.2 | 21 | 0.134 | 0.008 | 5.9701 | 2.2 | 2.04 | 0.16 | 27 | 7.41 | 48 | BMRL | 2.3 | 2.9 | 3.3 | 1.2 | 9.7 | BMRL | 1.3 | 1 | BMRL | BMRL | 1.3 | BMRL | BMRL | 1.4 | 2.3 | 3.6 | Construction Contingencies (% of construction costs) | 10
|  | 1: These are the characteristics before the carbon is ground for RSSCT experiments. |  | RSSCT GAC mesh size, upper (US standard mesh) | 80 | 12 | 1.68 |  |  |  | Sampling time | hh:mm | 17:30 | 10:00 | --- | --- |  |  | Sampling time | hh:mm | 17:30 | 10:00 | --- | --- |  | C4 | N | 1998-08-28 | 14:00 | 68.5 | 2621.6818 | 7.21 | 21 | 0.53 | 0.01 | 1.8868 | 2.3 | 1 | 1.3 | 27 | 7.33 | 48 | BMRL | NA | NA | NA | NA | 0 | BMRL | 1.1 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | 1.2 | 1.1 | 1.1 | C4 | N | 1998-08-29 | 9:00 | 87.5 | 1674.4318 | 7.31 | 21 | 0.243 | 0.008 | 3.2922 | 2.2 | 1.5 | 0.7 | 27 | 7.33 | 48 | BMRL | 1.4 | 2.4 | 2.8 | 1.4 | 8 | BMRL | BMRL | 1 | BMRL | BMRL | BMRL | BMRL | BMRL | 1.6 | 1 | 1 | Engineering Fee Factor (% of construction costs) | 10
Phone Number |  |  |  | RSSCT GAC mesh size, lower (US standard mesh) | 100 | 16 | 1.18 |  |  |  | Operation time | hh.hh | 0 | 184.5 | --- | --- |  |  | Operation time | hh.hh | 0 | 184.5 | --- | --- |  | C5 | N | 1998-08-29 | 9:00 | 87.5 | 3348.8636 | 7.23 | 21 | 0.514 | 0.006 | 1.1673 | 2.1 | 1.92 | 0.18 | 27 | 7.25 | 48 | BMRL | 1.3 | 2.2 | 3.2 | 1.7 | 8.4 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | 1.5 | 0 | 0 | Avg-C5 | Y | 1998-08-31 | 10:00 | 136.5 | 2612.1136 | 7.25 | 21 | 0.37 | 0.006 | 1.6216 | 2.1 | 1.355 | 0.745 | 27 | 7.29 | 48 | BMRL | 1.35 | 2.15 | 3.1 | 1.65 | 8.25 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | 1.6 | 0 | 0 | 1998 ENR Construction Cost Index (CCI base year 1913) | 77.8
FAX Number | [5 empty] | 20 | 0.85 |  |  |  | Bed volumes | (10 minutes) | 0 | 98.9993 | --- | --- |  |  | Bed volumes | (20 minutes) | 0 | 49.4996 | --- | --- |  | Avg-C6 | Y | 1998-08-31 | 10:00 | 136.5 | 5224.2273 | 7.125 | 20 | 0.5005 | 0.008 | 1.5984 | 2.2 | 1.365 | 0.835 | 27 | 7.29 | 48 | 31 | 2.7 | 5.65 | 8.4 | 3.6 | 20.35 | BMRL | 1.4 | 1.1 | BMRL | 2.15 | 2.25 | BMRL | 3.05 | 2.7 | 4.65 | 6.9 | C6 | N | 1998-09-01 | 13:00 | 163.5 | 3128.7955 | 7.2 | 21 | 0.382 | BMRL | BMRL | 2.1 | 1.31 | 0.79 | 27 | 7.25 | 48 | BMRL | 1.7 | 2.5 | 3 | 1.4 | 8.6 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | 1.5 | 0 | 0 | 1998 Producers Price Index (PPI base year 1982 = 100) | 131.3
E-Mail Address (optional) |  |  |  | Estimated Run Length |  | 30 | 0.6 |  |  |  | Alkalinity | mg/L as CaCO3 | 13.2 | 13.9 | 13.55 | 5.1661 |  |  | Alkalinity | mg/L as CaCO3 | 13.2 | 13.9 | 13.55 | 5.1661 |  | C7 | N | 1998-09-01 | 13:00 | 163.5 | 6257.5909 | 7.14 | 20 | 0.731 | 0.01 | 1.368 | 2.3 | 1.33 | 0.97 | 27 | 7.33 | 48 | 43 | 4.5 | 9.4 | 14 | 6.5 | 34.4 | BMRL | 1.8 | 1.4 | BMRL | 3.6 | 3.1 | BMRL | 4 | 3.6 | 6.8 | 9.9 | C7 | N | 1998-09-02 | 9:00 | 183.5 | 3511.5227 | 7.13 | 21 | 0.188 | 0.005 | 2.6596 | 2.1 | 1.3 | 0.8 | 27 | 7.35 | 48 | BMRL | 1.9 | 2.8 | 3.2 | 1.7 | 9.6 | BMRL | BMRL | 1 | BMRL | BMRL | BMRL | BMRL | BMRL | 1.7 | 1 | 1 | Labor Rate + Fringe ($/work-hour) | 21
|  |  |  | Bed volumes to 50% TOC breakthrough, BV50 | 5825.4199 | 40 | 0.425 |  |  |  | Total hardness | mg/L as CaCO3 | 24.4 | 24.4 | 24.4 | 0 |  |  | Total hardness | mg/L as CaCO3 | 24.4 | 24.4 | 24.4 | 0 |  | C8 | N | 1998-09-02 | 9:00 | 183.5 | 7023.0455 | 7.2 | 21 | 0.986 | 0.015 | 1.5213 | 2.8 | 1.22 | 1.58 | 27 | 7.41 | 48 | 57 | 7.5 | 13 | 17 | 5.6 | 43.1 | BMRL | 3 | 2.4 | 1 | 3.8 | 4.7 | BMRL | 5.2 | 5.5 | 10.2 | 14.9 | C8 | N | 1998-09-03 | 15:00 | 213.5 | 4085.6136 | 7.09 | 20 | 0.832 | 0.006 | 0.72115 | 2 | 1.33 | 0.67 | 27 | 7.27 | 48 | BMRL | 1.6 | 2.5 | 3 | 1.7 | 8.8 | BMRL | BMRL | 1 | BMRL | 1 | 1.1 | BMRL | BMRL | 1.3 | 2 | 3.1 | Labor Overhead Factor (% of labor) | 4.1
Technical ICR Contact Person |  |  |  | Estimated run length, BVT ( = 2 x BV50) | 11650.8397 | 50 | 0.3 |  |  |  | Calcium hardness | mg/L as CaCO3 | 13.1 | 13.2 | 13.15 | 0.76046 |  |  | Calcium hardness | mg/L as CaCO3 | 13.1 | 13.2 | 13.15 | 0.76046 |  | C9 | N | 1998-09-03 | 15:00 | 213.5 | 8171.2273 | 7.17 | 21 | 1.281 | 0.015 | 1.171 | 2.4 | 1.53 | 0.87 | 27 | 7.3 | 48 | 75 | 8.5 | 15 | 19 | 5.4 | 47.9 | BMRL | 3.3 | 2.5 | BMRL | 4.2 | 5 | BMRL | 4.4 | 5 | 10 | 15 | Avg-C9 | Y | 1998-09-04 | 11:00 | 233.5 | 4468.3409 | 7.05 | 20 | 0.55 | 0.006 | 1.0909 | 2 | 1.12 | 0.88 | 27 | 7.22 | 48 | BMRL | 1.7 | 2.6 | 3.55 | 2.05 | 9.9 | BMRL | 1.1 | 1.05 | BMRL | 1.35 | 1.35 | BMRL | BMRL | 1.25 | 3.5 | 4.85 | Electric Rate ($/kW-h) | 0.035
Mailing Address |  |  |  | BVT + 30% safety factor, BVT+30% ( = 2.6 x BV50) | 15146.0916 | 60 | 0.25 |  |  |  | Ammonia | mg NH3-N / L | 0.03 | 0.02 | 0.025 | 40 |  |  | Ammonia | mg NH3-N / L | 0.03 | 0.02 | 0.025 | 40 |  | Avg-C10 | Y | 1998-09-04 | 11:00 | 233.5 | 8936.6818 | 7.14 | 20 | 1.323 | 0.016 | 1.2094 | 2.4 | 1.085 | 1.315 | 27 | 7.26 | 48 | 100 | 8.5 | 14.5 | 17.5 | 4.7 | 45.2 | BMRL | 4 | 3.2 | 1 | 4.2 | 5.85 | BMRL | 5.1 | 6.15 | 12.4 | 18.25 | C10 | N | 1998-09-05 | 13:00 | 259.5 | 4965.8864 | 7.06 | 21 | 0.279 | 0.006 | 2.1505 | 2 | 1.25 | 0.75 | 27 | 7.2 | 48 | BMRL | BMRL | 1.6 | 2.1 | 1.1 | 4.8 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | 1.1 | 0 | 0 | Fuel Oil Rate ($/gal) | 0.55
[6 empty] | 70 | 0.21 |  |  |  | Bromide | mg/L | 90 | 92 | 91 | 2.1978 |  |  | Bromide | mg/L | 90 | 92 | 91 | 2.1978 |  | C11 | N | 1998-09-05 | 13:00 | 259.5 | 9931.7727 | 7.2 | 20 | 0.828 | 0.016 | 1.9324 | 2.4 | 1.08 | 1.32 | 27 | 7.44 | 48 | 98 | 8.7 | 15 | 18 | 4.9 | 46.6 | BMRL | 4.6 | 3.6 | 1 | 4.4 | 6.1 | BMRL | 5.3 | 6.8 | 13.6 | 19.7 | C11 | N | 1998-09-07 | 22:00 | 316.5 | 6056.6591 | 6.8 | 21 | 0.759 | 0.006 | 0.79051 | 2 | 0.96 | 1.04 | 27 | 7.19 | 48 | 26 | 1.8 | 3.2 | 4.6 | 2.7 | 12.3 | BMRL | 1.3 | 1.4 | BMRL | 1.5 | 1.7 | BMRL | BMRL | 1.4 | 4.2 | 5.9 | Natural Gas Rate ($/ft3) | 0.007
Phone Number |  |  |  | General RSSCT Design Parameters |  | 80 | 0.18 | [18 empty] | C12 | N | 1998-09-07 | 22:00 | 316.5 | 12113.3182 | 7.16 | 20 | 1.04 | 0.022 | 2.1154 | 2.6 | 1.24 | 1.36 | 27 | 7.23 | 48 | 130 | 13 | 18 | 18 | 3.8 | 52.8 | BMRL | 6.1 | 5 | 1.2 | 4.2 | 7.2 | BMRL | 4.2 | 6.7 | 16.5 | 23.7 | C12 | N | 1998-09-08 | 11:30 | 330 | 6315 | 6.97 | 21 | 0.942 | 0.011 | 1.1677 | 2.3 | 1.21 | 1.09 | 27 | 7.33 | 48 | 26 | 1.2 | 2.4 | 4.4 | 1.2 | 9.2 | BMRL | 1.2 | BMRL | BMRL | 1.8 | 1.4 | BMRL | BMRL | 1.1 | 3 | 4.4 | Current Process Water Rate ($/1000 gal) | 0.35
FAX Number |  |  |  | Kinematic viscosity at ToC, nLC (m2/s) | 8.1427e-07 | 100 | 0.15 |  |  |  | Group B, 3 samples per batch | [7 empty] | Group B, 3 samples per batch | [6 empty] | C13 | N | 1998-09-08 | 11:30 | 330 | 12630 | 7.14 | 21 | 1.642 | 0.025 | 1.5225 | 2.7 | 0.82 | 1.88 | 27 | 7.32 | 48 | 115 | 13 | 17 | 18 | 4.7 | 52.7 | BMRL | 6.2 | 4.9 | BMRL | 5.4 | 7.5 | NR | 3.5 | 5.7 | 16.5 | 24 | C13 | N | 1998-09-13 | 13:00 | 451.5 | 8640.0682 | 7.03 | 21 | 0.998 | 0.008 | 0.8016 | 2.2 | 1.21 | 0.99 | 27 | 7.33 | 48 | 49 | 2.6 | 6.4 | 11 | 5.1 | 25.1 | BMRL | 1.7 | 1.2 | BMRL | 2.9 | 2.9 | BMRL | 2.7 | 2.3 | 5.8 | 8.7 | Modifications to Existing Plant (% of construction costs) | 20
E-Mail Address (optional) |  |  |  | RSSCT carbon particle diameter, dSC (mm) | 0.165 | 120 | 0.125 |  |  |  | Parameter | Units | Sample B1-10 | Sample B2-10 | Sample B3-10 | Average | %SD |  | Parameter | Units | Sample B1-10 | Sample B2-10 | Sample B3-10 | Average | %SD | C17 | N | 1998-09-13 | 13:00 | 451.5 | 17280.1364 | 7.13 | 21 | 1.938 | 0.031 | 1.5996 | 2.8 | 0.91 | 1.89 | 27 | 7.26 | 48 | 145 | 21 | 24 | 20 | 3.3 | 68.3 | BMRL | 8.1 | 7 | 1.3 | 4 | 8 | NR | 5.3 | 9.4 | 20.4 | 28.4 | C17 | N | 1998-09-14 | 12:00 | 474.5 | 9080.2045 | 6.89 | 21 | 0.884 | 0.012 | 1.3575 | 2.3 | 1.14 | 1.16 | 27 | 7.28 | 48 | NA | 3.6 | 8.1 | 12 | 5.2 | 28.9 | BMRL | 2.2 | 1.5 | BMRL | 3.6 | 4.4 | BMRL | 2.9 | 3.2 | 7.3 | 11.7
|  |  |  | Scaling factor, SF | 6.3788 | 140 | 0.106 | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | Sampling date | MM/DD/YY | 1998-08-25 | 1998-09-02 | 1998-09-17 | --- | --- |  | Sampling date | MM/DD/YY | 1998-08-25 | 1998-09-02 | 1998-09-17 | --- | --- | C18 | N | 1998-09-14 | 12:00 | 474.5 | 18160.4091 | 7.07 | 22 | 2.024 | 0.034 | 1.5316 | 2.8 | 0.75 | 2.05 | 27 | 7.26 | 48 | 170 | 23 | 23 | 19 | 3.4 | 68.4 | BMRL | 9.9 | 8.8 | BMRL | 4.8 | 9.6 | BMRL | 4.2 | 9.2 | 23.5 | 33.1 | Avg-C18 | Y | 1998-09-15 | 12:00 | 498.5 | 9539.4773 | 6.87 | 22 | 1.0125 | 0.015 | 1.4815 | 2.4 | 1.06 | 1.34 | 27 | 7.29 | 48 | 56.5 | 4.2 | 9.6 | 14.5 | 5.65 | 33.95 | BMRL | 2.95 | 1.8 | BMRL | 5 | 4.1 | BMRL | 2.2 | 2.1 | 9.75 | 13.85
Plant Name | P.O. Hoffer Water Treatment Plant |  |  | RSSCT hydraulic loading rate, vSC (m/hr) | 1.5989 | 170 | 0.088 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | Sampling time | hh:mm | 17:30 | 10:00 | 14:00 | --- | --- |  | Sampling time | hh:mm | 17:30 | 10:00 | 14:00 | --- | --- | Avg-C19 | Y | 1998-09-15 | 12:00 | 498.5 | 19078.9545 | 6.955 | 22 | 2.0365 | 0.034 | 1.6695 | 3.2 | 0.78 | 2.42 | 27 | 7.285 | 48 | 165 | 23.5 | 24.5 | 19.5 | 2.9 | 70.4 | BMRL | 10.5 | 7.95 | BMRL | 3.75 | 8.05 | BMRL | 3.05 | 7.6 | 22.2 | 30.25 | C19 | N | 1998-09-28 | 11:00 | 809.5 | 15490.8864 | 6.9 | 22 | 2.6 | 0.023 | 0.88462 | 2.9 | 0.79 | 2.11 | 27 | 7.23 | 48 | 145 | 20 | 24 | 20 | 3.4 | 67.4 | BMRL | 8.4 | 7.3 | BMRL | 3.9 | 8.6 | NR | NR | 9.8 | 19.6 | 28.2
Treatment Plant Category | CONV |  |  | RSSCT flow rate, QSC (mL/min) | 4.7093 | 200 | 0.075 | is to list the pretreatment processes used in this particular RSSCT run. |  |  | Operation time | hh.hh | 0 | 184.5 | 548.5 | --- | --- |  | Operation time | hh.hh | 0 | 184.5 | 548.5 | --- | ---
Process Train Name | Conventional train |  |  | Estimated total influent volume required, VSCT (L) | 335.457 | 230 | 0.062 |  |  |  | Bed volumes | (10 minute) | 0 | 98.9993 | 294.3149 | --- | --- |  | Bed volumes | (20 minute) | 0 | 49.4996 | 147.1574 | --- | --- | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [13 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [10 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
ICR Treatment Plant Identification Number | 448 |  |  |  |  | 270 | 0.053 |  |  |  | pH | --- | 6.85 | 6.98 | 6.8 | 6.8767 | 1.3512 |  | pH | --- | 6.85 | 6.98 | 6.8 | 6.8767 | 1.3512 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [13 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [10 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
PWSID Number of Plant (if assigned) | NC 0326010 |  |  | 10-Minute EBCT Run |  | 325 | 0.044 |  |  |  | Turbidity | ntu | 0.15 | 0.26 | 0.38 | 0.26333 | 43.6846 |  | Turbidity | ntu | 0.15 | 0.26 | 0.38 | 0.26333 | 43.6846 | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for | [14 empty] | measured. the primary and duplicate analyses below. | [9 empty] | the primary and duplicate analyses below. | [8 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below.
Historical Minimum Water Temperature (oC) | 4 |  |  | Full-scale empty bed contact time, EBCTLC (min) | 10 | 400 | 0.037 |  |  |  | Temperature | oC | 20 | 21 | 20 | 20.3333 | 2.8394 |  | Temperature | oC | 20 | 21 | 20 | 20.3333 | 2.8394
Historical Average Water Temperature (oC) | 34 |  |  | Estimated full-scale run time, tLCT (days) | 105.1812 | [5 empty] | Total organic carbon | mg/L | 2.806 | 2.836 | 2.983 | 2.875 | 3.2948 |  | Total organic carbon | mg/L | 2.806 | 2.836 | 2.983 | 2.875 | 3.2948 | Group D, 3 duplicate effluent samples per run (results from primary and duplicate analyses) | [33 empty] | Group D, 3 duplicate effluent samples per run (results from primary and duplicate analyses)
State Approved Plant Capacity (MGD) | 32 |  |  | RSSCT empty bed contact time, EBCTSC (min) | 1.5677 | [5 empty] | UV254 | cm-1 | 0.052 | 0.057 | 0.058 | 0.055667 | 5.7746 |  | UV254 | cm-1 | 0.052 | 0.057 | 0.058 | 0.055667 | 5.7746 | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS
|  |  |  | Estimated RSSCT run time, tSCT (days) | 16.4892 | [5 empty] | SUVA | L/(mg*m) | 1.8532 | 2.0099 | 1.9444 | 1.9358 | 4.0655 |  | SUVA | L/(mg*m) | 1.8532 | 2.0099 | 1.9444 | 1.9358 | 4.0655 | ID | Type | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6
|  |  |  | RSSCT bed length, lSC (cm) | 4.1778 | [5 empty] | SDS-Cl2 dose | mg/L | 4.4 | 3.9 | 3.9 | 4.0667 | 7.0986 |  | SDS-Cl2 dose | mg/L | 4.4 | 3.9 | 3.9 | 4.0667 | 7.0986 |  |  | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L
|  |  |  | Estimated volume required for 10-minute EBCT, VSC (L) | 111.819 | [5 empty] | SDS-Free Cl2 residual | mg/L | 1.33 | 0.81 | 0.7 | 0.94667 | 35.5459 |  | SDS-Free Cl2 residual | mg/L | 1.33 | 0.81 | 0.7 | 0.94667 | 35.5459 | C6 | Primary | 1998-08-31 | 10:00 | 136.5 | 73.2434 | 7.1 | 20 | 0.498 | 0.008 | 1.6064 | 2.2 | 1.37 | 0.83 | 27 | 7.3 | 48 | 31 | 2.8 | 5.8 | 8.1 | 3.1 | 19.8 | BMRL | 1.4 | 1.1 | BMRL | 2 | 2.2 | BMRL | 3 | 2.7 | 4.5 | 6.7 | C5 | Primary | 1998-08-31 | 10:00 | 136.5 | 36.6217 | 7.25 | 21 | 0.39 | 0.006 | 1.5385 | 2.1 | 1.45 | 0.65 | 27 | 7.28 | 48 | BMRL | 1.3 | 2.1 | 2.7 | 1.2 | 7.3 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | 1.6 | 0 | 0
|  |  |  | Mass GAC required, mSC (g) | 3.4182 | [5 empty] | SDS-Cl2 demand | mg/L | 3.07 | 3.09 | 3.2 | 3.12 | 2.2436 |  | SDS-Cl2 demand | mg/L | 3.07 | 3.09 | 3.2 | 3.12 | 2.2436 | D-C6 | Duplicate | 1998-08-31 | 10:00 | 136.5 | 73.2434 | 7.15 | 20 | 0.503 | 0.008 | 1.5905 | 2.2 | 1.36 | 0.84 | 27 | 7.28 | 48 | BMRL | 2.6 | 5.5 | 8.7 | 4.1 | 20.9 | BMRL | 1.4 | 1.1 | BMRL | 2.3 | 2.3 | BMRL | 3.1 | 2.7 | 4.8 | 7.1 | D-C5 | Duplicate | 1998-08-31 | 10:00 | 136.5 | 36.6217 | 7.15 | 20 | 0.35 | 0.006 | 1.7143 | 2.1 | 1.26 | 0.84 | 27 | 7.29 | 48 | BMRL | 1.4 | 2.2 | 3.5 | 2.1 | 9.2 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | 1.6 | 0 | 0
[11 empty] | SDS-Chlorination temp. | oC | 27 | 27 | 27 | 27 | 0 |  | SDS-Chlorination temp. | oC | 27 | 27 | 27 | 27 | 0 | Avg-C6 | Average | --- | --- | --- | --- | 7.125 | 20 | 0.5005 | 0.008 | 1.5984 | 2.2 | 1.365 | 0.835 | 27 | 7.29 | 48 | 31 | 2.7 | 5.65 | 8.4 | 3.6 | 20.35 | BMRL | 1.4 | 1.1 | BMRL | 2.15 | 2.25 | BMRL | 3.05 | 2.7 | 4.65 | 6.9 | Avg-C5 | Average | --- | --- | --- | --- | 7.2 | 20.5 | 0.37 | 0.006 | 1.6264 | 2.1 | 1.355 | 0.745 | 27 | 7.285 | 48 | BMRL | 1.35 | 2.15 | 3.1 | 1.65 | 8.25 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | 1.6 | 0 | 0
|  |  |  | 20-Minute EBCT Run | [6 empty] | SDS-Chlorination pH | --- | 7.33 | 7.25 | 7.37 | 7.3167 | 0.83509 |  | SDS-Chlorination pH | --- | 7.33 | 7.25 | 7.37 | 7.3167 | 0.83509 | RPD-C6 | RPD | --- | --- | --- | --- | 0.70175 | 0 | 0.999 | 0 | 0.999 | 0 | 0.7326 | 1.1976 | 0 | 0.27435 | 0 | #VALUE! | 7.4074 | 5.3097 | 7.1429 | 27.7778 | 5.4054 | #VALUE! | 0 | 0 | #VALUE! | 13.9535 | 4.4444 | #VALUE! | 3.2787 | 0 | 6.4516 | 5.7971 | RPD-C5 | RPD | --- | --- | --- | --- | 1.3889 | 4.878 | 10.8108 | 0 | 10.8108 | 0 | 14.0221 | 25.5034 | 0 | 0.13727 | 0 | #VALUE! | 7.4074 | 4.6512 | 25.8065 | 54.5455 | 23.0303 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | #DIV/0! | #DIV/0!
|  |  |  | Full-scale empty bed contact time, EBCTLC (min) | 20 | [5 empty] | SDS-Incubation time | hours | 48 | 48 | 48 | 48 | 0 |  | SDS-Incubation time | hours | 48 | 48 | 48 | 48 | 0 | C10 | Primary | 1998-09-04 | 11:00 | 233.5 | 125.2917 | 7.13 | 20 | 1.329 | 0.016 | 1.2039 | 2.4 | 1.14 | 1.26 | 27 | 7.27 | 48 | 90 | 9 | 15 | 17 | 4.7 | 45.7 | BMRL | 4 | 3.2 | BMRL | 4.3 | 5.9 | BMRL | 5.3 | 6.3 | 11.5 | 17.4 | C9 | Primary | 1998-09-04 | 11:00 | 233.5 | 62.6459 | 7.05 | 20 | 0.551 | 0.006 | 1.0889 | 2 | 1.12 | 0.88 | 27 | 7.29 | 48 | BMRL | 1.9 | 2.7 | 3.5 | 1.9 | 10 | BMRL | 1 | 1 | BMRL | 1.3 | 1.3 | BMRL | BMRL | 1.2 | 3.3 | 4.6
|  |  |  | Estimated full-scale run time, tLCT (days) | 210.3624 | [5 empty] | SDS-TOX | mg Cl- /L | 305 | 260 | 280 | 281.6667 | 8.0046 |  | SDS-TOX | mg Cl- /L | 305 | 260 | 280 | 281.6667 | 8.0046 | D-C10 | Duplicate | 1998-09-04 | 11:00 | 233.5 | 125.2917 | 7.15 | 20 | 1.317 | 0.016 | 1.2149 | 2.4 | 1.03 | 1.37 | 27 | 7.25 | 48 | 110 | 8 | 14 | 18 | 4.7 | 44.7 | BMRL | 4 | 3.2 | 1 | 4.1 | 5.8 | BMRL | 4.9 | 6 | 12.3 | 18.1 | D-C9 | Duplicate | 1998-09-04 | 11:00 | 233.5 | 62.6459 | 7.1 | 20 | 0.549 | 0.006 | 1.0929 | 2 | 1.12 | 0.88 | 27 | 7.3 | 48 | BMRL | 1.5 | 2.5 | 3.6 | 2.2 | 9.8 | BMRL | 1.2 | 1.1 | BMRL | 1.4 | 1.4 | BMRL | BMRL | 1.3 | 3.7 | 5.1
|  |  |  | RSSCT empty bed contact time, EBCTSC (min) | 3.1354 | [5 empty] | SDS-CHCl3 | mg/L | 65 | 60 | 52 | 59 | 11.1143 |  | SDS-CHCl3 | mg/L | 65 | 60 | 52 | 59 | 11.1143 | Avg-C10 | Average | --- | --- | --- | --- | 7.14 | 20 | 1.323 | 0.016 | 1.2094 | 2.4 | 1.085 | 1.315 | 27 | 7.26 | 48 | 100 | 8.5 | 14.5 | 17.5 | 4.7 | 45.2 | BMRL | 4 | 3.2 | 1 | 4.2 | 5.85 | BMRL | 5.1 | 6.15 | 12.4 | 18.25 | Avg-C9 | Average | --- | --- | --- | --- | 7.075 | 20 | 0.55 | 0.006 | 1.0909 | 2 | 1.12 | 0.88 | 27 | 7.295 | 48 | BMRL | 1.7 | 2.6 | 3.55 | 2.05 | 9.9 | BMRL | 1.1 | 1.05 | BMRL | 1.35 | 1.35 | BMRL | BMRL | 1.25 | 3.5 | 4.85
|  |  |  | Estimated RSSCT run time, tSCT (days) | 32.9784 | [5 empty] | SDS-BDCM | mg/L | 33 | 37 | 32 | 34 | 7.7816 |  | SDS-BDCM | mg/L | 33 | 37 | 32 | 34 | 7.7816 | RPD-C10 | RPD | --- | --- | --- | --- | 0.28011 | 0 | 0.90703 | 0 | 0.90703 | 0 | 10.1382 | 8.365 | 0 | 0.27548 | 0 | 20 | 11.7647 | 6.8966 | 5.7143 | 0 | 2.2124 | #VALUE! | 0 | 0 | #VALUE! | 4.7619 | 1.7094 | #VALUE! | 7.8431 | 4.878 | 6.4516 | 3.8356 | RPD-C9 | RPD | --- | --- | --- | --- | 0.70671 | 0 | 0.36364 | 0 | 0.36364 | 0 | 0 | 0 | 0 | 0.13708 | 0 | #VALUE! | 23.5294 | 7.6923 | 2.8169 | 14.6341 | 2.0202 | #VALUE! | 18.1818 | 9.5238 | #VALUE! | 7.4074 | 7.4074 | #VALUE! | #VALUE! | 8 | 11.4286 | 10.3093
|  |  |  | RSSCT bed length, lSC (cm) | 8.3555 | [5 empty] | SDS-DBCM | mg/L | 16 | 17 | 15 | 16 | 6.25 |  | SDS-DBCM | mg/L | 16 | 17 | 15 | 16 | 6.25 | C19 | Primary | 1998-09-15 | 11:00 | 497.5 | 266.9492 | 6.95 | 22 | 2.034 | 0.034 | 1.6716 | 3.2 | 0.7 | 2.5 | 27 | 7.29 | 48 | 165 | 23 | 25 | 20 | 2.9 | 70.9 | BMRL | 10 | 7.7 | BMRL | 3.6 | 7.8 | BMRL | 3 | 7.3 | 21.3 | 29.1 | C18 | Primary | 1998-09-15 | 12:00 | 498.5 | 133.7429 | 6.87 | 22 | 1.015 | 0.015 | 1.4778 | 2.4 | 1.06 | 1.34 | 27 | 7.28 | 48 | 58 | 4.3 | 9.8 | 15 | 5.7 | 34.8 | BMRL | 3 | 1.7 | BMRL | 4.1 | 3.9 | BMRL | 2.2 | 2.6 | 8.8 | 12.7
|  |  |  | Estimated volume required for 20-minute EBCT, VSC (L) | 223.638 | [5 empty] | SDS-CHBr3 | mg/L | 1.3 | 1.6 | 1.2 | 1.3667 | 15.2317 |  | SDS-CHBr3 | mg/L | 1.3 | 1.6 | 1.2 | 1.3667 | 15.2317 | D-C19 | Duplicate | 1998-09-15 | 11:00 | 497.5 | 266.9492 | 6.96 | 22 | 2.039 | 0.034 | 1.6675 | 3.2 | 0.86 | 2.34 | 27 | 7.28 | 48 | 165 | 24 | 24 | 19 | 2.9 | 69.9 | BMRL | 11 | 8.2 | BMRL | 3.9 | 8.3 | BMRL | 3.1 | 7.9 | 23.1 | 31.4 | D-C18 | Duplicate | 1998-09-15 | 12:00 | 498.5 | 133.7429 | 6.91 | 22 | 1.01 | 0.015 | 1.4851 | 2.4 | 1.04 | 1.36 | 27 | 7.27 | 48 | 55 | 4.1 | 9.4 | 14 | 5.6 | 33.1 | BMRL | 2.9 | 1.9 | BMRL | 5.9 | 4.3 | BMRL | BMRL | 1.6 | 10.7 | 15
|  |  |  | Mass GAC required, mSC (g) | 6.8364 | [5 empty] | SDS-THM4 | mg/L | 115.3 | 115.6 | 100.2 | 110.3667 | 7.9787 |  | SDS-THM4 | mg/L | 115.3 | 115.6 | 100.2 | 110.3667 | 7.9787 | Avg-C19 | Average | --- | --- | --- | --- | 6.955 | 22 | 2.0365 | 0.034 | 1.6695 | 3.2 | 0.78 | 2.42 | 27 | 7.285 | 48 | 165 | 23.5 | 24.5 | 19.5 | 2.9 | 70.4 | BMRL | 10.5 | 7.95 | BMRL | 3.75 | 8.05 | BMRL | 3.05 | 7.6 | 22.2 | 30.25 | Avg-C18 | Average | --- | --- | --- | --- | 6.89 | 22 | 1.0125 | 0.015 | 1.4815 | 2.4 | 1.05 | 1.35 | 27 | 7.275 | 48 | 56.5 | 4.2 | 9.6 | 14.5 | 5.65 | 33.95 | BMRL | 2.95 | 1.8 | BMRL | 5 | 4.1 | BMRL | 2.2 | 2.1 | 9.75 | 13.85
[11 empty] | SDS-MCAA* | mg/L | 2.1 | 3.1 | BMRL | 2.6 | 27.1964 |  | SDS-MCAA* | mg/L | 2.1 | 3.1 | BMRL | 2.6 | 27.1964 | RPD-C19 | RPD | --- | --- | --- | --- | 0.14378 | 0 | 0.24552 | 0 | 0.24552 | 0 | 20.5128 | 6.6116 | 0 | 0.13727 | 0 | 0 | 4.2553 | 4.0816 | 5.1282 | 0 | 1.4205 | #VALUE! | 9.5238 | 6.2893 | #VALUE! | 8 | 6.2112 | #VALUE! | 3.2787 | 7.8947 | 8.1081 | 7.6033 | RPD-C18 | RPD | --- | --- | --- | --- | 0.58055 | 0 | 0.49383 | 0 | 0.49383 | 0 | 1.9048 | 1.4815 | 0 | 0.13746 | 0 | 5.3097 | 4.7619 | 4.1667 | 6.8966 | 1.7699 | 5.0074 | #VALUE! | 3.3898 | 11.1111 | #VALUE! | 36 | 9.7561 | #VALUE! | #VALUE! | 47.619 | 19.4872 | 16.6065
[11 empty] | SDS-DCAA* | mg/L | 23 | 19 | 20 | 20.6667 | 10.0726 |  | SDS-DCAA* | mg/L | 23 | 19 | 20 | 20.6667 | 10.0726 | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [13 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [10 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[11 empty] | SDS-TCAA* | mg/L | 27 | 19 | 25 | 23 | 34.7826 |  | SDS-TCAA* | mg/L | 27 | 19 | 25 | 23.6667 | 17.5915 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [13 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [10 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
[11 empty] | SDS-MBAA* | mg/L | 1.3 | 1.1 | 1 | 1.1333 | 13.4782 |  | SDS-MBAA* | mg/L | 1.3 | 1.1 | 1 | 1.1333 | 13.4782
[11 empty] | SDS-DBAA* | mg/L | 3.2 | 3 | 2.6 | 2.9333 | 10.4149 |  | SDS-DBAA* | mg/L | 3.2 | 3 | 2.6 | 2.9333 | 10.4149
[11 empty] | SDS-BCAA* | mg/L | 12 | 10 | 11 | 11 | 9.0909 |  | SDS-BCAA* | mg/L | 12 | 10 | 11 | 11 | 9.0909
[11 empty] | SDS-TBAA | mg/L | BMRL | BMRL | NR | NR | NR |  | SDS-TBAA | mg/L | BMRL | BMRL | NR | NR | NR
[11 empty] | SDS-CDBAA | mg/L | 5.7 | 5.7 | NR | 5.7 | 0 |  | SDS-CDBAA | mg/L | 5.7 | 5.7 | NR | 5.7 | 0
[11 empty] | SDS-DCBAA | mg/L | 21 | 16 | 21 | 19.3333 | 14.9315 |  | SDS-DCBAA | mg/L | 21 | 16 | 21 | 19.3333 | 14.9315
[11 empty] | SDS-HAA5 | mg/L | 56.6 | 45.2 | 48.6 | 50.1333 | 11.6741 |  | SDS-HAA5 | mg/L | 56.6 | 45.2 | 48.6 | 50.1333 | 11.6741
[11 empty] | SDS-HAA6 | mg/L | 68.6 | 55.2 | 59.6 | 61.1333 | 11.1728 |  | SDS-HAA6 | mg/L | 68.6 | 55.2 | 59.6 | 61.1333 | 11.1728
[11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [7 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [6 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
Note on AO18: CDM: No explanation was founnd for the observed dip in TOC values here.
Note on AU8: CDM: SDS Conditions: pH values are measured values Temperature values are the temperature of the fridgerator used for sample incubation.
Note on AY11: Parameswarc: THM vials broken in transit
Note on CG21: Parameswarc: Both vials broken

## Sheet4. 4th Quarter
FIELD-SET 4: 4th QUARTER RSSCT RESULTS (FILE: ICR448.xls)
Field 4-1: PWS And Treatment Plant Data |  | Field 4-2: Full-Scale GAC Characteristics1 |  | Field 4-3: RSSCT Design Parameters |  |  |  | Field 4-4: Pretreatment Used Prior To GAC1 |  |  |  | Field 4-5: GAC Influent Water Quality For The 10-Minute EBCT Run | [7 empty] | Field 4-6: GAC Influent Water Quality For The 20-Minute EBCT Run1 | [6 empty] | Field 4-7: GAC Effluent Water Quality For The 10-Minute EBCT Run1 | [15 empty] | Field 4-7: GAC Effluent Water Quality For The 10-Minute EBCT Run (continued) | [17 empty] | Field 4-8: GAC Effluent Water Quality For The 20-Minute EBCT Run1 | [19 empty] | Field 4-8: GAC Effluent Water Quality For The 20-Minute EBCT Run (continued) | [13 empty] | Field 4-9: GAC Cost Parameters
|  |  |  | Input Design Parameters |  | US Standard Mesh Sizes | [20 empty] | Group C, 12 effluent samples per run | [33 empty] | Group C, 12 effluent samples per run
PWS Name | Public Works Commision of the City of Fayettville | Carbon manufacturer | Calgon Corp. | RSSCT influent TOC (mg/L) | 2.75 | US standard | Opening | Process | Description | Scale |  | 10-min. EBCT Start Date | 1998-11-20 | [6 empty] | 20-min. EBCT Start Date | 1998-11-20 | [5 empty] | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Cost Parameter | Parameter value
Public Water System Identification Number | NC 0326010 | Carbon trade name | Filtrasorb-400 | Inner diameter of the RSSCT column, DSC (mm) | 15 | mesh size | (mm) | Coagulation | 30 - 60 mg/L alum as Al2(SO4)3*14H2O | Full-Scale |  | 10-min. EBCT Start Time | 10:00 | [6 empty] | 20-min. EBCT Start Time | 10:00 | [5 empty] | ID | duplicated? | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | Capital Recovery Interest Rate (%) | 5.3
Water Industry Data Base Number (optional) | 1244 | Carbon type | Bituminous | Minimum RSSCT Reynolds number, ReSC, min | 0.2 | 4 | 4.75 | Flocculation | 1-stage | Full-Scale | [17 empty] | Y/N | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | Capital Recovery Period (years) | 45
|  | Original GAC mesh size, upper (US standard mesh) | 12 | Full-scale operating temperature, ToC (oC) | 18.1 | 6 | 3.35 | Sedimentation | 3.1 hours conventional | Full-Scale |  | Group A, 2 samples per batch | [7 empty] | Group A, 2 samples per batch | [6 empty] | C1 | N | 1998-11-20 | 11:30 | 1.5 | 57.4091 | 7.75 | 23 | 0.265 | BMRL | BMRL | 3.3 | 3 | 0.3 | 15 | 7.4 | 48 | BMRL | 1.4 | 1.3 | 1.1 | BMRL | 3.8 | BMRL | 2.2 | 1.3 | BMRL | BMRL | 1.5 | BMRL | BMRL | 2.2 | 3.5 | 5 | C1 | N | 1998-11-20 | 11:30 | 1.5 | 28.7045 | 7.76 | 23 | 0.285 | BMRL | BMRL | 3.4 | 3.2 | 0.2 | 15 | 7.4 | 48 | 27 | 1.9 | 1.3 | BMRL | BMRL | 3.2 | BMRL | BMRL | 1 | BMRL | BMRL | BMRL | BMRL | BMRL | 1.6 | 1 | 1 | Overhead & Profit Factor (% of construction costs) | 10
Official ICR Contact Person |  | Original GAC mesh size, lower (US standard mesh) | 40 | Full-scale bed porosity, eLC | 0.45 | 8 | 2.36 | Cartridge filtration | 1um exclusion size | Bench-scale |  | Parameter | Units | Sample A1-10 | Sample A2-10 | Average | RPD |  |  | Parameter | Units | Sample A1-20 | Sample A2-20 | Average | RPD |  | C2 | N | 1998-11-21 | 14:00 | 28 | 1071.6364 | 6.22 | 22 | 0.301 | BMRL | BMRL | 2.9 | 2.2 | 0.7 | 15 | 7.23 | 48 | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | 1.3 | 0 | 0 | C2 | N | 1998-11-21 | 14:00 | 28 | 535.8182 | 6.56 | 22 | 0.173 | BMRL | BMRL | 2.9 | 2.9 | 0 | 15 | 7.26 | 48 | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | 1.2 | 0 | 0 | Special Sitework Factor (% of construction costs) | 5
Mailing Address |  | Original carbon particle diameter, dLC (mm) | 1.0525 | Measured RSSCT dry bed density, rSC (g/cm3) | 0.463 | 10 | 2 |  |  |  |  | Sampling date | MM/DD/YY | 1998-11-20 | 1998-12-01 | --- | --- |  |  | Sampling date | MM/DD/YY | 1998-11-20 | 1998-12-01 | --- | --- |  | C3 | N | 1998-11-24 | 13:00 | 99 | 3789 | 7.02 | 22 | 0.724 | 0.014 | 1.9337 | 3.2 | 2.4 | 0.8 | 15 | 7.33 | 48 | 50 | 3.3 | 6.4 | 8.7 | 2.4 | 20.8 | BMRL | 2.2 | 3.1 | BMRL | 2.7 | 3.8 | BMRL | 5.7 | 6.7 | 8 | 11.8 | C3 | N | 1998-11-24 | 13:00 | 99 | 1894.5 | 7.01 | 22 | 0.434 | 0.007 | 1.6129 | 3.1 | 1.84 | 1.26 | 15 | 7.33 | 48 | BMRL | 1.1 | 1.5 | 1.8 | BMRL | 4.4 | BMRL | BMRL | 1.7 | BMRL | BMRL | 1.2 | BMRL | 2 | 2.5 | 1.7 | 2.9 | Construction Contingencies (% of construction costs) | 10
|  | 1: These are the characteristics before the carbon is ground for RSSCT experiments. |  | RSSCT GAC mesh size, upper (US standard mesh) | 80 | 12 | 1.68 |  |  |  |  | Sampling time | hh:mm | 11:30 | 13:00 | --- | --- |  |  | Sampling time | hh:mm | 11:30 | 13:00 | --- | --- |  | C4 | N | 1998-11-25 | 12:00 | 122 | 4669.2727 | 6.92 | 22 | 0.999 | 0.013 | 1.3013 | 3.2 | 2.08 | 1.12 | 15 | 7.4 | 48 | 61 | 4.5 | 8.3 | 11 | 3.1 | 26.9 | BMRL | 2.8 | 2.1 | BMRL | 3.4 | 4.3 | BMRL | 3.1 | 3.4 | 8.3 | 12.6 | C4 | N | 1998-11-25 | 12:00 | 122 | 2334.6364 | 6.9 | 22 | 0.291 | BMRL | BMRL | 2.9 | 1.84 | 1.06 | 15 | 7.39 | 48 | BMRL | BMRL | 1 | 1.4 | BMRL | 2.4 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | 0 | Engineering Fee Factor (% of construction costs) | 10
Phone Number |  |  |  | RSSCT GAC mesh size, lower (US standard mesh) | 100 | 16 | 1.18 |  |  |  |  | Operation time | hh.hh | 1.5 | 267 | --- | --- |  |  | Operation time | hh.hh | 1.5 | 267 | --- | --- |  | C5 | N | 1998-11-27 | 13:00 | 171 | 6544.6364 | 7.05 | 22 | 1.305 | 0.024 | 1.8391 | 3.2 | 1.73 | 1.47 | 15 | 7.35 | 48 | 96 | 8.6 | 14 | 14 | 3 | 39.6 | BMRL | 3.7 | 4.2 | BMRL | 3.6 | 5.7 | BMRL | 5.9 | 9 | 11.5 | 17.2 | C5 | N | 1998-11-27 | 13:00 | 171 | 3272.3182 | 7.1 | 22 | 0.313 | BMRL | BMRL | 2.9 | 1.9 | 1 | 15 | 7.25 | 48 | BMRL | BMRL | 1.2 | 1.3 | BMRL | 2.5 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | 1.5 | 0 | 0 | 1998 ENR Construction Cost Index (CCI base year 1913) | 77.8
FAX Number | [5 empty] | 20 | 0.85 |  |  |  |  | Bed volumes | (10 minutes) | 57.4091 | 10218.8182 | --- | --- |  |  | Bed volumes | (20 minutes) | 57.4091 | 10218.8182 | --- | --- |  | Avg-C6 | Y | 1998-11-29 | 11:00 | 217 | 8305.1818 | 7.04 | 22 | 1.506 | 0.028 | 1.8592 | 3.4 | 1.735 | 1.665 | 15 | 7.31 | 48 | 112.5 | 11 | 15 | 15 | 2.7 | 43.7 | BMRL | 5.1 | 5.65 | BMRL | 3.7 | 6.6 | BMRL | 6.4 | 11 | 14.45 | 21.05 | Avg-C6 | Y | 1998-11-29 | 11:00 | 217 | 4152.5909 | 7.1 | 22 | 0.2655 | 0.007 | 2.6365 | 2.9 | 1.935 | 0.965 | 15 | 7.325 | 48 | BMRL | BMRL | 1.2 | 1.5 | BMRL | 2.7 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | 1.5 | 0 | 0 | 1998 Producers Price Index (PPI base year 1982 = 100) | 131.3
E-Mail Address (optional) |  |  |  | Estimated Run Length |  | 30 | 0.6 |  |  |  |  | Alkalinity | mg/L as CaCO3 | 15.3 | 15.4 | 15.35 | 0.65147 |  |  | Alkalinity | mg/L as CaCO3 | 15.3 | 15.4 | 15.35 | 0.65147 |  | C7 | N | 1998-11-30 | 16:00 | 246 | 9415.0909 | 7.15 | 22 | 1.598 | 0.028 | 1.7522 | 3.4 | 1.46 | 1.94 | 15 | 7.25 | 48 | 130 | 13 | 17 | 15 | 2.4 | 47.4 | BMRL | 6.3 | 6.6 | BMRL | 3.3 | 6.9 | BMRL | 6.5 | 11 | 16.2 | 23.1 | C7 | N | 1998-11-30 | 16:00 | 246 | 4707.5455 | 7.21 | 22 | 0.432 | 0.019 | 4.3981 | 3.1 | 2 | 1.1 | 15 | 7.39 | 48 | BMRL | BMRL | 1.9 | 2.6 | 1.1 | 5.6 | BMRL | BMRL | BMRL | BMRL | 1 | BMRL | BMRL | BMRL | 1.9 | 1 | 1 | Labor Rate + Fringe ($/work-hour) | 21
|  |  |  | Bed volumes to 50% TOC breakthrough, BV50 | 5825.4199 | 40 | 0.425 |  |  |  |  | Total hardness | mg/L as CaCO3 | 21.7 | 21.7 | 21.7 | 0 |  |  | Total hardness | mg/L as CaCO3 | 21.7 | 21.7 | 21.7 | 0 |  | Avg-C8 | Y | 1998-12-01 | 10:00 | 264 | 10104 | 7.19 | 23 | 1.974 | 0.032 | 1.6211 | 3.6 | 1.295 | 2.14 | 15 | 7.33 | 48 | 135 | 14 | 17 | 15 | 2.25 | 48.25 | BMRL | 6.9 | 6.75 | BMRL | 3.75 | 7.5 | BMRL | 5.9 | 11 | 17.4 | 24.9 | Avg-C8 | Y | 1998-12-01 | 10:00 | 264 | 5052 | 7.28 | 23 | 0.4865 | 0.013 | 2.6721 | 3.05 | 2.05 | 1 | 15 | 7.27 | 48 | BMRL | 1.45 | 2.7 | 3.8 | 1.45 | 9.4 | BMRL | 1.85 | 1.1 | BMRL | 1.35 | 1.45 | BMRL | 2.8 | 2.35 | 4.3 | 5.75 | Labor Overhead Factor (% of labor) | 4.1
Technical ICR Contact Person |  |  |  | Estimated run length, BVT ( = 2 x BV50) | 11650.8397 | 50 | 0.3 |  |  |  |  | Calcium hardness | mg/L as CaCO3 | 12.9 | 12.9 | 12.9 | 0 |  |  | Calcium hardness | mg/L as CaCO3 | 12.9 | 12.9 | 12.9 | 0 |  | C9 | N | 1998-12-03 | 14:00 | 316 | 12094.1818 | 7.28 | 23 | 1.722 | 0.024 | 1.3937 | 3.7 | 1.37 | 2.405 | 15 | 7.32 | 48 | 150 | 16 | 19 | 14 | 1.8 | 50.8 | BMRL | 7.7 | 7.8 | BMRL | 2.6 | 7.6 | NR | NR | NR | 18.1 | 25.7 | C9 | N | 1998-12-03 | 14:00 | 316 | 6047.0909 | 7.19 | 23 | 0.599 | 0.009 | 1.5025 | 3 | 1.8 | 1.2 | 15 | 7.42 | 48 | 49 | 3.5 | 7.2 | 8.1 | 2.7 | 21.5 | 2.2 | 3.1 | 1.3 | BMRL | 2.8 | 5.3 | NR | NR | NR | 9.4 | 14.7 | Electric Rate ($/kW-h) | 0.035
Mailing Address |  |  |  | BVT + 30% safety factor, BVT+30% ( = 2.6 x BV50) | 15146.0916 | 60 | 0.25 |  |  |  |  | Ammonia | mg NH3-N / L | 0.018 | 0.037 | 0.0275 | 69.0909 |  |  | Ammonia | mg NH3-N / L | 0.018 | 0.037 | 0.0275 | 69.0909 |  | C10 | N | 1998-12-04 | 13:00 | 339 | 12974.4545 | 7.18 | 24 | 1.858 | 0.03 | 1.6146 | 3.9 | 1.25 | 2.53 | 15 | 7.24 | 48 | 155 | 18 | 19 | 14 | 1.9 | 52.9 | BMRL | 7.7 | 8.5 | BMRL | 3.5 | 8.1 | NR | NR | NR | 19.7 | 27.8 | C10 | N | 1998-12-04 | 13:00 | 339 | 6487.2273 | 7.09 | 24 | NR | 0.01 | BMRL | 3 | 1.5 | 1.5 | 15 | 7.47 | 48 | 38 | 2.1 | 4.6 | 7.3 | 3 | 17 | BMRL | 1.1 | 1.5 | BMRL | 2.3 | 2.4 | NR | NR | NR | 4.9 | 7.3 | Fuel Oil Rate ($/gal) | 0.55
[6 empty] | 70 | 0.21 |  |  |  |  | Bromide | mg/L | 96 | 92 | 94 | 4.2553 |  |  | Bromide | mg/L | 96 | 92 | 94 | 4.2553 |  | Avg-C11 | Y | 1998-12-06 | 12:00 | 386 | 14773.2727 | 7.17 | 25 | 2.1305 | 0.045 | 2.1122 | 4.5 | 1.225 | 3.25 | 15 | 7.415 | 48 | 160 | 20 | 21 | 14.5 | 1.75 | 57.25 | BMRL | 7.85 | 8.9 | BMRL | 3.3 | 7.4 | BMRL | 4.45 | 10.8 | 20.05 | 27.45 | Avg-C11 | Y | 1998-12-06 | 12:00 | 386 | 7386.6364 | 7.15 | 25 | 0.968 | 0.02 | 2.0661 | 3.5 | 1.6 | 1.9 | 15 | 7.365 | 48 | 58 | 4.7 | 8.05 | 9.2 | 2.25 | 24.2 | BMRL | 2.5 | 2.3 | BMRL | 2.65 | 3.6 | BMRL | 3.75 | 4.7 | 7.45 | 11.05 | Natural Gas Rate ($/ft3) | 0.007
Phone Number |  |  |  | General RSSCT Design Parameters |  | 80 | 0.18 | [19 empty] | C12 | N | 1998-12-10 | 14:00 | 484 | 18524 | 7.24 | 25 | 2.02 | 0.05 | 2.4752 | 4.6 | NR | 3.375 | 15 | 7.35 | 48 | NA | 16 | 21 | 15 | 2 | 54 | BMRL | 6 | 5.6 | BMRL | 3.5 | 6.4 | NR | NR | NR | 15.1 | 21.5 | C12 | N | 1998-12-10 | 14:00 | 484 | 9262 | 7.03 | 25 | 1.344 | 0.026 | 1.9345 | 3.8 | 0.66 | 3.14 | 15 | 7.38 | 48 | 72 | 5.1 | 11 | 14 | 4.5 | 34.6 | BMRL | 2.3 | 2.2 | BMRL | 4.1 | 4.5 | NR | NR | NR | 8.6 | 13.1 | Current Process Water Rate ($/1000 gal) | 0.35
FAX Number |  |  |  | Kinematic viscosity at ToC, nLC (m2/s) | 1.0757e-06 | 100 | 0.15 |  |  |  |  | Group B, 3 samples per batch | [7 empty] | Group B, 3 samples per batch | [6 empty] | C13 | N | 1998-12-14 | 14:00 | 580 | 22198.1818 | 7.32 | 24 | 1.98 | 0.048 | 2.4242 | 5 | 1.8 | 3.2 | 15 | 7.29 | 48 | 180 | 24 | 21 | 12 | 1.4 | 58.4 | 2.4 | 9.3 | 13 | BMRL | 2.6 | 7.4 | NR | NR | NR | 27.3 | 34.7 | C13 | N | 1998-12-14 | 14:00 | 580 | 11099.0909 | 7.07 | 24 | 1.404 | 0.029 | 2.0655 | 4 | 1.5 | 2.5 | 15 | 7.32 | 48 | 100 | 8.2 | 12 | 12 | 2.3 | 34.5 | BMRL | 6.8 | 5 | BMRL | 3.1 | 5.6 | BMRL | 6.2 | 9.3 | 14.9 | 20.5 | Modifications to Existing Plant (% of construction costs) | 20
E-Mail Address (optional) |  |  |  | RSSCT carbon particle diameter, dSC (mm) | 0.165 | 120 | 0.125 |  |  |  |  | Parameter | Units | Sample B1-10 | Sample B2-10 | Sample B3-10 | Average | %SD |  | Parameter | Units | Sample B1-10 | Sample B2-10 | Sample B3-10 | Average | %SD | [47 empty] | 0
|  |  |  | Scaling factor, SF | 6.3788 | 140 | 0.106 |  |  |  |  | Sampling date | MM/DD/YY | 1998-11-20 | 1998-12-01 | 1998-12-06 | --- | --- |  | Sampling date | MM/DD/YY | 1998-11-20 | 1998-12-01 | 1998-12-06 | --- | --- | [47 empty] | 0
Plant Name | P.O. Hoffer Water Treatment Plant |  |  | RSSCT hydraulic loading rate, vSC (m/hr) | 2.1124 | 170 | 0.088 | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  |  | Sampling time | hh:mm | 11:30 | 13:00 | 10:00 | --- | --- |  | Sampling time | hh:mm | 11:30 | 13:00 | 10:00 | --- | --- | [47 empty] | 0
Treatment Plant Category | CONV |  |  | RSSCT flow rate, QSC (mL/min) | 6.2214 | 200 | 0.075 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  |  | Operation time | hh.hh | 1.5 | 267 | 384 | --- | --- |  | Operation time | hh.hh | 1.5 | 267 | 384 | --- | --- | [47 empty] | 0
Process Train Name | Conventional train |  |  | Estimated total influent volume required, VSCT (L) | 443.1718 | 230 | 0.062 | is to list the pretreatment processes used in this particular RSSCT run. |  |  |  | Bed volumes | (10 minute) | 57.4091 | 10218.8182 | 14696.7273 | --- | --- |  | Bed volumes | (20 minute) | 57.4091 | 10218.8182 | 14696.7273 | --- | --- | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [19 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
ICR Treatment Plant Identification Number | 448 |  |  |  |  | 270 | 0.053 |  |  |  |  | pH | --- | 6.78 | 6.68 | 6.82 | 6.76 | 1.0667 |  | pH | --- | 6.78 | 6.68 | 6.82 | 6.76 | 1.0667 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [19 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
PWSID Number of Plant (if assigned) | NC 0326010 |  |  | 10-Minute EBCT Run |  | 325 | 0.044 |  |  |  |  | Turbidity | ntu | 0.83 | 0.75 | 0.9 | 0.82667 | 9.0793 |  | Turbidity | ntu | 0.83 | 0.75 | 0.9 | 0.82667 | 9.0793 | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results | [15 empty] | for the primary and duplicate analyses below. | [17 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below.
Historical Minimum Water Temperature (oC) | 4 |  |  | Full-scale empty bed contact time, EBCTLC (min) | 10 | 400 | 0.037 |  |  |  |  | Temperature | oC | 23 | 22 | 23 | 22.6667 | 2.5471 |  | Temperature | oC | 23 | 22 | 23 | 22.6667 | 2.5471
Historical Average Water Temperature (oC) | 34 |  |  | Estimated full-scale run time, tLCT (days) | 105.1812 | [6 empty] | Total organic carbon | mg/L | 2.967 | 3.014 | 2.977 | 2.986 | 0.82916 |  | Total organic carbon | mg/L | 2.967 | 3.014 | 2.977 | 2.986 | 0.82916 | Group D, 3 duplicate effluent samples per run (results from primary and duplicate analyses) | [33 empty] | Group D, 3 duplicate effluent samples per run (results from primary and duplicate analyses)
State Approved Plant Capacity (MGD) | 32 |  |  | RSSCT empty bed contact time, EBCTSC (min) | 1.5677 | [6 empty] | UV254 | cm-1 | 0.064 | 0.06 | 0.067 | 0.063667 | 5.516 |  | UV254 | cm-1 | 0.064 | 0.06 | 0.067 | 0.063667 | 5.516 | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS
|  |  |  | Estimated RSSCT run time, tSCT (days) | 16.4892 | [6 empty] | SUVA | L/(mg*m) | 2.1571 | 1.9907 | 2.2506 | 2.1328 | 6.1717 |  | SUVA | L/(mg*m) | 2.1571 | 1.9907 | 2.2506 | 2.1328 | 6.1717 | ID | Type | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6
|  |  |  | RSSCT bed length, lSC (cm) | 5.5192 | [6 empty] | SDS-Cl2 dose | mg/L | 7 | 5 | 5 | 5.6667 | 20.3771 |  | SDS-Cl2 dose | mg/L | 7 | 5 | 5 | 5.6667 | 20.3771 |  |  | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L
|  |  |  | Estimated volume required for 10-minute EBCT, VSC (L) | 147.7239 | [6 empty] | SDS-Free Cl2 residual | mg/L | 3.8 | 1.58 | 1.8 | 2.3933 | 51.1072 |  | SDS-Free Cl2 residual | mg/L | 3.8 | 1.58 | 1.8 | 2.3933 | 51.1072 | C6 | Primary | 1998-11-29 | 11:00 | 217 | 8305.1818 | 7.1 | 22 | 1.482 | 0.028 | 1.8893 | 3.4 | 1.71 | 1.69 | 15 | 7.29 | 48 | 110 | 11 | 15 | 15 | 2.7 | 43.7 | BMRL | 5.2 | 5.4 | BMRL | 3.6 | 6.4 | BMRL | 6.2 | 11 | 14.2 | 20.6 | C6 | Primary | 1998-11-29 | 11:00 | 217 | 4152.5909 | 7.09 | 22 | 0.277 | 0.007 | 2.5271 | 2.9 | 2.11 | 0.79 | 15 | 7.31 | 48 | BMRL | BMRL | 1.2 | 1.5 | BMRL | 2.7 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | 1.5 | 0 | 0
|  |  |  | Mass GAC required, mSC (g) | 4.5158 | [6 empty] | SDS-Cl2 demand | mg/L | 3.2 | 3.42 | 3.2 | 3.2733 | 3.8804 |  | SDS-Cl2 demand | mg/L | 3.2 | 3.42 | 3.2 | 3.2733 | 3.8804 | D-C6 | Duplicate | 1998-11-29 | 11:00 | 217 | 8305.1818 | 6.98 | 22 | 1.53 | 0.028 | 1.8301 | 3.4 | 1.76 | 1.64 | 15 | 7.33 | 48 | 115 | 11 | 15 | 15 | 2.7 | 43.7 | BMRL | 5 | 5.9 | BMRL | 3.8 | 6.8 | BMRL | 6.6 | 11 | 14.7 | 21.5 | D-C6 | Duplicate | 1998-11-29 | 11:00 | 217 | 4152.5909 | 7.11 | 22 | 0.254 | 0.007 | 2.7559 | 2.9 | 1.76 | 1.14 | 15 | 7.34 | 48 | BMRL | BMRL | 1.2 | 1.5 | BMRL | 2.7 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | 1.5 | 0 | 0
[12 empty] | SDS-Chlorination temp. | oC | 15 | 15 | 15 | 15 | 0 |  | SDS-Chlorination temp. | oC | 15 | 15 | 15 | 15 | 0 | Avg-C6 | Average | --- | --- | --- | --- | 7.04 | 22 | 1.506 | 0.028 | 1.8597 | 3.4 | 1.735 | 1.665 | 15 | 7.31 | 48 | 112.5 | 11 | 15 | 15 | 2.7 | 43.7 | BMRL | 5.1 | 5.65 | BMRL | 3.7 | 6.6 | BMRL | 6.4 | 11 | 14.45 | 21.05 | Avg-C6 | Average | --- | --- | --- | --- | 7.1 | 22 | 0.2655 | 0.007 | 2.6415 | 2.9 | 1.935 | 0.965 | 15 | 7.325 | 48 | BMRL | BMRL | 1.2 | 1.5 | BMRL | 2.7 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | 1.5 | 0 | 0
|  |  |  | 20-Minute EBCT Run | [7 empty] | SDS-Chlorination pH | --- | 7.4 | 7.35 | 7.45 | 7.4 | 0.67568 |  | SDS-Chlorination pH | --- | 7.4 | 7.35 | 7.45 | 7.4 | 0.67568 | RPD-C6 | RPD | --- | --- | --- | --- | 1.7045 | 0 | 3.1873 | 0 | 3.1873 | 0 | 2.8818 | 3.003 | 0 | 0.5472 | 0 | 4.4444 | 0 | 0 | 0 | 0 | 0 | #VALUE! | 3.9216 | 8.8496 | #VALUE! | 5.4054 | 6.0606 | #VALUE! | 6.25 | 0 | 3.4602 | 4.2755 | RPD-C6 | RPD | --- | --- | --- | --- | 0.28169 | 0 | 8.6629 | 0 | 8.6629 | 0 | 18.0879 | 36.2694 | 0 | 0.40956 | 0 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | #DIV/0! | #DIV/0!
|  |  |  | Full-scale empty bed contact time, EBCTLC (min) | 20 | [6 empty] | SDS-Incubation time | hours | 48 | 48 | 48 | 48 | 0 |  | SDS-Incubation time | hours | 48 | 48 | 48 | 48 | 0 | C8 | Primary | 1998-12-01 | 10:00 | 264 | 10104 | 7.1 | 23 | 2.045 | 0.032 | 1.5648 | 3.6 | 1.35 | 2.25 | 15 | 7.36 | 48 | 130 | 14 | 17 | 15 | 2.2 | 48.2 | BMRL | 6.9 | 6.8 | BMRL | 3.8 | 7.5 | BMRL | 5.8 | 11 | 17.5 | 25 | C8 | Primary | 1998-12-01 | 10:00 | 264 | 5052 | 7.28 | 23 | 0.473 | 0.013 | 2.7484 | 3.1 | 2.1 | 1 | 15 | 7.27 | 48 | BMRL | 1.5 | 2.7 | 3.8 | 1.4 | 9.4 | BMRL | 1.8 | 1.1 | BMRL | 1.4 | 1.5 | BMRL | 2.7 | 2.5 | 4.3 | 5.8
|  |  |  | Estimated full-scale run time, tLCT (days) | 210.3624 | [6 empty] | SDS-TOX | mg Cl- /L | 295 | 260 | 270 | 275 | 6.5555 |  | SDS-TOX | mg Cl- /L | 295 | 260 | 270 | 275 | 6.5555 | D-C8 | Duplicate | 1998-12-01 | 10:00 | 264 | 10104 | 7.28 | 23 | 1.903 | 0.032 | 1.6816 | 3.6 | 1.24 | 2.36 | 15 | 7.3 | 48 | 140 | 14 | 17 | 15 | 2.3 | 48.3 | BMRL | 6.9 | 6.7 | BMRL | 3.7 | 7.5 | BMRL | 6 | 11 | 17.3 | 24.8 | D-C8 | Duplicate | 1998-12-01 | 10:00 | 264 | 5052 | 7.28 | 23 | 0.5 | 0.013 | 2.6 | 3 | 2 | 1 | 15 | 7.27 | 48 | BMRL | 1.4 | 2.7 | 3.8 | 1.5 | 9.4 | BMRL | 1.9 | BMRL | BMRL | 1.3 | 1.4 | BMRL | 2.9 | 2.2 | 3.2 | 4.6
|  |  |  | RSSCT empty bed contact time, EBCTSC (min) | 3.1354 | [6 empty] | SDS-CHCl3 | mg/L | 45 | 41 | 44 | 43.3333 | 4.8038 |  | SDS-CHCl3 | mg/L | 45 | 41 | 44 | 43.3333 | 4.8038 | Avg-C8 | Average | --- | --- | --- | --- | 7.19 | 23 | 1.974 | 0.032 | 1.6232 | 3.6 | 1.295 | 2.305 | 15 | 7.33 | 48 | 135 | 14 | 17 | 15 | 2.25 | 48.25 | BMRL | 6.9 | 6.75 | BMRL | 3.75 | 7.5 | BMRL | 5.9 | 11 | 17.4 | 24.9 | Avg-C8 | Average | --- | --- | --- | --- | 7.28 | 23 | 0.4865 | 0.013 | 2.6742 | 3.05 | 2.05 | 1 | 15 | 7.27 | 48 | BMRL | 1.45 | 2.7 | 3.8 | 1.45 | 9.4 | BMRL | 1.85 | 1.1 | BMRL | 1.35 | 1.45 | BMRL | 2.8 | 2.35 | 4.3 | 5.75
|  |  |  | Estimated RSSCT run time, tSCT (days) | 32.9784 | [6 empty] | SDS-BDCM | mg/L | 26 | 25 | 27 | 26 | 3.8462 |  | SDS-BDCM | mg/L | 26 | 25 | 27 | 26 | 3.8462 | RPD-C8 | RPD | --- | --- | --- | --- | 2.5035 | 0 | 7.1935 | 0 | 7.1935 | 0 | 8.4942 | 4.7722 | 0 | 0.81855 | 0 | 7.4074 | 0 | 0 | 0 | 4.4444 | 0.20725 | #VALUE! | 0 | 1.4815 | #VALUE! | 2.6667 | 0 | #VALUE! | 3.3898 | 0 | 1.1494 | 0.80321 | RPD-C8 | RPD | --- | --- | --- | --- | 0 | 0 | 5.5498 | 0 | 5.5498 | 3.2787 | 4.878 | 0 | 0 | 0 | 0 | #VALUE! | 6.8966 | 0 | 0 | 6.8966 | 0 | #VALUE! | 5.4054 | #VALUE! | #VALUE! | 7.4074 | 6.8966 | #VALUE! | 7.1429 | 12.766 | 25.5814 | 20.8696
|  |  |  | RSSCT bed length, lSC (cm) | 11.0384 | [6 empty] | SDS-DBCM | mg/L | 10 | 12 | 12 | 11.3333 | 10.1885 |  | SDS-DBCM | mg/L | 10 | 12 | 12 | 11.3333 | 10.1885 | C11 | Primary | 1998-12-06 | 12:00 | 386 | 14773.2727 | 7.17 | 25 | 2.194 | 0.045 | 2.051 | 4.5 | 1.22 | 3.28 | 15 | 7.4 | 48 | 160 | 20 | 21 | 14 | 1.7 | 56.7 | BMRL | 8 | 8.9 | BMRL | 3.5 | 7.8 | BMRL | 5 | 12 | 20.4 | 28.2 | C11 | Primary | 1998-12-06 | 12:00 | 386 | 7386.6364 | 7.15 | 25 | 1.022 | 0.02 | 1.9569 | 3.5 | 1.6 | 1.9 | 15 | 7.4 | 48 | 57 | 4.5 | 7.9 | 9 | 2.2 | 23.6 | BMRL | 2.4 | 2.3 | BMRL | 2.9 | 3.8 | BMRL | 4.8 | 5.9 | 7.6 | 11.4
|  |  |  | Estimated volume required for 20-minute EBCT, VSC (L) | 295.4478 | [6 empty] | SDS-CHBr3 | mg/L | BMRL | BMRL | BMRL | BMRL | BMRL |  | SDS-CHBr3 | mg/L | BMRL | BMRL | BMRL | BMRL | BMRL | D-C11 | Duplicate | 1998-12-06 | 12:00 | 386 | 14773.2727 | 7.17 | 25 | 2.067 | 0.045 | 2.1771 | 4.5 | 1.23 | 3.27 | 15 | 7.43 | 48 | 160 | 20 | 21 | 15 | 1.8 | 57.8 | BMRL | 7.7 | 8.9 | BMRL | 3.1 | 7 | BMRL | 3.9 | 9.6 | 19.7 | 26.7 | D-C11 | Duplicate | 1998-12-06 | 12:00 | 386 | 7386.6364 | 7.15 | 25 | 0.914 | 0.02 | 2.1882 | 3.5 | 1.6 | 1.9 | 15 | 7.33 | 48 | 59 | 4.9 | 8.2 | 9.4 | 2.3 | 24.8 | BMRL | 2.6 | 2.3 | BMRL | 2.4 | 3.4 | BMRL | 2.7 | 3.5 | 7.3 | 10.7
|  |  |  | Mass GAC required, mSC (g) | 9.0315 | [6 empty] | SDS-THM4 | mg/L | 81 | 78 | 83 | 80.6667 | 3.1198 |  | SDS-THM4 | mg/L | 81 | 78 | 83 | 80.6667 | 3.1198 | Avg-C11 | Average | --- | --- | --- | --- | 7.17 | 25 | 2.1305 | 0.045 | 2.1141 | 4.5 | 1.225 | 3.275 | 15 | 7.415 | 48 | 160 | 20 | 21 | 14.5 | 1.75 | 57.25 | BMRL | 7.85 | 8.9 | BMRL | 3.3 | 7.4 | BMRL | 4.45 | 10.8 | 20.05 | 27.45 | Avg-C11 | Average | --- | --- | --- | --- | 7.15 | 25 | 0.968 | 0.02 | 2.0726 | 3.5 | 1.6 | 1.9 | 15 | 7.365 | 48 | 58 | 4.7 | 8.05 | 9.2 | 2.25 | 24.2 | BMRL | 2.5 | 2.3 | BMRL | 2.65 | 3.6 | BMRL | 3.75 | 4.7 | 7.45 | 11.05
[12 empty] | SDS-MCAA* | mg/L | 2.1 | 2 | 2.3 | 2.1333 | 7.1603 |  | SDS-MCAA* | mg/L | 2.1 | 2 | 2.3 | 2.1333 | 7.1603 | RPD-C11 | RPD | --- | --- | --- | --- | 0 | 0 | 5.961 | 0 | 5.961 | 0 | 0.81633 | 0.30534 | 0 | 0.40459 | 0 | 0 | 0 | 0 | 6.8966 | 5.7143 | 1.9214 | #VALUE! | 3.8217 | 0 | #VALUE! | 12.1212 | 10.8108 | #VALUE! | 24.7191 | 22.2222 | 3.4913 | 5.4645 | RPD-C11 | RPD | --- | --- | --- | --- | 0 | 0 | 11.157 | 0 | 11.157 | 0 | 0 | 0 | 0 | 0.95044 | 0 | 3.4483 | 8.5106 | 3.7267 | 4.3478 | 4.4444 | 4.9587 | #VALUE! | 8 | 0 | #VALUE! | 18.8679 | 11.1111 | #VALUE! | 56 | 51.0638 | 4.0268 | 6.3348
[12 empty] | SDS-DCAA* | mg/L | 18 | 15 | 17 | 16.6667 | 9.1652 |  | SDS-DCAA* | mg/L | 18 | 15 | 17 | 16.6667 | 9.1652 | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[12 empty] | SDS-TCAA* | mg/L | 29 | 21 | 25 | 25 | 16 |  | SDS-TCAA* | mg/L | 29 | 21 | 25 | 25 | 16 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
[12 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | BMRL | BMRL | BMRL |  | SDS-MBAA* | mg/L | BMRL | BMRL | BMRL | BMRL | BMRL
[12 empty] | SDS-DBAA* | mg/L | 2.2 | 2.5 | 2.7 | 2.4667 | 10.2025 |  | SDS-DBAA* | mg/L | 2.2 | 2.5 | 2.7 | 2.4667 | 10.2025
[12 empty] | SDS-BCAA* | mg/L | 10 | 9.7 | 11 | 10.2333 | 6.6517 |  | SDS-BCAA* | mg/L | 10 | 9.7 | 11 | 10.2333 | 6.6517
[12 empty] | SDS-TBAA | mg/L | BMRL | BMRL | BMRL | BMRL | BMRL |  | SDS-TBAA | mg/L | BMRL | BMRL | BMRL | BMRL | BMRL
[12 empty] | SDS-CDBAA | mg/L | 6.6 | 5.7 | 6.2 | 6.1667 | 7.3123 |  | SDS-CDBAA | mg/L | 6.6 | 5.7 | 6.2 | 6.1667 | 7.3123
[12 empty] | SDS-DCBAA | mg/L | 23 | 19 | 21 | 21 | 9.5238 |  | SDS-DCBAA | mg/L | 23 | 19 | 21 | 21 | 9.5238
[12 empty] | SDS-HAA5 | mg/L | 51.3 | 40.5 | 47 | 46.2667 | 11.7519 |  | SDS-HAA5 | mg/L | 51.3 | 40.5 | 47 | 46.2667 | 11.7519
[12 empty] | SDS-HAA6 | mg/L | 61.3 | 50.2 | 58 | 56.5 | 10.0885 |  | SDS-HAA6 | mg/L | 61.3 | 50.2 | 58 | 56.5 | 10.0885
[12 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [7 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [7 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
Note on AU8: CDM: SDS Conditions: pH values are measured values Temperature values are the temperature of the fridgerator used for sample incubation.
Note on BX17: Parameswarc: DID NOT MEET PWC QC
Note on BX20: CDM: The 20 minute column run was stopped by the UNC laboratory personel when 70% TOC breakthrough was reached according to their on-site TOC analyses. The TOC values reported for this study are from ICR certified laboratory NC016. The TOC value reported from NC016 was slightly lower than the value from the UNC lab. Thus, while the UNC lab showed 70% breakthrough, the NC016 lab did not.