## Raw Water Data
Field 1-7: Source Water - Water Quality For Week 2 |  |  | Field 1-8: Source Water - Water Quality For Week 4 |  |  | Field 1-9: Source Water - Water Quality For Week 6 |  |  | Field 1-10: Source Water - Water Quality For Week 8 |  |  | Field 1-11: Source Water - Water Quality For Week 10 |  |  | Field 1-12: Duplicate Source Water - Water Quality For Week 10
Raw Water prior to acidification Water Quality Parameters |  |  | Raw Water prior to acidification Water Quality Parameters |  |  | Raw Water prior to acidification Water Quality Parameters |  |  | Raw Water prior to acidification Water Quality Parameters |  |  | Raw Water prior to acidification Water Quality Parameters |  |  | Raw Water prior to acidification Water Quality Parameters
Parameter | Units | Raw WATER | Parameter | Units | Raw WATER | Parameter | Units | Raw WATER | Parameter | Units | Raw WATER | Parameter | Units | Raw WATER | Parameter | Units | Raw WATER
Sampling date | MM/DD/YY | 1998-04-13 | Sampling date | MM/DD/YY | 1998-04-27 | Sampling date | MM/DD/YY | 1998-05-11 | Sampling date | MM/DD/YY | 1998-05-26 | Sampling date | MM/DD/YY | 1998-06-09 | Sampling date | MM/DD/YY | 1998-06-09
Sampling time | hh:mm | 9:43 | Sampling time | hh:mm | 8:44 | Sampling time | hh:mm | 7:59 | Sampling time | hh:mm | 7:55 | Sampling time | hh:mm | 7:59 | Sampling time | hh:mm | 7:59
Operation time | hh.hh | 24229.6 | Operation time | hh.hh | 24538.8 | Operation time | hh.hh | 24873.8 | Operation time | hh.hh | 25214.87 | Operation time | hh.hh | 25525.7 | Operation time | hh.hh | 25525.7
pH | --- | 7.27 | pH | --- | 7.41 | pH | --- | 7.22 | pH | --- | 7.21 | pH | --- | 7.18 | pH | --- | 7.18
Temperature | oC | 24.2 | Temperature | oC | 24.5 | Temperature | oC | 24.5 | Temperature | oC | 25.6 | Temperature | oC | 25.3 | Temperature | oC | 25.3
Alkalinity | mg/L as CaCO3 | 288 | Alkalinity | mg/L as CaCO3 | 224 | Alkalinity | mg/L as CaCO3 | 299 | Alkalinity | mg/L as CaCO3 | 294 | Alkalinity | mg/L as CaCO3 | 294 | Alkalinity | mg/L as CaCO3 | 290
Total dissolved solids | mg/L | 436 | Total dissolved solids | mg/L | 432 | Total dissolved solids | mg/L | 446 | Total dissolved solids | mg/L | 454 | Total dissolved solids | mg/L | 448 | Total dissolved solids | mg/L | 438
Total hardness | mg/L as CaCO3 | 306 | Total hardness | mg/L as CaCO3 | 300 | Total hardness | mg/L as CaCO3 | 302 | Total hardness | mg/L as CaCO3 | 300 | Total hardness | mg/L as CaCO3 | 294 | Total hardness | mg/L as CaCO3 | 298
Calcium hardness | mg/L as CaCO3 | 232 | Calcium hardness | mg/L as CaCO3 | 222 | Calcium hardness | mg/L as CaCO3 | 224 | Calcium hardness | mg/L as CaCO3 | 214 | Calcium hardness | mg/L as CaCO3 | 224 | Calcium hardness | mg/L as CaCO3 | 221
Turbidity | ntu | 0.31 | Turbidity | ntu | 0.2 | Turbidity | ntu | 0.2 | Turbidity | ntu | 0.27 | Turbidity | ntu | 0.22 | Turbidity | ntu | 0.23
Ammonia | mg NH3-N / L | 0.2 | Ammonia | mg NH3-N / L | 0.12 | Ammonia | mg NH3-N / L | 0.38 | Ammonia | mg NH3-N / L | 0.28 | Ammonia | mg NH3-N / L | 0.31 | Ammonia | mg NH3-N / L | 0.28
Total organic carbon | mg/L | 8 | Total organic carbon | mg/L | 8 | Total organic carbon | mg/L | 8 | Total organic carbon | mg/L | 9 | Total organic carbon | mg/L | 8 | Total organic carbon | mg/L | 8
UV254 | cm-1 | 0.225 | UV254 | cm-1 | 0.222 | UV254 | cm-1 | 0.2325 | UV254 | cm-1 | 0.226 | UV254 | cm-1 | 0.227 | UV254 | cm-1 | 0.231
SUVA | L/(mg*m) | 2.8125 | SUVA | L/(mg*m) | 2.775 | SUVA | L/(mg*m) | 2.91 | SUVA | L/(mg*m) | 2.5111 | SUVA | L/(mg*m) | 2.8375 | SUVA | L/(mg*m) | 2.8875
Field 2-7: Source Water - Water Quality For Week 12 |  |  | Field 2-8: Source Water - Water Quality For Week 14 |  |  | Field 2-9: Source Water - Water Quality For Week 16 |  |  | Field 2-10: Source Water - Water Quality For Week 18 |  |  | Field 2-11: Source Water - Water Quality For Week 20 |  |  | Field 2-12: Duplicate Source Water - Water Quality For Week 20 |  |  | Field 2-9: Duplicate Source Water - Water Quality For Week 16
Raw Water prior to acidification Water Quality Parameters |  |  | Raw Water prior to acidification Water Quality Parameters |  |  | Raw Water prior to acidification Water Quality Parameters |  |  | Raw Water prior to acidification Water Quality Parameters |  |  | Raw Water prior to acidification Water Quality Parameters |  |  | Raw Water prior to acidification Water Quality Parameters |  |  | Raw Water prior to acidification Water Quality Parameters
Parameter | Units | Raw WATER | Parameter | Units | Raw WATER | Parameter | Units | Raw WATER | Parameter | Units | Raw WATER | Parameter | Units | Raw WATER | Parameter | Units | Raw WATER | Parameter | Units | Raw WATER
Sampling date | MM/DD/YY | 1998-06-23 | Sampling date | MM/DD/YY | 1998-07-06 | Sampling date | MM/DD/YY | 1998-07-22 | Sampling date | MM/DD/YY | 1998-08-03 | Sampling date | MM/DD/YY | 1998-08-17 | Sampling date | MM/DD/YY | 1998-08-17 | Sampling date | MM/DD/YY | 1998-07-22
Sampling time | hh:mm | 8:25 | Sampling time | hh:mm | 8:06 | Sampling time | hh:mm | 8:02 | Sampling time | hh:mm | 7:50 | Sampling time | hh:mm | 6:10 | Sampling time | hh:mm | 6:10 | Sampling time | hh:mm | 8:02
Operation time | hh.hh | 25823.8 | Operation time | hh.hh | 26105.2 | Operation time | hh.hh | 26373.5 | Operation time | hh.hh | 26631.4 | Operation time | hh.hh | 26875 | Operation time | hh.hh | 26875 | Operation time | hh.hh | 26373.5
pH | --- | 7.21 | pH | --- | 7.2 | pH | --- | 7.25 | pH | --- | 7.19 | pH | --- | 7.24 | pH | --- | 7.24 | pH | --- | 7.25
Temperature | oC | 25 | Temperature | oC | 24.9 | Temperature | oC | 24.8 | Temperature | oC | 25.1 | Temperature | oC | 25.4 | Temperature | oC | 25.4 | Temperature | oC | 24.8
Alkalinity | mg/L as CaCO3 | 296 | Alkalinity | mg/L as CaCO3 | 282 | Alkalinity | mg/L as CaCO3 | 300 | Alkalinity | mg/L as CaCO3 | 300 | Alkalinity | mg/L as CaCO3 | 300 | Alkalinity | mg/L as CaCO3 | 300 | Alkalinity | mg/L as CaCO3 | 296
Total dissolved solids | mg/L | 470 | Total dissolved solids | mg/L | 464 | Total dissolved solids | mg/L | 438 | Total dissolved solids | mg/L | 444 | Total dissolved solids | mg/L | 452 | Total dissolved solids | mg/L | 461 | Total dissolved solids | mg/L | 452
Total hardness | mg/L as CaCO3 | 298 | Total hardness | mg/L as CaCO3 | 304 | Total hardness | mg/L as CaCO3 | 298 | Total hardness | mg/L as CaCO3 | 306 | Total hardness | mg/L as CaCO3 | 332 | Total hardness | mg/L as CaCO3 | 332 | Total hardness | mg/L as CaCO3 | 294
Calcium hardness | mg/L as CaCO3 | 226 | Calcium hardness | mg/L as CaCO3 | 232 | Calcium hardness | mg/L as CaCO3 | 228 | Calcium hardness | mg/L as CaCO3 | 240 | Calcium hardness | mg/L as CaCO3 | 256 | Calcium hardness | mg/L as CaCO3 | 252 | Calcium hardness | mg/L as CaCO3 | 228
Turbidity | ntu | 0.26 | Turbidity | ntu | 0.2 | Turbidity | ntu | 0.2 | Turbidity | ntu | 0.22 | Turbidity | ntu | 0.24 | Turbidity | ntu | 0.23 | Turbidity | ntu | 0.2
Ammonia | mg NH3-N / L | 0.29 | Ammonia | mg NH3-N / L | 0.36 | Ammonia | mg NH3-N / L | 0.32 | Ammonia | mg NH3-N / L | 0.35 | Ammonia | mg NH3-N / L | 0.38 | Ammonia | mg NH3-N / L | 0.38 | Ammonia | mg NH3-N / L | 0.32
Total organic carbon | mg/L | 8 | Total organic carbon | mg/L | 8 | Total organic carbon | mg/L | 7 | Total organic carbon | mg/L | 9 | Total organic carbon | mg/L | 9 | Total organic carbon | mg/L | 8 | Total organic carbon | mg/L | 7
UV254 | cm-1 | 0.23 | UV254 | cm-1 | 0.23 | UV254 | cm-1 | 0.261 | UV254 | cm-1 | 0.271 | UV254 | cm-1 | 0.246 | UV254 | cm-1 | 0.24 | UV254 | cm-1 | 0.288
SUVA | L/(mg*m) | 2.875 | SUVA | L/(mg*m) | 2.875 | SUVA | L/(mg*m) | 3.7286 | SUVA | L/(mg*m) | 3.0111 | SUVA | L/(mg*m) | 2.7333 | SUVA | L/(mg*m) | 3 | SUVA | L/(mg*m) | 4.1143
Field 3-7: Source Water - Water Quality For Week 22 |  |  | Field 3-8: Source Water - Water Quality For Week 24 |  |  | Field 3-9: Source Water - Water Quality For Week 26 |  |  | Field 3-10: Source Water - Water Quality For Week 28 |  |  | Field 3-11: Source Water - Water Quality For Week 30 |  |  | Field 3-12: Duplicate Source Water - Water Quality For Week 30
Raw Water prior to acidification Water Quality Parameters |  |  | Raw Water prior to acidification Water Quality Parameters |  |  | Raw Water prior to acidification Water Quality Parameters |  |  | Raw Water prior to acidification Water Quality Parameters |  |  | Raw Water prior to acidification Water Quality Parameters |  |  | Raw Water prior to acidification Water Quality Parameters
Parameter | Units | Raw WATER | Parameter | Units | Raw WATER | Parameter | Units | Raw WATER | Parameter | Units | Raw WATER | Parameter | Units | Raw WATER | Parameter | Units | Raw WATER
Sampling date | MM/DD/YY | 1998-09-08 | Sampling date | MM/DD/YY | 1998-09-14 | Sampling date | MM/DD/YY | NA | Sampling date | MM/DD/YY | 1998-10-12 | Sampling date | MM/DD/YY | 1998-10-26 | Sampling date | MM/DD/YY | 1998-10-26
Sampling time | hh:mm | 11:56 | Sampling time | hh:mm | 7:57 | Sampling time | hh:mm | NA | Sampling time | hh:mm | 8:02 | Sampling time | hh:mm | 8:05 | Sampling time | hh:mm | 8:05
Operation time | hh.hh | 27019.7 | Operation time | hh.hh | 27152.3 | Operation time | hh.hh | NA | Operation time | hh.hh | 27337.2 | Operation time | hh.hh | 27616.4 | Operation time | hh.hh | 27616.4
pH | --- | 7.27 | pH | --- | 7.29 | pH | --- | NA | pH | --- | 7.05 | pH | --- | 7.15 | pH | --- | 7.15
Temperature | oC | 25.5 | Temperature | oC | 24.88 | Temperature | oC | NA | Temperature | oC | 25.7 | Temperature | oC | 24.9 | Temperature | oC | 24.9
Alkalinity | mg/L as CaCO3 | 300 | Alkalinity | mg/L as CaCO3 | 308 | Alkalinity | mg/L as CaCO3 | NA | Alkalinity | mg/L as CaCO3 | 276 | Alkalinity | mg/L as CaCO3 | 296 | Alkalinity | mg/L as CaCO3 | 296
Total dissolved solids | mg/L | 494 | Total dissolved solids | mg/L | 474 | Total dissolved solids | mg/L | NA | Total dissolved solids | mg/L | 432 | Total dissolved solids | mg/L | 482 | Total dissolved solids | mg/L | 456
Total hardness | mg/L as CaCO3 | 300 | Total hardness | mg/L as CaCO3 | 298 | Total hardness | mg/L as CaCO3 | NA | Total hardness | mg/L as CaCO3 | 300 | Total hardness | mg/L as CaCO3 | 290 | Total hardness | mg/L as CaCO3 | 302
Calcium hardness | mg/L as CaCO3 | 216 | Calcium hardness | mg/L as CaCO3 | 226 | Calcium hardness | mg/L as CaCO3 | NA | Calcium hardness | mg/L as CaCO3 | 240 | Calcium hardness | mg/L as CaCO3 | 224 | Calcium hardness | mg/L as CaCO3 | 244
Turbidity | ntu | 0.24 | Turbidity | ntu | 0.24 | Turbidity | ntu | NA | Turbidity | ntu | 0.23 | Turbidity | ntu | 0.2 | Turbidity | ntu | 0.25
Ammonia | mg NH3-N / L | 0.32 | Ammonia | mg NH3-N / L | 0.27 | Ammonia | mg NH3-N / L | NA | Ammonia | mg NH3-N / L | 0.29 | Ammonia | mg NH3-N / L | 0.444 | Ammonia | mg NH3-N / L | 0.461
Total organic carbon | mg/L | 9 | Total organic carbon | mg/L | 2 | Total organic carbon | mg/L | NA | Total organic carbon | mg/L | 8 | Total organic carbon | mg/L | 9 | Total organic carbon | mg/L | 8
UV254 | cm-1 | 0.276 | UV254 | cm-1 | 0.222 | UV254 | cm-1 | NA | UV254 | cm-1 | 0.222 | UV254 | cm-1 | 0.219 | UV254 | cm-1 | 0.22
SUVA | L/(mg*m) | 3.0667 | SUVA | L/(mg*m) | 11.1 | SUVA | L/(mg*m) | #VALUE! | SUVA | L/(mg*m) | 2.775 | SUVA | L/(mg*m) | 2.4333 | SUVA | L/(mg*m) | 2.75
Field 4-7: Source Water - Water Quality For Week 32 |  |  | Field 4-8: Source Water - Water Quality For Week 34 |  |  | Field 4-9: Source Water - Water Quality For Week 36 |  |  | Field 4-10: Source Water - Water Quality For Week 38 |  |  | Field 4-11: Source Water - Water Quality For Week 40 |  |  | Field 4-12: Duplicate Source Water - Water Quality For Week 40
Raw Water prior to acidification Water Quality Parameters |  |  | Raw Water prior to acidification Water Quality Parameters |  |  | Raw Water prior to acidification Water Quality Parameters |  |  | Raw Water prior to acidification Water Quality Parameters |  |  | Raw Water prior to acidification Water Quality Parameters |  |  | Raw Water prior to acidification Water Quality Parameters
Parameter | Units | Raw WATER | Parameter | Units | Raw WATER | Parameter | Units | Raw WATER | Parameter | Units | Raw WATER | Parameter | Units | Raw WATER | Parameter | Units | Raw WATER
Sampling date | MM/DD/YY | 1998-11-10 | Sampling date | MM/DD/YY | 1998-11-23 | Sampling date | MM/DD/YY | 1998-12-07 | Sampling date | MM/DD/YY | 1998-12-21 | Sampling date | MM/DD/YY | 1999-01-04 | Sampling date | MM/DD/YY | 1999-01-04
Sampling time | hh:mm | 13:46 | Sampling time | hh:mm | 7:12 | Sampling time | hh:mm | 7:39 | Sampling time | hh:mm | 9:00 | Sampling time | hh:mm | 9:30 | Sampling time | hh:mm | 9:30
Operation time | hh.hh | 27864.6 | Operation time | hh.hh | 28126.7 | Operation time | hh.hh | 28379.2 | Operation time | hh.hh | 28614.2 | Operation time | hh.hh | 28909.73 | Operation time | hh.hh | 28909.73
pH | --- | 7.17 | pH | --- | 7.06 | pH | --- | 7.01 | pH | --- | 7.24 | pH | --- | 7.05 | pH | --- | 7.05
Temperature | oC | 25 | Temperature | oC | 243 | Temperature | oC | 24.4 | Temperature | oC | 25 | Temperature | oC | 23.7 | Temperature | oC | 23.7
Alkalinity | mg/L as CaCO3 | 284 | Alkalinity | mg/L as CaCO3 | 278 | Alkalinity | mg/L as CaCO3 | 290 | Alkalinity | mg/L as CaCO3 | 282 | Alkalinity | mg/L as CaCO3 | 274 | Alkalinity | mg/L as CaCO3 | 280
Total dissolved solids | mg/L | 458 | Total dissolved solids | mg/L | 406 | Total dissolved solids | mg/L | 452 | Total dissolved solids | mg/L | 442 | Total dissolved solids | mg/L | 450 | Total dissolved solids | mg/L | 422
Total hardness | mg/L as CaCO3 | 302 | Total hardness | mg/L as CaCO3 | 292 | Total hardness | mg/L as CaCO3 | 310 | Total hardness | mg/L as CaCO3 | 302 | Total hardness | mg/L as CaCO3 | 314 | Total hardness | mg/L as CaCO3 | 304
Calcium hardness | mg/L as CaCO3 | 250 | Calcium hardness | mg/L as CaCO3 | 228 | Calcium hardness | mg/L as CaCO3 | 254 | Calcium hardness | mg/L as CaCO3 | 244 | Calcium hardness | mg/L as CaCO3 | 250 | Calcium hardness | mg/L as CaCO3 | 250
Turbidity | ntu | 0.21 | Turbidity | ntu | 0.22 | Turbidity | ntu | 0.26 | Turbidity | ntu | 0.21 | Turbidity | ntu | 0.25 | Turbidity | ntu | 0.25
Ammonia | mg NH3-N / L | 0.501 | Ammonia | mg NH3-N / L | 0.31 | Ammonia | mg NH3-N / L | 0.3 | Ammonia | mg NH3-N / L | 0.23 | Ammonia | mg NH3-N / L | 0.27 | Ammonia | mg NH3-N / L | 0.27
Total organic carbon | mg/L | 8 | Total organic carbon | mg/L | 8 | Total organic carbon | mg/L | 8 | Total organic carbon | mg/L | 8 | Total organic carbon | mg/L | 7 | Total organic carbon | mg/L | 8
UV254 | cm-1 | 0.22 | UV254 | cm-1 | 0.24 | UV254 | cm-1 | 0.232 | UV254 | cm-1 | 0.24 | UV254 | cm-1 | 0.226 | UV254 | cm-1 | 0.229
SUVA | L/(mg*m) | 2.75 | SUVA | L/(mg*m) | 3 | SUVA | L/(mg*m) | 2.9 | SUVA | L/(mg*m) | 3 | SUVA | L/(mg*m) | 3.2286 | SUVA | L/(mg*m) | 2.8625
Field 5-7: Source Water - Water Quality For Week 42 |  |  | Field 5-8: Source Water - Water Quality For Week 44 |  |  | Field 5-9: Source Water - Water Quality For Week 46 |  |  | Field 5-10: Source Water - Water Quality For Week48 |  |  | Field 5-11: Source Water - Water Quality For Week 50 |  |  | Field 5-12: Duplicate Source Water - Water Quality For Week 50
Raw Water prior to acidification Water Quality Parameters |  |  | Raw Water prior to acidification Water Quality Parameters |  |  | Raw Water prior to acidification Water Quality Parameters |  |  | Raw Water prior to acidification Water Quality Parameters |  |  | Raw Water prior to acidification Water Quality Parameters |  |  | Raw Water prior to acidification Water Quality Parameters
Parameter | Units | Raw WATER | Parameter | Units | Raw WATER | Parameter | Units | Raw WATER | Parameter | Units | Raw WATER | Parameter | Units | Raw WATER | Parameter | Units | Raw WATER
Sampling date | MM/DD/YY | 1999-01-19 | Sampling date | MM/DD/YY | 1999-02-01 | Sampling date | MM/DD/YY | 1999-02-16 | Sampling date | MM/DD/YY | 1999-03-01 | Sampling date | MM/DD/YY | 1999-03-15 | Sampling date | MM/DD/YY | 1999-03-15
Sampling time | hh:mm | 8:22 | Sampling time | hh:mm | 8:00 | Sampling time | hh:mm | 9:20 | Sampling time | hh:mm | 8:30 | Sampling time | hh:mm | 8:36 | Sampling time | hh:mm | 8:36
Operation time | hh.hh | 29244.53 | Operation time | hh.hh | 29515.9 | Operation time | hh.hh | 29859.5 | Operation time | hh.hh | 30145.1 | Operation time | hh.hh | 30456.8 | Operation time | hh.hh | 30456.8
pH | --- | 7.24 | pH | --- | 7.17 | pH | --- | 7.3 | pH | --- | 7.28 | pH | --- | 7.31 | pH | --- | 7.31
Temperature | oC | 24.4 | Temperature | oC | 24.3 | Temperature | oC | 24 | Temperature | oC | 24 | Temperature | oC | 24 | Temperature | oC | 24
Alkalinity | mg/L as CaCO3 | 298 | Alkalinity | mg/L as CaCO3 | 302 | Alkalinity | mg/L as CaCO3 | 294 | Alkalinity | mg/L as CaCO3 | 286 | Alkalinity | mg/L as CaCO3 | 290 | Alkalinity | mg/L as CaCO3 | 290
Total dissolved solids | mg/L | 484 | Total dissolved solids | mg/L | 452 | Total dissolved solids | mg/L | 464 | Total dissolved solids | mg/L | 460 | Total dissolved solids | mg/L | 442 | Total dissolved solids | mg/L | 440
Total hardness | mg/L as CaCO3 | 308 | Total hardness | mg/L as CaCO3 | 300 | Total hardness | mg/L as CaCO3 | 304 | Total hardness | mg/L as CaCO3 | 286 | Total hardness | mg/L as CaCO3 | 302 | Total hardness | mg/L as CaCO3 | 292
Calcium hardness | mg/L as CaCO3 | 248 | Calcium hardness | mg/L as CaCO3 | 240 | Calcium hardness | mg/L as CaCO3 | 240 | Calcium hardness | mg/L as CaCO3 | 276 | Calcium hardness | mg/L as CaCO3 | 240 | Calcium hardness | mg/L as CaCO3 | 240
Turbidity | ntu | 0.26 | Turbidity | ntu | 0.23 | Turbidity | ntu | 0.2 | Turbidity | ntu | 0.2 | Turbidity | ntu | 0.25 | Turbidity | ntu | 0.25
Ammonia | mg NH3-N / L | 0.29 | Ammonia | mg NH3-N / L | 0.28 | Ammonia | mg NH3-N / L | 0.42 | Ammonia | mg NH3-N / L | 0.22 | Ammonia | mg NH3-N / L | 0.39 | Ammonia | mg NH3-N / L | 0.39
Total organic carbon | mg/L | 8 | Total organic carbon | mg/L | 8 | Total organic carbon | mg/L | 8 | Total organic carbon | mg/L | 7 | Total organic carbon | mg/L | 8 | Total organic carbon | mg/L | 7
UV254 | cm-1 | 0.23 | UV254 | cm-1 | 0.29 | UV254 | cm-1 | 0.23 | UV254 | cm-1 | 0.232 | UV254 | cm-1 | 0.246 | UV254 | cm-1 | 0.225
SUVA | L/(mg*m) | 2.875 | SUVA | L/(mg*m) | 3.625 | SUVA | L/(mg*m) | 2.875 | SUVA | L/(mg*m) | 3.3143 | SUVA | L/(mg*m) | 3.075 | SUVA | L/(mg*m) | 3.2143

## Sheet1. Weeks 1-10
FIELD-SET 1: PILOT-SCALE MEMBRANE RESULTS: WEEKS 1-10 (FILE: mempilot.xls)
Field 1-1: PWS And Treatment Plant Data |  | Field 1-2: Manufacturer Reported Membrane Characteristics1 |  | Field 1-3: 3-Stage Membrane Pilot System Design Parameters |  | Field 1-4: Foulants And Fouling Indices1 |  | Field 1-5: Pretreatment Used Prior To Membranes1 |  |  | Field 1-6: Membrane Performance Data During Operation With The Test Water | [18 empty] | Field 1-6: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 1-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 1-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 1-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 1-7: System And Stage Water Quality For Week 2 | [9 empty] | Field 1-7: System And Stage Water Quality For Week 2 (continued) | [7 empty] | Field 1-8: System And Stage Water Quality For Week 4 | [9 empty] | Field 1-8: System And Stage Water Quality For Week 4 (continued) | [7 empty] | Field 1-9: System And Stage Water Quality For Week 6 | [9 empty] | Field 1-9: System And Stage Water Quality For Week 6 (continued) | [7 empty] | Field 1-10: System And Stage Water Quality For Week 8 | [9 empty] | Field 1-10: System And Stage Water Quality For Week 8 (continued) | [7 empty] | Field 1-11: System And Stage Water Quality For Week 10 | [9 empty] | Field 1-11: System And Stage Water Quality For Week 10 (continued) | [7 empty] | Field 1-12: Duplicate Analysis Of System And Stage Water Quality For Week 10 | [9 empty] | Field 1-12: Duplicate Analysis Of System And Stage Water Quality For Week 10 (continued) | [7 empty] | Field 1-13: Membrane Cost Parameters
|  | General Information |  | Calculate Temperature Normalized MTCW |  | Parameters Evaluated Prior to Pretreatment |  |  |  |  | System Operating Parameters | [30 empty] | Stage 1 Operating Parameters | [23 empty] | Stage 2 Operating Parameters | [23 empty] | Stage 3 Operating Parameters | [23 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | General Cost Parameters
PWS Name | Collier County Water Department | Membrane manufacturer | Hydranautics | Average yearly temperature of feed water, TavgoC (oC) | 25 | Alkalinity (mg/L as CaCO3) | 290 | Process | Description | Scale | Date | Time | Operation |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  |  |  | System recovery during sample collection (decimal) | 0.89 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.6 | [6 empty] | System recovery during sample collection (decimal) | 0.9 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.6 | [6 empty] | System recovery during sample collection (decimal) | 0.8939 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.6003 | [6 empty] | System recovery during sample collection (decimal) | 0.89 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.6 | [6 empty] | System recovery during sample collection (decimal) | 0.89 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.6 | [6 empty] | System recovery during sample collection (decimal) | 0.89 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.6 |  |  |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | FL5114069 | Membrane trade name | PVD 1 | Temperature normalized MTCW (gfd/psi) | 0.24 | Calcium Hardness (mg/L as CaCO3) | 220 | Sulfuric Acid Addition | pH adjustment to 5.8-6.0 | full-scale |  |  | time | Influent | PI | PC | PP | QR | Qp | QW | Cleaning Event | QF | QI | Recovery | Recycle | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) |  |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) |  |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) | [6 empty] | System feed flow rate during sample collection (gpm) | 1452 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 873 | [6 empty] | System feed flow rate during sample collection (gpm) | 1450 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 867 | [6 empty] | System feed flow rate during sample collection (gpm) | 1461 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 877 | [6 empty] | System feed flow rate during sample collection (gpm) | 1449 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 866 | [6 empty] | System feed flow rate during sample collection (gpm) | 1457 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 873 | [6 empty] | System feed flow rate during sample collection (gpm) | 1457 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 873 |  |  |  |  | Capital Recovery Interest Rate (%) | N/A
Water Industry Data Base Number (optional) | NA | Membrane element model number | 8040-LSY-PVD1 |  |  | LSI | 7.26 | Anti-Scalant Addition | Argo Scientific Hyperspearse AS120UL | full-scale | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | Indicate with "X" | (gpm) | (gpm) | (decimal) | ratio | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHF (before acid) | pHF (after acid) | TDSp | TDSF (before acid) | TDSF (after acid) | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) |  |  | System influent flow rate during sample collection (gpm) | 1298 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 1452 | [6 empty] | System influent flow rate during sample collection (gpm) | 1298 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 1450 | [6 empty] | System influent flow rate during sample collection (gpm) | 1306 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 1461 | [6 empty] | System influent flow rate during sample collection (gpm) | 1294 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 1449 | [6 empty] | System influent flow rate during sample collection (gpm) | 1303 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 1457 | [6 empty] | System influent flow rate during sample collection (gpm) | 1303 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 1457 |  |  |  |  | Capital Recovery Period (years) | 25
|  | Molecular weight cutoff (Daltons) | 100-300 | Calculate System Permeate, Feed and Waste Flow Rates |  | Dissolved iron (mg/L) |  | Cartridge Filtration | 5 Micron | full-scale | 1998-04-06 | 2:07 | 24054 | 23.4 | 126.9 | 64 | 37.5192 | 0 | 1300 | 154 |  | 1454 | 1454 | 0.89409 | 0 | 14.013 | 14.6917 | 8.8231 | 49.1077 | 0.29917 | 7.08 | 5.95 | 218 | 379 | 387 | 1702 | 1813.6234 | -6.5584 | 43.6693 | 1100.3117 | 80.1874 | 126.9 | 96 | 49 | 873 | 581 | 1454 | 1454 | 0.43185 | 0.60041 | 15.9452 | 16.7174 | 4.2381 | 58.2119 | 0.28718 | 5.95 |  | 145 | 387 | 695 | 750.6248 | -8.0036 | 62.5323 | 568.8124 | 74.5083 | 96 | 84 | 21 | 307 | 274 | 581 | 581 | 0.36288 | 0.5284 | 11.2146 | 11.7577 | 8.1131 | 60.8869 | 0.19311 |  |  | 175 | 695 | 1282 | 1277.6277 | 0.34105 | 54.7804 | 986.3139 | 82.2572 | 84 | 64 | 21 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.8179 | 13.6877 | 39.3123 | 0.30062 |  | 6.15 | 297 | 1282 | 1702 | 2049.5325 | -20.4191 | 23.2558 | 1665.7662 | 82.1704 | [108 empty] | Overhead & Profit Factor (% of construction costs) | 10
Official ICR Contact Person |  | Membrane material (e.g., PVD, polyamide, etc.) | Poly Vinyl Derivative | Design system recovery, R (decimal) | 0.9 | Total iron (mg/L) | 0.03 |  |  |  | 1998-04-07 | 6:51 | 24082.8 | 24.1 | 131 | 67 | 42.1091 | 0 | 1302 | 145 |  | 1447 | 1447 | 0.89979 | 0 | 14.0346 | 14.413 | 10.2108 | 46.6801 | 0.30876 | 7.07 | 5.94 | 205 | 379 | 391 | 1766 | 2061.1517 | -16.713 | 47.5703 | 1226.0759 | 83.28 | 131 | 99 | 54 | 871 | 576 | 1447 | 1447 | 0.4293 | 0.60194 | 15.9087 | 16.3376 | 4.478 | 56.522 | 0.28905 | 5.94 |  | 136 | 391 | 712 | 776.599 | -9.0729 | 65.2174 | 583.7995 | 76.7043 | 99 | 88 | 25 | 310 | 266 | 576 | 576 | 0.35736 | 0.53819 | 11.3242 | 11.6295 | 9.1164 | 59.3836 | 0.19584 |  |  | 136 | 712 | 1331 | 1383.2782 | -3.9277 | 65.2174 | 1047.6391 | 87.0184 | 88 | 67 | 25 | 121 | 145 | 266 | 266 | 0.44855 | 0.45489 | 11.3659 | 11.6724 | 14.9661 | 37.5339 | 0.31098 |  | 6.27 | 275 | 1331 | 1766 | 2212.2138 | -25.2669 | 29.6675 | 1771.6069 | 84.4774 | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | Special Sitework Factor (% of construction costs) | N/A
Mailing Address |  | Membrane construction (e.g., thin-film composite) | Thin Film Composite | Design average system flux, FW (gfd) | 15 | Dissolved aluminum (mg/L) |  |  |  |  | 1998-04-08 | 1:59 | 24101.9 | 23.5 | 127.2 | 64 | 37.5192 | 0 | 1298 | 154 |  | 1452 | 1452 | 0.89394 | 0 | 13.9915 | 14.6258 | 7.5607 | 50.5201 | 0.2895 | 7.1 | 6.04 | 240 | 381 | 385 | 1648 | 1607.1429 | 2.4792 | 37.6623 | 996.0714 | 75.9053 | 127.2 | 96 | 49 | 870 | 582 | 1452 | 1452 | 0.43164 | 0.59917 | 15.8904 | 16.6108 | 4.089 | 58.511 | 0.28389 | 6.04 | 6.19 | 151 | 385 | 702 | 734.7938 | -4.6715 | 60.7792 | 559.8969 | 73.0307 | 96 | 85 | 21 | 307 | 279 | 586 | 586 | 0.36712 | 0.52389 | 11.2146 | 11.723 | 7.9989 | 61.5011 | 0.19062 | 6.19 | 6.27 | 186 | 702 | 1221 | 1269.7849 | -3.9955 | 51.6883 | 985.8925 | 81.1338 | 85 | 64 | 21 | 120 | 159 | 279 | 279 | 0.47802 | 0.43011 | 11.272 | 11.783 | 12.3274 | 41.1726 | 0.28619 | 6.27 | 6.27 | 326 | 1221 | 1648 | 1896.4717 | -15.0772 | 15.3247 | 1558.7358 | 79.0856 | Parameter | Units | Cp-sys-2 | CF-sys-2 | CC-sys-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-2 | CI-s1-2 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-4 | CF-sys-4 | CC-sys-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-4 | CI-s1-4 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-6 | CF-sys-6 | CC-sys-6 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-6 | CI-s1-6 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-8 | CF-sys-8 | CC-sys-8 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-8 | CI-s1-8 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-10 | CF-sys-10 | CC-sys-10 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-10 | CI-s1-10 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-10 (dup) | CF-sys-10 (dup) | CC-sys-10 (dup) | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-10 (dup) | CI-s1-10 (dup) | CC(calc) | RF (%) | CB | RB (%) | Construction Contingencies (% of construction costs) | N/A
|  | Membrane hydrophobicity | Hydrophillic | Number of elements per pressure vessel, Ne | 6 | Total aluminum (mg/L) | <0.10 |  |  |  | 1998-04-09 | 4:11 | 24128.1 | 24.1 | 128 | 67 | 37.1091 | 0 | 1301 | 159 |  | 1460 | 1460 | 0.8911 | 0 | 14.0238 | 14.4019 | 7.9932 | 52.3977 | 0.27486 | 7.06 | 6.13 | 237 | 379 | 394 | 1619 | 1678.6352 | -3.6835 | 39.8477 | 1036.3176 | 77.1306 | 128 | 96 | 49 | 874 | 586 | 1460 | 1460 | 0.43418 | 0.59863 | 15.9635 | 16.3938 | 4.1723 | 58.8277 | 0.27868 | 6.13 | 6.27 | 155 | 394 | 702 | 750.4608 | -6.9032 | 60.6599 | 572.2304 | 72.913 | 96 | 85 | 20 | 307 | 279 | 586 | 586 | 0.36712 | 0.52389 | 11.2146 | 11.517 | 8.4795 | 62.0205 | 0.1857 | 6.27 | 6.33 | 155 | 702 | 1260 | 1303.8961 | -3.4838 | 60.6599 | 1002.948 | 84.5456 | 85 | 67 | 20 | 120 | 159 | 279 | 279 | 0.47802 | 0.43011 | 11.272 | 11.5759 | 12.8645 | 43.1355 | 0.26836 | 6.33 | 6.39 | 326 | 1260 | 1619 | 1964.9057 | -21.3654 | 17.2589 | 1612.4528 | 79.7824 | Sampling date | MM/DD/YY | 1998-04-13 | 1998-04-13 | 1998-04-13 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-04-13 | 1999-04-13 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-04-27 | 1998-04-27 | 1998-04-27 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-04-27 | 1998-04-27 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-05-11 | 1998-05-11 | 1998-05-11 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-05-11 | 1998-05-11 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-05-26 | 1998-05-26 | 1998-05-26 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-05-26 | 1998-05-26 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-06-09 | 1998-06-09 | 1998-06-09 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-06-09 | 1998-06-09 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-06-09 | 1998-06-09 | 1998-06-09 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-06-09 | 1998-06-09 | --- | --- | --- | --- | Engineering Fee Factor (% of construction costs) | 19
Phone Number |  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Negative | Number of parallel pressure vessels in stage 1, Nv-s(1) | 36 | Fluoride (mg/L) | 0.3 |  |  |  | 1998-04-10 | 2:17 | 24150.2 | 23.5 | 127.6 | 65 | 37.5192 | 0 | 1301 | 155 |  | 1456 | 1456 | 0.89354 | 0 | 14.0238 | 14.6596 | 7.9511 | 50.8298 | 0.28841 | 7.04 | 5.96 | 239 | 392 | 392 | 1651 | 1676.2129 | -1.5271 | 39.0306 | 1034.1065 | 76.8883 | 127.6 | 96 | 49 | 874 | 582 | 1456 | 1456 | 0.43249 | 0.60027 | 15.9635 | 16.6872 | 4.2021 | 58.5979 | 0.28477 | 5.96 | 6.11 | 152 | 392 | 698 | 752.4124 | -7.7955 | 61.2245 | 572.2062 | 73.4361 | 96 | 84 | 21 | 307 | 275 | 582 | 582 | 0.36373 | 0.52749 | 11.2146 | 11.723 | 7.9935 | 61.0065 | 0.19216 | 6.11 | 6.18 | 185 | 698 | 1240 | 1270.6945 | -2.4754 | 52.8061 | 984.3473 | 81.2058 | 84 | 65 | 21 | 120 | 155 | 275 | 275 | 0.46929 | 0.43636 | 11.272 | 11.783 | 12.7058 | 40.7942 | 0.28884 | 6.18 | 6.21 | 324 | 1240 | 1651 | 1949.1613 | -18.0594 | 17.3469 | 1594.5806 | 79.6812 | Sampling time | hh:mm | 9:52 | 9:57 | 10:03 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 10:17 | 9:57 | --- | --- | --- | --- | Sampling time | hh:mm | 8:54 | 9:07 | 9:17 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 8:59 | 9:07 | --- | --- | --- | --- | Sampling time | hh:mm | 8:18 | 8:33 | 8:43 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 8:23 | 8:33 | --- | --- | --- | --- | Sampling time | hh:mm | 8:03 | 8:19 | 8:33 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 8:10 | 8:19 | --- | --- | --- | --- | Sampling time | hh:mm | 8:11 | 8:37 | 8:58 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 8:26 | 8:37 | --- | --- | --- | --- | Sampling time | hh:mm | 8:11 | 8:37 | 8:58 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 8:26 | 8:37 | --- | --- | --- | --- | 1998 ENR Construction Cost Index (CCI base year 1913) | 5895.11
FAX Number |  |  |  | Number of parallel pressure vessels in stage 2, Nv-s(2) | 18 | Phosphate (mg/L) | 0.05mg/L as PO4 |  |  |  | 1998-04-11 | 9:30 | 24181.3 | 23.9 | 128 | 65 | 37.1091 | 0 | 1300 | 154 |  | 1454 | 1454 | 0.89409 | 0 | 14.013 | 14.4761 | 7.3613 | 52.0296 | 0.27823 |  | 6.08 | 248 |  | 389 | 1588 | 1579.2597 | 0.55039 | 36.2468 | 984.1299 | 74.8001 | 128 | 96 | 49 | 872 | 582 | 1454 | 1454 | 0.43206 | 0.59972 | 15.9269 | 16.4533 | 4.0055 | 58.9945 | 0.2789 | 6.08 | 6.23 | 160 | 389 | 681 | 732.1065 | -7.5046 | 58.8689 | 560.5533 | 71.4568 | 96 | 85 | 20 | 308 | 274 | 582 | 582 | 0.3633 | 0.52921 | 11.2511 | 11.623 | 7.6384 | 62.8616 | 0.1849 | 6.23 | 6.36 | 192 | 681 | 1210 | 1230.6788 | -1.709 | 50.6427 | 955.8394 | 79.9129 | 85 | 65 | 20 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.6445 | 12.1174 | 42.8826 | 0.27154 | 6.36 | 6.42 | 338 | 1210 | 1588 | 1889.4805 | -18.9849 | 13.1105 | 1549.7403 | 78.1899 | Operation time | hh.hh | 24229.7 | 24229.8 | 24229.9 | --- | --- | --- | --- | --- | Operation time | hh.hh | 24230.1 | 24229.8 | --- | --- | --- | --- | Operation time | hh.hh | 24539 | 24539.2 | 24539.4 | --- | --- | --- | --- | --- | Operation time | hh.hh | 24539.1 | 24539.2 | --- | --- | --- | --- | Operation time | hh.hh | 24874.1 | 24874.4 | 24874.6 | --- | --- | --- | --- | --- | Operation time | hh.hh | 24874.2 | 24874.4 | --- | --- | --- | --- | Operation time | hh.hh | 25214.4 | 25214.67 | 25214.9 | --- | --- | --- | --- | --- | Operation time | hh.hh | 25214.52 | 25214.67 | --- | --- | --- | --- | Operation time | hh.hh | 25525.9 | 25526.4 | 25526.7 | --- | --- | --- | --- | --- | Operation time | hh.hh | 25526.2 | 25526.4 | --- | --- | --- | --- | Operation time | hh.hh | 25525.9 | 25526.4 | 25526.7 | --- | --- | --- | --- | --- | Operation time | hh.hh | 25526.2 | 25526.4 | --- | --- | --- | --- | 1998 Producers Price Index (PPI base year 1967 = 100) | 123.9
E-Mail Address (optional) |  | Design Parameters |  | Number of parallel pressure vessels in stage 3, Nv-s(3) | 7 | Sulfate (mg/L) | 20 |  |  |  | 1998-04-12 | 9:40 | 24205.4 | 24.1 | 129 | 66 | 37.6991 | 0 | 1302 | 155 |  | 1457 | 1457 | 0.89362 | 0 | 14.0346 | 14.413 | 7.54 | 52.2609 | 0.27579 |  | 6.09 | 236 |  | 381 | 1602 | 1599 | 0.18727 | 38.0577 | 990 | 76.1616 | 129 | 95 | 50 | 873 | 584 | 1457 | 1457 | 0.43312 | 0.59918 | 15.9452 | 16.3751 | 3.8968 | 58.1032 | 0.28183 | 6.09 | 6.22 | 158 | 381 | 692 | 714.3545 | -3.2304 | 58.5302 | 547.6772 | 71.1509 | 95 | 85 | 20 | 309 | 275 | 584 | 584 | 0.36458 | 0.52911 | 11.2877 | 11.592 | 7.7466 | 62.2534 | 0.18621 | 6.22 | 6.35 | 196 | 692 | 1220 | 1249.3236 | -2.4036 | 48.5564 | 970.6618 | 79.8076 | 85 | 66 | 20 | 120 | 155 | 275 | 275 | 0.46929 | 0.43636 | 11.272 | 11.5759 | 12.1232 | 43.3768 | 0.26687 | 6.35 | 6.44 | 346 | 1220 | 1602 | 1896.6452 | -18.3923 | 9.1864 | 1558.3226 | 77.7966 | pH | --- | 6.39 | 6.21 | 6.44 | --- | --- | --- | --- | --- | pH | --- | 6.17 | 6.21 | --- | --- | --- | --- | pH | --- | 6.61 | 6.48 | 6.64 | --- | --- | --- | --- | --- | pH | --- | 6.29 | 6.48 | --- | --- | --- | --- | pH | --- | 6.39 | 6.3 | 6.49 | --- | --- | --- | --- | --- | pH | --- | 6.24 | 6.3 | --- | --- | --- | --- | pH | --- | 6.21 | 6.05 | 6.18 | --- | --- | --- | --- | --- | pH | --- | 6 | 6.05 | --- | --- | --- | --- | pH | --- | 6.26 | 6.12 | 6.29 | --- | --- | --- | --- | --- | pH | --- | 6.1 | 6.12 | --- | --- | --- | --- | pH | --- | 6.26 | 6.12 | 6.29 | --- | --- | --- | --- | --- | pH | --- | 6.1 | 6.12 | --- | --- | --- | --- | Labor Rate + Fringe ($/work-hour) | 24.39
|  | Element size (e.g., 2.5" x 40", 4" x 40", etc.) | 8" X 40" | Permeate flow rate per element, Qp-e (gpm) | 3.8021 | Calcium (mg/L) | 82 |  |  |  | 1998-04-13 | 5:49 | 24225.7 | 23.7 | 128 | 64 | 37.1091 | 0 | 1299 | 157 |  | 1456 | 1456 | 0.89217 | 0 | 14.0022 | 14.5508 | 7.1404 | 51.7505 | 0.28117 | 7.03 | 6.2 | 251 | 380 | 390 | 1606 | 1540.0701 | 4.1052 | 35.641 | 965.035 | 73.9906 | 128 | 96 | 49 | 870 | 586 | 1456 | 1456 | 0.43333 | 0.59753 | 15.8904 | 16.5129 | 4.0422 | 58.9578 | 0.28008 | 6.2 | 6.38 | 158 | 390 | 695 | 734.4369 | -5.6744 | 59.4872 | 562.2184 | 71.897 | 96 | 84 | 20 | 309 | 277 | 586 | 586 | 0.36628 | 0.5273 | 11.2877 | 11.7299 | 7.8044 | 62.1956 | 0.1886 | 6.38 | 6.42 | 194 | 695 | 1235 | 1253.8773 | -1.5285 | 50.2564 | 974.4386 | 80.0911 | 84 | 64 | 20 | 120 | 157 | 277 | 277 | 0.47365 | 0.43321 | 11.272 | 11.7136 | 12.3427 | 41.6573 | 0.28119 | 6.42 | 6.46 | 342 | 1235 | 1606 | 1917.5478 | -19.399 | 12.3077 | 1576.2739 | 78.3033 | Temperature | oC | 24.3 | 24.9 | 24.1 | --- | --- | --- | --- | --- | Temperature | oC | 24.4 | 24.9 | --- | --- | --- | --- | Temperature | oC | 24.5 | 24.5 | 24.1 | --- | --- | --- | --- | --- | Temperature | oC | 24.4 | 24.5 | --- | --- | --- | --- | Temperature | oC | 24.4 | 25 | 25.2 | --- | --- | --- | --- | --- | Temperature | oC | 24.7 | 25 | --- | --- | --- | --- | Temperature | oC | 24.8 | 25.2 | 25.4 | --- | --- | --- | --- | --- | Temperature | oC | 25 | 25.2 | --- | --- | --- | --- | Temperature | oC | 25.2 | 25.3 | 25.5 | --- | --- | --- | --- | --- | Temperature | oC | 25.2 | 25.3 | --- | --- | --- | --- | Temperature | oC | 25.2 | 25.3 | 25.5 | --- | --- | --- | --- | --- | Temperature | oC | 25.2 | 25.3 | --- | --- | --- | --- | Labor Overhead Factor (% of labor) | 10
Technical ICR Contact Person |  | Active membrane area of membrane element used, A (ft2) | 365 | Permeate flow rate per pressure vessel, Qp-v (gpm) | 22.8125 | Barium (mg/L) | 0.008 |  |  |  | 1998-04-14 | 1:53 | 24245.8 | 23.8 | 128.3 | 66 | 37.5192 | 0 | 1302 | 160 |  | 1462 | 1462 | 0.89056 | 0 | 14.0346 | 14.5413 | 7.8566 | 51.7743 | 0.28086 | 7.04 | 6.06 | 236 | 355 | 391 | 1643 | 1652.3125 | -0.5668 | 39.6419 | 1021.6562 | 76.9003 | 128.3 | 96 | 49 | 875 | 587 | 1462 | 1462 | 0.43482 | 0.5985 | 15.9817 | 16.5588 | 4.1888 | 58.9612 | 0.28084 | 6.06 | 6.11 | 151 | 391 | 695 | 748.7513 | -7.734 | 61.3811 | 569.8756 | 73.503 | 96 | 84 | 21 | 307 | 280 | 587 | 587 | 0.36797 | 0.523 | 11.2146 | 11.6195 | 7.9114 | 61.0886 | 0.19021 | 6.11 | 6.2 | 184 | 695 | 1256 | 1255.275 | 0.057723 | 52.9412 | 975.1375 | 81.1309 | 84 | 66 | 21 | 120 | 160 | 280 | 280 | 0.4802 | 0.42857 | 11.272 | 11.679 | 12.8425 | 41.1575 | 0.28376 | 6.2 | 6.21 | 322 | 1256 | 1643 | 1956.5 | -19.0809 | 17.6471 | 1606.25 | 79.9533 | Alkalinity | mg/L as CaCO3 | 130 | NA | 280 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 78 | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 164 | 138 | 320 | -96 | 130 | -18.8406 | 34.7011 | -372.6078 | Alkalinity | mg/L as CaCO3 | 89 | 138 | 210.8696 | 35.5072 | 174.4348 | 48.9781 | Alkalinity | mg/L as CaCO3 | 151 | 129 | 295 | -56.3516 | 119.1022 | -17.0543 | 47.3233 | -219.082 | Alkalinity | mg/L as CaCO3 | 88 | 129 | 190.5702 | 31.7829 | 159.7851 | 44.926 | Alkalinity | mg/L as CaCO3 | 104 | 86 | 180 | -59.6364 | 133.1313 | -20.9302 | 21.9042 | -374.7938 | Alkalinity | mg/L as CaCO3 | 62 | 86 | 121.6501 | 27.907 | 103.825 | 40.2842 | Alkalinity | mg/L as CaCO3 | 128 | 78 | 210 | -326.5455 | 255.4978 | -64.1026 | -100.3664 | 227.5328 | Alkalinity | mg/L as CaCO3 | 100 | 78 | 45.113 | -28.2051 | 61.5565 | -62.4524 | Alkalinity | mg/L as CaCO3 | 128 | 76 | 210 | -344.7273 | 264.1558 | -68.4211 | -109.501 | 216.8939 | Alkalinity | mg/L as CaCO3 | 99 | 76 | 41.6182 | -30.2632 | 58.8091 | -68.3414 | Electric Rate ($/kW-h) | 0.05
Mailing Address |  | Design flux, FW (gfd) | 30 | Permeate flow rate from stage 1, Qp-s(1) (gpm) | 821.25 | Strontium (mg/L) | 0.6 |  |  |  | 1998-04-15 | 3:39 | 24271.16 | 21.9 | 128 | 65 | 37.1091 | 0 | 1302 | 143 |  | 1445 | 1445 | 0.90104 | 0 | 14.0346 | 15.3814 | 9.4947 | 49.8962 | 0.30827 | 7.08 | 6.03 | 221 | 385 | 392 | 1693 | 1948.9371 | -15.1174 | 43.6224 | 1170.4685 | 81.1187 | 128.3 | 96 | 49 | 871 | 574 | 1445 | 1445 | 0.42845 | 0.60277 | 15.9087 | 17.4353 | 4.3264 | 58.8236 | 0.2964 | 6.03 | 6.15 | 146 | 392 | 718 | 765.2857 | -6.5858 | 62.7551 | 578.6429 | 74.7685 | 96 | 85 | 20 | 310 | 264 | 574 | 574 | 0.35567 | 0.54007 | 11.3242 | 12.4109 | 8.6339 | 61.8661 | 0.20061 | 6.15 | 6.17 | 174 | 718 | 1303 | 1356.7879 | -4.128 | 55.6122 | 1037.3939 | 83.2272 | 85 | 65 | 20 | 121 | 143 | 264 | 264 | 0.44419 | 0.45833 | 11.3659 | 12.4566 | 14.3019 | 40.6981 | 0.30607 | 6.17 | 6.19 | 298 | 1303 | 1693 | 2153.3846 | -27.1934 | 23.9796 | 1728.1923 | 82.7565 | Total dissolved solids | mg/L | 270 | NA | 3176 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids |  | 170 | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 290 | 508 | 2988 | 2470 | 17.336 | 42.9134 | 1374.1217 | 78.8956 | Total dissolved solids | mg/L | 174 | 508 | 1004.7033 | 65.748 | 756.3516 | 76.9948 | Total dissolved solids | mg/L | 292 | 523 | 3072 | 2469.1913 | 19.6227 | 44.1683 | 1380.6058 | 78.8499 | Total dissolved solids | mg/L | 195 | 523 | 1015.5616 | 62.7151 | 769.2808 | 74.6516 | Total dissolved solids | mg/L | 246 | 540 | 3416 | 2918.7273 | 14.5572 | 54.4444 | 1586.8974 | 84.4981 | Total dissolved solids | mg/L | 170 | 540 | 1089.6055 | 68.5185 | 814.8027 | 79.1361 | Total dissolved solids | mg/L | 240 | 572 | 3452 | 3258.1818 | 5.6147 | 58.042 | 1756.3526 | 86.3353 | Total dissolved solids | mg/L | 166 | 572 | 1178.9144 | 70.979 | 875.4572 | 81.0385 | Total dissolved solids | mg/L | 260 | 564 | 3440 | 3023.6364 | 12.1036 | 53.9007 | 1648.4675 | 84.2278 | Total dissolved solids | mg/L | 164 | 564 | 1161.9452 | 70.922 | 862.9726 | 80.9959 | Fuel Oil Rate ($/gal) | 0.43
|  | Net driving pressure at the design flux, NDP (psi) | 125 | Permeate flow rate from stage 2, Qp-s(2) (gpm) | 410.625 | Reactive silica (mg/L as SiO2) | 18 |  |  |  | 1998-04-16 | 11:15 | 24300.8 | 23.9 | 129 | 64 | 36.5192 | 0 | 1271 | 148 |  | 1419 | 1419 | 0.8957 | 0 | 13.7004 | 14.1532 | 7.3056 | 52.6752 | 0.26869 |  | 6.28 | 254 |  | 392 | 1565 | 1577.1216 | -0.77454 | 35.2041 | 984.5608 | 74.2017 | 129 | 97 | 48 | 856 | 563 | 1419 | 1419 | 0.4206 | 0.60324 | 15.6347 | 16.1514 | 3.9781 | 61.0219 | 0.26468 | 6.28 | 6.33 | 166 | 392 | 687 | 735.6163 | -7.0766 | 57.6531 | 563.8082 | 70.5574 | 97 | 84 | 20 | 299 | 262 | 561 | 561 | 0.3493 | 0.53298 | 10.9224 | 11.2833 | 7.7117 | 62.7883 | 0.1797 | 6.33 | 6.5 | 196 | 687 | 1211 | 1247.3397 | -3.0008 | 50 | 967.1698 | 79.7347 | 84 | 64 | 20 | 116 | 148 | 264 | 264 | 0.44964 | 0.43939 | 10.8963 | 11.2564 | 12.0955 | 41.9045 | 0.26862 | 6.5 | 6.58 | 342 | 1211 | 1565 | 1892.1081 | -20.9015 | 12.7551 | 1551.5541 | 77.9576 | Total hardness | mg/L as CaCO3 | 148 | NA | 1930 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 88 | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 168 | 300 | 1890 | 1488 | 21.2698 | 44 | 824.4407 | 79.6225 | Total hardness | mg/L as CaCO3 | 94 | 300 | 606.3499 | 68.6667 | 453.175 | 79.2575 | Total hardness | mg/L as CaCO3 | 169 | 302 | 1900 | 1422.5344 | 25.1298 | 44.0397 | 795.773 | 78.7628 | Total hardness | mg/L as CaCO3 | 91 | 302 | 618.8613 | 69.8675 | 460.4307 | 80.2359 | Total hardness | mg/L as CaCO3 | 118 | 299 | 2075 | 1763.4545 | 15.0142 | 60.5351 | 943.5184 | 87.4936 | Total hardness | mg/L as CaCO3 | 75 | 299 | 631.7341 | 74.9164 | 465.3671 | 83.8837 | Total hardness | mg/L as CaCO3 | 126 | 300 | 1990 | 1707.8182 | 14.18 | 58 | 920.7149 | 86.315 | Total hardness | mg/L as CaCO3 | 82 | 300 | 625.8801 | 72.6667 | 462.9401 | 82.2871 | Total hardness | mg/L as CaCO3 | 126 | 300 | 2010 | 1707.8182 | 15.0339 | 58 | 920.7149 | 86.315 | Total hardness | mg/L as CaCO3 | 81 | 300 | 627.375 | 73 | 463.6875 | 82.5313 | Natural Gas Rate ($/ft3) | N/A
Phone Number |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.24 | Permeate flow rate from stage 3, Qp-s(3) (gpm) | 159.6875 | Turbidity (ntu) | <0.5 |  |  |  | 1998-04-17 | 1:30 | 24314.8 | 23.6 | 129.5 | 65 | 37.5192 | 0 | 1302 | 153 |  | 1455 | 1455 | 0.89485 | 0 | 14.0346 | 14.6276 | 7.4094 | 52.3214 | 0.27957 | 7.09 | 6.24 | 260 | 395 | 401 | 1570 | 1600.8824 | -1.967 | 35.1621 | 1000.9412 | 74.0244 | 129.5 | 96 | 49 | 874 | 581 | 1455 | 1455 | 0.43206 | 0.60069 | 15.9635 | 16.6379 | 4.0475 | 59.7025 | 0.27868 | 6.24 | 6.37 | 164 | 395 | 669 | 742.494 | -10.9856 | 59.1022 | 568.747 | 71.1647 | 96 | 84 | 21 | 308 | 273 | 581 | 581 | 0.36246 | 0.53012 | 11.2511 | 11.7265 | 7.3044 | 61.6956 | 0.19007 | 6.37 | 6.37 | 202 | 669 | 1204 | 1195.8718 | 0.6751 | 49.6259 | 932.4359 | 78.3363 | 84 | 64 | 21 | 120 | 153 | 273 | 273 | 0.46492 | 0.43956 | 11.272 | 11.7483 | 11.8751 | 41.1249 | 0.28567 | 6.37 | 6.38 | 351 | 1204 | 1570 | 1873.0196 | -19.3006 | 12.4688 | 1538.5098 | 77.1857 | Calcium hardness | mg/L as CaCO3 | 113 | NA | 1400 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 68 | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 126 | 232 | 1420 | 1186 | 16.4789 | 45.6897 | 653.1418 | 80.7086 | Calcium hardness | mg/L as CaCO3 | 69 | 232 | 474.4031 | 70.2586 | 353.2015 | 80.4644 | Calcium hardness | mg/L as CaCO3 | 134 | 244 | 1420 | 1170.7578 | 17.5523 | 45.082 | 652.3837 | 79.4599 | Calcium hardness | mg/L as CaCO3 | 72 | 244 | 502.2945 | 70.4918 | 373.1473 | 80.7047 | Calcium hardness | mg/L as CaCO3 | 86 | 226 | 1450 | 1358.7273 | 6.2947 | 61.9469 | 724.5226 | 88.1301 | Calcium hardness | mg/L as CaCO3 | 55 | 226 | 480.0069 | 75.6637 | 353.0034 | 84.4194 | Calcium hardness | mg/L as CaCO3 | 102 | 242 | 1430 | 1374.7273 | 3.8652 | 57.8512 | 741.4258 | 86.2427 | Calcium hardness | mg/L as CaCO3 | 65 | 242 | 506.5908 | 73.1405 | 374.2954 | 82.634 | Calcium hardness | mg/L as CaCO3 | 106 | 246 | 1450 | 1378.7273 | 4.9154 | 56.9106 | 745.4258 | 85.7799 | Calcium hardness | mg/L as CaCO3 | 66 | 246 | 515.0753 | 73.1707 | 380.5377 | 82.6561 | Current Process Water Rate ($/1000 gal) | 1.9
FAX Number |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | Permeate flow rate from system, Qp-sys (gpm) | 1391.5625 | SDI | 1.0-1.5 |  |  |  | 1998-04-18 | 5:00 | 24328.9 | 23.8 | 129 | 65 | 37.1091 | 0 | 1305 | 153 |  | 1458 | 1458 | 0.89506 | 0 | 14.0669 | 14.5748 | 7.0547 | 52.8361 | 0.27585 |  | 6.24 | 252 |  | 386 | 1610 | 1528.9412 | 5.0347 | 34.715 | 957.4706 | 73.6807 | 129 | 96 | 49 | 875 | 583 | 1458 | 1458 | 0.43312 | 0.60014 | 15.9817 | 16.5588 | 3.8684 | 59.6316 | 0.27769 | 6.24 | 6.36 | 165 | 386 | 680 | 717.6895 | -5.5426 | 57.2539 | 551.8448 | 70.1003 | 96 | 85 | 20 | 310 | 273 | 583 | 583 | 0.3633 | 0.53173 | 11.3242 | 11.7331 | 7.3685 | 63.1315 | 0.18585 | 6.36 | 6.38 | 210 | 680 | 1212 | 1213.6996 | -0.14023 | 45.5959 | 946.8498 | 77.8212 | 85 | 65 | 20 | 120 | 153 | 273 | 273 | 0.46492 | 0.43956 | 11.272 | 11.679 | 12.07 | 42.93 | 0.27205 | 6.38 | 6.39 | 345 | 1212 | 1610 | 1892 | -17.5155 | 10.6218 | 1552 | 77.7706 | Turbidity | ntu | 0.05 | NA | 22.5 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.065 | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.04 | 0.18 | 17 | 1.44 | 91.5294 | 77.7778 | 0.73622 | 94.5669 | Turbidity | ntu | 0.04 | 0.18 | 0.3882 | 77.7778 | 0.2841 | 85.9204 | Turbidity | ntu | 0.07 | 0.165 | 20 | 0.96538 | 95.1731 | 57.5758 | 0.5177 | 86.4785 | Turbidity | ntu | 0.04 | 0.165 | 0.35271 | 75.7576 | 0.25886 | 84.5475 | Turbidity | ntu | 0.095 | 0.21 | 20 | 1.1405 | 94.2977 | 54.7619 | 0.6195 | 84.6651 | Turbidity | ntu | 0.05 | 0.21 | 0.44767 | 76.1905 | 0.32883 | 84.7947 | Turbidity | ntu | 0.08 | 0.15 | 18 | 0.71636 | 96.0202 | 46.6667 | 0.39971 | 79.9856 | Turbidity | ntu | 0.045 | 0.15 | 0.30696 | 70 | 0.22848 | 80.3046 | Turbidity | ntu | 0.09 | 0.15 | 17.5 | 0.63545 | 96.3688 | 40 | 0.36404 | 75.2774 | Turbidity | ntu | 0.041 | 0.15 | 0.31294 | 72.6667 | 0.23147 | 82.2871 | Modifications to Existing Plant (% of construction costs) | N/A
E-Mail Address (optional) |  | Maximum flow rate to the element, QI, max (gpm) | 75 | Feed flow rate to system, QF-sys (gpm) | 1546.1806 | MFI |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | 1998-04-19 | 9:50 | 24366.9 | 23.9 | 128 | 64 | 37.1091 | 0 | 1299 | 154 |  | 1453 | 1453 | 0.89401 | 0 | 14.0022 | 14.465 | 7.5132 | 51.3776 | 0.28154 |  | 6.25 | 248 |  | 392 | 1520 | 1606.6494 | -5.7006 | 36.7347 | 999.3247 | 75.1832 | 128 | 96 | 49 | 871 | 582 | 1453 | 1453 | 0.43185 | 0.59945 | 15.9087 | 16.4344 | 3.9162 | 59.0838 | 0.27815 | 6.25 | 6.29 | 168 | 392 | 676 | 727.2302 | -7.5784 | 57.1429 | 559.6151 | 69.9794 | 96 | 85 | 20 | 308 | 274 | 582 | 582 | 0.3633 | 0.52921 | 11.2511 | 11.623 | 6.7793 | 63.7207 | 0.18241 | 6.29 | 6.35 | 242 | 676 | 1224 | 1163.854 | 4.9139 | 38.2653 | 919.927 | 73.6936 | 85 | 64 | 20 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.6445 | 11.8951 | 42.6049 | 0.27331 | 6.35 | 6.38 | 368 | 1224 | 1520 | 1891.013 | -24.4087 | 6.1224 | 1557.5065 | 76.3725 | Ammonia | mg NH3-N / L | 0.2 | NA | 0.76 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | 0.11 | 0.11 | 0.61 | 0.11 | 81.9672 | 0 | 0.11 | 0 | Total organic carbon | mg/L | BMRL | 8 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | 0.26 | 0.27 | 0.8 | 0.35425 | 55.7187 | 3.7037 | 0.30713 | 15.3441 | Total organic carbon | mg/L | BMRL | 8 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | 0.205 | 0.23 | 0.828 | 0.43227 | 47.7931 | 10.8696 | 0.31902 | 35.7411 | Total organic carbon | mg/L | BMRL | 8 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | 0.25 | 0.24 | 0.76 | 0.15909 | 79.067 | -4.1667 | 0.20433 | -22.3531 | Total organic carbon | mg/L | BMRL | 7 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | 0.22 | 0.25 | 0.84 | 0.49273 | 41.342 | 12 | 0.35702 | 38.3788 | Total organic carbon | mg/L | BMRL | 7 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | Minimum flow rate to the element, QI, min (gpm) | 72 | Concentrate-waste flow rate from system, QW-sys (gpm) | 154.6181 | MPFI |  | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | 1998-04-20 | 2:06 | 24382.6 | 23.6 | 128.5 | 65 | 37.5192 | 0 | 1303 | 154 |  | 1457 | 1457 | 0.8943 | 0 | 14.0454 | 14.6388 | 7.0089 | 52.2219 | 0.28032 | 7.04 | 6.11 | 258 | 384 | 392 | 1551 | 1525.7792 | 1.6261 | 34.1837 | 958.8896 | 73.0939 | 128.5 | 96 | 49 | 873 | 584 | 1457 | 1457 | 0.43312 | 0.59918 | 15.9452 | 16.6189 | 4.0191 | 59.2309 | 0.28058 | 6.11 | 6.27 | 162 | 392 | 679 | 735.8185 | -8.368 | 58.6735 | 563.9092 | 71.272 | 96 | 84 | 21 | 310 | 274 | 584 | 584 | 0.36415 | 0.53082 | 11.3242 | 11.8027 | 7.531 | 61.469 | 0.19201 | 6.27 | 6.35 | 198 | 679 | 1195 | 1223.1971 | -2.3596 | 49.4898 | 951.0985 | 79.182 | 84 | 65 | 21 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.7483 | 11.7144 | 41.7856 | 0.28116 | 6.35 | 6.44 | 352 | 1195 | 1551 | 1851.8831 | -19.3993 | 10.2041 | 1523.4416 | 76.8944 | Total organic carbon | mg/L | BMRL | NA | 77 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.071 | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 8 | 75 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.0208 | 0.223 | 0.5237 | 90.6726 | 0.37335 | 94.4288 | Total organic carbon | mg/L | BMRL | 8 | 85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.0159 | 0.2335 | 0.56027 | 93.1906 | 0.39689 | 95.9938 | Total organic carbon | mg/L | BMRL | 8 | 71 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.0091 | 0.2545 | 0.61902 | 96.4244 | 0.43676 | 97.9165 | Total organic carbon | mg/L | BMRL | 7 | 71 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.014 | 0.252 | 0.60778 | 94.4444 | 0.42989 | 96.7433 | Total organic carbon | mg/L | BMRL | 7 | 71 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.014 | 0.258 | 0.62275 | 94.5736 | 0.44037 | 96.8209
Plant Name | Collier Co. North Regional Water Plant | Total width of all membrane envelopes in the element, w (ft) | 63.4 |  |  |  |  | is to list the pretreatment processes used in this particular pilot-scale run. |  |  | 1998-04-21 | 4:46 | 24409.2 | 23.9 | 128 | 64 | 37.1091 | 0 | 1303 | 155 |  | 1458 | 1458 | 0.89369 | 0 | 14.0454 | 14.5095 | 6.9723 | 51.9185 | 0.27947 |  | 6.13 | 258 |  | 392 | 1563 | 1518.4645 | 2.8494 | 34.1837 | 955.2323 | 72.9909 | 128 | 96 | 49 | 873 | 585 | 1458 | 1458 | 0.43355 | 0.59877 | 15.9452 | 16.4722 | 3.9987 | 59.0013 | 0.27918 | 6.13 | 6.37 | 163 | 392 | 684 | 733.7385 | -7.2717 | 58.4184 | 562.8692 | 71.0412 | 96 | 84 | 20 | 310 | 275 | 585 | 585 | 0.365 | 0.52991 | 11.3242 | 11.6985 | 7.5993 | 62.4007 | 0.18747 | 6.37 | 6.5 | 198 | 684 | 1207 | 1231.8545 | -2.0592 | 49.4898 | 957.9273 | 79.3304 | 85 | 64 | 20 | 120 | 155 | 275 | 275 | 0.46929 | 0.43636 | 11.272 | 11.6445 | 11.8597 | 42.6403 | 0.27309 | 6.5 | 6.49 | 352 | 1207 | 1563 | 1868.9355 | -19.5736 | 10.2041 | 1537.9677 | 77.1127 | UV254 | cm-1 | 0.019 | NA | 2.15 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | NA | --- | --- | --- | --- | UV254 | cm-1 | 0.026 | 0.223 | 2.22 | 1.996 | 10.0901 | 88.3408 | 1.0057 | 97.4147 | SUVA | L/(mg*m) | NR | 2.7875 | --- | --- | --- | --- | UV254 | cm-1 | 0.0213 | 0.2335 | 2.315 | 2.0213 | 12.6868 | 90.8779 | 1.0213 | 97.9144 | SUVA | L/(mg*m) | NR | 2.9188 | --- | --- | --- | --- | UV254 | cm-1 | 0.0205 | 0.2545 | 2.215 | 2.1478 | 3.0351 | 91.945 | 1.0877 | 98.1154 | SUVA | L/(mg*m) | NR | 3.1812 | --- | --- | --- | --- | UV254 | cm-1 | 0.019 | 0.252 | 2.555 | 2.1372 | 16.353 | 92.4603 | 1.0832 | 98.2459 | SUVA | L/(mg*m) | NR | 3.6 | --- | --- | --- | --- | UV254 | cm-1 | 0.019 | 0.258 | 2.59 | 2.1917 | 15.3773 | 92.6357 | 1.1106 | 98.2892 | SUVA | L/(mg*m) | NR | 3.6857 | --- | --- | --- | ---
Treatment Plant Category | Category II | Feed spacer thickness, T (ft) | 0.0023 | Calculate the Feed Flow Rates at the End of Each Stage | [6 empty] | 1998-04-22 | 10:30 | 24420.7 | 24.1 | 128 | 64 | 37.1091 | 0 | 1302 | 155 |  | 1457 | 1457 | 0.89362 | 0 | 14.0346 | 14.413 | 6.812 | 52.0789 | 0.27675 |  | 6.15 | 259 |  | 390 | 1562 | 1490.4 | 4.5839 | 33.5897 | 940.2 | 72.4527 | 128 | 96 | 49 | 874 | 583 | 1457 | 1457 | 0.43291 | 0.59986 | 15.9635 | 16.3938 | 3.989 | 59.011 | 0.27781 | 6.15 | 6.41 | 162 | 390 | 685 | 731.8045 | -6.8328 | 58.4615 | 560.9022 | 71.118 | 96 | 84 | 20 | 308 | 275 | 583 | 583 | 0.36415 | 0.5283 | 11.2511 | 11.5545 | 7.566 | 62.434 | 0.18507 | 6.41 | 6.48 | 200 | 685 | 1209 | 1228.2 | -1.5881 | 48.7179 | 956.6 | 79.0926 | 84 | 64 | 20 | 120 | 155 | 275 | 275 | 0.46929 | 0.43636 | 11.272 | 11.5759 | 11.8458 | 42.1542 | 0.27461 | 6.48 | 6.5 | 355 | 1209 | 1562 | 1870.1613 | -19.7286 | 8.9744 | 1539.5806 | 76.9418 | SUVA | L/(mg*m) | NR | NA | 2.7922 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | 2.7875 | 2.96 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | 2.9188 | 2.7235 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | 3.1812 | 3.1197 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | 3.6 | 3.5986 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | 3.6857 | 3.6479 | --- | --- | --- | --- | ---
Process Train Name | Train D | Active membrane area of an equivalent 8" x 40" element (ft2) | 365 | Feed flow rate at the end of stage 1, (QF-s(1))end (gpm) | 861.8056 | [5 empty] | 1998-04-23 | 6:42 | 24440.9 | 23.7 | 128 | 64 | 37.1091 | 0 | 1300 | 155 |  | 1455 | 1455 | 0.89347 | 0 | 14.013 | 14.562 | 6.8035 | 52.0873 | 0.27957 |  | 6.09 | 261 |  | 392 | 1653 | 1490.7097 | 9.8179 | 33.4184 | 941.3548 | 72.274 | 128 | 96 | 49 | 872 | 583 | 1455 | 1455 | 0.43249 | 0.59931 | 15.9269 | 16.5509 | 3.9851 | 59.0149 | 0.28045 | 6.09 | 6.37 | 164 | 392 | 690 | 733.0223 | -6.2351 | 58.1633 | 562.5111 | 70.845 | 96 | 84 | 20 | 308 | 275 | 583 | 583 | 0.36415 | 0.5283 | 11.2511 | 11.6919 | 7.644 | 62.356 | 0.1875 | 6.37 | 6.46 | 200 | 690 | 1206 | 1238.8 | -2.7197 | 48.9796 | 964.4 | 79.2617 | 84 | 64 | 20 | 120 | 155 | 275 | 275 | 0.46929 | 0.43636 | 11.272 | 11.7136 | 11.7765 | 42.2235 | 0.27742 | 6.46 | 6.48 | 357 | 1206 | 1563 | 1863.2903 | -19.2124 | 8.9286 | 1534.6452 | 76.7373 | Bromide | mg/L | 160 | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | 160 | 150 | --- | 60 | --- | -6.6667 | 110.2696 | -45.0989 | [8 empty] | Bromide | mg/L | 150 | 140 | --- | 55.7493 | --- | -7.1429 | 102.8742 | -45.8091 | [8 empty] | Bromide | mg/L | 150 | 140 | --- | 59.0909 | --- | -7.1429 | 104.3912 | -43.6902 | [8 empty] | Bromide | mg/L | 150 | 120 | --- | -122.7273 | --- | -25 | 12.9802 | -1055.6075 | [8 empty] | Bromide | mg/L | 150 | 120 | --- | -122.7273 | --- | -25 | 12.9802 | -1055.6075
ICR Treatment Plant Identification Number | 1092 | Purchase price for an equivalent 8" x 40 " element ($) | 800 | Feed flow rate at the end of stage 2, (QF-s(2))end (gpm) | 382.7431 | [5 empty] | 1998-04-24 | 2:27 | 24460.6 | 23.6 | 127.8 | 66 | 37.5192 | 0 | 1301 | 155 |  | 1456 | 1456 | 0.89354 | 0 | 14.0238 | 14.6163 | 6.3401 | 53.0408 | 0.27557 |  | 6.14 | 264 |  | 386 | 1528 | 1410.0129 | 7.7217 | 31.6062 | 898.0065 | 70.6015 | 127.8 | 96 | 49 | 872 | 584 | 1456 | 1456 | 0.43291 | 0.5989 | 15.9269 | 16.5999 | 3.825 | 59.075 | 0.281 | 6.14 | 6.33 | 167 | 386 | 676 | 713 | -5.4734 | 56.7358 | 549.5 | 69.6087 | 96 | 84 | 21 | 309 | 273 | 582 | 582 | 0.36288 | 0.53093 | 11.2877 | 11.7646 | 7.4225 | 61.5775 | 0.19105 | 6.33 | 6.54 | 202 | 676 | 1187 | 1212.5055 | -2.1487 | 47.6684 | 944.2527 | 78.6074 | 84 | 66 | 21 | 120 | 155 | 275 | 275 | 0.46929 | 0.43636 | 11.272 | 11.7483 | 11.4852 | 42.5148 | 0.27633 | 6.51 | 6.41 | 359 | 1187 | 1528 | 1828.0323 | -19.6356 | 6.9948 | 1507.5161 | 76.186 | SDS-Cl2 dose | mg/L | 19.1 | 27.6 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 19.1 | 27.6 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 18.45 | 27.9 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 18 | NR | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | NR | NR | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 18 | 28 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection
PWSID Number of Plant (if assigned) | FL5114069 |  |  | Feed flow rate at the end of stage 3, (QF-s(3))end (gpm) | 181.2326 | [5 empty] | 1998-04-25 | 10:47 | 24492.9 | 23.2 | 128 | 65 | 37.5192 | 0 | 1303 | 154 |  | 1457 | 1457 | 0.8943 | 0 | 14.0454 | 14.8129 | 6.3812 | 52.5996 | 0.28162 |  | 6.19 | 268 |  | 390 | 1550 | 1422.2468 | 8.2421 | 31.2821 | 906.1234 | 70.4235 | 128 | 96 | 49 | 872 | 585 | 1457 | 1457 | 0.43333 | 0.59849 | 15.9269 | 16.7973 | 3.8746 | 59.1254 | 0.2841 | 6.19 | 6.42 | 168 | 390 | 686 | 720.9128 | -5.0893 | 56.9231 | 555.4564 | 69.7546 | 96 | 85 | 21 | 310 | 275 | 585 | 585 | 0.365 | 0.52991 | 11.3242 | 11.943 | 7.5055 | 61.9945 | 0.19265 | 6.42 | 6.51 | 206 | 686 | 1198 | 1227.0909 | -2.4283 | 47.1795 | 956.5455 | 78.4642 | 85 | 65 | 21 | 121 | 154 | 275 | 275 | 0.4682 | 0.44 | 11.3659 | 11.9871 | 11.5886 | 42.4114 | 0.28264 | 6.51 | 6.53 | 366 | 1198 | 1550 | 1851.7143 | -19.4654 | 6.1538 | 1524.8571 | 75.9978 | SDS-Free Cl2 residual | mg/L | 1.05 | NA | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.53 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 2.85 | 0.6 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.53 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 2.56 | 0.8 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.53 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 1.02 | NR | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.53 |  |  |  |  | SDS-Free Cl2 residual | mg/L | NR | NR | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.52 |  |  |  |  | SDS-Free Cl2 residual | mg/L | NR | NR | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.52
Historical Minimum Water Temperature (oC) | 22.7 | Additional Information |  |  |  | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | 1998-04-26 | 11:00 | 24526.8 | 23.3 | 129 | 65 | 37.5192 | 0 | 1300 | 154 |  | 1454 | 1454 | 0.89409 | 0 | 14.013 | 14.7352 | 6.2127 | 53.2681 | 0.27662 |  | 6.18 | 269 |  | 388 | 1585 | 1392.5455 | 12.1422 | 30.6701 | 890.2727 | 69.7845 | 129 | 96 | 49 | 872 | 582 | 1454 | 1454 | 0.43206 | 0.59972 | 15.9269 | 16.7477 | 3.8131 | 59.6869 | 0.28059 | 6.18 | 6.29 | 170 | 388 | 648 | 714.6254 | -10.2817 | 56.1856 | 551.3127 | 69.1645 | 96 | 84 | 21 | 308 | 274 | 582 | 582 | 0.3633 | 0.52921 | 11.2511 | 11.831 | 6.8418 | 62.1582 | 0.19034 | 6.29 | 6.49 | 210 | 648 | 1211 | 1140.3504 | 5.834 | 45.8763 | 894.1752 | 76.5147 | 84 | 65 | 21 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.8529 | 11.8256 | 41.6744 | 0.28442 | 6.49 | 6.5 | 360 | 1211 | 1585 | 1874.1169 | -18.2408 | 7.2165 | 1542.5584 | 76.6621 | SDS-Cl2 demand | mg/L | 18.05 | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 309 |  |  |  |  | SDS-Cl2 demand | mg/L | 16.25 | 27 | --- | 123.75 | --- | 39.8148 | 69.7101 | 76.6892 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 305 |  |  |  |  | SDS-Cl2 demand | mg/L | 15.89 | 27.1 | --- | 121.545 | --- | 41.3653 | 68.718 | 76.8765 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 308 |  |  |  |  | SDS-Cl2 demand | mg/L | 16.98 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 310 |  |  |  |  | SDS-Cl2 demand | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 307 |  |  |  |  | SDS-Cl2 demand | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 307
Historical Average Water Temperature (oC) | 25 | Design cross-flow velocity (fps) | 1 | Calculate the Minimum Recycle Flow Rates for Each Stage1 |  | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | 1998-04-27 | 3:56 | 24534.1 | 23.6 | 128 | 65 | 36.5192 | 0 | 1296 | 152 |  | 1448 | 1448 | 0.89503 | 0 | 13.9699 | 14.5601 | 6.4737 | 53.5071 | 0.27212 | 7.11 | 6.25 | 271 | 384 | 394 | 1551 | 1442.7368 | 6.9802 | 31.2183 | 918.3684 | 70.4911 | 128 | 96 | 48 | 872 | 576 | 1448 | 1448 | 0.42951 | 0.60221 | 15.9269 | 16.5999 | 3.9531 | 60.0469 | 0.27645 | 6.25 | 6.53 | 169 | 394 | 686 | 734.625 | -7.0882 | 57.1066 | 564.3125 | 70.0521 | 96 | 85 | 20 | 305 | 271 | 576 | 576 | 0.35949 | 0.52951 | 11.1416 | 11.6123 | 7.4855 | 63.0145 | 0.18428 | 6..53 | 6.49 | 207 | 686 | 1197 | 1225.0959 | -2.3472 | 47.4619 | 955.548 | 78.337 | 85 | 65 | 20 | 119 | 152 | 271 | 271 | 0.46165 | 0.43911 | 11.1781 | 11.6504 | 11.5073 | 43.4927 | 0.26787 | 6.49 | 6.54 | 370 | 1197 | 1551 | 1844.4539 | -18.9203 | 6.0914 | 1520.727 | 75.6695 | SDS-Chlorination temp. | oC | 24.1 | NA | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 586 |  |  |  |  | SDS-Chlorination temp. | oC | 24.1 | 24.1 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 576 |  |  |  |  | SDS-Chlorination temp. | oC | 22.4 | 22.4 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 582 |  |  |  |  | SDS-Chlorination temp. | oC | 23.5 | NR | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 585 |  |  |  |  | SDS-Chlorination temp. | oC | NR | NR | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 587 |  |  |  |  | SDS-Chlorination temp. | oC | NR | NR | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 587
State Approved Plant Capacity (MGD) | 12 MGD | Required influent flow to permeate flow rate ratio, QI:Qp | 5:1 | Minimum recycle flow rate for stage 1, (QR-s(1))min (gpm) | 1730.1944 | [5 empty] | 1998-04-28 | 2:00 | 24556 | 23.4 | 128.4 | 65 | 37.5192 | 0 | 1299 | 154 |  | 1453 | 1453 | 0.89401 | 0 | 14.0022 | 14.6804 | 5.7393 | 53.4415 | 0.2747 |  | 6.15 | 270 |  | 380 | 1520 | 1307.8571 | 13.9568 | 28.9474 | 843.9286 | 68.0068 | 128.4 | 96 | 49 | 870 | 583 | 1453 | 1453 | 0.43206 | 0.59876 | 15.8904 | 16.66 | 3.7717 | 59.4283 | 0.28034 | 6.15 | 6.28 | 164 | 380 | 672 | 702.3328 | -4.5138 | 56.8421 | 541.1664 | 69.6951 | 96 | 84 | 21 | 309 | 272 | 581 | 581 | 0.36203 | 0.53184 | 11.2877 | 11.8343 | 7.3383 | 61.6617 | 0.19192 | 6.28 | 6.4 | 204 | 672 | 1175 | 1203.6618 | -2.4393 | 46.3158 | 937.8309 | 78.2477 | 84 | 65 | 21 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.8179 | 11.2836 | 42.2164 | 0.27994 | 6.4 | 6.44 | 363 | 1175 | 1520 | 1807.7273 | -18.9294 | 4.4737 | 1491.3636 | 75.6599 | SDS-Chlorination pH | --- | 8.37 | NA | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.26 | 8.24 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.32 | 8.34 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.29 | NR | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | NR | NR | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | NR | NR | --- | --- | --- | --- | --- | ---
|  | Maximum element recovery (%) | 20 | Minimum recycle flow rate for stage 2, (QR-s(2))min (gpm) | 913.2569 | [5 empty] | 1998-04-29 | 3:52 | 24581.9 | 23.5 | 128 | 62 | 37.1091 | 0 | 1303 | 156 |  | 1459 | 1459 | 0.89308 | 0 | 14.0454 | 14.6821 | 6.5739 | 51.317 | 0.28611 |  | 6.17 | 259 |  | 386 | 1556 | 1446.7756 | 7.0196 | 32.9016 | 916.3878 | 71.7369 | 128 | 96 | 49 | 874 | 585 | 1459 | 1459 | 0.43376 | 0.59904 | 15.9635 | 16.6872 | 3.9133 | 59.0867 | 0.28242 | 6.17 | 6.39 | 162 | 386 | 676 | 720.6598 | -6.6065 | 58.0311 | 553.3299 | 70.7227 | 96 | 84 | 20 | 309 | 274 | 583 | 583 | 0.36373 | 0.53002 | 11.2877 | 11.7994 | 7.444 | 62.556 | 0.18862 | 6.39 | 6.47 | 200 | 676 | 1191 | 1212.8029 | -1.8306 | 48.1865 | 944.4015 | 78.8226 | 84 | 62 | 20 | 120 | 156 | 276 | 276 | 0.47147 | 0.43478 | 11.272 | 11.783 | 11.5615 | 41.4385 | 0.28435 | 6.47 | 6.47 | 356 | 1191 | 1556 | 1833.3077 | -17.8218 | 7.772 | 1512.1538 | 76.4574 | SDS-Incubation time | hours | 44.5 | NA | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 45.5 | 45.5 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 43.1 | 43.1 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 42.45 | NR | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | NR | NR | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | NR | NR | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters
|  | Variability of design flux (%) | 15 +/- | Minimum recycle flow rate for stage 3, (QR-s(3))min (gpm) | 322.7674 | [5 empty] | 1998-04-30 | 1:53 | 24603.9 | 23.4 | 128.6 | 65 | 37.5192 | 0 | 1299 | 153 |  | 1452 | 1452 | 0.89463 | 0 | 14.0022 | 14.6804 | 6.0319 | 53.249 | 0.27569 |  | 6.26 | 268 |  | 383 | 1492 | 1359.3725 | 8.8892 | 30.0261 | 871.1863 | 69.2373 | 128.6 | 96 | 49 | 872 | 585 | 1457 | 1457 | 0.43333 | 0.59849 | 15.9269 | 16.6983 | 3.7873 | 59.5127 | 0.28058 | 6.26 | 6.38 | 166 | 383 | 666 | 706.4598 | -6.075 | 56.658 | 544.7299 | 69.5262 | 96 | 84 | 21 | 307 | 273 | 580 | 580 | 0.36203 | 0.52931 | 11.2146 | 11.7577 | 7.2021 | 61.7979 | 0.19026 | 6.38 | 6.43 | 205 | 666 | 1160 | 1184.4139 | -2.1046 | 46.4752 | 925.207 | 77.8428 | 84 | 65 | 21 | 120 | 153 | 273 | 273 | 0.46492 | 0.43956 | 11.272 | 11.8179 | 11.0676 | 42.4324 | 0.27851 | 6.43 | 6.46 | 365 | 1160 | 1492 | 1783.5294 | -19.5395 | 4.6997 | 1471.7647 | 75.1998 | SDS-TOX | mg Cl- /L | BMRL | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-2 | CI-s2-2 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | 58 | 900 | --- | 8478 | --- | 93.5556 | 4245.2958 | 98.6338 | Parameter | Units | Cp-s2-4 | CI-s2-4 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | BMRL | 810 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-6 | CI-s2-6 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | 35 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-8 | CI-s2-8 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-10 | CI-s2-10 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-10 (dup) | CI-s2-10 (dup) | CC(calc) | RF (%) | CB | RB (%)
|  | Rejection of reference solute and conditions of test | 80 | 1: A negative minimum recycle flow rate indicates that recycle is not required to | [6 empty] | 1998-05-01 | 5:50 | 24631.9 | 22.4 | 126 | 63 | 34.5192 | 0 | 1303 | 156 |  | 1459 | 1459 | 0.89308 | 0 | 14.0454 | 15.1674 | 7.2986 | 52.6823 | 0.2879 |  | 6.16 | 243 |  | 384 | 1611 | 1561.7115 | 3.0595 | 36.7188 | 972.8558 | 75.022 | 126 | 94 | 46 | 875 | 584 | 1459 | 1459 | 0.43355 | 0.59973 | 15.9817 | 17.2584 | 3.988 | 60.012 | 0.28758 | 6.16 | 6.26 | 156 | 384 | 689 | 725.6096 | -5.3134 | 59.375 | 554.8048 | 71.882 | 94 | 83 | 18 | 308 | 272 | 580 | 580 | 0.36161 | 0.53103 | 11.2511 | 12.1499 | 7.8309 | 62.6691 | 0.19387 | 6.26 | 6.41 | 189 | 689 | 1229 | 1255.1765 | -2.1299 | 50.7812 | 972.0882 | 80.5573 | 83 | 63 | 18 | 120 | 156 | 276 | 276 | 0.47147 | 0.43478 | 11.272 | 12.1725 | 12.4062 | 42.5938 | 0.28578 | 6.41 | 6.41 | 333 | 1229 | 1611 | 1918.2308 | -19.0708 | 13.2812 | 1573.6154 | 78.8385 | SDS-CHCl3 | mg/L | 1 | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1998-04-13 | 1998-04-13 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 3 | 130 | --- | 1273 | --- | 97.6923 | 634.5755 | 99.5272 | Sampling date | MM/DD/YY | 1998-04-27 | 1998-04-27 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | BMRL | 210 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1998-05-11 | 1998-05-11 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 1.7 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1998-05-26 | 1998-05-26 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1998-06-09 | 1998-06-09 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1998-06-09 | 1998-06-09 | --- | --- | --- | ---
|  | (e.g., solute type and concentration) |  | meet the manufacturer's minimum flow requirement. | [6 empty] | 1998-05-02 | 2:00 | 24651.8 | 22.5 | 125 | 62 | 34.5192 | 0 | 1301 | 154 |  | 1455 | 1455 | 0.89416 | 0 | 14.0238 | 15.0994 | 6.8957 | 52.0851 | 0.2899 |  | 6.21 | 236 |  | 368 | 1608 | 1483.1429 | 7.7647 | 35.8696 | 925.5714 | 74.5022 | 125 | 92 | 46 | 872 | 583 | 1455 | 1455 | 0.43249 | 0.59931 | 15.9269 | 17.1485 | 3.6355 | 58.8645 | 0.29132 | 6.21 | 6.28 | 160 | 368 | 692 | 679.1081 | 1.863 | 56.5217 | 523.554 | 69.4396 | 92 | 81 | 18 | 309 | 274 | 583 | 583 | 0.36373 | 0.53002 | 11.2877 | 12.1534 | 7.8193 | 60.6807 | 0.20028 | 6.28 | 6.36 | 192 | 692 | 1310 | 1255.8686 | 4.1322 | 47.8261 | 973.9343 | 80.2861 | 81 | 62 | 18 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 12.1365 | 13.6738 | 39.8262 | 0.30474 | 6.36 | 6.42 | 326 | 1310 | 1608 | 2076.7532 | -29.1513 | 11.413 | 1693.3766 | 80.7485 | SDS-BDCM | mg/L | 1.3 | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 10:06 | 10:09 | --- | --- | --- | --- | SDS-BDCM | mg/L | 6 | 41 | --- | 356 | --- | 85.3659 | 180.0562 | 96.6677 | Sampling time | hh:mm | 9:02 | 9:11 | --- | --- | --- | --- | SDS-BDCM | mg/L | 0.9 | 56 | --- | 520.2214 | --- | 98.3929 | 260.5631 | 99.6546 | Sampling time | hh:mm | 8:27 | 8:37 | --- | --- | --- | --- | SDS-BDCM | mg/L | 2.9 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 8:13 | 8:25 | --- | --- | --- | --- | SDS-BDCM | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 8:28 | 8:46 | --- | --- | --- | --- | SDS-BDCM | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 8:28 | 8:46 | --- | --- | --- | ---
|  | Variability of rejection of reference solute (%) | 50 +/- | [7 empty] | 1998-05-03 | 10:30 | 24684.5 | 24.2 | 133 | 69 | 41.6991 | 0 | 1301 | 155 |  | 1456 | 1456 | 0.89354 | 0 | 14.0238 | 14.3594 | 6.9637 | 52.3372 | 0.27436 |  | 6.21 | 243 |  | 377 | 1518 | 1501.7355 | 1.0714 | 35.5438 | 939.3677 | 74.1315 | 133 | 101 | 54 | 869 | 587 | 1456 | 1456 | 0.43355 | 0.59684 | 15.8721 | 16.2519 | 3.811 | 59.189 | 0.27458 | 6.21 | 6.29 | 158 | 377 | 653 | 701.2095 | -7.3828 | 58.0902 | 539.1048 | 70.6922 | 101 | 89 | 24 | 311 | 276 | 587 | 587 | 0.36628 | 0.52981 | 11.3607 | 11.6326 | 7.2698 | 63.7302 | 0.18253 | 6.29 | 6.38 | 188 | 653 | 1156 | 1176.9674 | -1.8138 | 50.1326 | 914.9837 | 79.4532 | 89 | 69 | 24 | 121 | 155 | 276 | 276 | 0.47038 | 0.43841 | 11.3659 | 11.6379 | 11.5536 | 43.4464 | 0.26787 | 6.38 | 6.42 | 325 | 1156 | 1518 | 1804.7161 | -18.8878 | 13.7931 | 1480.3581 | 78.0459 | SDS-DBCM | mg/L | 2.2 | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 24229.9 | 24229.9 | --- | --- | --- | --- | SDS-DBCM | mg/L | 17 | 17 | --- | 17 | --- | 0 | 17 | 0 | Operation time | hh.hh | 24539.1 | 24539.3 | --- | --- | --- | --- | SDS-DBCM | mg/L | 2 | 16 | --- | 133.951 | --- | 87.5 | 67.9761 | 97.0578 | Operation time | hh.hh | 24874.3 | 24874.5 | --- | --- | --- | --- | SDS-DBCM | mg/L | 8.2 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 25214.57 | 25214.77 | --- | --- | --- | --- | SDS-DBCM | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 25526.2 | 25526.5 | --- | --- | --- | --- | SDS-DBCM | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 25526.2 | 25526.5 | --- | --- | --- | ---
|  | Standard testing recovery (%) | 15 | Calculate the Maximum Recycle Flow Rates for Each Stage | [6 empty] | 1998-05-04 | 1:54 | 24699.9 | 23.7 | 128.6 | 65 | 37.5192 | 0 | 1298 | 155 |  | 1453 | 1453 | 0.89332 | 0 | 13.9915 | 14.5396 | 6.0689 | 53.2119 | 0.27324 | 7.06 | 6.35 | 266 | 404 | 383 | 1484 | 1362.7806 | 8.1684 | 30.5483 | 872.8903 | 69.5265 | 128.6 | 96 | 49 | 871 | 582 | 1453 | 1453 | 0.43185 | 0.59945 | 15.9087 | 16.5319 | 3.7938 | 59.5062 | 0.27782 | 6.35 | 6.43 | 166 | 383 | 660 | 707.7543 | -7.2355 | 56.658 | 545.3771 | 69.5623 | 96 | 84 | 21 | 307 | 275 | 582 | 582 | 0.36373 | 0.52749 | 11.2146 | 11.6539 | 7.1209 | 61.8791 | 0.18833 | 6.43 | 6.55 | 203 | 660 | 1147 | 1170.1782 | -2.0208 | 46.9974 | 915.0891 | 77.8164 | 84 | 65 | 21 | 120 | 155 | 275 | 275 | 0.46929 | 0.43636 | 11.272 | 11.7136 | 10.8748 | 42.6252 | 0.2748 | 6.55 | 6.54 | 363 | 1147 | 1484 | 1753.9677 | -18.1919 | 5.2219 | 1450.4839 | 74.9739 | SDS-CHBr3 | mg/L | 0.9 | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 6.08 | 6.34 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | 9 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 6.51 | 6.62 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | 2 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 6.21 | 6.41 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | 6.2 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 6.05 | 6.16 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 6.08 | 6.27 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 6.08 | 6.27 | --- | --- | --- | ---
|  | Standard testing pH | 7.5 to 8.5 | Maximum recycle flow rate for stage 1, (QR-s(1))max (gpm) | 1153.8194 | [5 empty] | 1998-05-05 | 3:26 | 24725.5 | 23.6 | 126 | 61 | 34.1091 | 0 | 1300 | 157 |  | 1457 | 1457 | 0.89224 | 0 | 14.013 | 14.6051 | 7.813 | 51.5779 | 0.28317 |  | 6.09 | 238 |  | 390 | 1637 | 1648.5987 | -0.70854 | 38.9744 | 1019.2994 | 76.6506 | 126 | 94 | 46 | 873 | 584 | 1457 | 1457 | 0.43312 | 0.59918 | 15.9452 | 16.6189 | 4.0191 | 59.9809 | 0.27707 | 6.09 | 6.23 | 160 | 390 | 697 | 733.8185 | -5.2824 | 58.9744 | 561.9092 | 71.5257 | 94 | 82 | 17 | 307 | 277 | 584 | 584 | 0.36543 | 0.52568 | 11.2146 | 11.6884 | 7.9262 | 63.0738 | 0.18531 | 6.23 | 6.34 | 187 | 697 | 1248 | 1262.2347 | -1.1406 | 52.0513 | 979.6173 | 80.9109 | 82 | 61 | 17 | 120 | 157 | 277 | 277 | 0.47365 | 0.43321 | 11.272 | 11.7483 | 12.7297 | 41.7703 | 0.28126 | 6.34 | 6.4 | 327 | 1248 | 1637 | 1951.949 | -19.2394 | 16.1538 | 1599.9745 | 79.5622 | SDS-THM4 | mg/L | 5.4 | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Temperature | oC | 24.2 | 24 | --- | --- | --- | --- | SDS-THM4 | mg/L | 35 | 188 | --- | 1565 | --- | 81.383 | 795.8744 | 95.6023 | Temperature | oC | 24.1 | 24.4 | --- | --- | --- | --- | SDS-THM4 | mg/L | 4.9 | 282 | --- | 2616.5871 | --- | 98.2624 | 1310.7556 | 99.6262 | Temperature | oC | 24.9 | 25 | --- | --- | --- | --- | SDS-THM4 | mg/L | 19 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Temperature | oC | 25 | 25.2 | --- | --- | --- | --- | SDS-THM4 | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Temperature | oC | 25.2 | 25.3 | --- | --- | --- | --- | SDS-THM4 | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Temperature | oC | 25.2 | 25.3 | --- | --- | --- | ---
|  | Acceptable range of operating pressures | <400psi | Maximum recycle flow rate for stage 2, (QR-s(2))max (gpm) | 625.0694 | [5 empty] | 1998-05-06 | 3:33 | 24749.5 | 24.3 | 123.6 | 60 | 32.1091 | 0 | 1301 | 159 |  | 1460 | 1460 | 0.8911 | 0 | 14.0238 | 14.317 | 6.9749 | 52.7159 | 0.27159 |  | 6.1 | 250 |  | 387 | 1575 | 1507.9874 | 4.2548 | 35.4005 | 947.4937 | 73.6146 | 123.6 | 92 | 44 | 873 | 587 | 1460 | 1460 | 0.4344 | 0.59795 | 15.9452 | 16.2786 | 4.0103 | 59.7897 | 0.27226 | 6.1 | 6.26 | 157 | 387 | 683 | 729.0613 | -6.744 | 59.4315 | 558.0307 | 71.8653 | 92 | 80 | 15 | 308 | 279 | 587 | 587 | 0.36755 | 0.5247 | 11.2511 | 11.4864 | 7.5891 | 63.4109 | 0.18114 | 6.26 | 6.39 | 194 | 683 | 1210 | 1222.828 | -1.0602 | 49.8708 | 952.914 | 79.6414 | 80 | 60 | 15 | 120 | 159 | 279 | 279 | 0.47802 | 0.43011 | 11.272 | 11.5077 | 11.9692 | 43.0308 | 0.26743 | 6.39 | 6.4 | 341 | 1210 | 1575 | 1865.8491 | -18.4666 | 11.8863 | 1537.9245 | 77.8273 | SDS-MCAA* | mg/L | 4.3 | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 96 | 168 | 248.3177 | #VALUE! | 208.1588 | 53.8814 | SDS-MCAA* | mg/L | 2.5 | 5 | --- | 27.5 | --- | 50 | 14.9326 | 83.2581 | Alkalinity | mg/L as CaCO3 | 113 | 214 | 327.6716 | 18.1159 | 270.8358 | 58.2773 | SDS-MCAA* | mg/L | BMRL | 6.6 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 109.5 | 195 | 291.1095 | 15.1163 | 243.0547 | 54.9484 | SDS-MCAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 73 | 120 | 172.9818 | 15.1163 | 146.4909 | 50.1676 | SDS-MCAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 152 | 96 | 34.6 | -94.8718 | 65.3 | -132.7718 | SDS-MCAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 153 | 96 | 33.5036 | -101.3158 | 64.7518 | -136.2869
|  | Acceptable range of operating pH values | 2 to 8 | Maximum recycle flow rate for stage 3, (QR-s(3))max (gpm) | 210.6944 | [5 empty] | 1998-05-07 | 5:22 | 24775.4 | 23.6 | 128 | 65 | 37.1091 | 0 | 1298 | 155 |  | 1453 | 1453 | 0.89332 | 0 | 13.9915 | 14.5826 | 6.3283 | 53.0626 | 0.27482 |  | 6.19 | 264 |  | 386 | 1502 | 1407.6516 | 6.2815 | 31.6062 | 896.8258 | 70.5628 | 128 | 96 | 49 | 870 | 583 | 1453 | 1453 | 0.43206 | 0.59876 | 15.8904 | 16.5618 | 3.8764 | 59.1236 | 0.28012 | 6.19 | 6.39 | 164 | 386 | 669 | 717.2864 | -7.2177 | 57.513 | 551.6432 | 70.2706 | 96 | 85 | 20 | 308 | 275 | 583 | 583 | 0.36415 | 0.5283 | 11.2511 | 11.7265 | 7.3008 | 63.1992 | 0.18555 | 6.39 | 6.52 | 201 | 669 | 1164 | 1193.16 | -2.5052 | 47.9275 | 931.08 | 78.4122 | 85 | 65 | 20 | 120 | 155 | 275 | 275 | 0.46929 | 0.43636 | 11.272 | 11.7483 | 11.1384 | 43.8616 | 0.26785 | 6.52 | 6.54 | 361 | 1164 | 1502 | 1785.6774 | -18.8866 | 6.4767 | 1474.8387 | 75.5227 | SDS-DCAA* | mg/L | 3 | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 106 | 2080 | 4282.0433 | #VALUE! | 3181.0217 | 96.6677 | SDS-DCAA* | mg/L | 8.1 | 53 | --- | 457.1 | --- | 84.717 | 231.3893 | 96.4994 | Total dissolved solids | mg/L | 226 | 1040 | 1956.1255 | 55.5118 | 1498.0627 | 84.9138 | SDS-DCAA* | mg/L | 5.1 | 56 | --- | 484.8361 | --- | 90.8929 | 244.9703 | 97.9181 | Total dissolved solids | mg/L | 229 | 1032 | 1934.6423 | 56.2141 | 1483.3212 | 84.5617 | SDS-DCAA* | mg/L | 7.8 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 192 | 1128 | 2183.1273 | 64.4444 | 1655.5636 | 88.4027 | SDS-DCAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 200 | 1116 | 2120.3286 | 65.035 | 1618.1643 | 87.6403 | SDS-DCAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 214 | 1124 | 2121.75 | 62.0567 | 1622.875 | 86.8135
|  | Typical pressure drop across a single element (psi) | 3 to 4 psi | [7 empty] | 1998-05-08 | 1:56 | 24795.9 | 24.3 | 126.1 | 64 | 34.5192 | 0 | 1299 | 153 |  | 1452 | 1452 | 0.89463 | 0 | 14.0022 | 14.295 | 7.1858 | 53.345 | 0.26797 |  | 6.13 | 242 |  | 379 | 1534 | 1542.1569 | -0.53174 | 36.1478 | 960.5784 | 74.8068 | 126.1 | 94 | 46 | 872 | 580 | 1452 | 1452 | 0.43121 | 0.60055 | 15.9269 | 16.2599 | 3.9239 | 60.1261 | 0.27043 | 6.13 | 6.26 | 155 | 379 | 671 | 715.7724 | -6.6725 | 59.1029 | 547.3862 | 71.6836 | 94 | 82 | 18 | 307 | 273 | 580 | 580 | 0.36203 | 0.52931 | 11.2146 | 11.4491 | 7.5301 | 62.4699 | 0.18327 | 6.28 | 6.4 | 189 | 671 | 1180 | 1213.0293 | -2.7991 | 50.1319 | 942.0147 | 79.9366 | 82 | 64 | 18 | 120 | 153 | 273 | 273 | 0.46492 | 0.43956 | 11.272 | 11.5077 | 11.8055 | 43.1945 | 0.26642 | 6.4 | 6.43 | 332 | 1180 | 1534 | 1845.098 | -20.2802 | 12.4011 | 1512.549 | 78.0503 | SDS-TCAA* | mg/L | 1.9 | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 111 | 640 | 1230.1119 | #VALUE! | 935.056 | 88.1291 | SDS-TCAA* | mg/L | 3.8 | 67 | --- | 635.8 | --- | 94.3284 | 318.0958 | 98.8054 | Total hardness | mg/L as CaCO3 | 131 | 650 | 1234.1144 | 56.3333 | 942.0572 | 86.0943 | SDS-TCAA* | mg/L | 1.8 | 67 | --- | 616.3146 | --- | 97.3134 | 309.0602 | 99.4176 | Total hardness | mg/L as CaCO3 | 116 | 620 | 1186.5401 | 61.5894 | 903.2701 | 87.1578 | SDS-TCAA* | mg/L | 4.8 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 98 | 670 | 1314.8 | 67.2241 | 992.4 | 90.1249 | SDS-TCAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 104 | 650 | 1248.65 | 65.3333 | 949.325 | 89.0448 | SDS-TCAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 102 | 640 | 1229.8786 | 66 | 934.9393 | 89.0902
|  | Maximum permissible SDI | 4 | Select the Design System Recycle Flow Rate2 | [6 empty] | 1998-05-09 | 2:00 | 24819.9 | 24.2 | 125 | 65 | 34.9292 | 0 | 1300 | 154 |  | 1454 | 1454 | 0.89409 | 0 | 14.013 | 14.3483 | 7.4135 | 52.6573 | 0.27249 |  | 6.19 | 238 |  | 380 | 1602 | 1578.7013 | 1.4544 | 37.3684 | 979.3506 | 75.6982 | 125 | 95 | 46 | 872 | 582 | 1454 | 1454 | 0.43206 | 0.59972 | 15.9269 | 16.3081 | 3.8131 | 60.1869 | 0.27096 | 6.19 | 6.23 | 162 | 380 | 662 | 706.6254 | -6.741 | 57.3684 | 543.3127 | 70.1829 | 95 | 82 | 19 | 308 | 274 | 582 | 582 | 0.3633 | 0.52921 | 11.2511 | 11.5204 | 7.2947 | 62.2053 | 0.1852 | 6.23 | 6.38 | 195 | 662 | 1184 | 1186.9489 | -0.24906 | 48.6842 | 924.4745 | 78.9069 | 82 | 65 | 19 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.5417 | 11.7839 | 42.7161 | 0.2702 | 6.38 | 6.41 | 336 | 1184 | 1602 | 1844.7792 | -15.1548 | 11.5789 | 1514.3896 | 77.8128 | SDS-MBAA* | mg/L | BMRL | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 84 | 490 | 942.9025 | #VALUE! | 716.4513 | 88.2755 | SDS-MBAA* | mg/L | 1.2 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 89 | 470 | 898.8007 | 61.6379 | 684.4004 | 86.9959 | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 89 | 480 | 919.5182 | 63.5246 | 699.7591 | 87.2813 | SDS-MBAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 67 | 470 | 924.2909 | 70.354 | 697.1455 | 90.3894 | SDS-MBAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 75 | 490 | 945.0179 | 69.0083 | 717.5089 | 89.5472 | SDS-MBAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 77 | 510 | 984.7536 | 68.6992 | 747.3768 | 89.6973
|  | Maximum permissible turbidity (ntu) | 1 | Minimum system recycle flow rate, (QR-sys)min (gpm) | 1730.1944 | [5 empty] | 1998-05-10 | 2:15 | 24844 | 24.1 | 127 | 66 | 36.6991 | 0 | 1300 | 154 |  | 1454 | 1454 | 0.89409 | 0 | 14.013 | 14.3908 | 6.6826 | 53.1183 | 0.27092 |  | 6.24 | 240 |  | 368 | 1612 | 1448.5195 | 10.1415 | 34.7826 | 908.2597 | 73.5758 | 127 | 96 | 49 | 874 | 580 | 1454 | 1454 | 0.43164 | 0.6011 | 15.9635 | 16.3938 | 3.542 | 58.958 | 0.27806 | 6.24 | 6.28 | 166 | 368 | 381 | 672.3931 | -76.4811 | 54.8913 | 520.1966 | 68.089 | 96 | 83 | 19 | 307 | 273 | 580 | 580 | 0.36203 | 0.52931 | 11.2146 | 11.517 | 7.5458 | 62.9542 | 0.18294 | 6.28 | 6.31 | 198 | 681 | 1210 | 1224.1538 | -1.1697 | 46.1957 | 952.5769 | 79.2143 | 83 | 66 | 19 | 119 | 154 | 273 | 273 | 0.46601 | 0.4359 | 11.1781 | 11.4794 | 12.0336 | 43.4664 | 0.2641 | 6.31 | 6.39 | 342 | 1210 | 1612 | 1880.7273 | -16.6704 | 7.0652 | 1545.3636 | 77.8693 | SDS-DBAA* | mg/L | BMRL | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.06 | 6.1 | 12.8378 | #VALUE! | 9.4689 | 99.3663 | SDS-DBAA* | mg/L | 3.5 | 2.4 | --- | -7.5 | --- | -45.8333 | -1.9703 | 277.6344 | Turbidity | ntu | 0.05 | 2.8 | 5.895 | 72.2222 | 4.3475 | 98.8499 | SDS-DBAA* | mg/L | BMRL | 2.3 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.046 | 5.1 | 10.7811 | 72.1212 | 7.9406 | 99.4207 | SDS-DBAA* | mg/L | 1.9 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.06 | 7.2 | 15.2487 | 71.4286 | 11.2244 | 99.4654 | SDS-DBAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.08 | 5.6 | 11.6523 | 46.6667 | 8.6261 | 99.0726 | SDS-DBAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.07 | 5.8 | 12.0825 | 53.3333 | 8.9413 | 99.2171
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | 1 ppm | Maximum system recycle flow rate, (QR-sys)max (gpm) | 210.6944 | [5 empty] | 1998-05-11 | 5:20 | 24871.1 | 24.7 | 124.3 | 60 | 34.5192 | 0 | 1304 | 154 |  | 1458 | 1458 | 0.89438 | 0 | 14.0561 | 14.1813 | 6.1235 | 51.5073 | 0.27533 | 7.18 | 6.23 | 262 | 382 | 379 | 1540 | 1369.7013 | 11.0584 | 30.8707 | 874.3506 | 70.0349 | 124.3 | 94 | 46 | 876 | 582 | 1458 | 1458 | 0.43291 | 0.60082 | 16 | 16.1425 | 3.8907 | 59.2593 | 0.2724 | 6.23 | 6.23 | 157 | 379 | 665 | 713.1443 | -7.2397 | 58.5752 | 546.0722 | 71.2492 | 94 | 82 | 18 | 308 | 274 | 582 | 582 | 0.3633 | 0.52921 | 11.2511 | 11.3514 | 7.3728 | 62.6272 | 0.18125 | 6.36 | 6.5 | 193 | 665 | 1141 | 1195.5693 | -4.7826 | 49.0765 | 930.2847 | 79.2537 | 82 | 60 | 18 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.3724 | 11.1586 | 41.8414 | 0.2718 | 6.5 | 6.5 | 338 | 1141 | 1540 | 1766.7143 | -14.7217 | 10.8179 | 1453.8571 | 76.7515 | SDS-BCAA* | mg/L | 1.1 | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 20 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | 6.3 | 12 | --- | 63.3 | --- | 47.5 | 34.6463 | 81.8162 | Total organic carbon | mg/L | BMRL | 19 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | 12 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 20 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | 1.4 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 19 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 20 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 19 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | 1: All of the information requested in this field may not be available, but values for all of the Design |  | Design system recycle flow rate, QR-sys (gpm) | 0 | [5 empty] | 1998-05-12 | 1:51 | 24891.7 | 24.2 | 128.1 | 65 | 37.5192 | 0 | 1300 | 154 |  | 1454 | 1454 | 0.89409 | 0 | 14.013 | 14.3483 | 6.2649 | 52.7659 | 0.27192 | 7.14 | 6.26 | 263 | 360 | 383 | 1501 | 1395.987 | 6.9962 | 31.3316 | 889.4935 | 70.4326 | 128.1 | 96 | 49 | 873 | 581 | 1454 | 1454 | 0.43185 | 0.60041 | 15.9452 | 16.3268 | 3.7828 | 59.2672 | 0.27548 | 6.26 | 6.41 | 167 | 383 | 662 | 707.5577 | -6.8818 | 56.3969 | 545.2788 | 69.3735 | 96 | 84 | 21 | 307 | 274 | 581 | 581 | 0.36288 | 0.5284 | 11.2146 | 11.483 | 7.1614 | 61.8386 | 0.18569 | 6.41 | 6.52 | 203 | 662 | 1156 | 1176.281 | -1.7544 | 46.9974 | 919.1405 | 77.9141 | 84 | 65 | 21 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.5417 | 11.0613 | 42.4387 | 0.27196 | 6.52 | 6.52 | 360 | 1156 | 1501 | 1776.2597 | -18.3384 | 6.0052 | 1466.1299 | 75.4456 | SDS-TBAA | mg/L | BMRL | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.02 | 0.568 | 1.1793 | #VALUE! | 0.87365 | 97.7108 | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.0246 | 0.556 | 1.1541 | 88.9686 | 0.85504 | 97.1229 | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.0199 | 0.575 | 1.199 | 91.4775 | 0.88699 | 97.7565 | SDS-TBAA | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.0126 | 0.57 | 1.1983 | 95.0491 | 0.88417 | 98.5749 | SDS-TBAA | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.017 | 0.581 | 1.1994 | 93.254 | 0.89019 | 98.0903 | SDS-TBAA | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.016 | 0.577 | 1.1921 | 93.7984 | 0.88455 | 98.1912
|  | Parameters must be entered in cells E15:E26, since these parameters are used in calculations. |  | System influent flow rate, QI-sys (gpm) | 1546.1806 | [5 empty] | 1998-05-13 | 4:30 | 24917.6 | 23.7 | 124.7 | 62 | 34.1091 | 0 | 1298 | 154 |  | 1452 | 1452 | 0.89394 | 0 | 13.9915 | 14.5396 | 7.1957 | 52.0451 | 0.27936 | 7.12 | 6.2 | 255 | 379 | 393 | 1574 | 1556.1429 | 1.1345 | 35.1145 | 974.5714 | 73.8347 | 124.7 | 93 | 46 | 872 | 580 | 1452 | 1452 | 0.43121 | 0.60055 | 15.9269 | 16.5509 | 4.064 | 58.786 | 0.28154 | 6.2 | 6.35 | 161 | 393 | 687 | 741.8 | -7.9767 | 59.0331 | 567.4 | 71.625 | 93 | 82 | 17 | 307 | 273 | 580 | 580 | 0.36203 | 0.52931 | 11.2146 | 11.6539 | 7.6708 | 62.8292 | 0.18549 | 6.35 | 6.48 | 196 | 687 | 1211 | 1239.1502 | -2.3245 | 50.1272 | 963.0751 | 79.6485 | 82 | 62 | 17 | 119 | 154 | 273 | 273 | 0.46601 | 0.4359 | 11.1781 | 11.616 | 11.9782 | 43.0218 | 0.27 | 6.48 | 6.45 | 347 | 1211 | 1574 | 1878.6364 | -19.3543 | 11.7048 | 1544.8182 | 77.5378 | SDS-CDBAA | mg/L | BMRL | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 2.84 | --- | --- | --- | --- | SDS-CDBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 2.9263 | --- | --- | --- | --- | SDS-CDBAA | mg/L | BMRL | 2.9 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 2.875 | --- | --- | --- | --- | SDS-CDBAA | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3 | --- | --- | --- | --- | SDS-CDBAA | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 2.905 | --- | --- | --- | --- | SDS-CDBAA | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.0368 | --- | --- | --- | ---
|  |  |  | Recycle ratio, r | 0 | [5 empty] | 1998-05-14 | 3:29 | 24940.6 | 24.4 | 127.9 | 65 | 37.5192 | 0 | 1301 | 154 |  | 1455 | 1455 | 0.89416 | 0 | 14.0238 | 14.2747 | 6.0599 | 52.871 | 0.26999 | 7.1 | 6.36 | 266 | 377 | 382 | 1475 | 1361.974 | 7.6628 | 30.3665 | 871.987 | 69.495 | 127.9 | 96 | 49 | 875 | 580 | 1455 | 1455 | 0.43185 | 0.60137 | 15.9817 | 16.2677 | 3.7367 | 59.2133 | 0.27473 | 6.36 | 6.48 | 169 | 382 | 659 | 703.3362 | -6.7278 | 55.7592 | 542.6681 | 68.8576 | 96 | 84 | 21 | 307 | 273 | 580 | 580 | 0.36203 | 0.52931 | 11.2146 | 11.4153 | 7.0615 | 61.9385 | 0.1843 | 6.48 | 6.61 | 207 | 659 | 1140 | 1167.293 | -2.3941 | 45.8115 | 913.1465 | 77.3311 | 84 | 65 | 21 | 119 | 154 | 273 | 273 | 0.46601 | 0.4359 | 11.1781 | 11.3781 | 10.7443 | 42.7557 | 0.26612 | 6.61 | 6.57 | 365 | 1140 | 1475 | 1738.8636 | -17.8891 | 4.4503 | 1439.4318 | 74.6428 | SDS-DCBAA | mg/L | 1.6 | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | 3.6 | 18 | --- | 147.6 | --- | 80 | 75.2117 | 95.2135 | [8 empty] | SDS-DCBAA | mg/L | BMRL | 17 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | 1.5 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  |  |  | 2: The design system recycle flow rate must fall between the minimum and | [6 empty] | 1998-05-15 | 5:27 | 24966.4 | 23.9 | 127.6 | 65 | 37.5192 | 0 | 1305 | 155 |  | 1460 | 1460 | 0.89384 | 0 | 14.0669 | 14.5318 | 5.5223 | 53.2586 | 0.27285 | 7.19 | 6.26 | 284 | 381 | 390 | 1483 | 1282.4516 | 13.5232 | 27.1795 | 836.2258 | 66.0379 | 127.6 | 96 | 49 | 874 | 586 | 1460 | 1460 | 0.43418 | 0.59863 | 15.9635 | 16.491 | 3.7882 | 59.0118 | 0.27945 | 6.26 | 6.54 | 173 | 390 | 671 | 713.6485 | -6.356 | 55.641 | 551.8242 | 68.6494 | 96 | 85 | 21 | 310 | 276 | 586 | 586 | 0.36585 | 0.52901 | 11.3242 | 11.6985 | 7.7767 | 61.7233 | 0.18953 | 6.54 | 6.56 | 173 | 671 | 1153 | 1230.3478 | -6.7084 | 55.641 | 950.6739 | 81.8024 | 85 | 65 | 21 | 121 | 155 | 276 | 276 | 0.47038 | 0.43841 | 11.3659 | 11.7416 | 10.6777 | 43.3223 | 0.27103 | 6.56 | 6.63 | 385 | 1153 | 1483 | 1752.5355 | -18.175 | 1.2821 | 1452.7677 | 73.4989 | SDS-HAA5 | mg/L | 9.2 | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-HAA5 | mg/L | 19.1 | 127.4 | --- | 1102.1 | --- | 85.0078 | 557.6797 | 96.5751 | [8 empty] | SDS-HAA5 | mg/L | 6.9 | 131.9 | --- | 1185.0338 | --- | 94.7688 | 595.9724 | 98.8422 | [8 empty] | SDS-HAA5 | mg/L | 14.5 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-HAA5 | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-HAA5 | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  |  |  | maximum system recycle flow rates. | [6 empty] | 1998-05-16 | 5:40 | 24980.9 | 24.3 | 128 | 65 | 37.1091 | 0 | 1300 | 154 |  | 1454 | 1454 | 0.89409 | 0 | 14.013 | 14.306 | 4.8031 | 54.5877 | 0.26207 |  | 6.25 | 276 | 0 | 368 | 1468 | 1144.6234 | 22.0284 | 25 | 756.3117 | 63.5071 | 128 | 96 | 49 | 872 | 582 | 1454 | 1454 | 0.43206 | 0.59972 | 15.9269 | 16.2599 | 2.9036 | 60.0964 | 0.27056 | 6.25 | 6.38 | 202 | 368 | 668 | 616.7148 | 7.6774 | 45.1087 | 492.3574 | 58.9729 | 96 | 84 | 20 | 308 | 274 | 582 | 582 | 0.3633 | 0.52921 | 11.2511 | 11.4864 | 7.2791 | 62.7209 | 0.18313 | 6.38 | 6.48 | 202 | 668 | 1162 | 1191.8248 | -2.5667 | 45.1087 | 929.9124 | 78.2775 | 84 | 65 | 20 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.5077 | 10.7556 | 43.7444 | 0.26307 | 6.48 | 6.59 | 388 | 1162 | 1468 | 1765.1169 | -20.2396 | -5.4348 | 1463.5584 | 73.4893 | SDS-HAA6 | mg/L | 10.3 | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | 25.4 | 139.4 | --- | 1165.4 | --- | 81.7791 | 592.326 | 95.7118 | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | 6.9 | 143.9 | --- | 1298.1347 | --- | 95.205 | 652.5233 | 98.9426 | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | 15.9 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Stage 3 Operating Parameters During Sample Collection
[11 empty] | 1998-05-17 | 6:30 | 25005.1 | 23.6 | 128 | 64 | 36.6991 | 0 | 1297 | 154 |  | 1451 | 1451 | 0.89387 | 0 | 13.9807 | 14.5714 | 6.0969 | 53.204 | 0.27388 |  | 6.33 | 269 | 0 | 386 | 1485 | 1371.3831 | 7.651 | 30.3109 | 878.6916 | 69.3863 | 128 | 95 | 49 | 871 | 580 | 1451 | 1451 | 0.431 | 0.60028 | 15.9087 | 16.5808 | 3.2916 | 59.2084 | 0.28004 | 6.33 | 6.39 | 198 | 386 | 684 | 668.3241 | 2.2918 | 48.7047 | 527.1621 | 62.4404 | 95 | 85 | 19 | 307 | 273 | 580 | 580 | 0.36203 | 0.52931 | 11.2146 | 11.6884 | 7.5926 | 63.4074 | 0.18434 | 6.39 | 6.48 | 198 | 684 | 1210 | 1230.5275 | -1.6965 | 48.7047 | 957.2637 | 79.316 | 85 | 64 | 19 | 119 | 154 | 273 | 273 | 0.46601 | 0.4359 | 11.1781 | 11.6504 | 11.7564 | 43.7436 | 0.26633 | 6.48 | 6.61 | 362 | 1210 | 1485 | 1865.2727 | -25.6076 | 6.2176 | 1537.6364 | 76.4574 | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.43 |  |  |  |  | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.44 |  |  |  |  | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.44 |  |  |  |  | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.44 |  |  |  |  | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.43 |  |  |  |  | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.43
|  |  |  | Summary of the Stage and System Flow Rates | [6 empty] | 1998-05-18 | 3:32 | 25036.4 | 24.1 | 128.5 | 64 | 37.5192 | 0 | 1300 | 156 |  | 1456 | 1456 | 0.89286 | 0 | 14.013 | 14.3908 | 5.425 | 53.3058 | 0.26997 | 7.08 | 6.31 | 276 | 376 | 381 | 1469 | 1256 | 14.4997 | 27.5591 | 818.5 | 66.2798 | 128.5 | 96 | 49 | 874 | 582 | 1456 | 1456 | 0.43249 | 0.60027 | 15.9635 | 16.3938 | 3.6068 | 59.6432 | 0.27487 | 6.31 | 6.47 | 175 | 381 | 652 | 690.354 | -5.8825 | 54.0682 | 535.677 | 67.3311 | 96 | 85 | 21 | 307 | 275 | 582 | 582 | 0.36373 | 0.52749 | 11.2146 | 11.517 | 6.8404 | 62.6596 | 0.1838 | 6.47 | 6.61 | 213 | 652 | 1115 | 1142.0836 | -2.429 | 44.0945 | 897.0418 | 76.2553 | 85 | 64 | 21 | 119 | 156 | 275 | 275 | 0.47038 | 0.43273 | 11.1781 | 11.4794 | 10.181 | 43.319 | 0.265 | 6.61 | 6.64 | 378 | 1115 | 1469 | 1677.1987 | -14.1728 | 0.7874 | 1396.0994 | 72.9246 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 120 |  |  |  |  | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 119 |  |  |  |  | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 120 |  |  |  |  | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 120 |  |  |  |  | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 120 |  |  |  |  | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 120
|  |  |  | Influent flow rate to stage 1, QI-s(1) (gpm) | 1546.1806 | [5 empty] | 1998-05-19 | 7:24 | 25045.9 | 22.6 | 127.6 | 65 | 36.5192 | 0 | 1302 | 154 |  | 1456 | 1456 | 0.89423 | 0 | 14.0346 | 15.0664 | 8.5205 | 51.2604 | 0.29392 | 7.15 | 6.04 | 229 | 385 | 392 | 1682 | 1770.0909 | -5.2373 | 41.5816 | 1081.0455 | 78.8168 | 127.6 | 96 | 48 | 874 | 582 | 1456 | 1456 | 0.43249 | 0.60027 | 15.9635 | 17.1371 | 4.2021 | 59.5979 | 0.28754 | 6.04 | 6.21 | 152 | 392 | 702 | 752.4124 | -7.1812 | 61.2245 | 572.2062 | 73.4361 | 96 | 85 | 20 | 308 | 274 | 582 | 582 | 0.3633 | 0.52921 | 11.2511 | 12.0783 | 8.107 | 62.393 | 0.19358 | 6.21 | 6.3 | 183 | 702 | 1267 | 1285.4015 | -1.4524 | 53.3163 | 993.7007 | 81.584 | 85 | 65 | 20 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 12.1007 | 13.2291 | 41.7709 | 0.28969 | 6.3 | 6.32 | 315 | 1267 | 1682 | 2008.8182 | -19.4303 | 19.6429 | 1637.9091 | 80.7682 | [12 empty] | Stage 3 influent flow rate during sample collection (gpm) | 277 | [16 empty] | Stage 3 influent flow rate during sample collection (gpm) | 271 | [16 empty] | Stage 3 influent flow rate during sample collection (gpm) | 274 | [16 empty] | Stage 3 influent flow rate during sample collection (gpm) | 275 | [16 empty] | Stage 3 influent flow rate during sample collection (gpm) | 280 | [16 empty] | Stage 3 influent flow rate during sample collection (gpm) | 280
|  |  |  | Permeate flow rate from stage 1, Qp-s(1) (gpm) | 821.25 | [5 empty] | 1998-05-20 | 3:33 | 25066 | 24.5 | 128.1 | 65 | 38.1091 | 0 | 1300 | 155 |  | 1455 | 1455 | 0.89347 | 0 | 14.013 | 14.2217 | 8.5694 | 49.8715 | 0.28517 | 7.1 | 6.06 | 228 | 374 | 393 | 1658 | 1776.871 | -7.1695 | 41.9847 | 1084.9355 | 78.9849 | 128.1 | 96 | 50 | 872 | 583 | 1455 | 1455 | 0.43249 | 0.59931 | 15.9269 | 16.1641 | 4.1774 | 57.8726 | 0.2793 | 6.06 | 6.28 | 154 | 393 | 700 | 750.4751 | -7.2107 | 60.8142 | 571.7376 | 73.0646 | 96 | 85 | 21 | 308 | 275 | 583 | 583 | 0.36415 | 0.5283 | 11.2511 | 11.4187 | 8.5176 | 60.9824 | 0.18725 | 6.28 | 6.33 | 154 | 700 | 1268 | 1311.52 | -3.4322 | 60.8142 | 1005.76 | 84.6882 | 85 | 65 | 21 | 120 | 155 | 275 | 275 | 0.46929 | 0.43636 | 11.272 | 11.4398 | 13.2745 | 40.7255 | 0.2809 | 6.33 | 6.29 | 311 | 1268 | 1658 | 2008.9032 | -21.1642 | 20.8651 | 1638.4516 | 81.0187 | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs
|  |  |  | Concentrate flow rate from stage 1, QC-s(1) (gpm) | 724.9306 | [5 empty] | 1998-05-21 | 6:16 | 25092.8 | 23.9 | 127.7 | 65 | 38.1091 | 0 | 1302 | 153 |  | 1455 | 1455 | 0.89485 | 0 | 14.0346 | 14.4984 | 9.0384 | 49.2024 | 0.29467 | 7.2 | 6.1 | 219 | 383 | 391 | 1675 | 1854.6863 | -10.7275 | 43.9898 | 1122.8431 | 80.4959 | 127.7 | 96 | 50 | 872 | 583 | 1455 | 1455 | 0.43249 | 0.59931 | 15.9269 | 16.4533 | 4.2997 | 57.5503 | 0.28589 | 6.1 | 6.21 | 145 | 391 | 705 | 758.9451 | -7.6518 | 62.9156 | 574.9726 | 74.7814 | 96 | 85 | 21 | 310 | 273 | 583 | 583 | 0.3633 | 0.53173 | 11.3242 | 11.6985 | 8.3405 | 61.1595 | 0.19128 | 6.21 | 6.19 | 173 | 705 | 1281 | 1309.1026 | -2.1938 | 55.7545 | 1007.0513 | 82.8211 | 85 | 65 | 21 | 120 | 153 | 273 | 273 | 0.46492 | 0.43956 | 11.272 | 11.6445 | 13.6849 | 40.3151 | 0.28884 | 6.19 | 6.17 | 298 | 1281 | 1675 | 2051.9804 | -22.5063 | 23.7852 | 1666.4902 | 82.1181 |  | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters
|  |  |  | Influent flow rate to stage 2, QI-s(2) (gpm) | 724.9306 | [5 empty] | 1998-05-22 | 3:35 | 25114.1 | 24.3 | 128.1 | 66 | 38.1091 | 0 | 1296 | 154 |  | 1450 | 1450 | 0.89379 | 0 | 13.9699 | 14.262 | 9.4782 | 49.4627 | 0.28834 | 7.2 | 6.03 | 211 | 377 | 393 | 1713 | 1924.6364 | -12.3547 | 46.3104 | 1158.8182 | 81.7918 | 128.1 | 96 | 50 | 869 | 581 | 1450 | 1450 | 0.431 | 0.59931 | 15.8721 | 16.204 | 4.3521 | 57.6979 | 0.28084 | 6.03 | 6.11 | 144 | 393 | 710 | 765.4286 | -7.8068 | 63.3588 | 579.2143 | 75.1387 | 96 | 85 | 21 | 307 | 274 | 581 | 581 | 0.36288 | 0.5284 | 11.2146 | 11.4491 | 3.8849 | 65.6151 | 0.17449 | 6.11 | 6.15 | 144 | 393 | 1302 | 671.9891 | 48.3879 | 63.3588 | 532.4945 | 72.9575 | 85 | 66 | 21 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.5077 | 14.0906 | 40.4094 | 0.28478 | 6.15 | 6.11 | 288 | 1302 | 1713 | 2092.1299 | -22.1325 | 26.7176 | 1697.0649 | 83.0295 |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-2 | CI-s3-2 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-4 | CI-s3-4 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-6 | CI-s3-6 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-8 | CI-s3-8 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-10 | CI-s3-10 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-10 (dup) | CI-s3-10 (dup) | CC(calc) | RF (%) | CB | RB (%)
|  |  |  | Permeate flow rate from stage 2, Qp-s(2) (gpm) | 410.625 | [5 empty] | 1998-05-23 | 3:30 | 25138 | 24.1 | 128 | 65 | 37.6991 | 0 | 1300 | 154 |  | 1454 | 1454 | 0.89409 | 0 | 14.013 | 14.3908 | 9.4496 | 49.3513 | 0.2916 |  | 6.01 | 215 | 0 | 396 | 1710 | 1923.9221 | -12.5101 | 45.7071 | 1159.961 | 81.4649 | 128 | 96 | 50 | 872 | 582 | 1454 | 1454 | 0.43206 | 0.59972 | 15.9269 | 16.3563 | 4.3729 | 57.6271 | 0.28383 | 6.01 | 6.1 | 146 | 396 | 712 | 770.5704 | -8.2262 | 63.1313 | 583.2852 | 74.9694 | 96 | 85 | 20 | 308 | 274 | 582 | 582 | 0.3633 | 0.52921 | 11.2511 | 11.5545 | 8.3726 | 62.1274 | 0.18598 | 6.1 | 6.18 | 176 | 712 | 1290 | 1314.5109 | -1.9001 | 55.5556 | 1013.2555 | 82.6302 | 85 | 65 | 20 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.5759 | 13.8683 | 41.1317 | 0.28144 | 6.18 | 6.17 | 292 | 1290 | 1710 | 2067.6623 | -20.9159 | 26.2626 | 1678.8312 | 82.6069 | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | #VALUE! | #VALUE! |  |  |  | Sampling date | MM/DD/YY | 1998-04-13 | 1998-04-13 | --- | --- | --- | --- | Qp/QT (THM4), % | 75.817 | 99.3464 |  | Qp/QT (HAA5), % | 67.7747 | 92.7054 |  |  |  | Sampling date | MM/DD/YY | 1998-04-27 | 1998-04-27 | --- | --- | --- | --- | Qp/QT (THM4), % | 75.7849 | 88.7766 |  | Qp/QT (HAA5), % | 62.32 | 83.92 |  |  |  | Sampling date | MM/DD/YY | 1998-05-11 | 1998-05-11 | --- | --- | --- | --- | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | #VALUE! | #VALUE! |  |  |  | Sampling date | MM/DD/YY | 1998-05-26 | 1998-05-26 | --- | --- | --- | --- | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | #VALUE! | #VALUE! |  |  |  | Sampling date | MM/DD/YY | 1998-06-09 | 1998-06-09 | --- | --- | --- | --- | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | #VALUE! | #VALUE! |  |  |  | Sampling date | MM/DD/YY | 1998-06-09 | 1998-06-09 | --- | --- | --- | ---
|  |  |  | Concentrate flow rate from stage 2, QC-s(2) (gpm) | 314.3056 | [5 empty] | 1998-05-24 | 4:00 | 25162.3 | 24.2 | 128 | 65 | 37.6991 | 0 | 1300 | 156 |  | 1456 | 1456 | 0.89286 | 0 | 14.013 | 14.3483 | 9.0933 | 49.7076 | 0.28866 |  | 6.01 | 216 | 0 | 392 | 1720 | 1858.6667 | -8.062 | 44.898 | 1125.3333 | 80.8057 | 128 | 95 | 50 | 875 | 581 | 1456 | 1456 | 0.43227 | 0.60096 | 15.9817 | 16.3642 | 4.2248 | 57.2752 | 0.28571 | 6.01 | 6.11 | 151 | 392 | 710 | 754.9518 | -6.3312 | 61.4796 | 573.4759 | 73.6693 | 95 | 85 | 20 | 306 | 275 | 581 | 581 | 0.3633 | 0.52668 | 11.1781 | 11.4456 | 8.2487 | 61.7513 | 0.18535 | 6.11 | 6.2 | 180 | 710 | 1280 | 1299.7455 | -1.5426 | 54.0816 | 1004.8727 | 82.0873 | 85 | 65 | 20 | 119 | 156 | 275 | 275 | 0.47038 | 0.43273 | 11.1781 | 11.4456 | 13.6207 | 41.3793 | 0.2766 | 6.2 | 6.19 | 294 | 1280 | 1720 | 2032.141 | -18.1477 | 25 | 1656.0705 | 82.2471 | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  |  |  | Sampling time | hh:mm | 10:11 | 10:14 | --- | --- | --- | --- | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 84.3047 | 46.1607 |  |  |  | Sampling time | hh:mm | 9:04 | 9:14 | --- | --- | --- | --- | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 109.3113 | 49.4577 |  |  |  | Sampling time | hh:mm | 8:30 | 8:40 | --- | --- | --- | --- | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  |  |  | Sampling time | hh:mm | 8:16 | 8:29 | --- | --- | --- | --- | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  |  |  | Sampling time | hh:mm | 8:30 | 8:52 | --- | --- | --- | --- | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  |  |  | Sampling time | hh:mm | 8:30 | 8:52 | --- | --- | --- | ---
|  |  |  | Influent flow rate to stage 3, QI-s(3) (gpm) | 314.3056 | [5 empty] | 1998-05-25 | 6:20 | 25188.8 | 23.5 | 128.1 | 65 | 38.1091 | 0 | 1302 | 155 |  | 1457 | 1457 | 0.89362 | 0 | 14.0346 | 14.6709 | 9.412 | 49.0289 | 0.29923 | 7.22 | 6.02 | 215 | 377 | 396 | 1711 | 1916.4 | -12.0047 | 45.7071 | 1156.2 | 81.4046 | 128.1 | 96 | 50 | 874 | 583 | 1457 | 1457 | 0.43291 | 0.59986 | 15.9635 | 16.6872 | 4.4089 | 57.6411 | 0.2895 | 6.02 | 6.14 | 144 | 396 | 705 | 773.7839 | -9.7566 | 63.6364 | 584.8919 | 75.3801 | 96 | 85 | 21 | 308 | 275 | 583 | 583 | 0.36415 | 0.5283 | 11.2511 | 11.7612 | 8.3304 | 61.1696 | 0.19227 | 6.14 | 6.2 | 171 | 705 | 1288 | 1303.08 | -1.1708 | 56.8182 | 1004.04 | 82.9688 | 85 | 65 | 21 | 120 | 155 | 275 | 275 | 0.46929 | 0.43636 | 11.272 | 11.783 | 13.7877 | 40.2123 | 0.29302 | 6.2 | 6.14 | 294 | 1288 | 1711 | 2057.5484 | -20.2541 | 25.7576 | 1672.7742 | 82.4244 | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  |  |  | Operation time | hh.hh | 24230 | 24230.1 | --- | --- | --- | --- | SDS-HAA5b, mg/L | 45.2902 | 19.8078 |  | SDS-HAA5b, mg/L | 54 | 27 |  |  |  | Operation time | hh.hh | 24539.2 | 24539.3 | --- | --- | --- | --- | SDS-HAA5b, mg/L | 37.1689 | 20.9292 |  | SDS-HAA5b, mg/L | 54 | 27 |  |  |  | Operation time | hh.hh | 24874.3 | 24874.5 | --- | --- | --- | --- | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  |  |  | Operation time | hh.hh | 25214.62 | 25214.83 | --- | --- | --- | --- | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  |  |  | Operation time | hh.hh | 25526.2 | 25526.6 | --- | --- | --- | --- | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  |  |  | Operation time | hh.hh | 25526.2 | 25526.6 | --- | --- | --- | ---
|  |  |  | Permeate flow rate from stage 3, Qp-s(3) (gpm) | 159.6875 | [5 empty] | 1998-05-26 | 5:25 | 25211.8 | 24.5 | 127.7 | 66 | 38.1091 | 0 | 1306 | 155 |  | 1461 | 1461 | 0.89391 | 0 | 14.0777 | 14.2873 | 9.2268 | 49.514 | 0.28855 | 7.16 | 6.1 | 211 | 371 | 388 | 1689 | 1879.3677 | -11.271 | 45.6186 | 1133.6839 | 81.3881 | 127.7 | 96 | 50 | 876 | 585 | 1461 | 1461 | 0.43418 | 0.59959 | 16 | 16.2382 | 4.2494 | 57.6006 | 0.28191 | 6.1 | 6.15 | 145 | 388 | 701 | 751.8769 | -7.2578 | 62.6289 | 569.9385 | 74.5587 | 96 | 85 | 21 | 310 | 275 | 585 | 585 | 0.365 | 0.52991 | 11.3242 | 11.4928 | 8.3185 | 61.1815 | 0.18785 | 6.15 | 6.17 | 169 | 701 | 1281 | 1300.7091 | -1.5386 | 56.4433 | 1000.8545 | 83.1144 | 85 | 66 | 21 | 120 | 155 | 275 | 275 | 0.46929 | 0.43636 | 11.272 | 11.4398 | 13.7739 | 40.7261 | 0.2809 | 6.17 | 6.19 | 288 | 1281 | 1689 | 2049.7742 | -21.3602 | 25.7732 | 1665.3871 | 82.7067 | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  |  |  | pH | --- | 6.48 | 6.43 | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | 261.6209 | 63.5033 |  | SDS-TOXb, mg Cl- /L | 329.337 | 119.4201 |  |  |  | pH | --- | 6.63 | 6.63 | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  |  |  | pH | --- | 6.47 | 6.48 | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  |  |  | pH | --- | 6.23 | 6.2 | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  |  |  | pH | --- | 6.3 | 6.31 | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  |  |  | pH | --- | 6.3 | 6.31 | --- | --- | --- | ---
|  |  |  | Concentrate flow rate from stage 3, QC-s(3) (gpm) | 154.6181 | [5 empty] | 1998-05-27 | 6:20 | 25236.8 | 24.7 | 127.8 | 65 | 38.1091 | 0 | 1301 | 153 |  | 1454 | 1454 | 0.89477 | 0 | 14.0238 | 14.1487 | 9.3479 | 48.9429 | 0.28909 | 7.17 | 5.98 | 208 | 373 | 386 | 1742 | 1899.5817 | -9.046 | 46.114 | 1142.7908 | 81.7989 | 127.8 | 96 | 50 | 872 | 582 | 1454 | 1454 | 0.43206 | 0.59972 | 15.9269 | 16.0688 | 4.3379 | 57.5621 | 0.27916 | 5.98 | 6.13 | 138 | 386 | 698 | 757.5739 | -8.5349 | 64.2487 | 571.7869 | 75.8651 | 96 | 85 | 21 | 309 | 273 | 582 | 582 | 0.36288 | 0.53093 | 11.2877 | 11.3882 | 8.3308 | 61.1692 | 0.18618 | 6.13 | 6.15 | 166 | 698 | 1310 | 1300.1538 | 0.75161 | 56.9948 | 999.0769 | 83.3847 | 85 | 65 | 21 | 120 | 153 | 273 | 273 | 0.46492 | 0.43956 | 11.272 | 11.3724 | 14.2696 | 39.7304 | 0.28624 | 6.15 | 6.13 | 285 | 1310 | 1742 | 2113.9216 | -21.3503 | 26.1658 | 1711.9608 | 83.3524 | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | #VALUE! | #VALUE! |  |  |  | Temperature | oC | 24.2 | 23.7 | --- | --- | --- | --- | SDS-CDb, mg/L | 18.8497 | 16.3203 |  | SDS-CDb, mg/L | 19.7142 | 17.0342 |  |  |  | Temperature | oC | 24.2 | 24.2 | --- | --- | --- | --- | SDS-CDb, mg/L | 18.6045 | 17.1481 |  | SDS-CDb, mg/L | 20.1139 | 17.6926 |  |  |  | Temperature | oC | 25 | 25.2 | --- | --- | --- | --- | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | #VALUE! | #VALUE! |  |  |  | Temperature | oC | 25.1 | 25.3 | --- | --- | --- | --- | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | #VALUE! | #VALUE! |  |  |  | Temperature | oC | 25.3 | 25.4 | --- | --- | --- | --- | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | #VALUE! | #VALUE! |  |  |  | Temperature | oC | 25.3 | 25.4 | --- | --- | --- | ---
|  |  |  | System concentrate recycle flow rate, QR-sys (gpm) | 0 | [5 empty] | 1998-05-28 | 3:00 | 25261.3 | 24.4 | 127 | 62 | 37.6991 | 0 | 1295 | 156 |  | 1451 | 1451 | 0.89249 | 0 | 13.9591 | 14.2089 | 11.5374 | 45.2634 | 0.31392 |  | 5.97 | 160 | 0 | 384 | 1667 | 2243.4872 | -34.5823 | 58.3333 | 1313.7436 | 87.8211 | 127 | 96 | 50 | 866 | 585 | 1451 | 1451 | 0.43206 | 0.59683 | 15.8174 | 16.1004 | 4.4548 | 57.0452 | 0.28224 | 5.97 | 6.03 | 128 | 384 | 685 | 762.9675 | -11.3821 | 66.6667 | 573.4838 | 77.6803 | 96 | 82 | 20 | 309 | 274 | 583 | 583 | 0.36373 | 0.53002 | 11.2877 | 11.4896 | 8.4293 | 60.5707 | 0.18969 | 6.03 | 6.11 | 146 | 685 | 1278 | 1292.8504 | -1.162 | 61.9792 | 988.9252 | 85.2365 | 82 | 62 | 20 | 120 | 156 | 276 | 276 | 0.47147 | 0.43478 | 11.272 | 11.4737 | 14.3446 | 37.6554 | 0.3047 | 6.11 | 6.13 | 242 | 1278 | 1667 | 2074.9231 | -24.4705 | 36.9792 | 1676.4615 | 85.5648 | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! |  |  |  | Alkalinity | mg/L as CaCO3 | 198 | 232 | 257.9873 | #VALUE! | 244.9936 | 19.1816 | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! |  |  |  | Alkalinity | mg/L as CaCO3 | 234 | 268 | 294.6184 | -69.5652 | 281.3092 | 16.8175 | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! |  |  |  | Alkalinity | mg/L as CaCO3 | 221.5 | 259 | 288.2208 | -71.7054 | 273.6104 | 19.0455 | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! |  |  |  | Alkalinity | mg/L as CaCO3 | 140 | 146 | 150.6452 | -62.7907 | 148.3226 | 5.6111 | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! |  |  |  | Alkalinity | mg/L as CaCO3 | 188 | 178 | 170.5 | -141.0256 | 174.25 | -7.891 | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! |  |  |  | Alkalinity | mg/L as CaCO3 | 184 | 176 | 170 | -142.1053 | 173 | -6.3584
|  |  |  | System concentrate waste flow rate, QW-sys (gpm) | 154.6181 | [5 empty] | 1998-05-29 | 6:27 | 25276.1 | 24.2 | 122.2 | 59 | 32.1091 | 0 | 1300 | 155 |  | 1455 | 1455 | 0.89347 | 0 | 14.013 | 14.3483 | 8.6732 | 49.8176 | 0.28802 | 7.21 | 6.12 | 219 | 368 | 386 | 1642 | 1786.6452 | -8.8091 | 43.2642 | 1086.3226 | 79.8402 | 122.2 | 91 | 44 | 873 | 582 | 1455 | 1455 | 0.43227 | 0.6 | 15.9452 | 16.3268 | 2.9225 | 59.6775 | 0.27358 | 6.12 | 6.22 | 219 | 386 | 690 | 636.5 | 7.7536 | 43.2642 | 511.25 | 57.1638 | 91 | 79 | 15 | 307 | 275 | 582 | 582 | 0.36373 | 0.52749 | 11.2146 | 11.483 | 8.0402 | 61.9598 | 0.18533 | 6.22 | 6.29 | 174 | 690 | 1244 | 1266.0436 | -1.772 | 54.9223 | 978.0218 | 82.209 | 79 | 59 | 15 | 120 | 155 | 275 | 275 | 0.46929 | 0.43636 | 11.272 | 11.5417 | 13.0387 | 40.9613 | 0.28177 | 6.29 | 6.26 | 304 | 1244 | 1642 | 1971.7419 | -20.0817 | 21.2435 | 1607.871 | 81.093 | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  |  |  | Total dissolved solids | mg/L | 372 | 2212 | 3618.3694 | #VALUE! | 2915.1847 | 87.2392 | UV254 b, cm-1 | 0.073641 | 0.027288 |  | UV254 b, cm-1 | 0.089484 | 0.04037 |  |  |  | Total dissolved solids | mg/L | 418 | 2096 | 3409.6974 | 17.7165 | 2752.8487 | 84.8157 | UV254 b, cm-1 | 0.072684 | 0.045116 |  | UV254 b, cm-1 | 0.10126 | 0.055422 |  |  |  | Total dissolved solids | mg/L | 398 | 2114 | 3451.1429 | 23.9006 | 2782.5714 | 85.6967 | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  |  |  | Total dissolved solids | mg/L | 332 | 2424 | 4043.6129 | 38.5185 | 3233.8065 | 89.7335 | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  |  |  | Total dissolved solids | mg/L | 362 | 2388 | 3907.5 | 36.7133 | 3147.75 | 88.4997 | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  |  |  | Total dissolved solids | mg/L | 364 | 2384 | 3899 | 35.461 | 3141.5 | 88.4132
|  |  |  | System permeate flow rate, Qp-sys (gpm) | 1391.5625 | [5 empty] | 1998-05-30 | 5:00 | 25285.4 | 24.1 | 122 | 58 | 32.1091 | 0 | 1301 | 154 |  | 1455 | 1455 | 0.89416 | 0 | 14.0238 | 14.4019 | 8.3584 | 49.5324 | 0.29076 |  | 6.02 | 216 | 0 | 376 | 1810 | 1727.6883 | 4.5476 | 42.5532 | 1051.8442 | 79.4646 | 122 | 90 | 44 | 872 | 583 | 1455 | 1455 | 0.43249 | 0.59931 | 15.9269 | 16.3563 | 3.9851 | 58.0149 | 0.28193 | 6.02 | 6.08 | 148 | 376 | 696 | 717.0223 | -3.0204 | 60.6383 | 546.5111 | 72.9191 | 90 | 79 | 15 | 309 | 274 | 583 | 583 | 0.36373 | 0.53002 | 11.2877 | 11.592 | 8.1321 | 61.3679 | 0.18889 | 6.08 | 6.19 | 176 | 696 | 1260 | 1282.4234 | -1.7796 | 53.1915 | 989.2117 | 82.2081 | 79 | 58 | 15 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.5759 | 13.1735 | 40.3265 | 0.28705 | 6.19 | 6.21 | 312 | 1260 | 1810 | 1998.7013 | -10.4255 | 17.0213 | 1629.3506 | 80.8513 | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE! |  |  |  | Total hardness | mg/L as CaCO3 | 213 | 1380 | 2271.9745 | #VALUE! | 1825.9873 | 88.3351 | Bromideb, mg/L | 157.5817 | 159.9346 |  | Bromideb, mg/L | 156.7775 | 159.2705 |  |  |  | Total hardness | mg/L as CaCO3 | 243 | 1320 | 2163.1776 | 19 | 1741.5888 | 86.0472 | Bromideb, mg/L | 147.5785 | 148.8777 |  | Bromideb, mg/L | 146.232 | 148.392 |  |  |  | Total hardness | mg/L as CaCO3 | 227 | 1310 | 2153.8961 | 24.8344 | 1731.9481 | 86.8934 | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE! |  |  |  | Total hardness | mg/L as CaCO3 | 167 | 1395 | 2345.7097 | 44.1472 | 1870.3548 | 91.0712 | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE! |  |  |  | Total hardness | mg/L as CaCO3 | 190 | 139 | 100.75 | 36.6667 | 119.875 | -58.4984 | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE! |  |  |  | Total hardness | mg/L as CaCO3 | 190 | 137 | 97.25 | 36.6667 | 117.125 | -62.2199
|  |  |  | System feed flow rate, QF-sys (gpm) | 1546.1806 | [5 empty] | 1998-05-31 | 5:00 | 25309.4 | 24.3 | 124 | 60 | 34.5192 | 0 | 1300 | 154 |  | 1454 | 1454 | 0.89409 | 0 | 14.013 | 14.306 | 8.1444 | 49.3364 | 0.28997 |  | 6.03 | 212 | 0 | 368 | 1820 | 1684.8831 | 7.424 | 42.3913 | 1026.4416 | 79.3461 | 124 | 91 | 46 | 874 | 580 | 1454 | 1454 | 0.43164 | 0.6011 | 15.9635 | 16.2972 | 3.8927 | 57.6073 | 0.2829 | 6.03 | 6.11 | 146 | 368 | 682 | 702.531 | -3.0104 | 60.3261 | 535.2655 | 72.7238 | 91 | 80 | 18 | 307 | 273 | 580 | 580 | 0.36203 | 0.52931 | 11.2146 | 11.4491 | 7.9363 | 59.5637 | 0.19222 | 6.11 | 6.19 | 174 | 682 | 1230 | 1253.2674 | -1.8917 | 52.7174 | 967.6337 | 82.018 | 80 | 60 | 18 | 119 | 154 | 273 | 273 | 0.46601 | 0.4359 | 11.1781 | 11.4118 | 12.7545 | 39.2455 | 0.29078 | 6.19 | 6.23 | 310 | 1230 | 1820 | 1940.9091 | -6.6434 | 15.7609 | 1585.4545 | 80.4472 | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Calcium hardness | mg/L as CaCO3 | 165 | 1090 | 1797.0064 | #VALUE! | 1443.5032 | 88.5695 | Alkb, mg/L CaCO3 | 157.7124 | 163.8301 |  | Alkb, mg/L CaCO3 | 155.6214 | 162.1034 |  |  |  | Calcium hardness | mg/L as CaCO3 | 186 | 1010 | 1655.1053 | 19.8276 | 1332.5526 | 86.0418 | Alkb, mg/L CaCO3 | 145.6727 | 148.5309 |  | Alkb, mg/L CaCO3 | 142.7104 | 147.4624 |  |  |  | Calcium hardness | mg/L as CaCO3 | 180 | 970 | 1585.5844 | 26.2295 | 1277.7922 | 85.9132 | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Calcium hardness | mg/L as CaCO3 | 108 | 1100 | 1868 | 52.2124 | 1484 | 92.7224 | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Calcium hardness | mg/L as CaCO3 | 139 | 1080 | 1785.75 | 42.562 | 1432.875 | 90.2992 | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Calcium hardness | mg/L as CaCO3 | 143 | 1100 | 1817.75 | 41.8699 | 1458.875 | 90.1979
[11 empty] | 1998-06-01 | 5:16 | 25333.3 | 24.4 | 127.1 | 66 | 38.1091 | 0 | 1299 | 155 |  | 1454 | 1454 | 0.8934 | 0 | 14.0022 | 14.2528 | 8.564 | 49.8768 | 0.28576 | 7.09 | 6.05 | 224 | 363 | 389 | 1662 | 1771.8065 | -6.6069 | 42.4165 | 1080.4032 | 79.267 | 127.1 | 96 | 50 | 870 | 584 | 1454 | 1454 | 0.43249 | 0.59835 | 15.8904 | 16.1747 | 4.2051 | 57.3449 | 0.28206 | 6.05 | 6.2 | 148 | 389 | 697 | 748.024 | -7.3205 | 61.9537 | 568.512 | 73.9671 | 96 | 85 | 21 | 309 | 275 | 584 | 584 | 0.36458 | 0.52911 | 11.2877 | 11.4896 | 8.1058 | 61.3942 | 0.18715 | 6.2 | 6.24 | 178 | 697 | 1268 | 1280.1673 | -0.95956 | 54.2416 | 988.5836 | 81.9944 | 85 | 66 | 21 | 120 | 155 | 275 | 275 | 0.46929 | 0.43636 | 11.272 | 11.4737 | 13.3577 | 41.1423 | 0.27888 | 6.24 | 6.21 | 305 | 1268 | 1662 | 2013.5484 | -21.1521 | 21.5938 | 1640.7742 | 81.4112 | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Turbidity | ntu | 0.07 | 22 | 38.7618 | #VALUE! | 30.3809 | 99.7696 | T-Hdb, mg/L CaCO3 | 199.9216 | 168.8627 |  | T-Hdb, mg/L CaCO3 | 210.5374 | 177.6288 |  |  |  | Turbidity | ntu | 0.045 | 13 | 23.1424 | 75 | 18.0712 | 99.751 | T-Hdb, mg/L CaCO3 | 201.2061 | 183.9271 |  | T-Hdb, mg/L CaCO3 | 219.1144 | 190.3864 |  |  |  | Turbidity | ntu | 0.51 | 16 | 28.0701 | -209.0909 | 22.0351 | 97.6855 | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Turbidity | ntu | 0.07 | 18 | 31.8813 | 66.6667 | 24.9406 | 99.7193 | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Turbidity | ntu | 0.085 | 17.5 | 30.5613 | 43.3333 | 24.0306 | 99.6463 | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Turbidity | ntu | 0.081 | 16.5 | 28.8143 | 46 | 22.6571 | 99.6425
|  |  |  | Calculate the Required System Influent Pressure | [6 empty] | 1998-06-02 | 5:30 | 25357.9 | 23.6 | 127 | 65 | 37.6991 | 0 | 1302 | 145 |  | 1447 | 1447 | 0.89979 | 0 | 14.0346 | 14.6276 | 9.4971 | 48.8038 | 0.29972 |  | 6.08 | 219 | 0 | 392 | 1629 | 1945.4207 | -19.4242 | 44.1327 | 1168.7103 | 81.2614 | 127 | 96 | 50 | 870 | 577 | 1447 | 1447 | 0.42951 | 0.60124 | 15.8904 | 16.5618 | 4.2444 | 57.2556 | 0.28926 | 6.08 | 6.15 | 150 | 392 | 681 | 756.8873 | -11.1435 | 61.7347 | 574.4437 | 73.8878 | 96 | 85 | 20 | 311 | 266 | 577 | 577 | 0.35779 | 0.53899 | 11.3607 | 11.8407 | 7.9546 | 62.5454 | 0.18931 | 6.15 | 6.25 | 179 | 681 | 1214 | 1267.9248 | -4.4419 | 54.3367 | 974.4624 | 81.6309 | 85 | 65 | 20 | 121 | 145 | 266 | 266 | 0.44855 | 0.45489 | 11.3659 | 11.8462 | 12.9252 | 42.0748 | 0.28155 | 6.25 | 6.26 | 302 | 1214 | 1629 | 1975.0483 | -21.243 | 22.9592 | 1594.5241 | 81.0602 | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Total organic carbon | mg/L | BMRL | 48 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ca-Hdb, mg/L CaCO3 | 151.634 | 126.6928 |  | Ca-Hdb, mg/L CaCO3 | 160.1588 | 133.7322 |  |  |  | Total organic carbon | mg/L | BMRL | 45 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ca-Hdb, mg/L CaCO3 | 160.6366 | 146.3457 |  | Ca-Hdb, mg/L CaCO3 | 175.448 | 151.688 |  |  |  | Total organic carbon | mg/L | BMRL | 48 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Total organic carbon | mg/L | BMRL | 47 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Total organic carbon | mg/L | BMRL | 47 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Total organic carbon | mg/L | BMRL | 47 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  |  |  | Osmotic pressure for stage 13, Dp1 (psi) | 4 | [5 empty] | 1998-06-03 | 5:15 | 25379.6 | 24.4 | 127.4 | 65 | 38.1091 | 0 | 1299 | 154 |  | 1453 | 1453 | 0.89401 | 0 | 14.0022 | 14.2528 | 8.4524 | 49.6385 | 0.28713 | 7.15 | 6.05 | 225 | 376 | 387 | 1633 | 1753.4805 | -7.3779 | 41.8605 | 1070.2403 | 78.9767 | 127.4 | 96 | 50 | 872 | 581 | 1453 | 1453 | 0.43164 | 0.60014 | 15.9269 | 16.2119 | 4.1485 | 57.5515 | 0.28169 | 6.05 | 6.18 | 150 | 387 | 690 | 742.704 | -7.6383 | 61.2403 | 564.852 | 73.4444 | 96 | 84 | 21 | 307 | 274 | 581 | 581 | 0.36288 | 0.5284 | 11.2146 | 11.4153 | 7.9727 | 61.0273 | 0.18705 | 6.18 | 6.25 | 179 | 690 | 1250 | 1262.5438 | -1.0035 | 53.7468 | 976.2719 | 81.6649 | 84 | 65 | 21 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.4737 | 13.0901 | 40.4099 | 0.28393 | 6.25 | 6.24 | 308 | 1250 | 1633 | 1984.026 | -21.4958 | 20.4134 | 1617.013 | 80.9525 | Notes: | [9 empty] | UV254 | cm-1 | 0.02 | 1.4 | 2.4548 | #VALUE! | 1.9274 | 98.9623 | Notes: | [9 empty] | UV254 | cm-1 | 0.0298 | 1.345 | 2.3747 | 86.6368 | 1.8598 | 98.3977 | Notes: | [9 empty] | UV254 | cm-1 | 0.0251 | 1.4225 | 2.5114 | 89.2505 | 1.9669 | 98.7239 | Notes: | [9 empty] | UV254 | cm-1 | 0.0153 | 1.4375 | 2.5386 | 93.9882 | 1.988 | 99.2304 | Notes: | [9 empty] | UV254 | cm-1 | 0.026 | 1.433 | 2.4882 | 89.6825 | 1.9606 | 98.6739 | Notes: | [9 empty] | UV254 | cm-1 | 0.025 | 1.465 | 2.545 | 90.3101 | 2.005 | 98.7531
|  |  |  | Osmotic pressure for stage 23, Dp2 (psi) | 9 | [5 empty] | 1998-06-04 | 6:11 | 25404.1 | 24 | 126.3 | 64 | 37.1091 | 0 | 1301 | 157 |  | 1458 | 1458 | 0.89232 | 0 | 14.0238 | 14.4445 | 8.3322 | 49.7087 | 0.29058 | 7.07 | 5.94 | 225 | 374 | 387 | 1672 | 1729.4331 | -3.435 | 41.8605 | 1058.2166 | 78.7378 | 126.3 | 95 | 49 | 878 | 580 | 1458 | 1458 | 0.43249 | 0.60219 | 16.0365 | 16.5176 | 4.199 | 57.451 | 0.28751 | 5.94 | 6.12 | 148 | 387 | 687 | 748.7966 | -8.9951 | 61.7571 | 567.8983 | 73.939 | 95 | 84 | 20 | 305 | 275 | 580 | 580 | 0.36288 | 0.52586 | 11.1416 | 11.4758 | 7.9126 | 61.5874 | 0.18633 | 6.12 | 6.19 | 178 | 687 | 1273 | 1251.5273 | 1.6868 | 54.0052 | 969.2636 | 81.6355 | 84 | 64 | 20 | 118 | 157 | 275 | 275 | 0.47147 | 0.42909 | 11.0841 | 11.4167 | 13.2627 | 40.7373 | 0.28025 | 6.19 | 6.2 | 309 | 1273 | 1672 | 1997.535 | -19.4698 | 20.155 | 1635.2675 | 81.104 | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | NR | 2.9167 | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | NR | 2.9889 | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | NR | 2.9635 | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | NR | 3.0585 | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | NR | 3.0489 | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | NR | 3.117 | --- | --- | --- | ---
|  |  |  | Osmotic pressure for stage 33, Dp3 (psi) | 16 | [5 empty] | 1998-06-05 | 5:20 | 25427.2 | 24.6 | 127 | 65 | 38.1091 | 0 | 1296 | 156 |  | 1452 | 1452 | 0.89256 | 0 | 13.9699 | 14.1361 | 8.71 | 49.1809 | 0.28743 | 7.18 | 6.07 | 220 | 377 | 389 | 1664 | 1793 | -7.7524 | 43.4447 | 1091 | 79.835 | 127 | 96 | 50 | 869 | 583 | 1452 | 1452 | 0.43185 | 0.59848 | 15.8721 | 16.0609 | 4.241 | 57.259 | 0.2805 | 6.07 | 6.18 | 146 | 389 | 693 | 751.2075 | -8.3994 | 62.4679 | 570.1038 | 74.3906 | 96 | 85 | 21 | 307 | 276 | 583 | 583 | 0.36458 | 0.52659 | 11.2146 | 11.348 | 8.0609 | 61.4391 | 0.1847 | 6.18 | 6.24 | 175 | 693 | 1263 | 1269.1812 | -0.4894 | 55.0129 | 981.0906 | 82.1627 | 85 | 65 | 21 | 120 | 156 | 276 | 276 | 0.47147 | 0.43478 | 11.272 | 11.4061 | 13.3477 | 40.6523 | 0.28058 | 6.24 | 6.28 | 299 | 1263 | 1664 | 2004.5385 | -20.4651 | 23.1362 | 1633.7692 | 81.6988 | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs.
|  |  |  | Pressure losses due to stage hardware, DPs (psi) | 62 | [5 empty] | 1998-06-06 | 5:30 | 25451.3 | 24.5 | 125 | 64 | 35.9292 | 0 | 1303 | 155 |  | 1458 | 1458 | 0.89369 | 0 | 14.0454 | 14.2545 | 9.0536 | 49.5172 | 0.28787 |  | 6.03 | 218 |  | 392 | 1642 | 1854.7226 | -12.9551 | 44.3878 | 1123.3613 | 80.594 | 125 | 95 | 47 | 875 | 583 | 1458 | 1458 | 0.43312 | 0.60014 | 15.9817 | 16.2197 | 4.3061 | 58.6939 | 0.27634 | 6.03 | 6.09 | 146 | 392 | 688 | 761.211 | -10.6411 | 62.7551 | 576.6055 | 74.6794 | 95 | 84 | 20 | 308 | 275 | 583 | 583 | 0.36415 | 0.5283 | 11.2511 | 11.4187 | 7.9872 | 61.5128 | 0.18563 | 6.09 | 6.18 | 176 | 688 | 1256 | 1261.44 | -0.43312 | 55.102 | 974.72 | 81.9435 | 84 | 64 | 20 | 120 | 155 | 275 | 275 | 0.46929 | 0.43636 | 11.272 | 11.4398 | 13.4548 | 40.5452 | 0.28215 | 6.18 | 6.21 | 286 | 1256 | 1642 | 2006.9677 | -22.227 | 27.0408 | 1631.4839 | 82.4699 | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5.
|  |  |  | Pressure losses in a single element, DPe (psi) | 10.3 | [5 empty] | 1998-06-07 | 5:45 | 25475.5 | 24.1 | 127 | 65 | 37.6991 | 0 | 1299 | 154 |  | 1453 | 1453 | 0.89401 | 0 | 14.0022 | 14.3797 | 8.8698 | 49.4311 | 0.2909 |  | 6.06 | 216 |  | 386 | 1664 | 1819.961 | -9.3727 | 44.0415 | 1102.9805 | 80.4167 | 127 | 95 | 50 | 872 | 581 | 1453 | 1453 | 0.43164 | 0.60014 | 15.9269 | 16.3563 | 4.166 | 56.834 | 0.28779 | 6.06 | 6.14 | 148 | 386 | 682 | 743.2048 | -8.9743 | 61.658 | 564.6024 | 73.7869 | 96 | 85 | 20 | 307 | 274 | 581 | 581 | 0.36288 | 0.5284 | 11.2146 | 11.517 | 7.8635 | 62.6365 | 0.18387 | 6.14 | 6.21 | 178 | 682 | 1228 | 1246.7007 | -1.5229 | 53.886 | 964.3504 | 81.542 | 85 | 65 | 20 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.5759 | 13.0068 | 41.9932 | 0.27566 | 6.21 | 6.23 | 292 | 1228 | 1664 | 1957.3506 | -17.6292 | 24.3523 | 1592.6753 | 81.6661 | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters.
|  |  |  | Design permeate pressure, Pp (psi) | 18 | [5 empty] | 1998-06-08 | 5:50 | 25499.6 | 24.3 | 127 | 65 | 37.6991 | 0 | 1302 | 155 |  | 1457 | 1457 | 0.89362 | 0 | 14.0346 | 14.328 | 8.424 | 49.8769 | 0.28727 | 7.11 | 6.02 | 220 | 376 | 382 | 1672 | 1742.8 | -4.2344 | 42.4084 | 1062.4 | 79.2922 | 127 | 96 | 50 | 872 | 585 | 1457 | 1457 | 0.43333 | 0.59849 | 15.9269 | 16.2599 | 4.0491 | 57.4509 | 0.28302 | 6.02 | 6.14 | 150 | 382 | 686 | 727.8188 | -6.096 | 60.733 | 554.9094 | 72.9686 | 96 | 85 | 20 | 310 | 275 | 585 | 585 | 0.365 | 0.52991 | 11.3242 | 11.561 | 7.8807 | 62.6193 | 0.18462 | 6.14 | 6.23 | 182 | 686 | 1280 | 1254.1455 | 2.0199 | 52.356 | 970.0727 | 81.2385 | 85 | 65 | 20 | 120 | 155 | 275 | 275 | 0.46929 | 0.43636 | 11.272 | 11.5077 | 13.4271 | 41.5729 | 0.27681 | 6.23 | 6.24 | 312 | 1280 | 1672 | 2029.4194 | -21.3768 | 18.3246 | 1654.7097 | 81.1447 | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design.
|  |  |  | Mechanical pressure losses per stage, Ls (psi) | 123.8 | [5 empty] | 1998-06-09 | 5:23 | 25523.2 | 24.5 | 127.5 | 66 | 38.1091 | 0 | 1304 | 160 |  | 1464 | 1464 | 0.89071 | 0 | 14.0561 | 14.2654 | 8.2722 | 50.3686 | 0.28322 | 7.15 | 6.06 | 227 | 343 | 390 | 1637 | 1718.45 | -4.9756 | 41.7949 | 1054.225 | 78.4676 | 127.5 | 96 | 50 | 877 | 587 | 1464 | 1464 | 0.43524 | 0.59904 | 16.0183 | 16.2568 | 4.1754 | 57.5746 | 0.28236 | 6.06 | 6.17 | 151 | 390 | 695 | 747.075 | -7.4928 | 61.2821 | 568.5375 | 73.4406 | 96 | 85 | 21 | 307 | 280 | 587 | 587 | 0.36797 | 0.523 | 11.2146 | 11.3816 | 7.9733 | 61.5267 | 0.18499 | 6.17 | 6.21 | 180 | 695 | 1259 | 1259.6607 | -0.052479 | 53.8462 | 977.3304 | 81.5825 | 85 | 66 | 21 | 120 | 160 | 280 | 280 | 0.4802 | 0.42857 | 11.272 | 11.4398 | 13.0625 | 41.4375 | 0.27607 | 6.21 | 6.23 | 309 | 1259 | 1637 | 1971.5 | -20.4337 | 20.7692 | 1615.25 | 80.8698 | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
|  |  |  | Net driving pressure required for permeation, NDP (psi) | 62.5 | [5 empty] | 1998-06-10 | 6:30 | 25549 | 25.3 | 119.9 | 58 | 31.1091 | 0 | 1299 | 154 |  | 1453 | 1453 | 0.89401 | 0 | 14.0022 | 13.8786 | 8.035 | 49.8059 | 0.27865 |  | 6.14 | 242 |  | 396 | 1701 | 1695 | 0.35273 | 38.8889 | 1045.5 | 76.8532 | 119.9 | 90 | 43 | 870 | 583 | 1453 | 1453 | 0.43206 | 0.59876 | 15.8904 | 15.7501 | 4.2606 | 57.6894 | 0.27302 | 6.14 | 6.21 | 152 | 396 | 698 | 760.1166 | -8.8992 | 61.6162 | 578.0583 | 73.7051 | 90 | 78 | 14 | 309 | 274 | 583 | 583 | 0.36373 | 0.53002 | 11.2877 | 11.188 | 8.1165 | 61.8835 | 0.18079 | 6.21 | 6.31 | 179 | 698 | 1281 | 1283.2956 | -0.17921 | 54.798 | 990.6478 | 81.931 | 78 | 58 | 14 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.1725 | 13.6182 | 40.3818 | 0.27667 | 6.31 | 6.26 | 301 | 1281 | 1701 | 2044.6364 | -20.202 | 23.9899 | 1662.8182 | 81.8982 | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
|  |  |  | Flow weighted system pressure losses, Lsys (psi) | 133.6967 | [5 empty] | 1998-06-11 | 5:10 | 25561.5 | 24.6 | 123 | 62 | 33.6991 | 0 | 1303 | 159 |  | 1462 | 1462 | 0.89124 | 0 | 14.0454 | 14.2124 | 8.7677 | 50.0332 | 0.28406 | 7.15 | 6.05 | 224 | 378 | 396 | 1692 | 1805.5346 | -6.7101 | 43.4343 | 1100.7673 | 79.6506 | 123 | 93 | 46 | 872 | 590 | 1462 | 1462 | 0.43546 | 0.59644 | 15.9269 | 16.1164 | 4.2953 | 57.7047 | 0.27929 | 6.05 | 6.16 | 149 | 396 | 709 | 761.0576 | -7.3424 | 62.3737 | 578.5288 | 74.245 | 93 | 81 | 16 | 310 | 280 | 590 | 590 | 0.36925 | 0.52542 | 11.3242 | 11.4589 | 8.2495 | 62.7505 | 0.18261 | 6.16 | 6.21 | 178 | 709 | 1290 | 1296.8929 | -0.53433 | 55.0505 | 1002.9464 | 82.2523 | 81 | 62 | 16 | 121 | 159 | 280 | 280 | 0.47911 | 0.43214 | 11.3659 | 11.5011 | 13.5842 | 41.9158 | 0.27439 | 6.21 | 6.28 | 306 | 1290 | 1692 | 2038.8302 | -20.4982 | 22.7273 | 1664.4151 | 81.6152 | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio.
|  |  |  | Required influent pressure to the system, PI (psi) | 214.1967 | [5 empty] | 1998-06-12 | 6:00 | 25587 | 24.1 | 126.6 | 66 | 37.6991 | 0 | 1303 | 159 |  | 1462 | 1462 | 0.89124 | 0 | 14.0454 | 14.424 | 9.3284 | 49.2725 | 0.29274 |  | 5.9 | 209 |  | 392 | 1775 | 1891.6792 | -6.5735 | 46.6837 | 1141.8396 | 81.6962 | 126.6 | 96 | 50 | 874 | 588 | 1462 | 1462 | 0.43503 | 0.59781 | 15.9635 | 16.3938 | 4.4277 | 56.8723 | 0.28826 | 5.9 | 6.02 | 138 | 392 | 719 | 769.5442 | -7.0298 | 64.7959 | 580.7721 | 76.2385 | 96 | 84 | 20 | 309 | 279 | 588 | 588 | 0.36797 | 0.52551 | 11.2877 | 11.592 | 8.468 | 61.532 | 0.18839 | 6.02 | 6.26 | 174 | 719 | 1338 | 1322.6022 | 1.1508 | 55.6122 | 1020.8011 | 82.9546 | 84 | 66 | 20 | 120 | 159 | 279 | 279 | 0.47802 | 0.43011 | 11.272 | 11.5759 | 14.6275 | 40.3725 | 0.28673 | 6.26 | 6.2 | 276 | 1338 | 1775 | 2139.5094 | -20.5357 | 29.5918 | 1738.7547 | 84.1266 | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL.
|  |  |  | 3: The osmotic pressure can be estimated from Table 6-5 in Part 3 of the | [6 empty] | 1998-06-13 | 6:30 | 25609.9 | 24.2 | 127 | 65 | 37.6991 | 0 | 1299 | 154 |  | 1453 | 1453 | 0.89401 | 0 | 14.0022 | 14.3373 | 9.1829 | 49.118 | 0.29189 |  | 6.02 | 210 |  | 386 | 1726 | 1870.5714 | -8.3761 | 45.5959 | 1128.2857 | 81.3877 | 127 | 96 | 50 | 873 | 580 | 1453 | 1453 | 0.43142 | 0.60083 | 15.9452 | 16.3268 | 4.3114 | 57.1886 | 0.28549 | 6.02 | 6.08 | 140 | 386 | 726 | 756.2724 | -4.1698 | 63.7306 | 571.1362 | 75.4875 | 96 | 85 | 20 | 307 | 273 | 580 | 580 | 0.36203 | 0.52931 | 11.2146 | 11.483 | 8.5925 | 61.9075 | 0.18549 | 6.08 | 6.19 | 176 | 726 | 1356 | 1344.4982 | 0.84822 | 54.4041 | 1035.2491 | 82.9993 | 85 | 65 | 20 | 119 | 154 | 273 | 273 | 0.46601 | 0.4359 | 11.1781 | 11.4456 | 15.0282 | 39.9718 | 0.28634 | 6.19 | 6.2 | 272 | 1356 | 1726 | 2193.6364 | -27.0936 | 29.5337 | 1774.8182 | 84.6745 | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
"ICR Manual for Bench- and Pilot-Scale Treatment Studies."
Note on A1: TSC_ADM: This utility had trouble with their SDS chlorinations as in their response to EPA review and comments "Overall, all SDS residuals were very inconsistent. Our source water is very stable, but we experienced difficulty in retrieving good residuals on a regular basis. This could be in part to H2S levels in the water since odor removal is not preformed until after production. All SDS residuals below 0.1 were listed as 'NR'"
Note on E23: TSC_ADM: Reviewer entered a more appropriate membrane width
Note on S8: TSC_ADM: This is a full-scale plant, thus this time reflects the operational history of the membrane.
Note on W6: TSC_ADM: System Pp was approximated based on the number of parallel pressure vessels in each stage.
Note on DS16: C. Rice: Utility verified all alkalinity data stating that permeate values may be greater than feed values due to CO2.
Note on ED26: TSC_ADM: Data entered by the reviewer since utility did not so do
Note on ED48: TSC_ADM: Data entered by the reviewer since utility did not so do
Note on EM35: C. Rice: Utility verified DBCM data for week 4; the results were verified through the contract lab.
Note on EX26: TSC_ADM: Data entered by the reviewer since utility did not so do
Note on EX48: TSC_ADM: Data entered by the reviewer since utility did not so do
Note on FR26: TSC_ADM: Data entered by the reviewer since utility did not so do
Note on FR48: TSC_ADM: Data entered by the reviewer since utility did not so do
Note on GD26: 12/23/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '25.2'.
Note on GD27: 12/23/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '0.025'.
Note on GD28: 12/23/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '25.175'.
Note on GD29: 12/23/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '23.6'.
Note on GD30: 12/23/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '8.3'.
Note on GD31: 12/23/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '42.45'. 12/23/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NR'.
Note on GL26: TSC_ADM: Data entered by the reviewer since utility did not so do
Note on GL48: TSC_ADM: Data entered by the reviewer since utility did not so do
Note on GW26: 12/23/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '18'.
Note on GW27: 12/23/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '0'.
Note on GW28: 12/23/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '18'.
Note on GW29: 12/23/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '23.5'.
Note on GW30: 12/23/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '8.3'.
Note on GW31: 12/23/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '42'. 12/23/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NR'.
Note on GX26: 12/23/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '28'.
Note on GX27: 12/23/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '0'.
Note on GX28: 12/23/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '28'.
Note on GX29: 12/23/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '23.5'.
Note on GX30: 12/23/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '8.3'.
Note on GX31: 12/23/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '42'. 12/23/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NR'.
Note on HF26: TSC_ADM: Data entered by the reviewer since utility did not so do
Note on HF48: TSC_ADM: Data entered by the reviewer since utility did not so do
Note on HQ27: 12/23/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '0'.
Note on HQ28: 12/23/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '18'.
Note on HQ29: 12/23/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '23.5'.
Note on HQ30: 12/23/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '8.3'.
Note on HQ31: 12/23/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '42'.
Note on HR27: 12/23/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '0'.
Note on HR28: 12/23/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '28'.
Note on HR29: 12/23/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '23.5'.
Note on HR30: 12/23/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '8.3'.
Note on HR31: 12/23/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '42'. 12/23/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NR'.
Note on HZ26: TSC_ADM: Data entered by the reviewer since utility did not so do
Note on HZ48: TSC_ADM: Data entered by the reviewer since utility did not so do

## Sheet2. Weeks 11-20
FIELD-SET 2: PILOT-SCALE MEMBRANE RESULTS: WEEKS 11-20 (FILE: mempilot.xls)
Field 2-1: PWS And Treatment Plant Data |  | Field 2-2: Manufacturer Reported Membrane Characteristics1 |  | Field 2-3: 3-Stage Membrane Pilot System Design Parameters |  | Field 2-4: Foulants And Fouling Indices1 |  | Field 2-5: Pretreatment Used Prior To Membranes1 |  |  | Field 2-6: Membrane Performance Data During Operation With The Test Water | [18 empty] | Field 2-6: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 2-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 2-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 2-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 2-7: System And Stage Water Quality For Week 12 | [9 empty] | Field 2-7: System And Stage Water Quality For Week 12 (continued) | [7 empty] | Field 2-8: System And Stage Water Quality For Week 14 | [9 empty] | Field 2-8: System And Stage Water Quality For Week 14 (continued) | [7 empty] | Field 2-9: System And Stage Water Quality For Week 16 | [9 empty] | Field 2-9: System And Stage Water Quality For Week 16 (continued) | [7 empty] | Field 2-10: System And Stage Water Quality For Week 18 | [9 empty] | Field 2-10: System And Stage Water Quality For Week 18 (continued) | [7 empty] | Field 2-11: System And Stage Water Quality For Week 20 | [9 empty] | Field 2-11: System And Stage Water Quality For Week 20 (continued) | [7 empty] | Field 2-12: Duplicate Analysis Of System And Stage Water Quality For Week 20 | [9 empty] | Field 2-12: Duplicate Analysis Of System And Stage Water Quality For Week 20 (continued) | [7 empty] | Field 2-13: Membrane Cost Parameters
|  | General Information |  | Calculate Temperature Normalized MTCW |  | Parameters Evaluated Prior to Pretreatment |  |  |  |  | System Operating Parameters | [30 empty] | Stage 1 Operating Parameters | [23 empty] | Stage 2 Operating Parameters | [23 empty] | Stage 3 Operating Parameters | [23 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | General Cost Parameters
PWS Name | Collier County Water Department | Membrane manufacturer | Hydranautics | Average yearly temperature of feed water, TavgoC (oC) | 25 | Alkalinity (mg/L as CaCO3) | 290 | Process | Description | Scale | Date | Time | Operation |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  |  |  | System recovery during sample collection (decimal) | 0.8942 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.6 | [6 empty] | System recovery during sample collection (decimal) | 0.9 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.6 | [6 empty] | System recovery during sample collection (decimal) | 0.9 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.6 | [6 empty] | System recovery during sample collection (decimal) | 0.8941 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.5997 | [6 empty] | System recovery during sample collection (decimal) | 0.89 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.61 | [6 empty] | System recovery during sample collection (decimal) | 0.89 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.61 |  |  |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | FL5114069 | Membrane trade name | PVD 1 | Temperature normalized MTCW (gfd/psi) | 0.24 | Calcium Hardness (mg/L as CaCO3) | 220 | Sulfuric Acid Addition | pH adjustment to 5.8-6.0 | full-scale |  |  | time | Influent | PI | PC | PP | QR | Qp | QW | Cleaning Event | QF | QI | Recovery | Recycle | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) |  |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) |  |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) | [6 empty] | System feed flow rate during sample collection (gpm) | 1455 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 873 | [6 empty] | System feed flow rate during sample collection (gpm) | 1457 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 871 | [6 empty] | System feed flow rate during sample collection (gpm) | 1454 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 873 | [6 empty] | System feed flow rate during sample collection (gpm) | 1454 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 872 | [6 empty] | System feed flow rate during sample collection (gpm) | 1454 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 882 | [6 empty] | System feed flow rate during sample collection (gpm) | 1454 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 882 |  |  |  |  | Capital Recovery Interest Rate (%) | N/A
Water Industry Data Base Number (optional) | NA | Membrane element model number | 8040-LSY-PVD1 |  |  | LSI | 7.26 | Anti-Scalant Addition | Argo Scientific Hyperspearse AS120UL | full-scale | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | Indicate with "X" | (gpm) | (gpm) | (decimal) | ratio | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHF (before acid) | pHF (after acid) | TDSp | TDSF (before acid) | TDSF (after acid) | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) |  |  | System influent flow rate during sample collection (gpm) | 1301 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 1455 | [6 empty] | System influent flow rate during sample collection (gpm) | 1300 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 1457 | [6 empty] | System influent flow rate during sample collection (gpm) | 1300 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 1454 | [6 empty] | System influent flow rate during sample collection (gpm) | 1300 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 1454 | [6 empty] | System influent flow rate during sample collection (gpm) | 1300 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 1454 | [6 empty] | System influent flow rate during sample collection (gpm) | 1300 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 1454 |  |  |  |  | Capital Recovery Period (years) | 25
|  | Molecular weight cutoff (Daltons) | 100-300 | Calculate System Permeate, Feed and Waste Flow Rates |  | Dissolved iron (mg/L) |  | Cartridge Filtration | 5 Micron | full-scale | 1998-06-14 | 7:30 | 25635.7 | 24.4 | 122 | 60 | 34.1091 | 0 | 1298 | 154 |  | 1452 | 1452 | 0.89394 | 0 | 13.9915 | 14.2418 | 9.3857 | 47.5051 | 0.2998 |  | 6.01 | 218 |  | 398 | 1684 | 1915.1429 | -13.7258 | 45.2261 | 1156.5714 | 81.1512 | 122 | 92 | 46 | 870 | 582 | 1452 | 1452 | 0.43164 | 0.59917 | 15.8904 | 16.1747 | 4.3336 | 56.6664 | 0.28544 | 6.01 | 6.08 | 150 | 398 | 688 | 768.7216 | -11.7328 | 62.3116 | 583.3608 | 74.2869 | 92 | 81 | 17 | 308 | 274 | 582 | 582 | 0.3633 | 0.52921 | 11.2511 | 11.4525 | 7.9664 | 61.5336 | 0.18612 | 6.08 | 6.19 | 178 | 688 | 1280 | 1261.2847 | 1.4621 | 55.2764 | 974.6423 | 81.7369 | 92 | 81 | 17 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.4737 | 13.4514 | 56.0486 | 0.20471 | 6.19 | 6.22 | 312 | 1280 | 1684 | 2034.2857 | -20.8008 | 21.608 | 1657.1429 | 81.1724 | [108 empty] | Overhead & Profit Factor (% of construction costs) | 10
Official ICR Contact Person |  | Membrane material (e.g., PVD, polyamide, etc.) | Poly Vinyl Derivative | Design system recovery, R (decimal) | 0.9 | Total iron (mg/L) | 0.03 |  |  |  | 1998-06-15 | 5:21 | 25657.2 | 24.6 | 124.6 | 63 | 35.1091 | 0 | 1300 | 155 |  | 1455 | 1455 | 0.89347 | 0 | 14.013 | 14.1797 | 9.4003 | 49.2905 | 0.28768 | 7.19 | 6.02 | 215 | 378 | 396 | 1725 | 1914.0645 | -10.9603 | 45.7071 | 1155.0323 | 81.3858 | 124.6 | 94 | 47 | 872 | 583 | 1455 | 1455 | 0.43249 | 0.59931 | 15.9269 | 16.1164 | 4.3522 | 57.9478 | 0.27812 | 6.02 | 6.16 | 147 | 396 | 713 | 768.4322 | -7.7745 | 62.8788 | 582.2161 | 74.7516 | 94 | 82 | 18 | 308 | 275 | 583 | 583 | 0.36415 | 0.5283 | 11.2511 | 11.385 | 8.424 | 61.576 | 0.18489 | 6.16 | 6.18 | 173 | 713 | 1311 | 1317.8 | -0.51869 | 56.3131 | 1015.4 | 82.9624 | 82 | 63 | 18 | 120 | 155 | 275 | 275 | 0.46929 | 0.43636 | 11.272 | 11.4061 | 14.1345 | 40.3655 | 0.28257 | 6.18 | 6.17 | 292 | 1311 | 1725 | 2099.9032 | -21.7335 | 26.2626 | 1705.4516 | 82.8784 | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | Special Sitework Factor (% of construction costs) | N/A
Mailing Address |  | Membrane construction (e.g., thin-film composite) | Thin Film Composite | Design average system flux, FW (gfd) | 15 | Dissolved aluminum (mg/L) |  |  |  |  | 1998-06-16 | 5:56 | 25681.8 | 24.3 | 124.2 | 62 | 34.6991 | 0 | 1297 | 154 |  | 1451 | 1451 | 0.89387 | 0 | 13.9807 | 14.273 | 8.025 | 50.3759 | 0.28333 | 7.13 | 6.06 | 239 | 377 | 393 | 1637 | 1690 | -3.2376 | 39.1858 | 1041.5 | 77.0523 | 124.2 | 93 | 47 | 869 | 582 | 1451 | 1451 | 0.43142 | 0.5989 | 15.8721 | 16.204 | 4.1568 | 57.4432 | 0.28209 | 6.06 | 6.22 | 155 | 393 | 697 | 748.3643 | -7.3693 | 60.5598 | 570.6821 | 72.8395 | 93 | 82 | 17 | 308 | 274 | 582 | 582 | 0.3633 | 0.52921 | 11.2511 | 11.4864 | 7.9664 | 62.5336 | 0.18368 | 6.22 | 6.3 | 187 | 697 | 1284 | 1270.2847 | 1.0682 | 52.4173 | 983.6423 | 80.989 | 82 | 62 | 17 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.5077 | 13.3403 | 41.6597 | 0.27623 | 6.3 | 6.33 | 324 | 1284 | 1637 | 2032.0519 | -24.1327 | 17.5573 | 1658.026 | 80.4587 | Parameter | Units | Cp-sys-12 | CF-sys-12 | CC-sys-12 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-12 | CI-s1-12 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-14 | CF-sys-14 | CC-sys-14 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-14 | CI-s1-14 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-16 | CF-sys-16 | CC-sys-16 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-16 | CI-s1-16 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-18 | CF-sys-18 | CC-sys-18 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-18 | CI-s1-18 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-20 | CF-sys-20 | CC-sys-20 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-20 | CI-s1-20 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-20 (dup) | CF-sys-20 (dup) | CC-sys-20 (dup) | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-20 (dup) | CI-s1-20 (dup) | CC(calc) | RF (%) | CB | RB (%) | Construction Contingencies (% of construction costs) | N/A
|  | Membrane hydrophobicity | Hydrophillic | Number of elements per pressure vessel, Ne | 6 | Total aluminum (mg/L) | <0.10 |  |  |  | 1998-06-17 | 5:13 | 25705 | 24.6 | 124.5 | 62 | 34.1091 | 0 | 1295 | 154 |  | 1449 | 1449 | 0.89372 | 0 | 13.9591 | 14.1252 | 4.7361 | 54.4047 | 0.25963 | 7.12 | 6.42 | 297 | 375 | 388 | 1415 | 1153.2273 | 18.4998 | 23.4536 | 770.6136 | 61.4593 | 124.5 | 94 | 46 | 869 | 580 | 1449 | 1449 | 0.43058 | 0.59972 | 15.8721 | 16.0609 | 3.5857 | 59.6643 | 0.26919 | 6.42 | 6.61 | 183 | 388 | 659 | 695.1466 | -5.4851 | 52.8351 | 541.5733 | 66.2096 | 94 | 82 | 17 | 307 | 273 | 580 | 580 | 0.36203 | 0.52931 | 11.2146 | 11.348 | 6.749 | 64.251 | 0.17662 | 6.61 | 6.68 | 227 | 659 | 1110 | 1144.8022 | -3.1353 | 41.4948 | 901.9011 | 74.8309 | 82 | 62 | 17 | 119 | 154 | 273 | 273 | 0.46601 | 0.4359 | 11.1781 | 11.311 | 9.7323 | 45.2677 | 0.24987 | 6.68 | 6.72 | 408 | 1110 | 1415 | 1652.4545 | -16.7812 | -5.1546 | 1381.2273 | 70.4611 | Sampling date | MM/DD/YY | 1998-06-23 | 1998-06-23 | 1998-06-23 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-06-23 | 1998-06-23 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-07-06 | 1998-07-06 | 1998-07-06 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-07-06 | 1998-07-06 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-07-22 | 1998-07-22 | 1998-07-22 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-07-22 | 1998-07-22 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-08-03 | 1998-08-03 | 1998-08-03 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-08-03 | 1998-08-03 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-08-17 | 1998-08-17 | 1998-08-17 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-08-17 | 1998-08-17 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-08-17 | 1998-08-17 | 1998-08-17 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-08-17 | 1998-08-17 | --- | --- | --- | --- | Engineering Fee Factor (% of construction costs) | 19
Phone Number |  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Negative | Number of parallel pressure vessels in stage 1, Nv-s(1) | 36 | Fluoride (mg/L) | 0.3 |  |  |  | 1998-06-18 | 3:15 | 25726.9 | 24.9 | 127.9 | 65 | 38.1091 | 0 | 1296 | 157 |  | 1453 | 1453 | 0.89195 | 0 | 13.9699 | 14.0113 | 8.4602 | 49.8807 | 0.2809 | 7.19 | 6.11 | 230 | 384 | 395 | 1691 | 1757.0382 | -3.9053 | 41.7722 | 1076.0191 | 78.6249 | 127.9 | 97 | 50 | 868 | 585 | 1453 | 1453 | 0.43249 | 0.59738 | 15.8539 | 15.9008 | 4.2502 | 58.1998 | 0.27321 | 6.11 | 6.19 | 151 | 395 | 708 | 757.0376 | -6.9262 | 61.7722 | 576.0188 | 73.7856 | 97 | 85 | 21 | 308 | 277 | 585 | 585 | 0.36585 | 0.5265 | 11.2511 | 11.2844 | 8.1688 | 61.8312 | 0.1825 | 6.19 | 6.24 | 183 | 708 | 1286 | 1291.7545 | -0.44747 | 53.6709 | 999.8773 | 81.6978 | 85 | 65 | 21 | 120 | 157 | 277 | 277 | 0.47365 | 0.43321 | 11.272 | 11.3054 | 13.4623 | 40.5377 | 0.27889 | 6.24 | 6.26 | 312 | 1286 | 1691 | 2030.4586 | -20.0744 | 21.0127 | 1658.2293 | 81.1847 | Sampling time | hh:mm | 8:42 | 8:53 | 9:02 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 8:46 | 8:53 | --- | --- | --- | --- | Sampling time | hh:mm | 8:23 | 8:37 | 8:49 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 8:25 | 8:37 | --- | --- | --- | --- | Sampling time | hh:mm | 8:08 | 8:25 | 8:38 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 8:16 | 8:25 | --- | --- | --- | --- | Sampling time | hh:mm | 7:59 | 8:16 | 8:27 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 8:06 | 8:16 | --- | --- | --- | --- | Sampling time | hh:mm | 5:17 | 5:42 | 6:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 5:27 | 5:42 | --- | --- | --- | --- | Sampling time | hh:mm | 5:17 | 5:42 | 6:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 5:27 | 5:42 | --- | --- | --- | --- | 1998 ENR Construction Cost Index (CCI base year 1913) | 5895.11
FAX Number |  |  |  | Number of parallel pressure vessels in stage 2, Nv-s(2) | 18 | Phosphate (mg/L) | 0.05mg/L as PO4 |  |  |  | 1998-06-19 | 5:35 | 25753.2 | 24.5 | 128 | 66 | 38.1091 | 0 | 1303 | 145 |  | 1448 | 1448 | 0.89986 | 0 | 14.0454 | 14.2545 | 9.6129 | 49.2779 | 0.28927 | 7.11 | 6.03 | 223 | 384 | 398 | 1707 | 1970.5862 | -15.4415 | 43.9698 | 1184.2931 | 81.1702 | 128 | 97 | 50 | 873 | 575 | 1448 | 1448 | 0.4293 | 0.6029 | 15.9452 | 16.1826 | 4.3626 | 58.1374 | 0.27835 | 6.03 | 6.15 | 150 | 398 | 714 | 774.5287 | -8.4774 | 62.3116 | 586.2643 | 74.4143 | 97 | 85 | 21 | 310 | 265 | 575 | 575 | 0.35651 | 0.53913 | 11.3242 | 11.4928 | 8.4792 | 61.5208 | 0.18681 | 6.15 | 6.19 | 179 | 714 | 1299 | 1339.8491 | -3.1447 | 55.0251 | 1026.9245 | 82.5693 | 85 | 66 | 21 | 120 | 145 | 265 | 265 | 0.44746 | 0.45283 | 11.272 | 11.4398 | 14.0814 | 40.4186 | 0.28303 | 6.19 | 6.21 | 303 | 1299 | 1707 | 2123.2759 | -24.3864 | 23.8693 | 1711.1379 | 82.2925 | Operation time | hh.hh | 25824.1 | 25824.3 | 25824.5 | --- | --- | --- | --- | --- | Operation time | hh.hh | 25824.2 | 25824.3 | --- | --- | --- | --- | Operation time | hh.hh | 26105.5 | 26105.7 | 26105.9 | --- | --- | --- | --- | --- | Operation time | hh.hh | 26105.5 | 26105.7 | --- | --- | --- | --- | Operation time | hh.hh | 26373.6 | 26374.1 | 26374.1 | --- | --- | --- | --- | --- | Operation time | hh.hh | 26373.7 | 26373.9 | --- | --- | --- | --- | Operation time | hh.hh | 26631.5 | 26631.8 | 26632 | --- | --- | --- | --- | --- | Operation time | hh.hh | 26631.6 | 26631.8 | --- | --- | --- | --- | Operation time | hh.hh | 26874.1 | 26874.5 | 26874.8 | --- | --- | --- | --- | --- | Operation time | hh.hh | 26874.3 | 26874.5 | --- | --- | --- | --- | Operation time | hh.hh | 26874.1 | 26874.5 | 26874.8 | --- | --- | --- | --- | --- | Operation time | hh.hh | 26874.3 | 26874.5 | --- | --- | --- | --- | 1998 Producers Price Index (PPI base year 1967 = 100) | 123.9
E-Mail Address (optional) |  | Design Parameters |  | Number of parallel pressure vessels in stage 3, Nv-s(3) | 7 | Sulfate (mg/L) | 20 |  |  |  | 1998-06-20 | 5:30 | 25777.3 | 24.3 | 129 | 65 | 37.6991 | 0 | 1303 | 153 |  | 1456 | 1456 | 0.89492 | 0 | 14.0454 | 14.339 | 8.8337 | 50.4672 | 0.28413 |  | 5.97 | 218 |  | 386 | 1720 | 1816.7451 | -5.6247 | 43.5233 | 1101.3725 | 80.2065 | 129 | 96 | 50 | 873 | 583 | 1456 | 1456 | 0.4327 | 0.59959 | 15.9452 | 16.2786 | 4.1619 | 58.3381 | 0.27904 | 5.97 | 6.04 | 148 | 386 | 716 | 742.3877 | -3.6854 | 61.658 | 564.1938 | 73.7679 | 96 | 86 | 20 | 310 | 273 | 583 | 583 | 0.3633 | 0.53173 | 11.3242 | 11.561 | 8.5286 | 62.4714 | 0.18506 | 6.04 | 6.11 | 172 | 716 | 1302 | 1333.7289 | -2.4369 | 55.4404 | 1024.8645 | 83.2173 | 86 | 65 | 20 | 120 | 153 | 273 | 273 | 0.46492 | 0.43956 | 11.272 | 11.5077 | 13.8102 | 41.6898 | 0.27603 | 6.11 | 6.19 | 310 | 1302 | 1720 | 2080.0392 | -20.9325 | 19.6891 | 1691.0196 | 81.6679 | pH | --- | 6.24 | 6.04 | 6.27 | --- | --- | --- | --- | --- | pH | --- | 6.09 | 6.04 | --- | --- | --- | --- | pH | --- | 5.91 | 5.87 | 0.25139 | --- | --- | --- | --- | --- | pH | --- | 5.83 | 5.87 | --- | --- | --- | --- | pH | --- | 6.3 | 6.22 | 6.47 | --- | --- | --- | --- | --- | pH | --- | 613 | 6.22 | --- | --- | --- | --- | pH | --- | 6.2 | 6.03 | 6.19 | --- | --- | --- | --- | --- | pH | --- | 5.99 | 6.03 | --- | --- | --- | --- | pH | --- | 6.14 | 5.99 | 6.37 | --- | --- | --- | --- | --- | pH | --- | 5.94 | 5.99 | --- | --- | --- | --- | pH | --- | 6.14 | 5.99 | 6.37 | --- | --- | --- | --- | --- | pH | --- | 5.94 | 5.99 | --- | --- | --- | --- | Labor Rate + Fringe ($/work-hour) | 24.39
|  | Element size (e.g., 2.5" x 40", 4" x 40", etc.) | 8" X 40" | Permeate flow rate per element, Qp-e (gpm) | 3.8021 | Calcium (mg/L) | 82 |  |  |  | 1998-06-21 | 9:29 | 25789 | 24.6 | 121.9 | 60 | 32.6991 | 0 | 1308 | 147 |  | 1455 | 1455 | 0.89897 | 0 | 14.0993 | 14.267 | 9.3178 | 48.9331 | 0.29156 | 7.07 | 6.05 | 221 | 384 | 392 | 1718 | 1913.551 | -11.3825 | 43.6224 | 1152.7755 | 80.8289 | 121.9 | 92 | 45 | 876 | 579 | 1455 | 1455 | 0.43164 | 0.60206 | 16 | 16.1903 | 4.3736 | 57.5764 | 0.2812 | 6.05 | 6.1 | 143 | 392 | 710 | 768.7254 | -8.2712 | 63.5204 | 580.3627 | 75.3602 | 92 | 80 | 15 | 311 | 268 | 579 | 579 | 0.35949 | 0.53713 | 11.3607 | 11.4959 | 8.4858 | 62.5142 | 0.18389 | 6.1 | 6.19 | 173 | 710 | 1308 | 1333.1604 | -1.9236 | 55.8673 | 1021.5802 | 83.0655 | 80 | 60 | 15 | 121 | 147 | 268 | 268 | 0.45292 | 0.45149 | 11.3659 | 11.5011 | 14.3556 | 40.6444 | 0.28297 | 6.19 | 6.16 | 291 | 1308 | 1718 | 2145.1224 | -24.8616 | 25.7653 | 1726.5612 | 83.1457 | Temperature | oC | 24.5 | 25.1 | 25.3 | --- | --- | --- | --- | --- | Temperature | oC | 25 | 25.1 | --- | --- | --- | --- | Temperature | oC | 25 | 25.5 | 25.7 | --- | --- | --- | --- | --- | Temperature | oC | 25.2 | 25.5 | --- | --- | --- | --- | Temperature | oC | 24.8 | 25 | 25.2 | --- | --- | --- | --- | --- | Temperature | oC | 24.8 | 25 | --- | --- | --- | --- | Temperature | oC | 25.1 | 25.3 | 25.4 | --- | --- | --- | --- | --- | Temperature | oC | 25.1 | 25.3 | --- | --- | --- | --- | Temperature | oC | 25 | 25.4 | 25.6 | --- | --- | --- | --- | --- | Temperature | oC | 25.3 | 25.4 | --- | --- | --- | --- | Temperature | oC | 25 | 25.4 | 25.6 | --- | --- | --- | --- | --- | Temperature | oC | 25.3 | 25.4 | --- | --- | --- | --- | Labor Overhead Factor (% of labor) | 10
Technical ICR Contact Person |  | Active membrane area of membrane element used, A (ft2) | 365 | Permeate flow rate per pressure vessel, Qp-v (gpm) | 22.8125 | Barium (mg/L) | 0.008 |  |  |  | 1998-06-22 | 2:35 | 25794.1 | 24.3 | 122.2 | 60 | 32.6991 | 0 | 1299 | 156 |  | 1455 | 1455 | 0.89278 | 0 | 14.0022 | 14.295 | 8.8295 | 49.5714 | 0.28837 | 7.14 | 6.02 | 224 | 381 | 395 | 1728 | 1818.9038 | -5.2606 | 43.2911 | 1106.9519 | 79.7643 | 122.2 | 91 | 45 | 871 | 584 | 1455 | 1455 | 0.4327 | 0.59863 | 15.9087 | 16.2413 | 4.3643 | 57.2357 | 0.28376 | 6.02 | 6.14 | 145 | 395 | 716 | 767.8596 | -7.243 | 63.2911 | 581.4298 | 75.0615 | 91 | 80 | 15 | 308 | 276 | 584 | 584 | 0.365 | 0.5274 | 11.2511 | 11.4864 | 8.4754 | 62.0246 | 0.18519 | 6.14 | 6.16 | 172 | 716 | 1311 | 1323.0725 | -0.92086 | 56.4557 | 1019.5362 | 83.1296 | 80 | 60 | 15 | 120 | 156 | 276 | 276 | 0.47147 | 0.43478 | 11.272 | 11.5077 | 14.0677 | 40.9323 | 0.28114 | 6.16 | 6.17 | 295 | 1311 | 1728 | 2092.5385 | -21.096 | 25.3165 | 1701.7692 | 82.6651 | Alkalinity | mg/L as CaCO3 | 100 | 86 | 170 | -32.3251 | 119.0148 | -16.2791 | 33.8405 | -195.5036 | Alkalinity | mg/L as CaCO3 | 69 | 86 | 111.5 | 19.7674 | 98.75 | 30.1266 | Alkalinity | mg/L as CaCO3 | 100 | 82 | 210 | -80 | 138.0952 | -21.9512 | 10.7823 | -827.4452 | Alkalinity | mg/L as CaCO3 | 61 | 82 | 113.2133 | 25.6098 | 97.6067 | 37.5043 | Alkalinity | mg/L as CaCO3 | 128 | 112 | 230 | -32 | 113.913 | -14.2857 | 48.5292 | -163.7586 | Alkalinity | mg/L as CaCO3 | 77 | 112 | 164.5904 | 31.25 | 138.2952 | 44.322 | Alkalinity | mg/L as CaCO3 | 110 | 96 | 215 | -22.2002 | 110.3257 | -14.5833 | 43.901 | -150.5638 | Alkalinity | mg/L as CaCO3 | 70 | 96 | 134.9553 | 27.0833 | 115.4777 | 39.3822 | Alkalinity | mg/L as CaCO3 | 128 | 106 | 255 | -72 | 128.2353 | -20.7547 | 27.5431 | -364.7266 | Alkalinity | mg/L as CaCO3 | 77 | 106 | 150.7168 | 27.3585 | 128.3584 | 40.0117 | Alkalinity | mg/L as CaCO3 | 129 | 106 | 270 | -80.0909 | 129.6633 | -21.6981 | 23.9769 | -438.0189 | Alkalinity | mg/L as CaCO3 | 79 | 106 | 147.6329 | 25.4717 | 126.8164 | 37.7052 | Electric Rate ($/kW-h) | 0.05
Mailing Address |  | Design flux, FW (gfd) | 30 | Permeate flow rate from stage 1, Qp-s(1) (gpm) | 821.25 | Strontium (mg/L) | 0.6 |  |  |  | 1998-06-23 | 5:22 | 25820.8 | 24.4 | 127.9 | 65 | 38.1091 | 0 | 1300 | 155 |  | 1455 | 1455 | 0.89347 | 0 | 14.013 | 14.2638 | 9.0887 | 49.2521 | 0.28961 | 7.16 | 6.07 | 222 | 380 | 397 | 1700 | 1864.7419 | -9.6907 | 44.0806 | 1130.871 | 80.3691 | 127.9 | 97 | 50 | 870 | 585 | 1455 | 1455 | 0.43291 | 0.59794 | 15.8904 | 16.1747 | 4.3067 | 58.1433 | 0.27819 | 6.07 | 6.16 | 150 | 397 | 711 | 764.3333 | -7.5012 | 62.2166 | 580.6667 | 74.1676 | 97 | 85 | 21 | 310 | 275 | 585 | 585 | 0.365 | 0.52991 | 11.3242 | 11.5268 | 8.3342 | 61.6658 | 0.18692 | 6.16 | 6.22 | 178 | 711 | 1297 | 1311.8364 | -1.1439 | 55.1637 | 1011.4182 | 82.4009 | 85 | 65 | 21 | 120 | 155 | 275 | 275 | 0.46929 | 0.43636 | 11.272 | 11.4737 | 13.8016 | 40.1984 | 0.28543 | 6.22 | 6.2 | 302 | 1297 | 1700 | 2067.3226 | -21.6072 | 23.9295 | 1682.1613 | 82.0469 | Total dissolved solids | mg/L | 276 | 600 | 3528 | 3338.3819 | 5.3747 | 54 | 1807.1191 | 84.7271 | Total dissolved solids | mg/L | 182 | 600 | 1227 | 69.6667 | 913.5 | 80.0766 | Total dissolved solids | mg/L | 234 | 572 | 3580 | 3614 | -0.94972 | 59.0909 | 1909.31 | 87.7443 | Total dissolved solids | mg/L | 162 | 572 | 1181.4027 | 71.6783 | 876.7014 | 81.5216 | Total dissolved solids | mg/L | 266 | 540 | 3272 | 3006 | 8.1296 | 50.7407 | 1626.9369 | 83.6503 | Total dissolved solids | mg/L | 182 | 540 | 1077.9243 | 66.2963 | 808.9621 | 77.502 | Total dissolved solids | mg/L | 246 | 526 | 3502 | 2890.0038 | 17.4756 | 53.2319 | 1567.9801 | 84.311 | Total dissolved solids | mg/L | 165 | 526 | 1066.8797 | 68.6312 | 796.4399 | 79.2828 | Total dissolved solids | mg/L | 265 | 564 | 3396 | 2983.1818 | 12.156 | 53.0142 | 1630.3009 | 83.7453 | Total dissolved solids | mg/L | 169 | 564 | 1173.0734 | 70.0355 | 868.5367 | 80.542 | Total dissolved solids | mg/L | 253 | 546 | 3368 | 2916.6364 | 13.4015 | 53.663 | 1590.9036 | 84.0971 | Total dissolved solids | mg/L | 174 | 546 | 1119.6084 | 68.1319 | 832.8042 | 79.1067 | Fuel Oil Rate ($/gal) | 0.43
|  | Net driving pressure at the design flux, NDP (psi) | 125 | Permeate flow rate from stage 2, Qp-s(2) (gpm) | 410.625 | Reactive silica (mg/L as SiO2) | 18 |  |  |  | 1998-06-24 | 6:06 | 25844.2 | 24.4 | 122 | 60 | 32.6991 | 0 | 1298 | 154 |  | 1452 | 1452 | 0.89394 | 0 | 13.9915 | 14.2418 | 9.4379 | 48.863 | 0.29146 | 7.18 | 6.02 | 221 | 383 | 402 | 1752 | 1927.5714 | -10.0212 | 45.0249 | 1164.7857 | 81.0266 | 122 | 92 | 45 | 871 | 581 | 1452 | 1452 | 0.43142 | 0.59986 | 15.9087 | 16.1933 | 4.4614 | 57.5386 | 0.28143 | 6.02 | 6.08 | 147 | 402 | 723 | 784.2806 | -8.4759 | 63.4328 | 593.1403 | 75.2167 | 92 | 80 | 15 | 307 | 274 | 581 | 581 | 0.36288 | 0.5284 | 11.2146 | 11.4153 | 8.5656 | 62.4344 | 0.18284 | 6.08 | 6.15 | 174 | 723 | 1331 | 1338.1204 | -0.53497 | 56.7164 | 1030.5602 | 83.116 | 80 | 60 | 15 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.4737 | 14.4381 | 40.5619 | 0.28287 | 6.15 | 6.12 | 292 | 1331 | 1752 | 2140.6104 | -22.181 | 27.3632 | 1735.8052 | 83.1778 | Total hardness | mg/L as CaCO3 | 122 | 292 | 2030 | 1728.8053 | 14.8372 | 58.2192 | 925.365 | 86.816 | Total hardness | mg/L as CaCO3 | 77 | 292 | 614.5 | 73.6301 | 453.25 | 83.0116 | Total hardness | mg/L as CaCO3 | 110 | 310 | 2220 | 2110 | 4.955 | 64.5161 | 1101.3077 | 90.0119 | Total hardness | mg/L as CaCO3 | 71 | 310 | 665.2372 | 77.0968 | 487.6186 | 85.4394 | Total hardness | mg/L as CaCO3 | 136 | 290 | 1880 | 1676 | 10.8511 | 53.1034 | 900.9062 | 84.9041 | Total hardness | mg/L as CaCO3 | 85 | 290 | 598.0293 | 70.6897 | 444.0146 | 80.8565 | Total hardness | mg/L as CaCO3 | 124 | 324 | 2140 | 2012.5741 | 5.9545 | 61.7284 | 1068.2715 | 88.3925 | Total hardness | mg/L as CaCO3 | 79.5 | 324 | 690.3299 | 75.463 | 507.1649 | 84.3246 | Total hardness | mg/L as CaCO3 | 145 | 334 | 2160 | 1863.1818 | 13.7416 | 56.5868 | 1008.0163 | 85.6153 | Total hardness | mg/L as CaCO3 | 87 | 334 | 714.8636 | 73.9521 | 524.4318 | 83.4106 | Total hardness | mg/L as CaCO3 | 146 | 336 | 2140 | 1873.2727 | 12.4639 | 56.5476 | 1013.5825 | 85.5956 | Total hardness | mg/L as CaCO3 | 86 | 336 | 721.4895 | 74.4048 | 528.7448 | 83.7351 | Natural Gas Rate ($/ft3) | N/A
Phone Number |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.24 | Permeate flow rate from stage 3, Qp-s(3) (gpm) | 159.6875 | Turbidity (ntu) | <0.5 |  |  |  | 1998-06-25 | 5:27 | 25860.3 | 24.5 | 127.4 | 66 | 38.6991 | 0 | 1304 | 142 |  | 1446 | 1446 | 0.9018 | 0 | 14.0561 | 14.2654 | 9.2261 | 48.7748 | 0.29248 | 7.11 | 6.1 | 227 | 375 | 392 | 1660 | 1907.2113 | -14.8922 | 42.0918 | 1149.6056 | 80.2541 | 127.4 | 97 | 51 | 874 | 572 | 1446 | 1446 | 0.42824 | 0.60443 | 15.9635 | 16.2012 | 4.2512 | 56.9488 | 0.28449 | 6.1 | 6.31 | 151 | 392 | 699 | 760.2413 | -8.7613 | 61.4796 | 576.1206 | 73.7902 | 97 | 85 | 21 | 310 | 262 | 572 | 572 | 0.35397 | 0.54196 | 11.3242 | 11.4928 | 8.2604 | 61.7396 | 0.18615 | 6.31 | 6.28 | 180 | 699 | 1270 | 1313.084 | -3.3924 | 54.0816 | 1006.042 | 82.1081 | 85 | 66 | 21 | 120 | 142 | 262 | 262 | 0.44091 | 0.45802 | 11.272 | 11.4398 | 13.6421 | 40.8579 | 0.27999 | 6.28 | 6.27 | 311 | 1270 | 1660 | 2080.4225 | -25.3267 | 20.6633 | 1675.2113 | 81.4352 | Calcium hardness | mg/L as CaCO3 | 92 | 230 | 1540 | 1396.3478 | 9.3281 | 60 | 744.1433 | 87.6368 | Calcium hardness | mg/L as CaCO3 | 57 | 230 | 489.5 | 75.2174 | 359.75 | 84.1557 | Calcium hardness | mg/L as CaCO3 | 84 | 228 | 1550 | 1524 | 1.6774 | 63.1579 | 797.7415 | 89.4703 | Calcium hardness | mg/L as CaCO3 | 56 | 228 | 483.6519 | 75.4386 | 355.8259 | 84.262 | Calcium hardness | mg/L as CaCO3 | 100 | 230 | 1460 | 1400 | 4.1096 | 56.5217 | 745.7 | 86.5898 | Calcium hardness | mg/L as CaCO3 | 64 | 230 | 479.4286 | 72.1739 | 354.7143 | 81.9573 | Calcium hardness | mg/L as CaCO3 | 98 | 240 | 1620 | 1438.8876 | 11.1798 | 59.1667 | 768.4328 | 87.2468 | Calcium hardness | mg/L as CaCO3 | 63 | 240 | 505.1959 | 73.75 | 372.5979 | 83.0917 | Calcium hardness | mg/L as CaCO3 | 108 | 276 | 1660 | 1635.2727 | 1.4896 | 60.8696 | 875.1256 | 87.6589 | Calcium hardness | mg/L as CaCO3 | 68 | 276 | 596.7273 | 75.3623 | 436.3636 | 84.4167 | Calcium hardness | mg/L as CaCO3 | 110 | 272 | 1640 | 1582.7273 | 3.4922 | 59.5588 | 849.7283 | 87.0547 | Calcium hardness | mg/L as CaCO3 | 69 | 272 | 585.0175 | 74.6324 | 428.5087 | 83.8976 | Current Process Water Rate ($/1000 gal) | 1.9
FAX Number |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | Permeate flow rate from system, Qp-sys (gpm) | 1391.5625 | SDI | 1.0-1.5 |  |  |  | 1998-06-26 | 0:28 | 25873.5 | 24.4 | 127.1 | 65 | 37.6991 | 0 | 1299 | 154 |  | 1453 | 1453 | 0.89401 | 0 | 14.0022 | 14.2528 | 9.6524 | 48.6984 | 0.29267 | 7.14 | 5.98 | 210 | 378 | 395 | 1749 | 1955.487 | -11.806 | 46.8354 | 1175.2435 | 82.1314 | 127.1 | 97 | 50 | 871 | 582 | 1453 | 1453 | 0.43185 | 0.59945 | 15.9087 | 16.1933 | 4.4581 | 57.5919 | 0.28117 | 5.98 | 6.08 | 140 | 395 | 718 | 776.6237 | -8.1649 | 64.557 | 585.8119 | 76.1015 | 97 | 85 | 20 | 308 | 274 | 582 | 582 | 0.3633 | 0.52921 | 11.2511 | 11.4525 | 8.6225 | 62.3775 | 0.1836 | 6.08 | 6.13 | 166 | 718 | 1326 | 1338.4964 | -0.94241 | 57.9747 | 1028.2482 | 83.856 | 85 | 65 | 20 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.4737 | 14.5075 | 40.4925 | 0.28335 | 6.13 | 6.13 | 282 | 1326 | 1749 | 2139.5065 | -22.3274 | 28.6076 | 1732.7532 | 83.7253 | Turbidity | ntu | 0.1 | 0.21 | 18 | 1.1397 | 93.6683 | 52.381 | 0.61982 | 83.8664 | Turbidity | ntu | 0.07 | 0.21 | 0.42 | 66.6667 | 0.315 | 77.7778 | Turbidity | ntu | 0.06 | 0.65 | 22 | 5.96 | 72.9091 | 90.7692 | 2.9844 | 97.9895 | Turbidity | ntu | 0.05 | 0.65 | 1.5418 | 92.3077 | 1.0959 | 95.4376 | Turbidity | ntu | 0.04 | 0.16 | 17 | 1.24 | 92.7059 | 75 | 0.63603 | 93.711 | Turbidity | ntu | 0.04 | 0.16 | 0.34031 | 75 | 0.25015 | 84.0099 | Turbidity | ntu | 0.055 | 0.67 | 20 | 5.8624 | 70.6882 | 91.791 | 2.9586 | 98.141 | Turbidity | ntu | 0.085 | 0.67 | 1.5465 | 87.3134 | 1.1082 | 92.3302 | Turbidity | ntu | 0.065 | 0.26 | 18 | 1.8377 | 89.7904 | 75 | 0.95541 | 93.1967 | Turbidity | ntu | 0.055 | 0.26 | 0.5761 | 78.8462 | 0.41805 | 86.8437 | Turbidity | ntu | 0.065 | 0.3 | 18 | 2.2014 | 87.7702 | 78.3333 | 1.1381 | 94.2885 | Turbidity | ntu | 0.055 | 0.3 | 0.67778 | 81.6667 | 0.48889 | 88.75 | Modifications to Existing Plant (% of construction costs) | N/A
E-Mail Address (optional) |  | Maximum flow rate to the element, QI, max (gpm) | 75 | Feed flow rate to system, QF-sys (gpm) | 1546.1806 | MFI |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | 1998-06-27 | 3:00 | 25890.1 | 24.2 | 126 | 65 | 37.6991 | 0 | 1300 | 154 |  | 1454 | 1454 | 0.89409 | 0 | 14.013 | 14.3483 | 9.0842 | 48.7167 | 0.29453 |  | 5.97 | 212 |  | 386 | 1762 | 1854.8312 | -5.2685 | 45.0777 | 1120.4156 | 81.0784 | 126 | 96 | 50 | 874 | 580 | 1454 | 1454 | 0.43164 | 0.6011 | 15.9635 | 16.3455 | 4.2784 | 56.7216 | 0.28817 | 5.97 | 6.02 | 142 | 386 | 752 | 753.6828 | -0.22377 | 63.2124 | 569.8414 | 75.0808 | 96 | 85 | 20 | 307 | 273 | 580 | 580 | 0.36203 | 0.52931 | 11.2146 | 11.483 | 9.1237 | 61.3763 | 0.18709 | 6.02 | 6.09 | 168 | 752 | 1336 | 1408.7326 | -5.4441 | 56.4767 | 1080.3663 | 84.4497 | 85 | 65 | 20 | 119 | 154 | 273 | 273 | 0.46601 | 0.4359 | 11.1781 | 11.4456 | 14.5568 | 40.4432 | 0.283 | 6.09 | 6.11 | 286 | 1336 | 1762 | 2147.3636 | -21.8708 | 25.9067 | 1741.6818 | 83.5791 | Ammonia | mg NH3-N / L | 0.24 | 0.29 | 0.84 | 0.71259 | 15.1679 | 17.2414 | 0.47628 | 49.6099 | Total organic carbon | mg/L | BMRL | 8 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | 0.21 | 0.22 | 0.84 | 0.31 | 63.0952 | 4.5455 | 0.25957 | 19.0955 | Total organic carbon | mg/L | BMRL | 8 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | 0.21 | 0.24 | 0.89 | 0.51 | 42.6966 | 12.5 | 0.35901 | 41.5054 | Total organic carbon | mg/L | BMRL | 8 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | 0.223 | 0.234 | 0.92 | 0.32687 | 64.4705 | 4.7009 | 0.27493 | 18.8899 | Total organic carbon | mg/L | BMRL | 8 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | 0.32 | 0.32 | 0.94 | 0.32 | 65.9574 | 0 | 0.32 | 0 | Total organic carbon | mg/L | BMRL | NR | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | 0.33 | 0.32 | 0.96 | 0.23909 | 75.0947 | -3.125 | 0.28434 | -16.0592 | Total organic carbon | mg/L | BMRL | 8 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | Minimum flow rate to the element, QI, min (gpm) | 72 | Concentrate-waste flow rate from system, QW-sys (gpm) | 154.6181 | MPFI |  | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | 1998-06-28 | 6:00 | 25917.1 | 24.1 | 122 | 62 | 33.6991 | 0 | 1300 | 154 |  | 1454 | 1454 | 0.89409 | 0 | 14.013 | 14.3908 | 8.3532 | 49.9476 | 0.28812 |  | 6.02 | 208 |  | 368 | 1740 | 1718.6494 | 1.227 | 43.4783 | 1043.3247 | 80.0637 | 122 | 94 | 46 | 872 | 582 | 1454 | 1454 | 0.43206 | 0.59972 | 15.9269 | 16.3563 | 3.988 | 58.012 | 0.28195 | 6.02 | 6.11 | 140 | 368 | 688 | 709.6082 | -3.1407 | 61.9565 | 538.8041 | 74.0165 | 94 | 82 | 16 | 308 | 274 | 582 | 582 | 0.3633 | 0.52921 | 11.2511 | 11.5545 | 8.0601 | 63.9399 | 0.18071 | 6.11 | 6.18 | 172 | 688 | 1362 | 1268.0292 | 6.8995 | 53.2609 | 978.0146 | 82.4134 | 82 | 62 | 16 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.5759 | 15.0078 | 40.9922 | 0.28239 | 6.18 | 6.19 | 282 | 1362 | 1740 | 2203.5584 | -26.6413 | 23.3696 | 1782.7792 | 84.182 | Total organic carbon | mg/L | BMRL | 8 | 72 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.011 | 0.243 | 0.591 | 95.4733 | 0.417 | 97.3621 | Total organic carbon | mg/L | BMRL | 8 | 70 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.011 | 0.233 | 0.56297 | 95.279 | 0.39798 | 97.2361 | Total organic carbon | mg/L | BMRL | 8 | 68 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.028 | 0.276 | 0.64864 | 89.8551 | 0.46232 | 93.9436 | Total organic carbon | mg/L | BMRL | 8 | 74 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.0094 | 0.242 | 0.5905 | 96.1157 | 0.41625 | 97.7417 | Total organic carbon | mg/L | BMRL | NR | 79 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.01 | 0.227 | 0.5616 | 95.5947 | 0.3943 | 97.4639 | Total organic carbon | mg/L | BMRL | 8 | 79 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.006 | 0.226 | 0.56523 | 97.3451 | 0.39562 | 98.4834
Plant Name | Collier Co. North Regional Water Plant | Total width of all membrane envelopes in the element, w (ft) | 63.4 |  |  |  |  | is to list the pretreatment processes used in this particular pilot-scale run. |  |  | 1998-06-29 | 5:44 | 25942.2 | 24.4 | 121.8 | 61 | 32.6991 | 0 | 1301 | 154 |  | 1455 | 1455 | 0.89416 | 0 | 14.0238 | 14.2747 | 8.9853 | 49.7156 | 0.28713 | 7.05 | 6.04 | 215 | 381 | 387 | 1674 | 1840.0649 | -9.9202 | 44.4444 | 1113.5325 | 80.6921 | 121.8 | 92 | 45 | 874 | 581 | 1455 | 1455 | 0.43206 | 0.60069 | 15.9635 | 16.2491 | 4.2577 | 57.6423 | 0.2819 | 6.04 | 6.15 | 144 | 387 | 695 | 752.5456 | -8.2799 | 62.7907 | 569.7728 | 74.7268 | 92 | 80 | 15 | 307 | 274 | 581 | 581 | 0.36288 | 0.5284 | 11.2146 | 11.4153 | 8.1599 | 62.8401 | 0.18166 | 6.15 | 6.2 | 172 | 695 | 1273 | 1280.9891 | -0.62758 | 55.5556 | 987.9945 | 82.591 | 80 | 61 | 15 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.4737 | 13.6043 | 41.8957 | 0.27386 | 6.2 | 6.2 | 294 | 1273 | 1674 | 2035.8571 | -21.6163 | 24.031 | 1654.4286 | 82.2295 | UV254 | cm-1 | 0.013 | 0.243 | 2.33 | 2.1869 | 6.1411 | 94.6502 | 1.0999 | 98.8181 | SUVA | L/(mg*m) | NR | 3.0375 | --- | --- | --- | --- | UV254 | cm-1 | 0.011 | 0.233 | 2.2 | 2.231 | -1.4091 | 95.279 | 1.1114 | 99.0102 | SUVA | L/(mg*m) | NR | 2.9125 | --- | --- | --- | --- | UV254 | cm-1 | 0.028 | 0.276 | 2.71 | 2.508 | 7.4539 | 89.8551 | 1.2598 | 97.7774 | SUVA | L/(mg*m) | NR | 3.45 | --- | --- | --- | --- | UV254 | cm-1 | BMRL | 0.242 | 2.245 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.025 | --- | --- | --- | --- | UV254 | cm-1 | 0.014 | 0.227 | 2.09 | 1.9504 | 6.6812 | 93.8326 | 0.98661 | 98.581 | SUVA | L/(mg*m) | NR | NR | --- | --- | --- | --- | UV254 | cm-1 | 0.01 | 0.226 | 2.07 | 1.9736 | 4.6552 | 95.5752 | 0.9963 | 98.9963 | SUVA | L/(mg*m) | NR | 2.825 | --- | --- | --- | ---
Treatment Plant Category | Category II | Feed spacer thickness, T (ft) | 0.0023 | Calculate the Feed Flow Rates at the End of Each Stage | [6 empty] | 1998-06-30 | 2:47 | 25963.2 | 24.4 | 122.1 | 61 | 32.6991 | 0 | 1301 | 154 |  | 1455 | 1455 | 0.89416 | 0 | 14.0238 | 14.2747 | 8.8286 | 50.0223 | 0.28537 | 7.12 | 6.03 | 220 | 371 | 389 | 1676 | 1816.7208 | -8.3962 | 43.4447 | 1102.8604 | 80.0519 | 122.1 | 92 | 45 | 872 | 583 | 1455 | 1455 | 0.43249 | 0.59931 | 15.9269 | 16.2119 | 4.2648 | 57.7852 | 0.28055 | 6.03 | 6.15 | 145 | 389 | 697 | 753.9537 | -8.1713 | 62.7249 | 571.4768 | 74.6271 | 92 | 81 | 15 | 309 | 274 | 583 | 583 | 0.36373 | 0.53002 | 11.2877 | 11.4896 | 8.1947 | 63.3053 | 0.1815 | 6.15 | 6.2 | 173 | 697 | 1278 | 1287.9343 | -0.77733 | 55.527 | 992.4672 | 82.5687 | 81 | 61 | 15 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.4737 | 13.6182 | 42.3818 | 0.27072 | 6.2 | 6.21 | 298 | 1278 | 1676 | 2041.6364 | -21.816 | 23.3933 | 1659.8182 | 82.0462 | SUVA | L/(mg*m) | NR | 3.0375 | 3.2361 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | 2.9125 | 3.1429 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | 3.45 | 3.9853 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | 3.025 | 3.0338 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | NR | 2.6456 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | 2.825 | 2.6203 | --- | --- | --- | --- | ---
Process Train Name | Train D | Active membrane area of an equivalent 8" x 40" element (ft2) | 365 | Feed flow rate at the end of stage 1, (QF-s(1))end (gpm) | 861.8056 | [5 empty] | 1998-07-01 | 1:36 | 25986 | 24.6 | 122 | 60 | 32.6991 | 0 | 1300 | 154 |  | 1454 | 1454 | 0.89409 | 0 | 14.013 | 14.1797 | 8.5099 | 49.791 | 0.28478 | 7.09 | 6.06 | 223 | 376 | 386 | 1639 | 1761.974 | -7.503 | 42.228 | 1073.987 | 79.2362 | 122 | 92 | 45 | 871 | 583 | 1454 | 1454 | 0.43227 | 0.59904 | 15.9087 | 16.0979 | 4.2103 | 57.7897 | 0.27856 | 6.06 | 6.19 | 145 | 386 | 691 | 746.0532 | -7.9672 | 62.4352 | 566.0266 | 74.3828 | 92 | 80 | 15 | 309 | 274 | 583 | 583 | 0.36373 | 0.53002 | 11.2877 | 11.4219 | 8.0539 | 62.9461 | 0.18146 | 6.19 | 6.31 | 176 | 691 | 1251 | 1271.7847 | -1.6614 | 54.4041 | 981.3923 | 82.0663 | 80 | 60 | 15 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.4061 | 13.1179 | 41.8821 | 0.27234 | 6.31 | 6.34 | 307 | 1251 | 1639 | 1986.5844 | -21.2071 | 20.4663 | 1618.7922 | 81.0352 | Bromide | mg/L | 140 | 140 | --- | 140 | --- | 0 | 140 | 0 | [8 empty] | Bromide | mg/L | NR | 140 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | 180 | 160 | --- | -20 | --- | -12.5 | 80.6615 | -123.1547 | [8 empty] | Bromide | mg/L | 170 | 170 | --- | 170 | --- | 0 | 170 | 0 | [8 empty] | Bromide | mg/L | 160 | 140 | --- | -21.8182 | --- | -14.2857 | 68.6755 | -132.9797 | [8 empty] | Bromide | mg/L | 160 | 160 | --- | 160 | --- | 0 | 160 | 0
ICR Treatment Plant Identification Number | 1092 | Purchase price for an equivalent 8" x 40 " element ($) | 800 | Feed flow rate at the end of stage 2, (QF-s(2))end (gpm) | 382.7431 | [5 empty] | 1998-07-02 | 2:25 | 26010.8 | 24.4 | 127.6 | 66 | 37.6991 | 0 | 1299 | 157 |  | 1456 | 1456 | 0.89217 | 0 | 14.0022 | 14.2528 | 8.8869 | 50.214 | 0.28384 | 7.13 | 6.1 | 228 | 385 | 401 | 1705 | 1832.3822 | -7.4711 | 43.1421 | 1116.6911 | 79.5825 | 127.6 | 97 | 50 | 872 | 584 | 1456 | 1456 | 0.43291 | 0.5989 | 15.9269 | 16.2119 | 4.349 | 57.951 | 0.27975 | 6.1 | 6.17 | 152 | 401 | 715 | 772.7945 | -8.0831 | 62.0948 | 586.8973 | 74.1011 | 97 | 85 | 20 | 307 | 277 | 584 | 584 | 0.36543 | 0.52568 | 11.2146 | 11.4153 | 8.3147 | 62.6853 | 0.1821 | 6.17 | 6.26 | 180 | 715 | 1306 | 1307.9422 | -0.14872 | 55.1122 | 1011.4711 | 82.2041 | 85 | 66 | 20 | 120 | 157 | 277 | 277 | 0.47365 | 0.43321 | 11.272 | 11.4737 | 13.7802 | 41.7198 | 0.27502 | 6.26 | 6.25 | 309 | 1306 | 1705 | 2068.0382 | -21.2926 | 22.9426 | 1687.0191 | 81.6837 | SDS-Cl2 dose | mg/L | 19 | 29 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 19.1 | 27.5 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 18.5 | 27.5 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 20 | 30 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 19 | 28 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 19 | 28 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection
PWSID Number of Plant (if assigned) | FL5114069 |  |  | Feed flow rate at the end of stage 3, (QF-s(3))end (gpm) | 181.2326 | [5 empty] | 1998-07-03 | 1:49 | 26034.1 | 24.5 | 128.1 | 66 | 38.6991 | 0 | 1300 | 155 |  | 1455 | 1455 | 0.89347 | 0 | 14.013 | 14.2217 | 8.7771 | 49.5738 | 0.28688 | 7.06 | 6.08 | 229 | 377 | 398 | 1707 | 1815.4194 | -6.3515 | 42.4623 | 1106.7097 | 79.308 | 128.1 | 98 | 51 | 872 | 583 | 1455 | 1455 | 0.43249 | 0.59931 | 15.9269 | 16.1641 | 4.2997 | 57.7503 | 0.2799 | 6.08 | 6.22 | 152 | 398 | 711 | 765.9451 | -7.7279 | 61.809 | 581.9726 | 73.8819 | 98 | 87 | 21 | 308 | 275 | 583 | 583 | 0.36415 | 0.5283 | 11.2511 | 11.4187 | 8.2368 | 63.2632 | 0.18049 | 6.22 | 6.31 | 183 | 711 | 1286 | 1302.36 | -1.2722 | 54.0201 | 1006.68 | 81.8214 | 87 | 66 | 21 | 120 | 155 | 275 | 275 | 0.46929 | 0.43636 | 11.272 | 11.4398 | 13.4826 | 42.0174 | 0.27226 | 6.31 | 6.32 | 314 | 1286 | 1707 | 2038.5161 | -19.421 | 21.1055 | 1662.2581 | 81.11 | SDS-Free Cl2 residual | mg/L | 3.58 | 3.42 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.53 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 3.02 | 1.03 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.73 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 0.5 | 0.1 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.53 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 4.4 | 3.1 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.54 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 4.15 | 1.2 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.53 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 3.15 | 1.6 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.53
Historical Minimum Water Temperature (oC) | 22.7 | Additional Information |  |  |  | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | 1998-07-04 | 2:00 | 26058.1 | 24.4 | 125 | 65 | 35.6991 | 0 | 1300 | 154 |  | 1454 | 1454 | 0.89409 | 0 | 14.013 | 14.2638 | 8.4577 | 50.8432 | 0.28054 |  | 6.02 | 224 |  | 386 | 1686 | 1753.5325 | -4.0055 | 41.9689 | 1069.7662 | 79.0608 | 125 | 97 | 48 | 871 | 583 | 1454 | 1454 | 0.43227 | 0.59904 | 15.9087 | 16.1933 | 4.053 | 58.947 | 0.27471 | 6.02 | 6.08 | 154 | 386 | 696 | 732.6072 | -5.2597 | 60.1036 | 559.3036 | 72.4658 | 97 | 86 | 18 | 309 | 274 | 583 | 583 | 0.36373 | 0.53002 | 11.2877 | 11.4896 | 8.0383 | 65.4617 | 0.17552 | 6.08 | 6.17 | 182 | 696 | 1282 | 1275.6569 | 0.49478 | 52.8497 | 985.8285 | 81.5384 | 86 | 65 | 18 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.4737 | 13.4792 | 44.0208 | 0.26064 | 6.17 | 6.23 | 312 | 1282 | 1686 | 2037.8442 | -20.8686 | 19.171 | 1659.9221 | 81.2039 | SDS-Cl2 demand | mg/L | 15.42 | 25.58 | --- | 111.4502 | --- | 39.7185 | 63.4329 | 75.6908 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 310 |  |  |  |  | SDS-Cl2 demand | mg/L | 16.08 | 26.47 | --- | 119.98 | --- | 39.252 | 67.5784 | 76.2054 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 428 |  |  |  |  | SDS-Cl2 demand | mg/L | 18 | 27.4 | --- | 112 | --- | 34.3066 | 64.6891 | 72.1746 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 308 |  |  |  |  | SDS-Cl2 demand | mg/L | 15.6 | 26.9 | --- | 122.3044 | --- | 42.0074 | 68.9513 | 77.3753 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 311 |  |  |  |  | SDS-Cl2 demand | mg/L | 14.85 | 26.8 | --- | 123.4864 | --- | 44.5896 | 69.4164 | 78.6074 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 301 |  |  |  |  | SDS-Cl2 demand | mg/L | 15.85 | 26.4 | --- | 111.7591 | --- | 39.9621 | 64.0237 | 75.2435 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 301
Historical Average Water Temperature (oC) | 25 | Design cross-flow velocity (fps) | 1 | Calculate the Minimum Recycle Flow Rates for Each Stage1 |  | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | 1998-07-05 | 3:00 | 26083.1 | 24.1 | 122 | 62 | 33.6991 | 0 | 1300 | 154 |  | 1454 | 1454 | 0.89409 | 0 | 14.013 | 14.3908 | 8.5621 | 49.7388 | 0.28933 |  | 6.02 | 212 |  | 376 | 1626 | 1760.4156 | -8.2666 | 43.617 | 1068.2078 | 80.1537 | 122 | 94 | 46 | 872 | 582 | 1454 | 1454 | 0.43206 | 0.59972 | 15.9269 | 16.3563 | 3.988 | 58.012 | 0.28195 | 6.02 | 6.11 | 148 | 376 | 712 | 717.6082 | -0.78768 | 60.6383 | 546.8041 | 72.9336 | 94 | 84 | 16 | 308 | 274 | 582 | 582 | 0.3633 | 0.52921 | 11.2511 | 11.5545 | 8.3101 | 64.6899 | 0.17861 | 6.11 | 6.19 | 180 | 712 | 1260 | 1310.0146 | -3.9694 | 52.1277 | 1011.0073 | 82.196 | 84 | 62 | 16 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.5759 | 13.3681 | 43.6319 | 0.26531 | 6.19 | 6.22 | 298 | 1260 | 1626 | 2009.6104 | -23.5923 | 20.7447 | 1634.8052 | 81.7715 | SDS-Chlorination temp. | oC | 23.2 | 22.6 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 585 |  |  |  |  | SDS-Chlorination temp. | oC | 21 | 21.1 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 585 |  |  |  |  | SDS-Chlorination temp. | oC | 21.5 | 21.6 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 582 |  |  |  |  | SDS-Chlorination temp. | oC | 24.1 | 24.2 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 575 |  |  |  |  | SDS-Chlorination temp. | oC | 24.4 | 24.5 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 572 |  |  |  |  | SDS-Chlorination temp. | oC | 24.4 | 24.5 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 572
State Approved Plant Capacity (MGD) | 12 MGD | Required influent flow to permeate flow rate ratio, QI:Qp | 5:1 | Minimum recycle flow rate for stage 1, (QR-s(1))min (gpm) | 1730.1944 | [5 empty] | 1998-07-06 | 3:40 | 26100.8 | 24.5 | 124.9 | 61 | 35.2891 | 0 | 1301 | 154 |  | 1455 | 1455 | 0.89416 | 0 | 14.0238 | 14.2326 | 9.6122 | 48.0487 | 0.29621 | 7.15 | 6.03 | 209 | 363 | 393 | 1732 | 1947.4416 | -12.4389 | 46.8193 | 1170.2208 | 82.1401 | 124.9 | 95 | 48 | 872 | 583 | 1455 | 1455 | 0.43249 | 0.59931 | 15.9269 | 16.1641 | 4.457 | 57.493 | 0.28115 | 6.03 | 6.14 | 138 | 393 | 713 | 774.4065 | -8.6124 | 64.8855 | 583.7033 | 76.3579 | 95 | 83 | 17 | 309 | 274 | 583 | 583 | 0.36373 | 0.53002 | 11.2877 | 11.4557 | 8.3198 | 63.6802 | 0.17989 | 6.14 | 6.16 | 181 | 713 | 1315 | 1312.9562 | 0.15542 | 53.944 | 1012.9781 | 82.1319 | 83 | 61 | 17 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.4398 | 14.3686 | 40.6314 | 0.28155 | 6.16 | 6.16 | 281 | 1315 | 1732 | 2120.7143 | -22.4431 | 28.4987 | 1717.8571 | 83.6424 | SDS-Chlorination pH | --- | 8.27 | 8.34 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.31 | 8.23 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.41 | 8.23 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.28 | 8.19 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.27 | 8.18 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.27 | 8.18 | --- | --- | --- | --- | --- | ---
|  | Maximum element recovery (%) | 20 | Minimum recycle flow rate for stage 2, (QR-s(2))min (gpm) | 913.2569 | [5 empty] | 1998-07-07 | 5:19 | 26126.4 | 24.5 | 124.6 | 63 | 35.6991 | 0 | 1302 | 153 |  | 1455 | 1455 | 0.89485 | 0 | 14.0346 | 14.2435 | 9.1435 | 48.9574 | 0.29094 | 7.09 | 5.97 | 219 | 381 | 393 | 1687 | 1873.7059 | -11.0673 | 44.2748 | 1133.3529 | 80.6768 | 124.6 | 94 | 48 | 872 | 583 | 1455 | 1455 | 0.43249 | 0.59931 | 15.9269 | 16.1641 | 4.2648 | 57.0352 | 0.28341 | 5.97 | 6.09 | 149 | 393 | 704 | 757.9537 | -7.6639 | 62.0865 | 575.4768 | 74.1084 | 94 | 82 | 18 | 310 | 273 | 583 | 583 | 0.3633 | 0.53173 | 11.3242 | 11.4928 | 8.2778 | 61.7222 | 0.1862 | 6.09 | 6.16 | 176 | 704 | 1285 | 1303.5604 | -1.4444 | 55.2163 | 1003.7802 | 82.4663 | 82 | 63 | 18 | 120 | 153 | 273 | 273 | 0.46492 | 0.43956 | 11.272 | 11.4398 | 13.7267 | 40.7733 | 0.28057 | 6.16 | 6.21 | 299 | 1285 | 1687 | 2058.3333 | -22.0115 | 23.9186 | 1671.6667 | 82.1137 | SDS-Incubation time | hours | 40.25 | 40.3 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 46 | 46 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 44 | 44 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 46.1 | 46.1 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 47 | 47 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 47 | 47 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters
|  | Variability of design flux (%) | 15 +/- | Minimum recycle flow rate for stage 3, (QR-s(3))min (gpm) | 322.7674 | [5 empty] | 1998-07-08 | 6:33 | 26151.1 | 24.4 | 127.9 | 66 | 38.2891 | 0 | 1302 | 154 |  | 1456 | 1456 | 0.89423 | 0 | 14.0346 | 14.2857 | 8.7295 | 49.9314 | 0.28611 | 7.12 | 6.06 | 227 | 378 | 394 | 1686 | 1805.9091 | -7.112 | 42.3858 | 1099.9545 | 79.3628 | 127.9 | 97 | 51 | 874 | 582 | 1456 | 1456 | 0.43249 | 0.60027 | 15.9635 | 16.2491 | 4.2721 | 57.1779 | 0.28419 | 6.06 | 6.21 | 150 | 394 | 706 | 760.4192 | -7.7081 | 61.9289 | 577.2096 | 74.0129 | 97 | 86 | 20 | 308 | 274 | 582 | 582 | 0.3633 | 0.52921 | 11.2511 | 11.4525 | 8.2164 | 63.2836 | 0.18097 | 6.21 | 6.22 | 180 | 706 | 1284 | 1297.2701 | -1.0335 | 54.3147 | 1001.635 | 82.0294 | 86 | 66 | 20 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.4737 | 13.5765 | 42.4235 | 0.27046 | 6.22 | 6.26 | 307 | 1284 | 1686 | 2045.2987 | -21.3107 | 22.0812 | 1664.6494 | 81.5577 | SDS-TOX | mg Cl- /L | BMRL | 860 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-12 | CI-s2-12 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | BMRL | 770 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-14 | CI-s2-14 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | BMRL | 635 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-16 | CI-s2-16 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | BMRL | 805 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-18 | CI-s2-18 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | BMRL | 800 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-20 | CI-s2-20 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | BMRL | 830 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-20 (dup) | CI-s2-20 (dup) | CC(calc) | RF (%) | CB | RB (%)
|  | Rejection of reference solute and conditions of test | 80 | 1: A negative minimum recycle flow rate indicates that recycle is not required to | [6 empty] | 1998-07-09 | 5:40 | 26165.3 | 24.4 | 127.7 | 66 | 38.6991 | 0 | 1299 | 154 |  | 1453 | 1453 | 0.89401 | 0 | 14.0022 | 14.2528 | 9.0263 | 49.1246 | 0.29014 | 7.1 | 5.99 | 222 | 382 | 395 | 1690 | 1854.2662 | -9.7199 | 43.7975 | 1124.6331 | 80.2602 | 127.7 | 97 | 51 | 872 | 581 | 1453 | 1453 | 0.43164 | 0.60014 | 15.9269 | 16.2119 | 4.2886 | 57.0614 | 0.28411 | 5.99 | 6.14 | 150 | 395 | 707 | 762.7108 | -7.8799 | 62.0253 | 578.8554 | 74.0868 | 97 | 86 | 21 | 307 | 274 | 581 | 581 | 0.36288 | 0.5284 | 11.2146 | 11.4153 | 8.2536 | 62.2464 | 0.18339 | 6.14 | 6.19 | 178 | 707 | 1284 | 1299.7117 | -1.2237 | 54.9367 | 1003.3558 | 82.2595 | 86 | 66 | 21 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.4737 | 13.6321 | 41.3679 | 0.27736 | 6.19 | 6.21 | 303 | 1284 | 1690 | 2048.4156 | -21.208 | 23.2911 | 1666.2078 | 81.815 | SDS-CHCl3 | mg/L | 1 | 230 | --- | 2165.4612 | --- | 99.5652 | 1083.1799 | 99.9077 | Sampling date | MM/DD/YY | 1998-06-23 | 1998-06-23 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 1 | 180 | --- | 1791 | --- | 99.4444 | 888.2204 | 99.8874 | Sampling date | MM/DD/YY | 1998-07-06 | 1998-07-06 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | BMRL | 180 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1998-07-22 | 1998-07-22 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 0.6 | 230 | --- | 2166.7945 | --- | 99.7391 | 1083.6794 | 99.9446 | Sampling date | MM/DD/YY | 1998-08-03 | 1998-08-03 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 1.1 | 250 | --- | 2263.8273 | --- | 99.56 | 1137.6331 | 99.9033 | Sampling date | MM/DD/YY | 1998-08-17 | 1998-08-17 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 0.5 | 260 | --- | 2359.5909 | --- | 99.8077 | 1185.4351 | 99.9578 | Sampling date | MM/DD/YY | 1998-08-17 | 1998-08-17 | --- | --- | --- | ---
|  | (e.g., solute type and concentration) |  | meet the manufacturer's minimum flow requirement. | [6 empty] | 1998-07-10 | 3:19 | 26187 | 24 | 122.5 | 60 | 33.2891 | 0 | 1303 | 151 |  | 1454 | 1454 | 0.89615 | 0 | 14.0454 | 14.4667 | 9.4068 | 48.5541 | 0.29795 | 7.1 | 5.93 | 224 | 387 | 401 | 1815 | 1928.3576 | -6.2456 | 44.1397 | 1164.6788 | 80.7672 | 122.5 | 93 | 46 | 873 | 581 | 1454 | 1454 | 0.43185 | 0.60041 | 15.9452 | 16.4236 | 4.4308 | 57.3192 | 0.28653 | 5.93 | 6.07 | 148 | 401 | 729 | 781.1532 | -7.1541 | 63.0923 | 591.0766 | 74.9609 | 93 | 81 | 15 | 310 | 271 | 581 | 581 | 0.36161 | 0.53356 | 11.3242 | 11.6639 | 8.7086 | 63.2914 | 0.18429 | 6.07 | 6.13 | 175 | 729 | 1351 | 1362.7269 | -0.86802 | 56.3591 | 1045.8635 | 83.2674 | 81 | 60 | 15 | 120 | 151 | 271 | 271 | 0.46056 | 0.4428 | 11.272 | 11.6102 | 14.6722 | 40.8278 | 0.28437 | 6.13 | 6.15 | 301 | 1351 | 1815 | 2185.4371 | -20.4098 | 24.9377 | 1768.2185 | 82.9772 | SDS-BDCM | mg/L | 2 | 65 | --- | 597.4631 | --- | 96.9231 | 299.7176 | 99.3327 | Sampling time | hh:mm | 8:48 | 8:57 | --- | --- | --- | --- | SDS-BDCM | mg/L | 1.7 | 43 | --- | 414.7 | --- | 96.0465 | 206.405 | 99.1764 | Sampling time | hh:mm | 8:31 | 8:45 | --- | --- | --- | --- | SDS-BDCM | mg/L | BMRL | 44 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 8:19 | 8:32 | --- | --- | --- | --- | SDS-BDCM | mg/L | 1.5 | 63 | --- | 582.2365 | --- | 97.619 | 291.8635 | 99.4861 | Sampling time | hh:mm | 8:10 | 8:22 | --- | --- | --- | --- | SDS-BDCM | mg/L | 2.3 | 61 | --- | 535.9364 | --- | 96.2295 | 270.3373 | 99.1492 | Sampling time | hh:mm | 5:33 | 5:51 | --- | --- | --- | --- | SDS-BDCM | mg/L | 1.1 | 63 | --- | 563.8273 | --- | 98.254 | 283.7493 | 99.6123 | Sampling time | hh:mm | 5:33 | 5:51 | --- | --- | --- | ---
|  | Variability of rejection of reference solute (%) | 50 +/- | [7 empty] | 1998-07-11 | 3:15 | 26211.1 | 24.1 | 123 | 61 | 33.2891 | 0 | 1300 | 153 |  | 1453 | 1453 | 0.8947 | 0 | 14.013 | 14.3908 | 9.0272 | 49.6837 | 0.28965 |  | 5.96 | 220 |  | 392 | 1862 | 1853.4379 | 0.45983 | 43.8776 | 1122.719 | 80.4047 | 123 | 94 | 46 | 872 | 581 | 1453 | 1453 | 0.43164 | 0.60014 | 15.9269 | 16.3563 | 4.201 | 58.299 | 0.28056 | 5.96 | 6.05 | 152 | 392 | 722 | 752.2065 | -4.1837 | 61.2245 | 572.1033 | 73.4314 | 94 | 82 | 15 | 308 | 273 | 581 | 581 | 0.36246 | 0.53012 | 11.2511 | 11.5545 | 8.4774 | 64.5226 | 0.17908 | 6.05 | 6.18 | 180 | 722 | 1326 | 1333.4872 | -0.56464 | 54.0816 | 1027.7436 | 82.4859 | 82 | 61 | 15 | 120 | 153 | 273 | 273 | 0.46492 | 0.43956 | 11.272 | 11.5759 | 14.3114 | 42.1886 | 0.27438 | 6.18 | 6.19 | 298 | 1326 | 1862 | 2132.2745 | -14.5153 | 23.9796 | 1729.1373 | 82.766 | SDS-DBCM | mg/L | 3 | 18 | --- | 144.7769 | --- | 83.3333 | 73.8851 | 95.9396 | Operation time | hh.hh | 25824.2 | 25824.4 | --- | --- | --- | --- | SDS-DBCM | mg/L | 2.5 | 12 | --- | 97.5 | --- | 79.1667 | 49.5871 | 94.9584 | Operation time | hh.hh | 26105.6 | 26105.9 | --- | --- | --- | --- | SDS-DBCM | mg/L | 1 | 13 | --- | 121 | --- | 92.3077 | 60.6031 | 98.3499 | Operation time | hh.hh | 26373.8 | 26374 | --- | --- | --- | --- | SDS-DBCM | mg/L | 2.1 | 14 | --- | 114.4702 | --- | 85 | 58.2842 | 96.397 | Operation time | hh.hh | 26631.7 | 26631.9 | --- | --- | --- | --- | SDS-DBCM | mg/L | 3.7 | 13 | --- | 88.2455 | --- | 71.5385 | 46.1659 | 91.9854 | Operation time | hh.hh | 26874.4 | 26874.7 | --- | --- | --- | --- | SDS-DBCM | mg/L | 1.9 | 13 | --- | 102.8091 | --- | 85.3846 | 52.5851 | 96.3868 | Operation time | hh.hh | 26874.4 | 26874.7 | --- | --- | --- | ---
|  | Standard testing recovery (%) | 15 | Calculate the Maximum Recycle Flow Rates for Each Stage | [6 empty] | 1998-07-12 | 0:15 | 26232.1 | 24.2 | 124 | 60 | 32.6991 | 0 | 1300 | 154 |  | 1454 | 1454 | 0.89409 | 0 | 14.013 | 14.3483 | 8.7709 | 50.53 | 0.28396 |  | 6.02 | 218 |  | 386 | 1850 | 1804.1818 | 2.4767 | 43.5233 | 1095.0909 | 80.093 | 124 | 93 | 45 | 871 | 583 | 1454 | 1454 | 0.43227 | 0.59904 | 15.9087 | 16.2894 | 4.1579 | 59.3421 | 0.2745 | 6.02 | 6.11 | 148 | 386 | 712 | 741.5712 | -4.1533 | 61.658 | 563.7856 | 73.7489 | 93 | 81 | 15 | 309 | 274 | 583 | 583 | 0.36373 | 0.53002 | 11.2877 | 11.5578 | 8.2572 | 63.7428 | 0.18132 | 6.11 | 6.19 | 184 | 712 | 1312 | 1307.4453 | 0.34716 | 52.3316 | 1009.7226 | 81.7772 | 81 | 60 | 15 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.5417 | 14.0351 | 41.4649 | 0.27835 | 6.19 | 6.18 | 302 | 1312 | 1850 | 2099.013 | -13.4602 | 21.7617 | 1705.5065 | 82.2927 | SDS-CHBr3 | mg/L | 2 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 6.1 | 6.3 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | 1 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 5.86 | 6.13 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | 3 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 6.11 | 6.37 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | 0.9 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 6.02 | 6.15 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | 1.6 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 5.97 | 6.17 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | 0.9 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 5.97 | 6.17 | --- | --- | --- | ---
|  | Standard testing pH | 7.5 to 8.5 | Maximum recycle flow rate for stage 1, (QR-s(1))max (gpm) | 1153.8194 | [5 empty] | 1998-07-13 | 3:29 | 26243.2 | 24.5 | 122.1 | 61 | 32.6991 | 0 | 1299 | 154 |  | 1453 | 1453 | 0.89401 | 0 | 14.0022 | 14.2107 | 8.6611 | 50.1898 | 0.28314 | 7.03 | 6.06 | 226 | 387 | 392 | 1666 | 1792.2208 | -7.5763 | 42.3469 | 1092.1104 | 79.3061 | 122.1 | 92 | 45 | 872 | 581 | 1453 | 1453 | 0.43164 | 0.60014 | 15.9269 | 16.1641 | 4.236 | 57.814 | 0.27959 | 6.06 | 6.2 | 150 | 392 | 701 | 755.2083 | -7.733 | 61.7347 | 573.6041 | 73.8496 | 92 | 80 | 15 | 307 | 274 | 581 | 581 | 0.36288 | 0.5284 | 11.2146 | 11.3816 | 8.1443 | 62.8557 | 0.18107 | 6.2 | 6.24 | 179 | 701 | 1272 | 1285.8686 | -1.0903 | 54.3367 | 993.4343 | 81.9817 | 80 | 61 | 15 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.4398 | 13.3958 | 42.1042 | 0.2717 | 6.24 | 6.26 | 308 | 1272 | 1666 | 2023.1688 | -21.4387 | 21.4286 | 1647.5844 | 81.306 | SDS-THM4 | mg/L | 8 | 313 | --- | 2890.7977 | --- | 97.4441 | 1449.3313 | 99.448 | Temperature | oC | 25 | 25.2 | --- | --- | --- | --- | SDS-THM4 | mg/L | 6.2 | 235 | --- | 2294.2 | --- | 97.3617 | 1140.256 | 99.4563 | Temperature | oC | 25.3 | 25.6 | --- | --- | --- | --- | SDS-THM4 | mg/L | 4 | 237 | --- | 2334 | --- | 98.3122 | 1161.2931 | 99.6556 | Temperature | oC | 24.9 | 25 | --- | --- | --- | --- | SDS-THM4 | mg/L | 5.1 | 307 | --- | 2855.9026 | --- | 98.3388 | 1430.4779 | 99.6435 | Temperature | oC | 25.2 | 25.3 | --- | --- | --- | --- | SDS-THM4 | mg/L | 8.7 | 324 | --- | 2875.0636 | --- | 97.3148 | 1448.4304 | 99.3993 | Temperature | oC | 25.4 | 25.4 | --- | --- | --- | --- | SDS-THM4 | mg/L | 4.4 | 336 | --- | 3018.9455 | --- | 98.6905 | 1518.5598 | 99.7103 | Temperature | oC | 25.4 | 25.4 | --- | --- | --- | ---
|  | Acceptable range of operating pressures | <400psi | Maximum recycle flow rate for stage 2, (QR-s(2))max (gpm) | 625.0694 | [5 empty] | 1998-07-14 | 3:28 | 26254.1 | 24.4 | 122.1 | 61 | 32.6991 | 0 | 1298 | 154 |  | 1452 | 1452 | 0.89394 | 0 | 13.9915 | 14.2418 | 8.7079 | 50.143 | 0.28402 | 7.17 | 6.04 | 234 | 384 | 401 | 1699 | 1808.5714 | -6.4492 | 41.6459 | 1104.7857 | 78.8194 | 122.1 | 92 | 45 | 871 | 581 | 1452 | 1452 | 0.43142 | 0.59986 | 15.9087 | 16.1933 | 4.3039 | 57.7461 | 0.28042 | 6.04 | 6.23 | 155 | 401 | 714 | 769.7883 | -7.8135 | 61.3466 | 585.3941 | 73.5221 | 92 | 81 | 15 | 307 | 274 | 581 | 581 | 0.36288 | 0.5284 | 11.2146 | 11.4153 | 8.2692 | 63.2308 | 0.18053 | 6.23 | 6.26 | 184 | 714 | 1294 | 1307.8321 | -1.0689 | 54.1147 | 1010.9161 | 81.7987 | 81 | 61 | 15 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.4737 | 13.5904 | 42.4096 | 0.27055 | 6.26 | 6.28 | 316 | 1294 | 1699 | 2056.0779 | -21.0169 | 21.197 | 1675.039 | 81.1348 | SDS-MCAA* | mg/L | BMRL | 6 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 82 | 128 | 179.8545 | 4.6512 | 153.9273 | 46.7281 | SDS-MCAA* | mg/L | BMRL | 4.6 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 79 | 116 | 216.8662 | 3.6585 | 166.4331 | 52.5335 | SDS-MCAA* | mg/L | BMRL | 3.8 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 99 | 162 | 232.8175 | 11.6071 | 197.4088 | 49.8502 | SDS-MCAA* | mg/L | BMRL | 5 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 87 | 140 | 202.4356 | 9.375 | 171.2178 | 49.1875 | SDS-MCAA* | mg/L | BMRL | 5.9 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 92 | 154 | 222.8635 | 13.2075 | 188.4317 | 51.176 | SDS-MCAA* | mg/L | BMRL | 6.6 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 93 | 154 | 221.7528 | 12.2642 | 187.8764 | 50.4994
|  | Acceptable range of operating pH values | 2 to 8 | Maximum recycle flow rate for stage 3, (QR-s(3))max (gpm) | 210.6944 | [5 empty] | 1998-07-15 | 5:39 | 26273.7 | 24.5 | 123.3 | 62 | 34.2891 | 0 | 1301 | 154 |  | 1455 | 1455 | 0.89416 | 0 | 14.0238 | 14.2326 | 9.4032 | 48.9577 | 0.29071 | 7.08 | 6.03 | 222 | 383 | 402 | 1740 | 1922.6494 | -10.4971 | 44.7761 | 1162.3247 | 80.9003 | 123.3 | 93 | 47 | 873 | 582 | 1455 | 1455 | 0.43227 | 0.6 | 15.9452 | 16.1826 | 4.3925 | 56.7575 | 0.28512 | 6.03 | 6.11 | 151 | 402 | 723 | 778.5 | -7.6763 | 62.4378 | 590.25 | 74.4176 | 93 | 82 | 16 | 308 | 274 | 582 | 582 | 0.3633 | 0.52921 | 11.2511 | 11.4187 | 8.4975 | 63.0025 | 0.18124 | 6.11 | 6.17 | 179 | 723 | 1325 | 1334.5036 | -0.71726 | 55.4726 | 1028.7518 | 82.6003 | 82 | 62 | 16 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.4398 | 14.1879 | 41.8121 | 0.2736 | 6.17 | 6.22 | 304 | 1325 | 1740 | 2120.5844 | -21.8727 | 24.3781 | 1722.7922 | 82.3542 | SDS-DCAA* | mg/L | BMRL | 54 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 214 | 1172 | 2251.9273 | 64.3333 | 1711.9636 | 87.4997 | SDS-DCAA* | mg/L | 1.1 | 44 | --- | 430.1 | --- | 97.5 | 213.7355 | 99.4853 | Total dissolved solids | mg/L | 172 | 1124 | 3719.2611 | 69.9301 | 2421.6306 | 92.8973 | SDS-DCAA* | mg/L | BMRL | 32 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 172 | 1076 | 2092.1752 | 68.1481 | 1584.0876 | 89.142 | SDS-DCAA* | mg/L | BMRL | 58 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 186 | 1082 | 2137.5152 | 64.6388 | 1609.7576 | 88.4455 | SDS-DCAA* | mg/L | 1 | 61 | --- | 546.4545 | --- | 98.3607 | 274.9734 | 99.6363 | Total dissolved solids | mg/L | 206 | 1114 | 2122.5166 | 63.4752 | 1618.2583 | 87.2703 | SDS-DCAA* | mg/L | BMRL | 61 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 200 | 1116 | 2133.4022 | 63.37 | 1624.7011 | 87.69
|  | Typical pressure drop across a single element (psi) | 3 to 4 psi | [7 empty] | 1998-07-16 | 0:26 | 26292.5 | 24 | 123.7 | 62 | 34.2891 | 0 | 1304 | 154 |  | 1458 | 1458 | 0.89438 | 0 | 14.0561 | 14.4778 | 9.4208 | 49.1401 | 0.29462 | 7.11 | 6.01 | 227 | 386 | 407 | 1740 | 1931.1558 | -10.986 | 44.226 | 1169.0779 | 80.583 | 123.7 | 93 | 47 | 873 | 585 | 1458 | 1458 | 0.43355 | 0.59877 | 15.9452 | 16.4236 | 4.4876 | 56.8624 | 0.28883 | 6.01 | 6.13 | 150 | 407 | 724 | 790.5231 | -9.1883 | 63.145 | 598.7615 | 74.9483 | 93 | 82 | 16 | 310 | 275 | 585 | 585 | 0.365 | 0.52991 | 11.3242 | 11.6639 | 8.5531 | 62.9469 | 0.1853 | 6.13 | 6.17 | 177 | 724 | 1324 | 1340.6182 | -1.2551 | 56.5111 | 1032.3091 | 82.854 | 82 | 62 | 16 | 121 | 154 | 275 | 275 | 0.4682 | 0.44 | 11.3659 | 11.7069 | 14.2211 | 41.7789 | 0.28021 | 6.17 | 6.16 | 303 | 1324 | 1740 | 2126.2143 | -22.1962 | 25.5528 | 1725.1071 | 82.4359 | SDS-TCAA* | mg/L | BMRL | 75 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 96 | 620 | 1210.6909 | 67.1233 | 915.3455 | 89.5122 | SDS-TCAA* | mg/L | BMRL | 59 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 88 | 650 | 2182.0764 | 71.6129 | 1416.0382 | 93.7855 | SDS-TCAA* | mg/L | BMRL | 38 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 109 | 640 | 1236.8905 | 62.4138 | 938.4453 | 88.385 | SDS-TCAA* | mg/L | BMRL | 79 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 120 | 650 | 1274.3561 | 62.963 | 962.178 | 87.5283 | SDS-TCAA* | mg/L | BMRL | 78 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 114 | 730 | 1414.1919 | 65.8683 | 1072.0959 | 89.3666 | SDS-TCAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 112 | 740 | 1437.5203 | 66.6667 | 1088.7601 | 89.7131
|  | Maximum permissible SDI | 4 | Select the Design System Recycle Flow Rate2 | [6 empty] | 1998-07-17 | 3:37 | 26298 | 24.5 | 122.5 | 62 | 33.2891 | 0 | 1298 | 151 |  | 1449 | 1449 | 0.89579 | 0 | 13.9915 | 14.1998 | 9.2185 | 49.7424 | 0.28547 |  | 6.04 | 227 |  | 401 | 1680 | 1896.7086 | -12.8993 | 43.3915 | 1148.8543 | 80.2412 | 122.5 | 93 | 46 | 871 | 578 | 1449 | 1449 | 0.43015 | 0.6011 | 15.9087 | 16.1455 | 4.3135 | 57.4365 | 0.2811 | 6.04 | 6.13 | 155 | 401 | 717 | 771.7024 | -7.6293 | 61.3466 | 586.3512 | 73.5653 | 93 | 81 | 15 | 307 | 271 | 578 | 578 | 0.36033 | 0.53114 | 11.2146 | 11.3816 | 8.3804 | 63.6196 | 0.1789 | 6.13 | 6.24 | 182 | 717 | 1290 | 1323.0701 | -2.5636 | 54.6135 | 1020.0351 | 82.1575 | 81 | 62 | 15 | 120 | 151 | 271 | 271 | 0.46056 | 0.4428 | 11.272 | 11.4398 | 13.722 | 42.778 | 0.26742 | 6.24 | 6.24 | 308 | 1290 | 1680 | 2070.3974 | -23.2379 | 23.192 | 1680.1987 | 81.6688 | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 74 | 490 | 958.9455 | 67.8261 | 724.4727 | 89.7857 | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 66 | 510 | 1720.3949 | 71.0526 | 1115.1975 | 94.0818 | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 82 | 500 | 969.8686 | 64.3478 | 734.9343 | 88.8425 | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 78 | 500 | 997.1288 | 67.5 | 748.5644 | 89.5801 | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 79 | 560 | 1094.2472 | 71.3768 | 827.1236 | 90.4488 | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 80 | 570 | 1114.2435 | 70.5882 | 842.1218 | 90.5002
|  | Maximum permissible turbidity (ntu) | 1 | Minimum system recycle flow rate, (QR-sys)min (gpm) | 1730.1944 | [5 empty] | 1998-07-18 | 17:32 | 26326.3 | 24.6 | 127.7 | 66 | 38.1091 | 0 | 1302 | 154 |  | 1456 | 1456 | 0.89423 | 0 | 14.0346 | 14.2015 | 7.8409 | 50.8999 | 0.27901 |  | 6.11 | 240 |  | 390 | 1594 | 1658.1818 | -4.0265 | 38.4615 | 1024.0909 | 76.5646 | 127.7 | 98 | 50 | 873 | 583 | 1456 | 1456 | 0.4327 | 0.59959 | 15.9452 | 16.1349 | 4.1095 | 58.7405 | 0.27468 | 6.11 | 6.3 | 155 | 390 | 693 | 741.8954 | -7.0556 | 60.2564 | 565.9477 | 72.6123 | 98 | 86 | 21 | 309 | 274 | 583 | 583 | 0.36373 | 0.53002 | 11.2877 | 11.4219 | 7.8975 | 63.1025 | 0.18101 | 6.3 | 6.35 | 188 | 693 | 1240 | 1262.5073 | -1.8151 | 51.7949 | 977.7536 | 80.7723 | 86 | 66 | 21 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.4061 | 12.6732 | 42.3268 | 0.26948 | 6.35 | 6.42 | 328 | 1240 | 1594 | 1950.6494 | -22.3745 | 15.8974 | 1595.3247 | 79.4399 | SDS-DBAA* | mg/L | BMRL | 2.2 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.08 | 8.2 | 17.3535 | 61.9048 | 12.7767 | 99.3739 | SDS-DBAA* | mg/L | BMRL | 2.2 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.05 | 7.6 | 28.1822 | 92.3077 | 17.8911 | 99.7205 | SDS-DBAA* | mg/L | BMRL | 2 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.04 | 5.7 | 12.0623 | 75 | 8.8812 | 99.5496 | SDS-DBAA* | mg/L | BMRL | 2.3 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.07 | 7 | 15.1638 | 89.5522 | 11.0819 | 99.3683 | SDS-DBAA* | mg/L | BMRL | 1.8 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.055 | 6.85 | 14.3972 | 78.8462 | 10.6236 | 99.4823 | SDS-DBAA* | mg/L | BMRL | 1.8 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.055 | 6.6 | 13.8695 | 81.6667 | 10.2348 | 99.4626
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | 1 ppm | Maximum system recycle flow rate, (QR-sys)max (gpm) | 210.6944 | [5 empty] | 1998-07-19 | 21:53 | 26345.6 | 24 | 127.6 | 66 | 38.2891 | 0 | 1300 | 148 |  | 1448 | 1448 | 0.89779 | 0 | 14.013 | 14.4334 | 5.7154 | 52.7955 | 0.27338 |  | 6.12 | 267 |  | 373 | 1591 | 1304.0811 | 18.0339 | 28.4182 | 838.5405 | 68.159 | 127.6 | 98 | 51 | 874 | 578 | 1452 | 1452 | 0.43079 | 0.60193 | 15.9635 | 16.4424 | 3.6702 | 58.1298 | 0.28286 | 6.12 | 6.26 | 164 | 373 | 635 | 689.0311 | -8.5088 | 56.0322 | 531.0156 | 69.1158 | 98 | 88 | 20 | 310 | 268 | 578 | 578 | 0.35906 | 0.53633 | 11.3242 | 11.6639 | 6.1082 | 66.8918 | 0.17437 | 6.26 | 6.34 | 248 | 635 | 1147 | 1082.6493 | 5.6104 | 33.5121 | 858.8246 | 71.1233 | 88 | 66 | 20 | 120 | 148 | 268 | 268 | 0.45401 | 0.44776 | 11.272 | 11.6102 | 10.2032 | 46.7968 | 0.2481 | 6.34 | 6.4 | 421 | 1147 | 1591 | 1735.6486 | -9.0917 | -12.8686 | 1441.3243 | 70.7908 | SDS-BCAA* | mg/L | BMRL | 13 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 20 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | 11 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 20 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | 8.7 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 19 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | 13 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 20 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | 1 | 12 | --- | 101 | --- | 91.6667 | 51.2285 | 98.048 | Total organic carbon | mg/L | BMRL | 21 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | 12 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 21 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | 1: All of the information requested in this field may not be available, but values for all of the Design |  | Design system recycle flow rate, QR-sys (gpm) | 0 | [5 empty] | 1998-07-20 | 1:44 | 26349.4 | 24.5 | 127.6 | 66 | 37.6991 | 0 | 1299 | 155 |  | 1454 | 1454 | 0.8934 | 0 | 14.0022 | 14.2107 | 8.4602 | 50.6407 | 0.28062 | 7.02 | 6.1 | 230 | 386 | 393 | 1644 | 1759.0452 | -6.9979 | 41.4758 | 1076.0226 | 78.625 | 127.6 | 98 | 50 | 871 | 583 | 1454 | 1454 | 0.43227 | 0.59904 | 15.9087 | 16.1455 | 4.2277 | 58.5723 | 0.27565 | 6.1 | 6.21 | 151 | 393 | 701 | 754.5472 | -7.6387 | 61.5776 | 573.7736 | 73.683 | 98 | 86 | 20 | 308 | 275 | 583 | 583 | 0.36415 | 0.5283 | 11.2511 | 11.4187 | 8.0964 | 63.9036 | 0.17869 | 6.21 | 6.28 | 182 | 701 | 1261 | 1282.28 | -1.6875 | 53.6896 | 991.64 | 81.6466 | 86 | 66 | 20 | 120 | 155 | 275 | 275 | 0.46929 | 0.43636 | 11.272 | 11.4398 | 13.1358 | 42.8642 | 0.26689 | 6.28 | 6.37 | 314 | 1261 | 1644 | 1994.1613 | -21.2993 | 20.1018 | 1627.5806 | 80.7076 | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.013 | 0.592 | 1.2447 | 94.6502 | 0.91835 | 98.5844 | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.015 | 0.572 | 2.0904 | 93.5622 | 1.3312 | 98.8732 | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.029 | 0.668 | 1.3863 | 89.4928 | 1.0271 | 97.1766 | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.013 | 0.596 | 1.2828 | 94.6281 | 0.9394 | 98.6161 | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.01 | 0.569 | 1.1899 | 95.5947 | 0.87944 | 98.8629 | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.012 | 0.557 | 1.1623 | 94.6903 | 0.85967 | 98.6041
|  | Parameters must be entered in cells E15:E26, since these parameters are used in calculations. |  | System influent flow rate, QI-sys (gpm) | 1546.1806 | [5 empty] | 1998-07-21 | 3:32 | 26359.7 | 24.5 | 127.3 | 66 | 38.2891 | 0 | 1295 | 154 |  | 1449 | 1449 | 0.89372 | 0 | 13.9591 | 14.167 | 9.3682 | 48.9927 | 0.28916 |  | 6.01 | 211 |  | 391 | 1703 | 1904.6364 | -11.8401 | 46.0358 | 1147.8182 | 81.6173 | 127.3 | 97 | 51 | 871 | 578 | 1449 | 1449 | 0.43015 | 0.6011 | 15.9087 | 16.1455 | 4.3661 | 56.7839 | 0.28433 | 6.01 | 6.1 | 142 | 391 | 707 | 766.2232 | -8.3767 | 63.6829 | 578.6116 | 75.4585 | 97 | 85 | 20 | 305 | 273 | 578 | 578 | 0.36118 | 0.52768 | 11.1416 | 11.3074 | 8.3697 | 62.6303 | 0.18054 | 6.1 | 6.2 | 170 | 707 | 1300 | 1306.9451 | -0.53423 | 56.5217 | 1006.9725 | 83.1177 | 85 | 66 | 20 | 119 | 154 | 273 | 273 | 0.46601 | 0.4359 | 11.1781 | 11.3445 | 14.0161 | 41.4839 | 0.27347 | 6.2 | 6.2 | 289 | 1300 | 1703 | 2081.2273 | -22.2095 | 26.087 | 1690.6136 | 82.9056 | SDS-CDBAA | mg/L | BMRL | 3.9 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 2.96 | --- | --- | --- | --- | SDS-CDBAA | mg/L | BMRL | 8.1 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 2.86 | --- | --- | --- | --- | SDS-CDBAA | mg/L | BMRL | 2.2 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.5158 | --- | --- | --- | --- | SDS-CDBAA | mg/L | BMRL | 3.6 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 2.98 | --- | --- | --- | --- | SDS-CDBAA | mg/L | BMRL | 2.6 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 2.7095 | --- | --- | --- | --- | SDS-CDBAA | mg/L | BMRL | 2.5 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 2.6524 | --- | --- | --- | ---
|  |  |  | Recycle ratio, r | 0 | [5 empty] | 1998-07-22 | 5:32 | 26371 | 24.5 | 124.5 | 64 | 35.2891 | 0 | 1303 | 154 |  | 1457 | 1457 | 0.8943 | 0 | 14.0454 | 14.2545 | 8.5257 | 50.4352 | 0.28263 |  | 6.07 | 234 |  | 397 | 1660 | 1776.1494 | -6.9969 | 41.0579 | 1086.5747 | 78.4644 | 124.5 | 94 | 48 | 875 | 582 | 1457 | 1457 | 0.4327 | 0.60055 | 15.9817 | 16.2197 | 4.2392 | 57.0108 | 0.2845 | 6.07 | 6.21 | 155 | 397 | 705 | 760.8316 | -7.9194 | 60.9572 | 578.9158 | 73.2258 | 94 | 82 | 17 | 308 | 274 | 582 | 582 | 0.3633 | 0.52921 | 11.2511 | 11.4187 | 8.0914 | 62.9086 | 0.18151 | 6.21 | 6.29 | 187 | 705 | 1276 | 1287.2774 | -0.88381 | 52.8967 | 996.1387 | 81.2275 | 82 | 64 | 17 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.4398 | 13.243 | 42.757 | 0.26755 | 6.29 | 6.29 | 323 | 1276 | 1660 | 2018.5974 | -21.6023 | 18.6398 | 1647.2987 | 80.3921 | SDS-DCBAA | mg/L | BMRL | 21 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | 1.2 | 17 | --- | 159.2 | --- | 92.9412 | 79.5133 | 98.4908 | [8 empty] | SDS-DCBAA | mg/L | BMRL | 11 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | BMRL | 22 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | 1 | 18 | --- | 155.5455 | --- | 94.4444 | 78.6258 | 98.7282 | [8 empty] | SDS-DCBAA | mg/L | BMRL | 18 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  |  |  | 2: The design system recycle flow rate must fall between the minimum and | [6 empty] | 1998-07-23 | 5:26 | 26394.9 | 24.5 | 124.8 | 63 | 35.6991 | 0 | 1299 | 154 |  | 1453 | 1453 | 0.89401 | 0 | 14.0022 | 14.2107 | 9.2872 | 48.9137 | 0.29053 |  | 5.99 | 226 |  | 404 | 1729 | 1905.4416 | -10.2048 | 44.0594 | 1154.7208 | 80.4282 | 124.8 | 95 | 48 | 871 | 582 | 1453 | 1453 | 0.43185 | 0.59945 | 15.9087 | 16.1455 | 4.3882 | 57.5118 | 0.28073 | 5.99 | 6.13 | 153 | 404 | 722 | 779.6375 | -7.983 | 62.1287 | 591.8187 | 74.1475 | 95 | 83 | 18 | 308 | 274 | 582 | 582 | 0.3633 | 0.52921 | 11.2511 | 11.4187 | 8.4507 | 62.5493 | 0.18255 | 6.13 | 6.23 | 181 | 722 | 1319 | 1330.1314 | -0.84393 | 55.198 | 1026.0657 | 82.3598 | 83 | 63 | 18 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.4398 | 14.049 | 40.951 | 0.27935 | 6.23 | 6.21 | 308 | 1319 | 1729 | 2106.7922 | -21.8503 | 23.7624 | 1712.8961 | 82.0188 | SDS-HAA5 | mg/L | 0 | 137.2 | --- | 1296.7864 | --- | 100 | 648.3628 | 100 | [8 empty] | SDS-HAA5 | mg/L | 1.1 | 109.8 | --- | 1088.1 | --- | 98.9982 | 539.8757 | 99.7962 | [8 empty] | SDS-HAA5 | mg/L | 0 | 75.8 | --- | 758 | --- | 100 | 376.4928 | 100 | [8 empty] | SDS-HAA5 | mg/L | 0 | 144.3 | --- | 1362.6062 | --- | 100 | 681.2919 | 100 | [8 empty] | SDS-HAA5 | mg/L | 1 | 146.7 | --- | 1325.5455 | --- | 99.3183 | 666.2988 | 99.8499 | [8 empty] | SDS-HAA5 | mg/L | 0 | 69.4 | --- | 630.9091 | --- | 100 | 316.8959 | 100
|  |  |  | maximum system recycle flow rates. | [6 empty] | 1998-07-24 | 5:30 | 26418.8 | 24.5 | 126.8 | 66 | 37.6991 | 0 | 1300 | 154 |  | 1454 | 1454 | 0.89409 | 0 | 14.013 | 14.2217 | 9.0319 | 49.6689 | 0.28633 |  | 6.06 | 220 |  | 393 | 1675 | 1853.3896 | -10.6501 | 44.0204 | 1123.1948 | 80.413 | 126.8 | 96 | 50 | 870 | 584 | 1454 | 1454 | 0.43249 | 0.59835 | 15.8904 | 16.127 | 4.2749 | 57.1251 | 0.28231 | 6.06 | 6.21 | 148 | 393 | 707 | 757.9829 | -7.2112 | 62.341 | 575.4914 | 74.2828 | 96 | 86 | 20 | 310 | 274 | 584 | 584 | 0.36415 | 0.53082 | 11.3242 | 11.4928 | 8.3608 | 62.6392 | 0.18348 | 6.21 | 6.22 | 173 | 707 | 1281 | 1311.1606 | -2.3545 | 55.9796 | 1009.0803 | 82.8557 | 86 | 66 | 20 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.4398 | 13.8127 | 42.1873 | 0.27117 | 6.22 | 6.27 | 287 | 1281 | 1675 | 2055.5455 | -22.7191 | 26.972 | 1668.2727 | 82.7966 | SDS-HAA6 | mg/L | 0 | 150.2 | --- | 1419.6597 | --- | 100 | 709.7966 | 100 | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | 1.1 | 120.8 | --- | 1198.1 | --- | 99.0894 | 594.3977 | 99.8149 | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | 0 | 84.5 | --- | 845 | --- | 100 | 419.705 | 100 | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | 0 | 157.3 | --- | 1485.3636 | --- | 100 | 742.6695 | 100 | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | 2 | 158.7 | --- | 1426.5455 | --- | 98.7398 | 717.5273 | 99.7213 | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | 0 | 81.4 | --- | 740 | --- | 100 | 371.6906 | 100 | Stage 3 Operating Parameters During Sample Collection
[11 empty] | 1998-07-25 | 5:20 | 26442.8 | 24.4 | 128 | 65 | 37.6991 | 0 | 1300 | 154 |  | 1454 | 1454 | 0.89409 | 0 | 14.013 | 14.2638 | 8.7709 | 50.03 | 0.2851 |  | 6.02 | 222 |  | 390 | 1687 | 1808.1818 | -7.1833 | 43.0769 | 1099.0909 | 79.8015 | 128 | 96 | 50 | 864 | 590 | 1454 | 1454 | 0.43376 | 0.59422 | 15.7808 | 16.0632 | 4.2266 | 57.7734 | 0.27804 | 6.02 | 6.08 | 146 | 390 | 686 | 747.3153 | -8.9381 | 62.5641 | 568.6576 | 74.3255 | 96 | 85 | 20 | 314 | 276 | 590 | 590 | 0.36755 | 0.5322 | 11.4703 | 11.6756 | 7.907 | 62.593 | 0.18653 | 6.08 | 6.18 | 182 | 686 | 1262 | 1259.3913 | 0.20671 | 53.3333 | 972.6957 | 81.2891 | 85 | 65 | 20 | 122 | 154 | 276 | 276 | 0.46929 | 0.44203 | 11.4599 | 11.6649 | 13.5981 | 41.4019 | 0.28175 | 6.18 | 6.23 | 288 | 1262 | 1687 | 2033.6104 | -20.546 | 26.1538 | 1647.8052 | 82.5222 | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.44 |  |  |  |  | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.44 |  |  |  |  | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.44 |  |  |  |  | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.46 |  |  |  |  | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.43 |  |  |  |  | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.43
|  |  |  | Summary of the Stage and System Flow Rates | [6 empty] | 1998-07-26 | 11:00 | 26461.6 | 24.5 | 127 | 64 | 37.6991 | 0 | 1300 | 154 |  | 1454 | 1454 | 0.89409 | 0 | 14.013 | 14.2217 | 8.3532 | 49.4476 | 0.28761 |  | 6.03 | 226 |  | 386 | 1712 | 1736.6494 | -1.4398 | 41.4508 | 1061.3247 | 78.7059 | 127 | 95 | 50 | 873 | 581 | 1454 | 1454 | 0.43185 | 0.60041 | 15.9452 | 16.1826 | 4.2731 | 56.7269 | 0.28527 | 6.03 | 6.11 | 142 | 386 | 692 | 752.6299 | -8.7616 | 63.2124 | 569.315 | 75.0577 | 95 | 85 | 20 | 307 | 274 | 581 | 581 | 0.36288 | 0.5284 | 11.2146 | 11.3816 | 7.8323 | 62.1677 | 0.18308 | 6.11 | 6.2 | 190 | 692 | 1302 | 1254.4599 | 3.6513 | 50.7772 | 973.2299 | 80.4774 | 85 | 64 | 20 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.4398 | 14.1462 | 40.3538 | 0.28349 | 6.2 | 6.23 | 284 | 1302 | 1712 | 2095.2468 | -22.3859 | 26.4249 | 1698.6234 | 83.2806 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 120 |  |  |  |  | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 120 |  |  |  |  | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 120 |  |  |  |  | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 121 |  |  |  |  | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 117 |  |  |  |  | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 117
|  |  |  | Influent flow rate to stage 1, QI-s(1) (gpm) | 1546.1806 | [5 empty] | 1998-07-27 | 1:45 | 26473.1 | 24.5 | 122.6 | 61 | 33.2891 | 0 | 1301 | 154 |  | 1455 | 1455 | 0.89416 | 0 | 14.0238 | 14.2326 | 9.0376 | 49.4733 | 0.28768 | 7.06 | 6.21 | 235 | 393 | 408 | 1719 | 1869.513 | -8.7558 | 42.402 | 1138.7565 | 79.3635 | 122.6 | 93 | 46 | 872 | 583 | 1455 | 1455 | 0.43249 | 0.59931 | 15.9269 | 16.1641 | 4.3522 | 57.4478 | 0.28137 | 6.21 | 6.23 | 159 | 408 | 730 | 780.4322 | -6.9085 | 61.0294 | 594.2161 | 73.2421 | 93 | 81 | 15 | 309 | 274 | 583 | 583 | 0.36373 | 0.53002 | 11.2877 | 11.4557 | 8.4762 | 63.5238 | 0.18034 | 6.23 | 6.34 | 188 | 730 | 1318 | 1341.2336 | -1.7628 | 53.9216 | 1035.6168 | 81.8466 | 81 | 61 | 15 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.4398 | 13.8683 | 42.1317 | 0.27153 | 6.34 | 6.28 | 320 | 1318 | 1719 | 2095.6623 | -21.9117 | 21.5686 | 1706.8312 | 81.2518 | [12 empty] | Stage 3 influent flow rate during sample collection (gpm) | 275 | [16 empty] | Stage 3 influent flow rate during sample collection (gpm) | 274 | [16 empty] | Stage 3 influent flow rate during sample collection (gpm) | 274 | [16 empty] | Stage 3 influent flow rate during sample collection (gpm) | 264 | [16 empty] | Stage 3 influent flow rate during sample collection (gpm) | 271 | [16 empty] | Stage 3 influent flow rate during sample collection (gpm) | 271
|  |  |  | Permeate flow rate from stage 1, Qp-s(1) (gpm) | 821.25 | [5 empty] | 1998-07-28 | 6:04 | 26491.4 | 24.5 | 121.8 | 61 | 33.2891 | 0 | 1302 | 154 |  | 1456 | 1456 | 0.89423 | 0 | 14.0346 | 14.2435 | 8.9909 | 49.12 | 0.28997 |  | 6.03 | 219 |  | 391 | 1669 | 1845.1818 | -10.5561 | 43.9898 | 1118.0909 | 80.413 | 121.8 | 92 | 46 | 873 | 583 | 1456 | 1456 | 0.4327 | 0.59959 | 15.9452 | 16.1826 | 4.2843 | 56.6157 | 0.28583 | 6.03 | 6.16 | 146 | 391 | 702 | 757.8696 | -7.9586 | 62.6598 | 574.4348 | 74.5837 | 92 | 80 | 15 | 309 | 274 | 583 | 583 | 0.36373 | 0.53002 | 11.2877 | 11.4557 | 8.2416 | 62.7584 | 0.18254 | 6.16 | 6.25 | 175 | 702 | 1262 | 1296.3175 | -2.7193 | 55.243 | 999.1588 | 82.4853 | 80 | 61 | 15 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.4398 | 13.3542 | 42.1458 | 0.27143 | 6.25 | 6.24 | 301 | 1262 | 1669 | 2010.8312 | -20.4812 | 23.0179 | 1636.4156 | 81.6061 | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs
|  |  |  | Concentrate flow rate from stage 1, QC-s(1) (gpm) | 724.9306 | [5 empty] | 1998-07-29 | 5:15 | 26509 | 24.5 | 126.8 | 66 | 38.1091 | 0 | 1304 | 154 |  | 1458 | 1458 | 0.89438 | 0 | 14.0561 | 14.2654 | 7.0132 | 51.2776 | 0.2782 |  | 6.07 | 248 |  | 382 | 1640 | 1516.6494 | 7.5214 | 35.0785 | 949.3247 | 73.8762 | 126.8 | 98 | 50 | 876 | 582 | 1458 | 1458 | 0.43291 | 0.60082 | 16 | 16.2382 | 3.9082 | 58.4918 | 0.27762 | 6.07 | 6.27 | 159 | 382 | 705 | 717.6495 | -1.7943 | 58.377 | 549.8247 | 71.0817 | 98 | 85 | 21 | 308 | 274 | 582 | 582 | 0.3633 | 0.52921 | 11.2511 | 11.4187 | 7.982 | 62.518 | 0.18265 | 6.27 | 6.36 | 194 | 705 | 1264 | 1279.4088 | -1.219 | 49.2147 | 992.2044 | 80.4476 | 85 | 66 | 21 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.4398 | 13.0068 | 41.4932 | 0.2757 | 6.36 | 6.38 | 328 | 1264 | 1640 | 1993.3506 | -21.5458 | 14.1361 | 1628.6753 | 79.8609 |  | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters
|  |  |  | Influent flow rate to stage 2, QI-s(2) (gpm) | 724.9306 | [5 empty] | 1998-07-30 | 2:10 | 26529.9 | 23.9 | 127.3 | 66 | 37.6991 | 0 | 1304 | 155 |  | 1459 | 1459 | 0.89376 | 0 | 14.0561 | 14.5207 | 7.4452 | 51.5057 | 0.28192 |  | 6.01 | 256 |  | 399 | 1722 | 1602.0452 | 6.966 | 35.8396 | 1000.5226 | 74.4134 | 127.3 | 98 | 50 | 876 | 583 | 1459 | 1459 | 0.43333 | 0.60041 | 16 | 16.5288 | 4.0805 | 58.5695 | 0.28221 | 6.01 | 6.13 | 166 | 399 | 681 | 749.0995 | -9.9999 | 58.396 | 574.0497 | 71.0826 | 98 | 86 | 20 | 308 | 275 | 583 | 583 | 0.36415 | 0.5283 | 11.2511 | 11.623 | 6.864 | 65.136 | 0.17844 | 6.13 | 6.19 | 241 | 681 | 1163 | 1173.8 | -0.92863 | 39.599 | 927.4 | 74.0134 | 86 | 66 | 20 | 120 | 155 | 275 | 275 | 0.46929 | 0.43636 | 11.272 | 11.6445 | 10.5835 | 45.4165 | 0.25639 | 6.19 | 6.23 | 400 | 1163 | 1722 | 1753.7097 | -1.8414 | -0.25063 | 1458.3548 | 72.5718 |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-12 | CI-s3-12 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-14 | CI-s3-14 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-16 | CI-s3-16 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-18 | CI-s3-18 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-20 | CI-s3-20 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-20 (dup) | CI-s3-20 (dup) | CC(calc) | RF (%) | CB | RB (%)
|  |  |  | Permeate flow rate from stage 2, Qp-s(2) (gpm) | 410.625 | [5 empty] | 1998-07-31 | 12:09 | 26551.9 | 23.8 | 127 | 66 | 38.2891 | 0 | 1301 | 153 |  | 1454 | 1454 | 0.89477 | 0 | 14.0238 | 14.5302 | 8.035 | 50.1759 | 0.28958 |  | 5.97 | 237 |  | 390 | 1677 | 1691 | -0.83482 | 39.2308 | 1040.5 | 77.2225 | 127 | 98 | 51 | 876 | 578 | 1454 | 1454 | 0.43121 | 0.60248 | 16 | 16.5777 | 4.0781 | 57.4219 | 0.2887 | 5.97 | 6.13 | 158 | 390 | 652 | 741.6125 | -13.7442 | 59.4872 | 565.8062 | 72.0752 | 98 | 86 | 20 | 306 | 272 | 578 | 578 | 0.36076 | 0.52941 | 11.1781 | 11.5817 | 7 | 65 | 0.17818 | 6.13 | 6.25 | 204 | 652 | 1278 | 1156 | 9.5462 | 47.6923 | 904 | 77.4336 | 86 | 66 | 20 | 119 | 153 | 272 | 272 | 0.46383 | 0.4375 | 11.1781 | 11.5817 | 11.3472 | 44.6528 | 0.25937 | 6.25 | 6.26 | 461 | 1278 | 1677 | 1913.4444 | -14.0993 | -18.2051 | 1595.7222 | 71.1103 | Qp/QT (THM4), % | 79.0164 | 90.8197 |  | Qp/QT (HAA5), % | 60.6414 | 80.3207 |  |  |  | Sampling date | MM/DD/YY | 1998-06-23 | 1998-06-23 | --- | --- | --- | --- | Qp/QT (THM4), % | 71.2413 | 86.9755 |  | Qp/QT (HAA5), % | 51.3339 | 76.173 |  |  |  | Sampling date | MM/DD/YY | 1998-07-06 | 1998-07-06 | --- | --- | --- | --- | Qp/QT (THM4), % | 70.8155 | 86.2661 |  | Qp/QT (HAA5), % | 28.7599 | 64.3799 |  |  |  | Sampling date | MM/DD/YY | 1998-07-22 | 1998-07-22 | --- | --- | --- | --- | Qp/QT (THM4), % | 77.8403 | 89.7648 |  | Qp/QT (HAA5), % | 62.578 | 81.289 |  |  |  | Sampling date | MM/DD/YY | 1998-08-03 | 1998-08-03 | --- | --- | --- | --- | Qp/QT (THM4), % | 79.9239 | 91.3416 |  | Qp/QT (HAA5), % | 63.6239 | 82.1551 |  |  |  | Sampling date | MM/DD/YY | 1998-08-17 | 1998-08-17 | --- | --- | --- | --- | Qp/QT (THM4), % | 79.614 | 90.4704 |  | Qp/QT (HAA5), % | 22.1902 | 61.0951 |  |  |  | Sampling date | MM/DD/YY | 1998-08-17 | 1998-08-17 | --- | --- | --- | ---
|  |  |  | Concentrate flow rate from stage 2, QC-s(2) (gpm) | 314.3056 | [5 empty] | 1998-08-01 | 5:00 | 26580.1 | 23.4 | 127 | 65 | 38.2891 | 0 | 1300 | 154 |  | 1454 | 1454 | 0.89409 | 0 | 14.013 | 14.6917 | 8.04 | 49.6709 | 0.29578 |  | 6.02 | 232 |  | 386 | 1682 | 1686 | -0.23781 | 39.8964 | 1036 | 77.6062 | 127 | 96 | 51 | 873 | 581 | 1454 | 1454 | 0.43185 | 0.60041 | 15.9452 | 16.7174 | 4.1681 | 56.3319 | 0.29677 | 6.02 | 6.11 | 148 | 386 | 632 | 743.6145 | -17.6605 | 61.658 | 564.8072 | 73.7964 | 96 | 86 | 20 | 307 | 274 | 581 | 581 | 0.36288 | 0.5284 | 11.2146 | 11.7577 | 6.5529 | 64.4471 | 0.18244 | 6.11 | 6.19 | 212 | 632 | 1316 | 1102.5839 | 16.217 | 45.0777 | 867.292 | 75.5561 | 86 | 65 | 20 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.8179 | 13.1735 | 42.3265 | 0.27921 | 6.19 | 6.23 | 368 | 1316 | 1682 | 2054.7013 | -22.1582 | 4.6632 | 1685.3506 | 78.1648 | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 128.0437 | 68.0219 |  |  |  | Sampling time | hh:mm | 8:51 | 8:59 | --- | --- | --- | --- | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 117.5479 | 60.7163 |  |  |  | Sampling time | hh:mm | 8:34 | 8:46 | --- | --- | --- | --- | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 169.9894 | 86.9947 |  |  |  | Sampling time | hh:mm | 8:22 | 8:35 | --- | --- | --- | --- | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 118.0771 | 61.5886 |  |  |  | Sampling time | hh:mm | 8:13 | 8:24 | --- | --- | --- | --- | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 123.3939 | 64.9649 |  |  |  | Sampling time | hh:mm | 5:38 | 5:55 | --- | --- | --- | --- | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 262.4173 | 133.4086 |  |  |  | Sampling time | hh:mm | 5:38 | 5:55 | --- | --- | --- | ---
|  |  |  | Influent flow rate to stage 3, QI-s(3) (gpm) | 314.3056 | [5 empty] | 1998-08-02 | 10:30 | 26610.4 | 24.1 | 123 | 64 | 34.9292 | 0 | 1299 | 154 |  | 1453 | 1453 | 0.89401 | 0 | 14.0022 | 14.3797 | 8.2437 | 50.3271 | 0.28573 |  | 6.02 | 234 |  | 392 | 1651 | 1724.7403 | -4.4664 | 40.3061 | 1058.3701 | 77.8905 | 123 | 95 | 46 | 875 | 578 | 1453 | 1453 | 0.431 | 0.6022 | 15.9817 | 16.4126 | 4.3923 | 58.6077 | 0.28004 | 6.02 | 6.13 | 142 | 392 | 656 | 770.4602 | -17.4482 | 63.7755 | 581.2301 | 75.5691 | 95 | 85 | 19 | 305 | 273 | 578 | 578 | 0.36118 | 0.52768 | 11.1416 | 11.4419 | 6.7644 | 64.2356 | 0.17812 | 6.13 | 6.2 | 222 | 656 | 1286 | 1140.8718 | 11.2852 | 43.3673 | 898.4359 | 75.2904 | 85 | 64 | 19 | 119 | 154 | 273 | 273 | 0.46601 | 0.4359 | 11.1781 | 11.4794 | 12.5327 | 42.9673 | 0.26717 | 6.2 | 6.23 | 382 | 1286 | 1651 | 1984.5455 | -20.2026 | 2.551 | 1635.2727 | 76.64 | SDS-HAA5b, mg/L | 28.7895 | 12.5954 |  | SDS-HAA5b, mg/L | 54 | 27 |  |  |  | Operation time | hh.hh | 25824.3 | 25824.4 | --- | --- | --- | --- | SDS-HAA5b, mg/L | 32.3608 | 15.2576 |  | SDS-HAA5b, mg/L | 54 | 27 |  |  |  | Operation time | hh.hh | 26105.7 | 26105.9 | --- | --- | --- | --- | SDS-HAA5b, mg/L | 22.1219 | 10.4103 |  | SDS-HAA5b, mg/L | 54 | 27 |  |  |  | Operation time | hh.hh | 26373.9 | 26374.1 | --- | --- | --- | --- | SDS-HAA5b, mg/L | 31.9764 | 14.7694 |  | SDS-HAA5b, mg/L | 54 | 27 |  |  |  | Operation time | hh.hh | 26631.8 | 26636.9 | --- | --- | --- | --- | SDS-HAA5b, mg/L | 30.2509 | 13.6153 |  | SDS-HAA5b, mg/L | 54 | 27 |  |  |  | Operation time | hh.hh | 26874.5 | 26874.8 | --- | --- | --- | --- | SDS-HAA5b, mg/L | 14.1479 | 6.6135 |  | SDS-HAA5b, mg/L | 54 | 27 |  |  |  | Operation time | hh.hh | 26874.5 | 26874.8 | --- | --- | --- | ---
|  |  |  | Permeate flow rate from stage 3, Qp-s(3) (gpm) | 159.6875 | [5 empty] | 1998-08-03 | 10:39 | 26634.3 | 24 | 127 | 60 | 38.2891 | 0 | 1308 | 143 |  | 1451 | 1451 | 0.90145 | 0 | 14.0993 | 14.5222 | 8.0815 | 47.1294 | 0.30814 | 7.08 | 6.08 | 253 | 383 | 398 | 1571 | 1724.2937 | -9.7577 | 36.4322 | 1061.1469 | 76.1579 | 127 | 98 | 51 | 876 | 575 | 1451 | 1451 | 0.42994 | 0.60372 | 16 | 16.48 | 4.3163 | 57.1837 | 0.28819 | 6.08 | 6.18 | 153 | 398 | 651 | 771.2522 | -18.4719 | 61.5578 | 584.6261 | 73.8294 | 98 | 86 | 20 | 311 | 264 | 575 | 575 | 0.35609 | 0.54087 | 11.3607 | 11.7016 | 7.4048 | 64.5952 | 0.18115 | 6.18 | 6.32 | 185 | 651 | 1251 | 1199.9621 | 4.0798 | 53.5176 | 925.4811 | 80.0104 | 86 | 60 | 20 | 121 | 143 | 264 | 264 | 0.44419 | 0.45833 | 11.3659 | 11.7069 | 12.6938 | 40.3062 | 0.29045 | 6.32 | 6.2 | 359 | 1251 | 1571 | 2005.7692 | -27.6747 | 9.799 | 1628.3846 | 77.9536 | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  |  |  | pH | --- | 6.28 | 6.28 | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  |  |  | pH | --- | 6.13 | 6.08 | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  |  |  | pH | --- | 6.31 | 6.37 | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  |  |  | pH | --- | 6.19 | 6.2 | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  |  |  | pH | --- | 6.19 | 6.23 | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  |  |  | pH | --- | 6.19 | 6.23 | --- | --- | --- | ---
|  |  |  | Concentrate flow rate from stage 3, QC-s(3) (gpm) | 154.6181 | [5 empty] | 1998-08-04 | 5:00 | 26653.4 | 24.1 | 128 | 60 | 38.2891 | 0 | 1300 | 155 |  | 1455 | 1455 | 0.89347 | 0 | 14.013 | 14.3908 | 3.3758 | 52.3351 | 0.27497 |  | 6.06 | 319 |  | 384 | 1554 | 929.1613 | 40.2084 | 16.9271 | 656.5806 | 51.415 | 128 | 98 | 51 | 874 | 581 | 1455 | 1455 | 0.43206 | 0.60069 | 15.9635 | 16.3938 | 3.9073 | 58.0927 | 0.2822 | 6.06 | 6.28 | 161 | 384 | 675 | 719.4596 | -6.5866 | 58.0729 | 551.7298 | 70.819 | 98 | 86 | 20 | 307 | 274 | 581 | 581 | 0.36288 | 0.5284 | 11.2146 | 11.517 | 7.5359 | 64.4641 | 0.17866 | 6.28 | 6.37 | 192 | 675 | 1254 | 1216.1715 | 3.0166 | 50 | 945.5858 | 79.6951 | 86 | 60 | 20 | 119 | 155 | 274 | 274 | 0.4682 | 0.43431 | 11.1781 | 11.4794 | 12.5794 | 40.4206 | 0.284 | 6.37 | 6.37 | 345 | 1254 | 1554 | 1951.8774 | -25.6034 | 10.1562 | 1602.9387 | 78.477 | SDS-CDb, mg/L | 17.5519 | 16.3527 |  | SDS-CDb, mg/L | 19.4188 | 17.4194 |  |  |  | Temperature | oC | 25.2 | 25.3 | --- | --- | --- | --- | SDS-CDb, mg/L | 19.068 | 17.4332 |  | SDS-CDb, mg/L | 21.1364 | 18.5556 |  |  |  | Temperature | oC | 25.5 | 25.7 | --- | --- | --- | --- | SDS-CDb, mg/L | 20.7433 | 19.291 |  | SDS-CDb, mg/L | 24.6966 | 21.3483 |  |  |  | Temperature | oC | 25.1 | 25 | --- | --- | --- | --- | SDS-CDb, mg/L | 18.104 | 16.7566 |  | SDS-CDb, mg/L | 19.8287 | 17.7143 |  |  |  | Temperature | oC | 25.4 | 25.3 | --- | --- | --- | --- | SDS-CDb, mg/L | 17.2491 | 15.8847 |  | SDS-CDb, mg/L | 19.1969 | 16.9825 |  |  |  | Temperature | oC | 25.5 | 25.5 | --- | --- | --- | --- | SDS-CDb, mg/L | 18.0007 | 16.8554 |  | SDS-CDb, mg/L | 24.0589 | 19.9545 |  |  |  | Temperature | oC | 25.5 | 25.5 | --- | --- | --- | ---
|  |  |  | System concentrate recycle flow rate, QR-sys (gpm) | 0 | [5 empty] | 1998-08-05 | 5:10 | 26671.4 | 24.3 | 128 | 62 | 38.2891 | 0 | 1300 | 154 |  | 1454 | 1454 | 0.89409 | 0 | 14.013 | 14.306 | 4.9075 | 51.8034 | 0.27616 |  | 6.03 | 288 |  | 382 | 1612 | 1175.5065 | 27.0778 | 24.6073 | 778.7532 | 63.0178 | 128 | 97 | 51 | 873 | 581 | 1454 | 1454 | 0.43185 | 0.60041 | 15.9452 | 16.2786 | 3.9579 | 57.5421 | 0.2829 | 6.03 | 6.11 | 156 | 382 | 712 | 721.5835 | -1.346 | 59.1623 | 551.7917 | 71.7285 | 97 | 86 | 20 | 307 | 274 | 581 | 581 | 0.36288 | 0.5284 | 11.2146 | 11.4491 | 8.2068 | 63.2932 | 0.18089 | 6.11 | 6.19 | 186 | 712 | 1186 | 1301.3504 | -9.726 | 51.3089 | 1006.6752 | 81.5233 | 86 | 62 | 20 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.5077 | 11.9229 | 42.0771 | 0.27349 | 6.19 | 6.24 | 328 | 1186 | 1612 | 1854.5714 | -15.0479 | 14.1361 | 1520.2857 | 78.4251 | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! |  |  |  | Alkalinity | mg/L as CaCO3 | 152 | 160 | 166.1935 | -76.7442 | 163.0968 | 6.8038 | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! |  |  |  | Alkalinity | mg/L as CaCO3 | 134 | 144 | 151.7922 | -63.4146 | 147.8961 | 9.3959 | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! |  |  |  | Alkalinity | mg/L as CaCO3 | 184 | 204 | 219.5844 | -64.2857 | 211.7922 | 13.1224 | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! |  |  |  | Alkalinity | mg/L as CaCO3 | 152 | 174 | 192.6154 | -58.3333 | 183.3077 | 17.0793 | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! |  |  |  | Alkalinity | mg/L as CaCO3 | 174 | 204 | 226.7922 | -64.1509 | 215.3961 | 19.2186 | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! |  |  |  | Alkalinity | mg/L as CaCO3 | 175 | 206 | 229.5519 | -65.0943 | 217.776 | 19.6422
|  |  |  | System concentrate waste flow rate, QW-sys (gpm) | 154.6181 | [5 empty] | 1998-08-06 | 1:34 | 26692 | 24.2 | 127.4 | 66 | 38.2891 | 0 | 1300 | 154 |  | 1454 | 1454 | 0.89409 | 0 | 14.013 | 14.3483 | 6.787 | 51.6239 | 0.27794 |  | 6.03 | 259 |  | 389 | 1620 | 1486.4026 | 8.2468 | 33.419 | 937.7013 | 72.3793 | 127.4 | 98 | 51 | 871 | 583 | 1454 | 1454 | 0.43227 | 0.59904 | 15.9087 | 16.2894 | 3.3717 | 58.3283 | 0.27927 | 6.03 | 6.24 | 196 | 389 | 618 | 677.3413 | -9.6022 | 49.6144 | 533.1707 | 63.2388 | 98 | 86 | 20 | 309 | 274 | 583 | 583 | 0.36373 | 0.53002 | 11.2877 | 11.5578 | 5.5517 | 66.4483 | 0.17394 | 6.24 | 6.35 | 263 | 618 | 1256 | 1018.3467 | 18.9214 | 32.3907 | 818.1734 | 67.8552 | 86 | 66 | 20 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.5417 | 12.8956 | 43.1044 | 0.26776 | 6.35 | 6.23 | 328 | 1256 | 1620 | 1979.1169 | -22.1677 | 15.6812 | 1617.5584 | 79.7225 | UV254 b, cm-1 | 0.061262 | 0.034115 |  | UV254 b, cm-1 | 0.10352 | 0.058262 |  |  |  | Total dissolved solids | mg/L | 356 | 2528 | 4209.5484 | 40.6667 | 3368.7742 | 89.4324 | UV254 b, cm-1 | 0.074844 | 0.039914 |  | UV254 b, cm-1 | 0.11904 | 0.063896 |  |  |  | Total dissolved solids | mg/L | 318 | 2460 | 4129.0909 | 44.4056 | 3294.5455 | 90.3477 | UV254 b, cm-1 | 0.10038 | 0.06206 |  | UV254 b, cm-1 | 0.20468 | 0.11634 |  |  |  | Total dissolved solids | mg/L | 376 | 2300 | 3799.2208 | 30.3704 | 3049.6104 | 87.6706 | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  |  |  | Total dissolved solids | mg/L | 340 | 2402 | 4146.7692 | 35.3612 | 3274.3846 | 89.6164 | UV254 b, cm-1 | 0.056762 | 0.032442 |  | UV254 b, cm-1 | 0.091481 | 0.05201 |  |  |  | Total dissolved solids | mg/L | 363 | 2348 | 3856.0844 | 35.6383 | 3102.0422 | 88.298 | UV254 b, cm-1 | 0.054034 | 0.030584 |  | UV254 b, cm-1 | 0.17807 | 0.094035 |  |  |  | Total dissolved solids | mg/L | 361 | 2360 | 3878.7208 | 33.8828 | 3119.3604 | 88.4271
|  |  |  | System permeate flow rate, Qp-sys (gpm) | 1391.5625 | [5 empty] | 1998-08-07 | 12:34 | 26714.4 | 24.4 | 127.2 | 66 | 38.1091 | 0 | 1301 | 154 |  | 1455 | 1455 | 0.89416 | 0 | 14.0238 | 14.2747 | 4.1792 | 54.3116 | 0.26283 |  | 6.32 | 289 |  | 369 | 1579 | 1044.8442 | 33.8287 | 21.6802 | 706.9221 | 59.1185 | 127.2 | 98 | 50 | 873 | 582 | 1455 | 1455 | 0.43227 | 0.6 | 15.9452 | 16.2305 | 3.115 | 59.485 | 0.27285 | 6.32 | 6.5 | 191 | 369 | 666 | 636 | 4.5045 | 48.2385 | 502.5 | 61.99 | 98 | 86 | 21 | 308 | 274 | 582 | 582 | 0.3633 | 0.52921 | 11.2511 | 11.4525 | 6.8418 | 64.1582 | 0.1785 | 6.5 | 6.71 | 228 | 666 | 1205 | 1158.3504 | 3.8713 | 38.2114 | 912.1752 | 75.0048 | 86 | 66 | 21 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.4737 | 11.8673 | 43.1327 | 0.26601 | 6.71 | 6.7 | 351 | 1205 | 1579 | 1870.4545 | -18.4582 | 4.878 | 1537.7273 | 77.1741 | Bromideb, mg/L | 140 | 140 |  | Bromideb, mg/L | 140 | 140 |  |  |  | Total hardness | mg/L as CaCO3 | 172 | 1440 | 2421.6774 | 41.0959 | 1930.8387 | 91.092 | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE! |  |  |  | Total hardness | mg/L as CaCO3 | 154 | 1470 | 2495.4545 | 50.3226 | 1982.7273 | 92.2329 | Bromideb, mg/L | 174.1631 | 177.2532 |  | Bromideb, mg/L | 165.752 | 172.876 |  |  |  | Total hardness | mg/L as CaCO3 | 192 | 1350 | 2252.3377 | 33.7931 | 1801.1688 | 89.3403 | Bromideb, mg/L | 170 | 170 |  | Bromideb, mg/L | 170 | 170 |  |  |  | Total hardness | mg/L as CaCO3 | 176 | 1470 | 2564.9231 | 45.679 | 2017.4615 | 91.2762 | Bromideb, mg/L | 155.9848 | 158.2683 |  | Bromideb, mg/L | 152.7248 | 156.431 |  |  |  | Total hardness | mg/L as CaCO3 | 202 | 1580 | 2626.9221 | 39.521 | 2103.461 | 90.3968 | Bromideb, mg/L | 160 | 160 |  | Bromideb, mg/L | 160 | 160 |  |  |  | Total hardness | mg/L as CaCO3 | 202 | 1580 | 2626.9221 | 39.881 | 2103.461 | 90.3968
|  |  |  | System feed flow rate, QF-sys (gpm) | 1546.1806 | [5 empty] | 1998-08-08 | 10:10 | 26746.8 | 24.3 | 125 | 64 | 36.1091 | 0 | 1302 | 156 |  | 1458 | 1458 | 0.893 | 0 | 14.0346 | 14.328 | 5.8973 | 52.4935 | 0.27295 |  | 6.04 | 268 |  | 382 | 1612 | 1333.4615 | 17.2791 | 29.8429 | 857.7308 | 68.7548 | 125 | 96 | 48 | 882 | 576 | 1458 | 1458 | 0.43164 | 0.60494 | 16.1096 | 16.4464 | 3.5312 | 58.9688 | 0.2789 | 6.04 | 6.12 | 182 | 382 | 680 | 688.25 | -1.2132 | 52.356 | 535.125 | 65.9893 | 96 | 85 | 19 | 302 | 274 | 576 | 576 | 0.36076 | 0.52431 | 11.032 | 11.2626 | 7.104 | 64.396 | 0.1749 | 6.12 | 6.23 | 222 | 680 | 1312 | 1184.8029 | 9.6949 | 41.8848 | 932.4015 | 76.1905 | 85 | 64 | 19 | 118 | 156 | 274 | 274 | 0.46929 | 0.43066 | 11.0841 | 11.3159 | 13.3686 | 42.1314 | 0.26859 | 6.23 | 6.3 | 342 | 1312 | 1612 | 2045.7179 | -26.9056 | 10.4712 | 1678.859 | 79.629 | Alkb, mg/L CaCO3 | 97.0623 | 98.7148 |  | Alkb, mg/L CaCO3 | 94.4898 | 97.2449 |  |  |  | Calcium hardness | mg/L as CaCO3 | 126 | 1100 | 1854.0645 | 45.2174 | 1477.0323 | 91.4694 | Alkb, mg/L CaCO3 | 94.8234 | 97.6556 |  | Alkb, mg/L CaCO3 | 91.2401 | 95.7111 |  |  |  | Calcium hardness | mg/L as CaCO3 | 136 | 1080 | 1815.5844 | 40.3509 | 1447.7922 | 90.6064 | Alkb, mg/L CaCO3 | 123.3305 | 125.8026 |  | Alkb, mg/L CaCO3 | 116.6016 | 122.3008 |  |  |  | Calcium hardness | mg/L as CaCO3 | 144 | 1010 | 1684.8052 | 37.3913 | 1347.4026 | 89.3128 | Alkb, mg/L CaCO3 | 106.8976 | 108.5671 |  | Alkb, mg/L CaCO3 | 104.7609 | 107.3805 |  |  |  | Calcium hardness | mg/L as CaCO3 | 138 | 1200 | 2098.6154 | 42.5 | 1649.3077 | 91.6329 | Alkb, mg/L CaCO3 | 123.5833 | 126.0951 |  | Alkb, mg/L CaCO3 | 119.9973 | 124.0741 |  |  |  | Calcium hardness | mg/L as CaCO3 | 158 | 1200 | 1991.6494 | 42.7536 | 1595.8247 | 90.0992 | Alkb, mg/L CaCO3 | 124.3112 | 126.8082 |  | Alkb, mg/L CaCO3 | 111.1037 | 120.0519 |  |  |  | Calcium hardness | mg/L as CaCO3 | 156 | 1210 | 2010.7662 | 42.6471 | 1610.3831 | 90.3129
[11 empty] | 1998-08-09 | 10:05 | 26770.1 | 24.1 | 125 | 63 | 36.1091 | 0 | 1300 | 154 |  | 1454 | 1454 | 0.89409 | 0 | 14.013 | 14.3908 | 6.4738 | 51.4171 | 0.27988 |  | 5.95 | 262 |  | 386 | 1626 | 1432.7532 | 11.8848 | 32.1244 | 909.3766 | 71.1891 | 125 | 95 | 48 | 872 | 582 | 1454 | 1454 | 0.43206 | 0.59972 | 15.9269 | 16.3563 | 3.6732 | 58.3268 | 0.28043 | 5.95 | 6.05 | 176 | 386 | 692 | 700.6392 | -1.2484 | 54.4041 | 543.3196 | 67.6065 | 95 | 84 | 19 | 308 | 274 | 582 | 582 | 0.3633 | 0.52921 | 11.2511 | 11.5545 | 8.0601 | 62.4399 | 0.18505 | 6.05 | 6.16 | 176 | 692 | 1326 | 1272.0292 | 4.0702 | 54.4041 | 982.0146 | 82.0777 | 84 | 63 | 19 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.5759 | 13.4792 | 41.0208 | 0.2822 | 6.16 | 6.23 | 356 | 1326 | 1626 | 2081.8442 | -28.0347 | 7.772 | 1703.9221 | 79.107 | T-Hdb, mg/L CaCO3 | 157.6721 | 137.6066 |  | T-Hdb, mg/L CaCO3 | 188.9096 | 155.4548 |  |  |  | Turbidity | ntu | 0.14 | 17 | 30.0529 | 33.3333 | 23.5265 | 99.4049 | T-Hdb, mg/L CaCO3 | 167.5175 | 136.049 |  | T-Hdb, mg/L CaCO3 | 207.3321 | 157.6541 |  |  |  | Turbidity | ntu | 0.07 | 17 | 30.1922 | 89.2308 | 23.5961 | 99.7033 | T-Hdb, mg/L CaCO3 | 180.9442 | 157.1502 |  | T-Hdb, mg/L CaCO3 | 245.7098 | 190.8549 |  |  |  | Turbidity | ntu | 0.09 | 17 | 30.1766 | 43.75 | 23.5883 | 99.6185 | T-Hdb, mg/L CaCO3 | 168.3193 | 144.4704 |  | T-Hdb, mg/L CaCO3 | 198.8441 | 161.422 |  |  |  | Turbidity | ntu | 0.06 | 17 | 31.3338 | 91.0448 | 24.1669 | 99.7517 | T-Hdb, mg/L CaCO3 | 182.9439 | 161.3644 |  | T-Hdb, mg/L CaCO3 | 213.7509 | 178.7268 |  |  |  | Turbidity | ntu | 0.11 | 15.5 | 27.1924 | 57.6923 | 21.3462 | 99.4847 | T-Hdb, mg/L CaCO3 | 184.7334 | 164.1062 |  | T-Hdb, mg/L CaCO3 | 293.8386 | 219.9193 |  |  |  | Turbidity | ntu | 0.115 | 16 | 28.0685 | 61.6667 | 22.0342 | 99.4781
|  |  |  | Calculate the Required System Influent Pressure | [6 empty] | 1998-08-13 | 12:17 | 26782 | 23.9 | 124.9 | 64 | 37.1091 | 0 | 1297 | 154 |  | 1451 | 1451 | 0.89387 | 0 | 13.9807 | 14.4427 | 9.5883 | 47.7525 | 0.30245 |  | 5.95 | 210 |  | 394 | 1637 | 1943.6623 | -18.7332 | 46.7005 | 1168.8312 | 82.0333 | 124.9 | 96 | 49 | 881 | 570 | 1451 | 1451 | 0.42888 | 0.60717 | 16.0913 | 16.6231 | 4.1129 | 57.3371 | 0.28992 | 5.95 | 6.19 | 162 | 394 | 654 | 752.5825 | -15.0738 | 58.8832 | 573.2912 | 71.7421 | 96 | 86 | 20 | 300 | 270 | 570 | 570 | 0.35651 | 0.52632 | 10.9589 | 11.3211 | 6.1911 | 64.8089 | 0.17468 | 6.19 | 6.18 | 256 | 654 | 1178 | 1096.2222 | 6.9421 | 35.0254 | 875.1111 | 70.7466 | 86 | 64 | 20 | 116 | 154 | 270 | 270 | 0.46274 | 0.42963 | 10.8963 | 11.2564 | 10.9029 | 44.0971 | 0.25526 | 6.18 | 6.21 | 386 | 1178 | 1637 | 1774.5714 | -8.4039 | 2.0305 | 1476.2857 | 73.8533 | Ca-Hdb, mg/L CaCO3 | 120.9574 | 104.6689 |  | Ca-Hdb, mg/L CaCO3 | 146.3149 | 119.1574 |  |  |  | Total organic carbon | mg/L | BMRL | 49 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ca-Hdb, mg/L CaCO3 | 125.4126 | 102.7552 |  | Ca-Hdb, mg/L CaCO3 | 154.0791 | 118.3109 |  |  |  | Total organic carbon | mg/L | BMRL | 49 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ca-Hdb, mg/L CaCO3 | 137.9399 | 117.8541 |  | Ca-Hdb, mg/L CaCO3 | 192.6121 | 146.3061 |  |  |  | Total organic carbon | mg/L | BMRL | 47 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ca-Hdb, mg/L CaCO3 | 129.4667 | 112.534 |  | Ca-Hdb, mg/L CaCO3 | 151.1393 | 124.5696 |  |  |  | Total organic carbon | mg/L | BMRL | 49 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ca-Hdb, mg/L CaCO3 | 141.7279 | 122.5461 |  | Ca-Hdb, mg/L CaCO3 | 169.1119 | 137.9794 |  |  |  | Total organic carbon | mg/L | BMRL | 49 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ca-Hdb, mg/L CaCO3 | 143.0253 | 125.4379 |  | Ca-Hdb, mg/L CaCO3 | 236.0519 | 173.0259 |  |  |  | Total organic carbon | mg/L | BMRL | 51 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  |  |  | Osmotic pressure for stage 13, Dp1 (psi) | 4 | [5 empty] | 1998-08-14 | 0:14 | 26805.1 | 23.5 | 118.5 | 58 | 31.1091 | 0 | 1301 | 158 |  | 1459 | 1459 | 0.89171 | 0 | 14.0238 | 14.6596 | 3.3773 | 53.7636 | 0.27267 |  | 6.01 | 316 |  | 382 | 1695 | 925.4557 | 45.4008 | 17.2775 | 653.7278 | 51.6618 | 118.5 | 90 | 43 | 879 | 580 | 1459 | 1459 | 0.4327 | 0.60247 | 16.0548 | 16.7827 | 3.4452 | 57.8048 | 0.29033 | 6.01 | 6.23 | 186 | 382 | 697 | 679.0414 | 2.5766 | 51.3089 | 530.5207 | 64.9401 | 90 | 78 | 14 | 304 | 276 | 580 | 580 | 0.3633 | 0.52414 | 11.105 | 11.6085 | 7.2884 | 62.7116 | 0.18511 | 6.23 | 6.26 | 227 | 697 | 1293 | 1214.6812 | 6.0571 | 40.5759 | 955.8406 | 76.2513 | 78 | 58 | 14 | 118 | 158 | 276 | 276 | 0.47365 | 0.42754 | 11.0841 | 11.5867 | 13.0063 | 40.9937 | 0.28264 | 6.26 | 6.32 | 346 | 1293 | 1695 | 2000.2532 | -18.009 | 9.4241 | 1646.6266 | 78.9873 | Notes: | [9 empty] | UV254 | cm-1 | 0.015 | 1.52 | 2.6852 | 93.8272 | 2.1026 | 99.2866 | Notes: | [9 empty] | UV254 | cm-1 | 0.018 | 1.435 | 2.5392 | 92.2747 | 1.9871 | 99.0941 | Notes: | [9 empty] | UV254 | cm-1 | 0.032 | 1.66 | 2.9286 | 88.4058 | 2.2943 | 98.6052 | Notes: | [9 empty] | UV254 | cm-1 | 0.01 | 1.49 | 2.7423 | 95.8678 | 2.1162 | 99.5274 | Notes: | [9 empty] | UV254 | cm-1 | 0.009 | 1.382 | 2.4251 | 96.0352 | 1.9036 | 99.5272 | Notes: | [9 empty] | UV254 | cm-1 | 0.01 | 1.42 | 2.4912 | 95.5752 | 1.9556 | 99.4887
|  |  |  | Osmotic pressure for stage 23, Dp2 (psi) | 9 | [5 empty] | 1998-08-15 | 5:17 | 26834.1 | 24.5 | 118.5 | 56 | 30.1091 | 0 | 1302 | 151 |  | 1453 | 1453 | 0.89608 | 0 | 14.0346 | 14.2435 | 9.1885 | 47.9524 | 0.29704 |  | 6 | 225 |  | 398 | 1711 | 1889.6954 | -10.4439 | 43.4673 | 1143.8477 | 80.3295 | 118.5 | 90 | 42 | 880 | 573 | 1453 | 1453 | 0.42994 | 0.60564 | 16.0731 | 16.3124 | 4.3667 | 57.8833 | 0.28181 | 6 | 6.14 | 151 | 398 | 719 | 777.3368 | -8.1136 | 62.0603 | 587.6684 | 74.3052 | 90 | 86 | 13 | 304 | 269 | 573 | 573 | 0.35736 | 0.53054 | 11.105 | 11.2704 | 8.4357 | 66.5643 | 0.16932 | 6.14 | 6.26 | 180 | 719 | 1319 | 1328.1301 | -0.6922 | 54.7739 | 1023.5651 | 82.4144 | 86 | 56 | 13 | 118 | 151 | 269 | 269 | 0.45838 | 0.43866 | 11.0841 | 11.2492 | 14.102 | 43.898 | 0.25626 | 6.26 | 6.26 | 305 | 1319 | 1711 | 2111.3974 | -23.4014 | 23.3668 | 1715.1987 | 82.2178 | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | NR | 3.102 | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | NR | 2.9286 | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | NR | 3.5319 | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | NR | 3.0408 | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | NR | 2.8204 | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | NR | 2.7843 | --- | --- | --- | ---
|  |  |  | Osmotic pressure for stage 33, Dp3 (psi) | 16 | [5 empty] | 1998-08-16 | 6:00 | 26858.1 | 24.3 | 120 | 55 | 31.6991 | 0 | 1298 | 156 |  | 1454 | 1454 | 0.89271 | 0 | 13.9915 | 14.284 | 8.4628 | 47.3381 | 0.30174 |  | 5.95 | 222 |  | 386 | 1689 | 1750.5641 | -3.645 | 42.487 | 1068.2821 | 79.219 | 120 | 92 | 44 | 878 | 576 | 1454 | 1454 | 0.43079 | 0.60385 | 16.0365 | 16.3718 | 4.1234 | 57.8766 | 0.28287 | 5.95 | 6.11 | 152 | 386 | 810 | 742.6875 | 8.3102 | 60.6218 | 564.3438 | 73.0661 | 92 | 85 | 14 | 302 | 274 | 576 | 576 | 0.36076 | 0.52431 | 11.032 | 11.2626 | 9.6788 | 64.8212 | 0.17375 | 6.11 | 6.19 | 186 | 810 | 1284 | 1497.7664 | -16.6485 | 51.8135 | 1153.8832 | 83.8805 | 85 | 55 | 14 | 118 | 156 | 274 | 274 | 0.46929 | 0.43066 | 11.0841 | 11.3159 | 13.7269 | 42.2731 | 0.26769 | 6.19 | 6.24 | 288 | 1284 | 1689 | 2037.3846 | -20.6267 | 25.3886 | 1660.6923 | 82.6578 | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs.
|  |  |  | Pressure losses due to stage hardware, DPs (psi) | 62 | [5 empty] | 1998-08-17 | 3:28 | 26872.3 | 24.6 | 122.5 | 62 | 34.5192 | 0 | 1300 | 154 |  | 1454 | 1454 | 0.89409 | 0 | 14.013 | 14.1797 | 8.5099 | 49.221 | 0.28808 |  | 6.05 | 227 |  | 390 | 1663 | 1765.974 | -6.1921 | 41.7949 | 1077.987 | 78.9422 | 122.5 | 94 | 46 | 882 | 572 | 1454 | 1454 | 0.42994 | 0.6066 | 16.1096 | 16.3012 | 4.2326 | 58.0174 | 0.28097 | 6.05 | 6.18 | 151 | 390 | 706 | 758.528 | -7.4402 | 61.2821 | 574.264 | 73.7055 | 94 | 82 | 18 | 301 | 271 | 572 | 572 | 0.35779 | 0.52622 | 10.9954 | 11.1262 | 8.1811 | 61.8189 | 0.17998 | 6.18 | 6.25 | 180 | 706 | 1276 | 1290.2288 | -1.1151 | 53.8462 | 998.1144 | 81.966 | 82 | 62 | 18 | 117 | 154 | 271 | 271 | 0.46383 | 0.43173 | 10.9902 | 11.1209 | 13.3571 | 40.6429 | 0.27363 | 6.25 | 6.25 | 308 | 1276 | 1663 | 2011.4286 | -20.9518 | 21.0256 | 1643.7143 | 81.262 | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5.
|  |  |  | Pressure losses in a single element, DPe (psi) | 10.3 | [5 empty] | 1998-08-18 | 5:15 | 26885.4 | 24.5 | 120 | 58 | 31.6991 | 0 | 1302 | 154 |  | 1456 | 1456 | 0.89423 | 0 | 14.0346 | 14.2435 | 8.5205 | 48.7804 | 0.29199 |  | 5.95 | 223 |  | 386 | 1658 | 1764.0909 | -6.3987 | 42.228 | 1075.0455 | 79.2567 | 120 | 91 | 44 | 884 | 572 | 1456 | 1456 | 0.43036 | 0.60714 | 16.1461 | 16.3865 | 4.1482 | 57.3518 | 0.28572 | 5.95 | 6.03 | 152 | 386 | 780 | 747.6364 | 4.1492 | 60.6218 | 566.8182 | 73.1836 | 91 | 79 | 14 | 301 | 271 | 572 | 572 | 0.35779 | 0.52622 | 10.9954 | 11.1591 | 9.3632 | 61.6368 | 0.18105 | 6.03 | 6.14 | 178 | 780 | 1306 | 1448.6421 | -10.9221 | 53.886 | 1114.321 | 84.0261 | 79 | 58 | 14 | 117 | 154 | 271 | 271 | 0.46383 | 0.43173 | 10.9902 | 11.1539 | 13.9367 | 40.5633 | 0.27497 | 6.14 | 6.19 | 296 | 1306 | 1658 | 2073.3377 | -25.0505 | 23.3161 | 1689.6688 | 82.4818 | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters.
|  |  |  | Design permeate pressure, Pp (psi) | 18 | [5 empty] | 1998-08-19 | 5:30 | 26894.5 | 24.3 | 126 | 66 | 37.1091 | 0 | 1307 | 143 |  | 1450 | 1450 | 0.90138 | 0 | 14.0885 | 14.383 | 6.9624 | 51.9284 | 0.27698 |  | 6.05 | 251 |  | 376 | 1612 | 1518.4825 | 5.8013 | 33.2447 | 947.2413 | 73.502 | 126 | 96 | 49 | 884 | 566 | 1450 | 1450 | 0.42782 | 0.60966 | 16.1461 | 16.4837 | 3.3837 | 58.6163 | 0.28121 | 6.05 | 6.13 | 186 | 376 | 688 | 672.7491 | 2.2167 | 50.5319 | 524.3746 | 64.5292 | 96 | 84 | 20 | 305 | 261 | 566 | 566 | 0.351 | 0.53887 | 11.1416 | 11.3745 | 7.4462 | 62.5538 | 0.18184 | 6.13 | 6.21 | 218 | 688 | 1286 | 1237.2337 | 3.7921 | 42.0213 | 962.6169 | 77.3534 | 84 | 66 | 20 | 118 | 143 | 261 | 261 | 0.44091 | 0.45211 | 11.0841 | 11.3159 | 13.2501 | 41.7499 | 0.27104 | 6.21 | 6.23 | 348 | 1286 | 1612 | 2060.014 | -27.7924 | 7.4468 | 1673.007 | 79.1991 | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design.
|  |  |  | Mechanical pressure losses per stage, Ls (psi) | 123.8 | [5 empty] | 1998-08-20 | 12:30 | 26901.3 | 23.4 | 124.9 | 64 | 36.5192 | 0 | 1302 | 155 |  | 1457 | 1457 | 0.89362 | 0 | 14.0346 | 14.7143 | 5.72 | 52.2108 | 0.28182 |  | 6.01 | 273 |  | 383 | 1562 | 1307 | 16.3252 | 28.7206 | 845 | 67.6923 | 124.9 | 96 | 48 | 885 | 572 | 1457 | 1457 | 0.43058 | 0.60741 | 16.1644 | 16.9472 | 3.7068 | 58.7432 | 0.2885 | 6.01 | 6.17 | 174 | 383 | 683 | 706.3654 | -3.421 | 54.5692 | 544.6827 | 68.0548 | 96 | 84 | 20 | 300 | 272 | 572 | 572 | 0.35821 | 0.52448 | 10.9589 | 11.4896 | 6.3455 | 63.6545 | 0.1805 | 6.23 | 6.23 | 274 | 683 | 1169 | 1134.1029 | 2.9852 | 28.4595 | 908.5515 | 69.8421 | 84 | 64 | 20 | 117 | 155 | 272 | 272 | 0.46601 | 0.43015 | 10.9902 | 11.5225 | 11.3362 | 42.6638 | 0.27008 | 6.23 | 6.24 | 346 | 1169 | 1562 | 1790.2323 | -14.6115 | 9.6606 | 1479.6161 | 76.6156 | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
|  |  |  | Net driving pressure required for permeation, NDP (psi) | 62.5 | [5 empty] | 1998-08-21 | 1:45 | 26913.7 | 24.6 | 125.364 | 64 | 37.1091 | 0 | 1299 | 153 |  | 1452 | 1452 | 0.89463 | 0 | 14.0022 | 14.1688 | 8.9691 | 48.6037 | 0.29152 |  | 6.04 | 233 |  | 404 | 1701 | 1855.8235 | -9.1019 | 42.3267 | 1129.9118 | 79.3789 | 125.3 | 96 | 49 | 881 | 571 | 1452 | 1452 | 0.4293 | 0.60675 | 16.0913 | 16.2827 | 4.3932 | 57.2568 | 0.28438 | 6.04 | 6.21 | 156 | 404 | 729 | 786.641 | -7.9069 | 61.3861 | 595.3205 | 73.7956 | 96 | 84 | 20 | 301 | 270 | 571 | 571 | 0.35694 | 0.52715 | 10.9954 | 11.1262 | 8.4723 | 61.5277 | 0.18083 | 6.21 | 6.23 | 185 | 729 | 1313 | 1335.4593 | -1.7105 | 54.2079 | 1032.2296 | 82.0776 | 84 | 64 | 20 | 117 | 153 | 270 | 270 | 0.46165 | 0.43333 | 10.9902 | 11.1209 | 13.7821 | 40.2179 | 0.27652 | 6.23 | 6.26 | 316 | 1313 | 1701 | 2075.4118 | -22.0113 | 21.7822 | 1694.2059 | 81.3482 | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
|  |  |  | Flow weighted system pressure losses, Lsys (psi) | 133.6967 | [6 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [19 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [18 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [18 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [19 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [19 empty] | The subscript "b" refers to the blended water quality for a given blend ratio.
|  |  |  | Required influent pressure to the system, PI (psi) | 214.1967 | [6 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [19 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [18 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [18 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [19 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [19 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL.
|  |  |  | 3: The osmotic pressure can be estimated from Table 6-5 in Part 3 of the | [109 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
"ICR Manual for Bench- and Pilot-Scale Treatment Studies."
Note on A1: TSC_ADM: This utility had trouble with their SDS chlorinations as in their response to EPA review and comments "Overall, all SDS residuals were very inconsistent. Our source water is very stable, but we experienced difficulty in retrieving good residuals on a regular basis. This could be in part to H2S levels in the water since odor removal is not preformed until after production. All SDS residuals below 0.1 were listed as 'NR'"
Note on E23: TSC_ADM: Reviewer entered a more appropriate membrane width
Note on W6: TSC_ADM: System Pp was approximated based on the number of parallel pressure vessels in each stage.
Note on DS16: C. Rice: Utility verified all alkalinity data stating that permeate values may be greater than feed values due to CO2.
Note on DV22: C. Rice: Utility verified that the feed TOC was constant at 8.0 mg/L.
Note on ED26: TSC_ADM: Data entered by the reviewer since utility did not so do
Note on ED48: TSC_ADM: Data entered by the reviewer since utility did not so do
Note on EF22: TSC_ADM: Reviewer changed from 0.11 to 0.011
Note on EP22: C. Rice: Utility verified that the feed TOC was constant at 8.0 mg/L.
Note on EX26: TSC_ADM: Data entered by the reviewer since utility did not so do
Note on EX48: TSC_ADM: Data entered by the reviewer since utility did not so do
Note on FJ22: C. Rice: Utility verified that the feed TOC was constant at 8.0 mg/L.
Note on FJ39: C. Rice: Utility verified value.
Note on FJ40: C. Rice: Utility verified value.
Note on FR26: TSC_ADM: Data entered by the reviewer since utility did not so do
Note on FR48: TSC_ADM: Data entered by the reviewer since utility did not so do
Note on GD22: C. Rice: Utility verified that the feed TOC was constant at 8.0 mg/L.
Note on GL26: TSC_ADM: Data entered by the reviewer since utility did not so do
Note on GL48: TSC_ADM: Data entered by the reviewer since utility did not so do
Note on HF26: TSC_ADM: Data entered by the reviewer since utility did not so do
Note on HF48: TSC_ADM: Data entered by the reviewer since utility did not so do
Note on HR22: C. Rice: Utility verified that the feed TOC was constant at 8.0 mg/L.
Note on HZ26: TSC_ADM: Data entered by the reviewer since utility did not so do
Note on HZ48: TSC_ADM: Data entered by the reviewer since utility did not so do

## Sheet3. Weeks 21-30
FIELD-SET 3: PILOT-SCALE MEMBRANE RESULTS: WEEKS 21-30 (FILE: mempilot.xls)
Field 3-1: PWS And Treatment Plant Data |  | Field 3-2: Manufacturer Reported Membrane Characteristics1 |  | Field 3-3: 3-Stage Membrane Pilot System Design Parameters |  | Field 3-4: Foulants And Fouling Indices1 |  | Field 3-5: Pretreatment Used Prior To Membranes1 |  |  | Field 3-6: Membrane Performance Data During Operation With The Test Water | [18 empty] | Field 3-6: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 3-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 3-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 3-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 3-7: System And Stage Water Quality For Week 22 | [9 empty] | Field 3-7: System And Stage Water Quality For Week 22 (continued) | [7 empty] | Field 3-8: System And Stage Water Quality For Week 24 | [9 empty] | Field 3-8: System And Stage Water Quality For Week 24 (continued) | [7 empty] | Field 3-9: System And Stage Water Quality For Week 26 | [9 empty] | Field 3-9: System And Stage Water Quality For Week 26 (continued) | [7 empty] | Field 3-10: System And Stage Water Quality For Week 28 | [9 empty] | Field 3-10: System And Stage Water Quality For Week 28 (continued) | [7 empty] | Field 3-11: System And Stage Water Quality For Week 30 | [9 empty] | Field 3-11: System And Stage Water Quality For Week 30 (continued) | [7 empty] | Field 3-12: Duplicate Analysis Of System And Stage Water Quality For Week 30 | [9 empty] | Field 3-12: Duplicate Analysis Of System And Stage Water Quality For Week 30 (continued) | [7 empty] | Field 3-13: Membrane Cost Parameters
|  | General Information |  | Calculate Temperature Normalized MTCW |  | Parameters Evaluated Prior to Pretreatment |  |  |  |  | System Operating Parameters | [30 empty] | Stage 1 Operating Parameters | [23 empty] | Stage 2 Operating Parameters | [23 empty] | Stage 3 Operating Parameters | [23 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | General Cost Parameters
PWS Name | Collier County Water Department | Membrane manufacturer | Hydranautics | Average yearly temperature of feed water, TavgoC (oC) | 25 | Alkalinity (mg/L as CaCO3) | 290 | Process | Description | Scale | Date | Time | Operation |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  |  |  | System recovery during sample collection (decimal) | 0.89 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.61 | [6 empty] | System recovery during sample collection (decimal) | 0.89 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.6 | [6 empty] | System recovery during sample collection (decimal) | NA | [8 empty] | Stage 1 recovery during sample collection (decimal) | NA | [6 empty] | System recovery during sample collection (decimal) | 0.89 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.6 | [6 empty] | System recovery during sample collection (decimal) | 0.89 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.6 | [6 empty] | System recovery during sample collection (decimal) | 0.89 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.6 |  |  |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | FL5114069 | Membrane trade name | PVD 1 | Temperature normalized MTCW (gfd/psi) | 0.24 | Calcium Hardness (mg/L as CaCO3) | 220 | Sulfuric Acid Addition | pH adjustment to 5.8-6.0 | full-scale |  |  | time | Influent | PI | PC | PP | QR | Qp | QW | Cleaning Event | QF | QI | Recovery | Recycle | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) |  |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) |  |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) | [6 empty] | System feed flow rate during sample collection (gpm) | 1454 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 894 | [6 empty] | System feed flow rate during sample collection (gpm) | 1455 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 873 | [6 empty] | System feed flow rate during sample collection (gpm) | NA | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | NA | [6 empty] | System feed flow rate during sample collection (gpm) | 1462 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 874 | [6 empty] | System feed flow rate during sample collection (gpm) | 1454 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 871 | [6 empty] | System feed flow rate during sample collection (gpm) | 1454 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 871 |  |  |  |  | Capital Recovery Interest Rate (%) | N/A
Water Industry Data Base Number (optional) | NA | Membrane element model number | 8040-LSY-PVD1 |  |  | LSI | 7.26 | Anti-Scalant Addition | Argo Scientific Hyperspearse AS120UL | full-scale | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | Indicate with "X" | (gpm) | (gpm) | (decimal) | ratio | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHF (before acid) | pHF (after acid) | TDSp | TDSF (before acid) | TDSF (after acid) | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) |  |  | System influent flow rate during sample collection (gpm) | 1301 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 1454 | [6 empty] | System influent flow rate during sample collection (gpm) | 1301 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 1455 | [6 empty] | System influent flow rate during sample collection (gpm) | NA | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | NA | [6 empty] | System influent flow rate during sample collection (gpm) | 1302 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 1462 | [6 empty] | System influent flow rate during sample collection (gpm) | 1300 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 1454 | [6 empty] | System influent flow rate during sample collection (gpm) | 1300 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 1454 |  |  |  |  | Capital Recovery Period (years) | 25
|  | Molecular weight cutoff (Daltons) | 100-300 | Calculate System Permeate, Feed and Waste Flow Rates |  | Dissolved iron (mg/L) |  | Cartridge Filtration | 5 Micron | full-scale | 1998-09-04 | 6:05 | 26929.7 | 24.3 | 123.6 | 64 | 34.7493 | 0 | 1305 | 153 |  | 1458 | 1458 | 0.89506 | 0 | 14.0669 | 14.361 | 7.7918 | 51.259 | 0.28017 |  | 6.13 | 249 |  | 397 | 1652 | 1659.3529 | -0.44509 | 37.2796 | 1028.1765 | 75.7824 | 123.6 | 94 | 45 | 896 | 562 | 1458 | 1458 | 0.42867 | 0.61454 | 16.3653 | 16.7074 | 4.3132 | 59.4868 | 0.28086 | 6.13 | 6.25 | 157 | 397 | 724 | 779.6335 | -7.6842 | 60.4534 | 588.3167 | 73.3137 | 94 | 82 | 20 | 294 | 268 | 562 | 562 | 0.35227 | 0.52313 | 10.7397 | 10.9643 | 8.0987 | 59.9013 | 0.18304 | 6.25 | 6.34 | 201 | 724 | 1289 | 1297.7388 | -0.67795 | 49.3703 | 1010.8694 | 80.1161 | 82 | 64 | 20 | 115 | 153 | 268 | 268 | 0.45947 | 0.4291 | 10.8023 | 11.0282 | 12.9877 | 40.0123 | 0.27562 | 6.34 | 6.32 | 345 | 1289 | 1652 | 1998.5425 | -20.9771 | 13.0982 | 1643.7712 | 79.0117 | [108 empty] | Overhead & Profit Factor (% of construction costs) | 10
Official ICR Contact Person |  | Membrane material (e.g., PVD, polyamide, etc.) | Poly Vinyl Derivative | Design system recovery, R (decimal) | 0.9 | Total iron (mg/L) | 0.03 |  |  |  | 1998-09-05 | 9:48 | 26945.6 | 24.5 | 118.1 | 58 | 30.3392 | 0 | 1303 | 154 |  | 1457 | 1457 | 0.8943 | 0 | 14.0454 | 14.2545 | 8.9442 | 48.7666 | 0.2923 |  | 5.96 | 223 |  | 394 | 1802 | 1840.8377 | -2.1553 | 43.401 | 1117.4188 | 80.0433 | 118.1 | 88 | 41 | 897 | 560 | 1457 | 1457 | 0.42803 | 0.61565 | 16.3836 | 16.6275 | 4.5563 | 57.4937 | 0.28921 | 5.96 | 6.17 | 141 | 394 | 738 | 799.2518 | -8.2997 | 64.2132 | 596.6259 | 76.3671 | 88 | 78 | 15 | 292 | 268 | 560 | 560 | 0.35142 | 0.52143 | 10.6667 | 10.8255 | 8.5581 | 59.4419 | 0.18212 | 6.17 | 6.23 | 184 | 738 | 1343 | 1341.6119 | 0.10336 | 53.2995 | 1039.806 | 82.3044 | 78 | 58 | 15 | 114 | 154 | 268 | 268 | 0.46056 | 0.42537 | 10.7084 | 10.8679 | 14.3042 | 38.6958 | 0.28085 | 6.23 | 6.16 | 299 | 1343 | 1802 | 2115.8312 | -17.4157 | 24.1117 | 1729.4156 | 82.7109 | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | Special Sitework Factor (% of construction costs) | N/A
Mailing Address |  | Membrane construction (e.g., thin-film composite) | Thin Film Composite | Design average system flux, FW (gfd) | 15 | Dissolved aluminum (mg/L) |  |  |  |  | 1998-09-06 | 9:00 | 26969.1 | 24.4 | 121 | 61 | 32.7493 | 0 | 1296 | 154 |  | 1450 | 1450 | 0.89379 | 0 | 13.9699 | 14.2199 | 8.8012 | 49.4496 | 0.28756 |  | 5.95 | 222 |  | 391 | 1768 | 1813.2338 | -2.5585 | 43.2225 | 1102.1169 | 79.8569 | 121 | 91 | 43 | 893 | 557 | 1450 | 1450 | 0.42591 | 0.61586 | 16.3105 | 16.6024 | 4.486 | 58.514 | 0.28373 | 5.95 | 6.12 | 142 | 391 | 742 | 790.2047 | -6.4966 | 63.6829 | 590.6023 | 75.9567 | 91 | 80 | 18 | 290 | 267 | 557 | 557 | 0.34972 | 0.52065 | 10.5936 | 10.7832 | 8.5486 | 58.9514 | 0.18292 | 6.12 | 6.22 | 188 | 742 | 1312 | 1343.7228 | -2.4179 | 51.9182 | 1042.8614 | 81.9727 | 80 | 61 | 18 | 113 | 154 | 267 | 267 | 0.45947 | 0.42322 | 10.6145 | 10.8044 | 13.6688 | 38.8312 | 0.27824 | 6.22 | 6.24 | 312 | 1312 | 1768 | 2045.7662 | -15.7108 | 20.2046 | 1678.8831 | 81.4162 | Parameter | Units | Cp-sys-22 | CF-sys-22 | CC-sys-22 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-22 | CI-s1-22 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-24 | CF-sys-24 | CC-sys-24 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-24 | CI-s1-24 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-26 | CF-sys-26 | CC-sys-26 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-26 | CI-s1-26 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-28 | CF-sys-28 | CC-sys-28 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-28 | CI-s1-28 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-30 | CF-sys-30 | CC-sys-30 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-30 | CI-s1-30 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-30 (dup) | CF-sys-30 (dup) | CC-sys-30 (dup) | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-30 (dup) | CI-s1-30 (dup) | CC(calc) | RF (%) | CB | RB (%) | Construction Contingencies (% of construction costs) | NONE
|  | Membrane hydrophobicity | Hydrophillic | Number of elements per pressure vessel, Ne | 6 | Total aluminum (mg/L) | <0.10 |  |  |  | 1998-09-08 | 6:00 | 27014 | 24.4 | 119 | 58 | 30.7493 | 0 | 1300 | 156 |  | 1456 | 1456 | 0.89286 | 0 | 14.013 | 14.2638 | 8.2667 | 49.4841 | 0.28825 |  | 5.98 | 236 |  | 396 | 1652 | 1729.3333 | -4.6812 | 40.404 | 1062.6667 | 77.7917 | 119 | 88 | 41 | 892 | 564 | 1456 | 1456 | 0.42867 | 0.61264 | 16.2922 | 16.5838 | 4.4411 | 58.0589 | 0.28564 | 5.98 | 6.19 | 148 | 396 | 732 | 788.227 | -7.6813 | 62.6263 | 592.1135 | 75.0048 | 88 | 78 | 16 | 294 | 270 | 564 | 564 | 0.35397 | 0.52128 | 10.7397 | 10.9319 | 8.34 | 58.66 | 0.18636 | 6.19 | 6.28 | 192 | 732 | 1308 | 1320 | -0.91743 | 51.5152 | 1026 | 81.2865 | 78 | 58 | 16 | 114 | 156 | 270 | 270 | 0.46492 | 0.42222 | 10.7084 | 10.9 | 13.3808 | 38.6192 | 0.28224 | 6.28 | 6.33 | 328 | 1308 | 1652 | 2024.1538 | -22.5275 | 17.1717 | 1666.0769 | 80.313 | Sampling date | MM/DD/YY | 1998-09-08 | 1998-09-08 | 1998-09-08 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-09-08 | 1998-09-08 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-09-14 | 1998-09-14 | 1998-09-14 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-09-14 | 1998-09-14 | --- | --- | --- | --- | Sampling date | MM/DD/YY | NA | NA | NA | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | NA | NA | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-10-12 | 1998-10-12 | 1998-10-12 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-10-12 | 1998-10-12 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-10-26 | 1998-10-26 | 1998-10-26 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-10-26 | 1998-10-26 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-10-26 | 1998-10-26 | 1998-10-26 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-10-26 | 1998-10-26 | --- | --- | --- | --- | Engineering Fee Factor (% of construction costs) | 19
Phone Number |  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Negative | Number of parallel pressure vessels in stage 1, Nv-s(1) | 36 | Fluoride (mg/L) | 0.3 |  |  |  | 1998-09-10 | 0:12 | 27050.5 | 22.9 | 124.5 | 63 | 34.5192 | 0 | 1298 | 154 |  | 1452 | 1452 | 0.89394 | 0 | 13.9915 | 14.8875 | 4.2236 | 55.0073 | 0.27065 |  | 6.1 | 314 |  | 395 | 1682 | 1077.7143 | 35.9266 | 20.5063 | 736.3571 | 57.3576 | 124.5 | 95 | 46 | 872 | 580 | 1452 | 1452 | 0.43121 | 0.60055 | 15.9269 | 16.9469 | 4.029 | 59.721 | 0.28377 | 6.1 | 6.27 | 165 | 395 | 660 | 740.7931 | -12.2414 | 58.2278 | 567.8966 | 70.9454 | 95 | 83 | 18 | 307 | 273 | 580 | 580 | 0.36203 | 0.52931 | 11.2146 | 11.9328 | 7.3427 | 63.6573 | 0.18745 | 6.27 | 6.3 | 190 | 660 | 1259 | 1188.5348 | 5.5969 | 51.8987 | 924.2674 | 79.4432 | 83 | 63 | 18 | 119 | 154 | 273 | 273 | 0.46601 | 0.4359 | 11.1781 | 11.8939 | 12.8377 | 42.1623 | 0.2821 | 6.3 | 6.39 | 333 | 1259 | 1682 | 1974.5455 | -17.3927 | 15.6962 | 1616.7727 | 79.4034 | Sampling time | hh:mm | 12:05 | 12:23 | 12:32 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 12:13 | 12:23 | --- | --- | --- | --- | Sampling time | hh:mm | 8:03 | 8:27 | 8:39 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 8:11 | 8:27 | --- | --- | --- | --- | Sampling time | hh:mm | NA | NA | NA | --- | --- | --- | --- | --- | Sampling time | hh:mm | NA | NA | --- | --- | --- | --- | Sampling time | hh:mm | 7:30 | 7:42 | 7:54 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 7:35 | 7:42 | --- | --- | --- | --- | Sampling time | hh:mm | 7:02 | 7:26 | 7:47 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 7:12 | 7:26 | --- | --- | --- | --- | Sampling time | hh:mm | 7:02 | 7:26 | 7:47 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 7:12 | 7:26 | --- | --- | --- | --- | 1998 ENR Construction Cost Index (CCI base year 1913) | 5895.11
FAX Number |  |  |  | Number of parallel pressure vessels in stage 2, Nv-s(2) | 18 | Phosphate (mg/L) | 0.05mg/L as PO4 |  |  |  | 1998-09-11 | 0:10 | 27072.6 | 22.2 | 122.5 | 60 | 33.2891 | 0 | 1302 | 155 |  | 1457 | 1457 | 0.89362 | 0 | 14.0346 | 15.2456 | 4.472 | 53.4889 | 0.28502 |  | 6.04 | 329 |  | 415 | 1680 | 1137.4 | 32.2976 | 20.7229 | 776.2 | 57.614 | 122.5 | 92 | 46 | 874 | 583 | 1457 | 1457 | 0.43291 | 0.59986 | 15.9635 | 17.3409 | 4.3564 | 56.8936 | 0.3048 | 6.04 | 6.24 | 166 | 415 | 685 | 788.2864 | -15.0783 | 60 | 601.6432 | 72.4089 | 92 | 81 | 15 | 308 | 275 | 583 | 583 | 0.36415 | 0.5283 | 11.2511 | 12.222 | 7.5036 | 63.9964 | 0.19098 | 6.24 | 6.3 | 204 | 685 | 1212 | 1223.72 | -0.967 | 50.8434 | 954.36 | 78.6244 | 81 | 60 | 15 | 120 | 155 | 275 | 275 | 0.46929 | 0.43636 | 11.272 | 12.2446 | 11.3742 | 44.1258 | 0.27749 | 6.3 | 6.37 | 392 | 1212 | 1680 | 1846.8387 | -9.9309 | 5.5422 | 1529.4194 | 74.3694 | Operation time | hh.hh | 27019.9 | 27020.2 | 27020.3 | --- | --- | --- | --- | --- | Operation time | hh.hh | 27020 | 27020.2 | --- | --- | --- | --- | Operation time | hh.hh | 27152.4 | 27152.8 | 27153.1 | --- | --- | --- | --- | --- | Operation time | hh.hh | 27152.5 | 27152.8 | --- | --- | --- | --- | Operation time | hh.hh | NA | NA | NA | --- | --- | --- | --- | --- | Operation time | hh.hh | NA | NA | --- | --- | --- | --- | Operation time | hh.hh | 27336.7 | 27336.9 | 27337.1 | --- | --- | --- | --- | --- | Operation time | hh.hh | 27336.8 | 27336.9 | --- | --- | --- | --- | Operation time | hh.hh | 27615.4 | 27615.8 | 27616.1 | --- | --- | --- | --- | --- | Operation time | hh.hh | 27615.6 | 27615.8 | --- | --- | --- | --- | Operation time | hh.hh | 27615.4 | 27615.8 | 27616.1 | --- | --- | --- | --- | --- | Operation time | hh.hh | 27615.6 | 27615.8 | --- | --- | --- | --- | 1998 Producers Price Index (PPI base year 1967 = 100) | 123.9
E-Mail Address (optional) |  | Design Parameters |  | Number of parallel pressure vessels in stage 3, Nv-s(3) | 7 | Sulfate (mg/L) | 20 |  |  |  | 1998-09-14 | 1:30 | 27146.3 | 24.2 | 121 | 51 | 30.8791 | 0 | 1301 | 155 |  | 1456 | 1456 | 0.89354 | 0 | 14.0238 | 14.3594 | 9.2503 | 45.8707 | 0.31304 | 7.02 | 5.95 | 202 | 368 | 380 | 1652 | 1874.0516 | -13.4414 | 46.8421 | 1127.0258 | 82.0767 | 121 | 85 | 44 | 873 | 583 | 1456 | 1456 | 0.4327 | 0.59959 | 15.9452 | 16.3268 | 4.1969 | 54.8031 | 0.29792 | 5.95 | 6.1 | 140 | 380 | 692 | 739.3825 | -6.8472 | 63.1579 | 559.6913 | 74.9862 | 85 | 74 | 12 | 308 | 275 | 583 | 583 | 0.36415 | 0.5283 | 11.2511 | 11.5204 | 7.8 | 59.7 | 0.19297 | 6.1 | 6.28 | 192 | 692 | 1402 | 1252 | 10.699 | 49.4737 | 972 | 80.2469 | 74 | 51 | 12 | 120 | 155 | 275 | 275 | 0.46929 | 0.43636 | 11.272 | 11.5417 | 15.9794 | 34.5206 | 0.33434 | 6.28 | 6.3 | 250 | 1402 | 1652 | 2293.871 | -38.8542 | 34.2105 | 1847.9355 | 86.4714 | pH | --- | 6.15 | 6.07 | 6.22 | --- | --- | --- | --- | --- | pH | --- | 6.07 | 6.07 | --- | --- | --- | --- | pH | --- | 6.18 | 6.16 | 6.28 | --- | --- | --- | --- | --- | pH | --- | 6.08 | 6.16 | --- | --- | --- | --- | pH | --- | NA | NA | NA | --- | --- | --- | --- | --- | pH | --- | NA | NA | --- | --- | --- | --- | pH | --- | 6.1 | 6.08 | 6.21 | --- | --- | --- | --- | --- | pH | --- | 5.99 | 6.08 | --- | --- | --- | --- | pH | --- | 6.25 | 6.15 | 6.28 | --- | --- | --- | --- | --- | pH | --- | 6.01 | 6.15 | --- | --- | --- | --- | pH | --- | 6.25 | 6.15 | 6.28 | --- | --- | --- | --- | --- | pH | --- | 6.01 | 6.15 | --- | --- | --- | --- | Labor Rate + Fringe ($/work-hour) | 24.39
|  | Element size (e.g., 2.5" x 40", 4" x 40", etc.) | 8" X 40" | Permeate flow rate per element, Qp-e (gpm) | 3.8021 | Calcium (mg/L) | 82 |  |  |  | 1998-09-19 | 7:30 | 27154.1 | 24.3 | 120 | 60 | 31.8791 | 0 | 1300 | 155 |  | 1455 | 1455 | 0.89347 | 0 | 14.013 | 14.306 | 6.9594 | 51.1616 | 0.27962 |  | 6.08 | 259 |  | 393 | 1708 | 1516.871 | 11.1902 | 34.0967 | 954.9355 | 72.8777 | 120 | 90 | 45 | 870 | 585 | 1455 | 1455 | 0.43291 | 0.59794 | 15.8904 | 16.2226 | 4.1149 | 55.8851 | 0.29029 | 6.08 | 6.18 | 157 | 393 | 706 | 743.9744 | -5.3788 | 60.0509 | 568.4872 | 72.3828 | 90 | 80 | 13 | 310 | 275 | 585 | 585 | 0.365 | 0.52991 | 11.3242 | 11.561 | 8.2247 | 63.7753 | 0.18128 | 6.18 | 6.34 | 180 | 706 | 1251 | 1298.9455 | -3.8326 | 54.1985 | 1002.4727 | 82.0444 | 80 | 60 | 13 | 120 | 155 | 275 | 275 | 0.46929 | 0.43636 | 11.272 | 11.5077 | 13.011 | 43.989 | 0.2616 | 6.34 | 6.34 | 313 | 1251 | 1708 | 1977.1935 | -15.7607 | 20.3562 | 1614.0968 | 80.6083 | Temperature | oC | 25.58 | 25.5 | 26.48 | --- | --- | --- | --- | --- | Temperature | oC | 25.58 | 25.58 | --- | --- | --- | --- | Temperature | oC | 24.8 | 25 | 25.3 | --- | --- | --- | --- | --- | Temperature | oC | 25.1 | 25 | --- | --- | --- | --- | Temperature | oC | NA | NA | NA | --- | --- | --- | --- | --- | Temperature | oC | NA | NA | --- | --- | --- | --- | Temperature | oC | 24.8 | 25.1 | 25.2 | --- | --- | --- | --- | --- | Temperature | oC | 25 | 25.1 | --- | --- | --- | --- | Temperature | oC | 24.8 | 24.5 | 24.5 | --- | --- | --- | --- | --- | Temperature | oC | 24.4 | 24.5 | --- | --- | --- | --- | Temperature | oC | 24.8 | 24.5 | 24.5 | --- | --- | --- | --- | --- | Temperature | oC | 24.4 | 24.5 | --- | --- | --- | --- | Labor Overhead Factor (% of labor) | 10
Technical ICR Contact Person |  | Active membrane area of membrane element used, A (ft2) | 365 | Permeate flow rate per pressure vessel, Qp-v (gpm) | 22.8125 | Barium (mg/L) | 0.008 |  |  |  | 1998-09-20 | 9:30 | 27180.2 | 24.2 | 122 | 60 | 31.2891 | 0 | 1300 | 154 |  | 1454 | 1454 | 0.89409 | 0 | 14.013 | 14.3483 | 7.8312 | 51.8797 | 0.27657 |  | 6.02 | 236 |  | 386 | 1688 | 1652.2338 | 2.1189 | 38.8601 | 1019.1169 | 76.8427 | 122 | 92 | 44 | 872 | 582 | 1454 | 1454 | 0.43206 | 0.59972 | 15.9269 | 16.3081 | 4.058 | 58.942 | 0.27668 | 6.02 | 6.14 | 154 | 386 | 686 | 733.6014 | -6.939 | 60.1036 | 559.8007 | 72.4902 | 92 | 80 | 13 | 308 | 274 | 582 | 582 | 0.3633 | 0.52921 | 11.2511 | 11.5204 | 7.8727 | 65.1273 | 0.17689 | 6.14 | 6.28 | 182 | 686 | 1286 | 1252.5401 | 2.6019 | 52.8497 | 969.2701 | 81.223 | 80 | 60 | 13 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.5417 | 13.4236 | 43.5764 | 0.26486 | 6.28 | 6.31 | 320 | 1286 | 1688 | 2038.7273 | -20.7777 | 17.0984 | 1662.3636 | 80.7503 | Alkalinity | mg/L as CaCO3 | 126 | 106 | 210 | -55.8182 | 126.5801 | -18.8679 | 34.606 | -264.0991 | Alkalinity | mg/L as CaCO3 | 72 | 106 | 160.2786 | 32.0755 | 133.1393 | 45.9213 | Alkalinity | mg/L as CaCO3 | 128 | 92 | 200 | -199.2727 | 199.6364 | -39.1304 | -36.3973 | 451.6743 | Alkalinity | mg/L as CaCO3 | 74 | 92 | 119 | 19.5652 | 105.5 | 29.8578 | Alkalinity | mg/L as CaCO3 | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 92 | 77 | 165 | -44.3636 | 126.8871 | -19.4805 | 23.7752 | -286.9572 | Alkalinity | mg/L as CaCO3 | 58 | 77 | 105.2415 | 24.6753 | 91.1207 | 36.3482 | Alkalinity | mg/L as CaCO3 | 130 | 116 | 290 | 2.7273 | 99.0596 | -12.069 | 66.0729 | -96.7525 | Alkalinity | mg/L as CaCO3 | 74 | 116 | 178.7479 | 36.2069 | 147.3739 | 49.7876 | Alkalinity | mg/L as CaCO3 | 132 | 116 | 300 | -13.4545 | 104.4848 | -13.7931 | 58.9404 | -123.955 | Alkalinity | mg/L as CaCO3 | 72 | 116 | 181.7358 | 37.931 | 148.8679 | 51.635 | Electric Rate ($/kW-h) | 0.05
Mailing Address |  | Design flux, FW (gfd) | 30 | Permeate flow rate from stage 1, Qp-s(1) (gpm) | 821.25 | Strontium (mg/L) | 0.6 |  |  |  | 1998-09-22 | 6:15 | 27225.1 | 24.3 | 122 | 60 | 33.6991 | 0 | 1302 | 154 |  | 1456 | 1456 | 0.89423 | 0 | 14.0346 | 14.328 | 8.2591 | 49.0418 | 0.29216 |  | 5.95 | 230 |  | 388 | 1720 | 1723.8182 | -0.22199 | 40.7216 | 1055.9091 | 78.2178 | 122 | 92 | 46 | 875 | 581 | 1456 | 1456 | 0.43227 | 0.60096 | 15.9817 | 16.3159 | 4.1371 | 56.8629 | 0.28693 | 5.95 | 6.06 | 152 | 388 | 722 | 743.4217 | -2.967 | 60.8247 | 565.7108 | 73.1311 | 92 | 80 | 16 | 307 | 274 | 581 | 581 | 0.36288 | 0.5284 | 11.2146 | 11.4491 | 8.3628 | 61.6372 | 0.18575 | 6.06 | 6.17 | 186 | 722 | 1296 | 1322.5547 | -2.049 | 52.0619 | 1022.2774 | 81.8053 | 80 | 60 | 16 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.5077 | 13.8683 | 40.1317 | 0.28675 | 6.17 | 6.22 | 298 | 1296 | 1720 | 2073.6623 | -20.5618 | 23.1959 | 1684.8312 | 82.3128 | Total dissolved solids | mg/L | 304 | 600 | 3512 | 2994.9091 | 14.7235 | 49.3333 | 1656.6317 | 81.6495 | Total dissolved solids | mg/L | 202 | 600 | 1235.3786 | 66.3333 | 917.6893 | 77.9882 | Total dissolved solids | mg/L | 262 | 568 | 3540 | 3043.8182 | 14.0164 | 53.8732 | 1659.3772 | 84.2109 | Total dissolved solids | mg/L | 168 | 568 | 1168 | 70.4225 | 868 | 80.6452 | Total dissolved solids | mg/L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 222 | 536 | 3552 | 3076.5455 | 13.3855 | 58.5821 | 1650.1716 | 86.5469 | Total dissolved solids | mg/L | 140 | 536 | 1124.6122 | 73.8806 | 830.3061 | 83.1387 | Total dissolved solids | mg/L | 286 | 556 | 3308 | 2740.5455 | 17.154 | 48.5612 | 1518.8804 | 81.1703 | Total dissolved solids | mg/L | 196 | 556 | 1093.8388 | 64.7482 | 824.9194 | 76.2401 | Total dissolved solids | mg/L | 266 | 542 | 3260 | 2775.0909 | 14.8745 | 50.9225 | 1526.2778 | 82.572 | Total dissolved solids | mg/L | 176 | 542 | 1088.8027 | 67.5277 | 815.4014 | 78.4155 | Fuel Oil Rate ($/gal) | 0.43
|  | Net driving pressure at the design flux, NDP (psi) | 125 | Permeate flow rate from stage 2, Qp-s(2) (gpm) | 410.625 | Reactive silica (mg/L as SiO2) | 18 |  |  |  | 1998-09-23 | 2:00 | 27238.4 | 23.8 | 128.4 | 66 | 38.2891 | 0 | 1301 | 154 |  | 1455 | 1455 | 0.89416 | 0 | 14.0238 | 14.5302 | 8.9331 | 49.9778 | 0.29073 |  | 6.06 | 236 |  | 407 | 1718 | 1851.6169 | -7.7775 | 42.0147 | 1129.3084 | 79.1023 | 128.4 | 98 | 51 | 873 | 582 | 1455 | 1455 | 0.43227 | 0.6 | 15.9452 | 16.5209 | 4.5325 | 57.6675 | 0.28649 | 6.06 | 6.16 | 148 | 407 | 716 | 795.5 | -11.1034 | 63.6364 | 601.25 | 75.3846 | 98 | 86 | 20 | 308 | 274 | 582 | 582 | 0.3633 | 0.52921 | 11.2511 | 11.6574 | 8.4507 | 63.5493 | 0.18344 | 6.16 | 6.29 | 175 | 716 | 1310 | 1324.1314 | -1.0787 | 57.0025 | 1020.0657 | 82.8442 | 86 | 66 | 20 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.679 | 13.9517 | 42.0483 | 0.27775 | 6.29 | 6.27 | 306 | 1310 | 1718 | 2092.3377 | -21.7892 | 24.8157 | 1701.1688 | 82.0124 | Total hardness | mg/L as CaCO3 | 136 | 324 | 2020 | 1845.0909 | 8.6589 | 58.0247 | 995.1039 | 86.3331 | Total hardness | mg/L as CaCO3 | 81 | 324 | 711.9321 | 75 | 517.9661 | 84.3619 | Total hardness | mg/L as CaCO3 | 120 | 304 | 2080 | 1792.7273 | 13.8112 | 60.5263 | 960.253 | 87.5033 | Total hardness | mg/L as CaCO3 | 75 | 304 | 647.5 | 75.3289 | 475.75 | 84.2354 | Total hardness | mg/L as CaCO3 | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 120 | 320 | 2110 | 1938.1818 | 8.143 | 62.5 | 1029.6635 | 88.3457 | Total hardness | mg/L as CaCO3 | 70 | 320 | 691.5986 | 78.125 | 505.7993 | 86.1605 | Total hardness | mg/L as CaCO3 | 142 | 312 | 2030 | 1687.4545 | 16.8742 | 54.4872 | 918.258 | 84.5359 | Total hardness | mg/L as CaCO3 | 83 | 312 | 654.1252 | 73.3974 | 483.0626 | 82.818 | Total hardness | mg/L as CaCO3 | 142 | 308 | 2010 | 1651.0909 | 17.8562 | 53.8961 | 899.9931 | 84.2221 | Total hardness | mg/L as CaCO3 | 83 | 308 | 644.1492 | 73.0519 | 476.0746 | 82.5658 | Natural Gas Rate ($/ft3) | N/A
Phone Number |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.24 | Permeate flow rate from stage 3, Qp-s(3) (gpm) | 159.6875 | Turbidity (ntu) | <0.5 |  |  |  | 1998-10-08 | 5:54 | 27267.5 | 24 | 131.2 | 67 | 38.8791 | 0 | 1303 | 160 |  | 1463 | 1463 | 0.89064 | 0 | 14.0454 | 14.4667 | 9.4844 | 50.7365 | 0.28513 |  | 5.88 | 210 |  | 397 | 1770 | 1919.8812 | -8.4679 | 47.1033 | 1158.4406 | 81.8722 | 131.2 | 100 | 52 | 877 | 586 | 1463 | 1463 | 0.43482 | 0.59945 | 16.0183 | 16.4988 | 3.7239 | 59.8761 | 0.27555 | 5.88 | 6.06 | 184 | 397 | 728 | 715.773 | 1.6795 | 53.6524 | 556.3865 | 66.9295 | 100 | 88 | 20 | 307 | 279 | 586 | 586 | 0.36712 | 0.52389 | 11.2146 | 11.5511 | 8.712 | 65.288 | 0.17692 | 6.06 | 6.19 | 166 | 728 | 1347 | 1346.4014 | 0.044437 | 58.1864 | 1037.2007 | 83.9954 | 88 | 67 | 20 | 119 | 160 | 279 | 279 | 0.47911 | 0.42652 | 11.1781 | 11.5134 | 14.5144 | 42.9856 | 0.26784 | 6.19 | 6.18 | 289 | 1347 | 1770 | 2133.8875 | -20.5586 | 27.204 | 1740.4437 | 83.395 | Calcium hardness | mg/L as CaCO3 | 100 | 220 | 1540 | 1190.9091 | 22.6682 | 54.5455 | 648.3642 | 84.5766 | Calcium hardness | mg/L as CaCO3 | 59 | 220 | 477.025 | 73.1818 | 348.5125 | 83.0709 | Calcium hardness | mg/L as CaCO3 | 86 | 224 | 1160 | 1340.5455 | -15.5643 | 61.6071 | 716.1897 | 87.992 | Calcium hardness | mg/L as CaCO3 | 55 | 224 | 477.5 | 75.4464 | 350.75 | 84.3193 | Calcium hardness | mg/L as CaCO3 | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 88 | 240 | 1660 | 1469.8182 | 11.4567 | 63.3333 | 779.3442 | 88.7085 | Calcium hardness | mg/L as CaCO3 | 57 | 240 | 512.0102 | 76.25 | 376.0051 | 84.8406 | Calcium hardness | mg/L as CaCO3 | 100 | 242 | 1570 | 1390.9091 | 11.4071 | 58.6777 | 748.4038 | 86.6382 | Calcium hardness | mg/L as CaCO3 | 65 | 242 | 506.4374 | 73.1405 | 374.2187 | 82.6305 | Calcium hardness | mg/L as CaCO3 | 100 | 240 | 1480 | 1372.7273 | 7.2482 | 58.3333 | 739.2713 | 86.4732 | Calcium hardness | mg/L as CaCO3 | 67 | 240 | 498.4614 | 72.0833 | 369.2307 | 81.8542 | Current Process Water Rate ($/1000 gal) | 1.8
FAX Number |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | Permeate flow rate from system, Qp-sys (gpm) | 1391.5625 | SDI | 1.0-1.5 |  |  |  | 1998-10-09 | 0:02 | 27272.1 | 23.6 | 127.1 | 66 | 37.6991 | 0 | 1300 | 155 |  | 1455 | 1455 | 0.89347 | 0 | 14.013 | 14.6051 | 8.3616 | 50.4893 | 0.28927 |  | 5.94 | 234 |  | 395 | 1688 | 1745.3226 | -3.3959 | 40.7595 | 1070.1613 | 78.1341 | 127.1 | 97 | 50 | 872 | 583 | 1455 | 1455 | 0.43249 | 0.59931 | 15.9269 | 16.5999 | 4.1075 | 57.9425 | 0.28649 | 5.94 | 6.11 | 160 | 395 | 685 | 746.4923 | -8.977 | 59.4937 | 570.7461 | 71.9665 | 97 | 86 | 20 | 308 | 275 | 583 | 583 | 0.36415 | 0.5283 | 11.2511 | 11.7265 | 7.3476 | 64.1524 | 0.18279 | 6.11 | 6.21 | 214 | 685 | 1304 | 1212.52 | 7.0153 | 45.8228 | 948.76 | 77.4442 | 86 | 66 | 20 | 120 | 155 | 275 | 275 | 0.46929 | 0.43636 | 11.272 | 11.7483 | 13.5381 | 42.4619 | 0.27668 | 6.21 | 6.17 | 328 | 1304 | 1688 | 2059.6129 | -22.015 | 16.962 | 1681.8065 | 80.4972 | Turbidity | ntu | 0.085 | 0.81 | 20 | 6.6759 | 66.6205 | 89.5062 | 3.398 | 97.4986 | Turbidity | ntu | 0.056 | 0.81 | 2.0137 | 93.0864 | 1.4119 | 96.0336 | Turbidity | ntu | 0.048 | 1.3 | 21 | 11.4298 | 45.5723 | 96.3077 | 5.7654 | 99.1674 | Turbidity | ntu | 0.04 | 1.3 | 3.19 | 96.9231 | 2.245 | 98.2183 | Turbidity | ntu | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.07 | 0.83 | 19.5 | 6.9791 | 64.2098 | 91.5663 | 3.5267 | 98.0152 | Turbidity | ntu | 0.06 | 0.83 | 1.9745 | 92.7711 | 1.4023 | 95.7212 | Turbidity | ntu | 0.06 | 0.25 | 19 | 1.7873 | 90.5933 | 76 | 0.92758 | 93.5316 | Turbidity | ntu | 0.06 | 0.25 | 0.53386 | 76 | 0.39193 | 84.6911 | Turbidity | ntu | 0.06 | 0.26 | 20 | 1.8782 | 90.6091 | 76.9231 | 0.97324 | 93.8351 | Turbidity | ntu | 0.07 | 0.26 | 0.54386 | 73.0769 | 0.40193 | 82.584 | Modifications to Existing Plant (% of construction costs) | N/A
E-Mail Address (optional) |  | Maximum flow rate to the element, QI, max (gpm) | 75 | Feed flow rate to system, QF-sys (gpm) | 1546.1806 | MFI |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | 1998-10-10 | 8:20 | 27290 | 23.6 | 127.9 | 66 | 44.7788 | 0 | 1297 | 155 |  | 1452 | 1452 | 0.89325 | 0 | 13.9807 | 14.5714 | 6.9982 | 45.173 | 0.32257 |  | 6.11 | 257 |  | 392 | 1555 | 1521.6452 | 2.145 | 34.4388 | 956.8226 | 73.1403 | 127.9 | 100 | 62 | 870 | 582 | 1452 | 1452 | 0.43164 | 0.59917 | 15.8904 | 16.5618 | 4.054 | 47.896 | 0.34579 | 6.11 | 6.35 | 160 | 392 | 697 | 738.8041 | -5.9977 | 59.1837 | 565.4021 | 71.7016 | 100 | 78 | 20 | 307 | 275 | 582 | 582 | 0.36373 | 0.52749 | 11.2146 | 11.6884 | 7.7753 | 61.2247 | 0.19091 | 6.35 | 6.35 | 198 | 697 | 1236 | 1254.0655 | -1.4616 | 49.4898 | 975.5327 | 79.7034 | 78 | 66 | 20 | 120 | 155 | 275 | 275 | 0.46929 | 0.43636 | 11.272 | 11.7483 | 12.1926 | 39.8074 | 0.29513 | 6.35 | 6.38 | 357 | 1236 | 1555 | 1916.5161 | -23.2486 | 8.9286 | 1576.2581 | 77.3514 | Ammonia | mg NH3-N / L | 0.22 | 0.27 | 0.81 | 0.67455 | 16.7228 | 18.5185 | 0.44849 | 50.946 | Total organic carbon | mg/L | BMRL | 9 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | 0.23 | 0.23 | 0.82 | 0.23 | 71.9512 | 0 | 0.23 | 0 | Total organic carbon | mg/L | 6 | 10 | 16 | 40 | 13 | 53.8462 | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | 0.19 | 0.22 | 0.86 | 0.46273 | 46.1945 | 13.6364 | 0.32645 | 41.798 | Total organic carbon | mg/L | BMRL | 8 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | 0.382 | 0.402 | 0.978 | 0.56382 | 42.3499 | 4.9751 | 0.47332 | 19.2943 | Total organic carbon | mg/L | BMRL | 8 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | 0.394 | 0.412 | 0.973 | 0.55764 | 42.689 | 4.3689 | 0.47619 | 17.2603 | Total organic carbon | mg/L | BMRL | 8 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | Minimum flow rate to the element, QI, min (gpm) | 72 | Concentrate-waste flow rate from system, QW-sys (gpm) | 154.6181 | MPFI |  | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | 1998-10-11 | 2:00 | 27307.4 | 23.6 | 128.1 | 66 | 45.1888 | 0 | 1299 | 154 |  | 1453 | 1453 | 0.89401 | 0 | 14.0022 | 14.5938 | 6.2089 | 45.6523 | 0.31967 |  | 6.05 | 272 |  | 391 | 1678 | 1394.7727 | 16.8789 | 30.4348 | 892.8864 | 69.537 | 128.1 | 98 | 62 | 870 | 583 | 1453 | 1453 | 0.43206 | 0.59876 | 15.8904 | 16.5618 | 4.0685 | 46.9815 | 0.35252 | 6.05 | 6.17 | 158 | 391 | 692 | 738.7015 | -6.7488 | 59.5908 | 564.8508 | 72.028 | 98 | 86 | 21 | 309 | 274 | 583 | 583 | 0.36373 | 0.53002 | 11.2877 | 11.7646 | 7.616 | 63.384 | 0.18561 | 6.17 | 6.24 | 205 | 692 | 1283 | 1241.208 | 3.2574 | 47.5703 | 966.604 | 78.7917 | 86 | 66 | 21 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.7483 | 13.1457 | 41.8543 | 0.28069 | 6.24 | 6.27 | 337 | 1283 | 1678 | 2020.1429 | -20.3899 | 13.8107 | 1651.5714 | 79.5952 | Total organic carbon | mg/L | NR | 9 | 78 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.0087 | 0.251 | 0.63781 | 96.5339 | 0.44441 | 98.0423 | Total organic carbon | mg/L | BMRL | 10 | 90 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.0098 | 0.229 | 0.5578 | 95.7205 | 0.3934 | 97.5089 | Total organic carbon | mg/L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 8 | 76 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.007 | 0.222 | 0.54157 | 96.8468 | 0.38179 | 98.1665 | Total organic carbon | mg/L | BMRL | 8 | 74 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.003 | 0.219 | 0.5417 | 98.6301 | 0.38035 | 99.2113 | Total organic carbon | mg/L | BMRL | 8 | 79 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.001 | 0.22 | 0.54719 | 99.5455 | 0.38359 | 99.7393
Plant Name | Collier Co. North Regional Water Plant | Total width of all membrane envelopes in the element, w (ft) | 63.4 |  |  |  |  | is to list the pretreatment processes used in this particular pilot-scale run. |  |  | 1998-10-12 | 1:50 | 27331.3 | 24.1 | 129 | 65 | 37.6991 | 0 | 1302 | 160 |  | 1462 | 1462 | 0.89056 | 0 | 14.0346 | 14.413 | 6.7921 | 52.5088 | 0.27449 | 7.05 | 6.04 | 252 | 398 | 386 | 1628 | 1476.425 | 9.3105 | 34.715 | 931.2125 | 72.9385 | 129 | 97 | 50 | 874 | 588 | 1462 | 1462 | 0.43503 | 0.59781 | 15.9635 | 16.3938 | 4.0791 | 58.9209 | 0.27823 | 6.04 | 6.16 | 152 | 386 | 686 | 733.8163 | -6.9703 | 60.6218 | 559.9082 | 72.8527 | 97 | 86 | 20 | 308 | 280 | 588 | 588 | 0.3684 | 0.52381 | 11.2511 | 11.5545 | 7.3625 | 64.1375 | 0.18015 | 6.16 | 6.28 | 211 | 686 | 1268 | 1208.5 | 4.6924 | 45.3368 | 947.25 | 77.725 | 86 | 65 | 20 | 120 | 160 | 280 | 280 | 0.4802 | 0.42857 | 11.272 | 11.5759 | 12.925 | 42.575 | 0.27189 | 6.28 | 6.31 | 328 | 1268 | 1628 | 1973 | -21.1916 | 15.0259 | 1620.5 | 79.7593 | UV254 | cm-1 | 0.0155 | 0.251 | 2.24 | 2.1564 | 3.7317 | 93.8247 | 1.0917 | 98.5802 | SUVA | L/(mg*m) | NR | 2.7889 | --- | --- | --- | --- | UV254 | cm-1 | 0.0138 | 0.229 | 2.06 | 1.9702 | 4.361 | 93.9738 | 0.99653 | 98.6152 | SUVA | L/(mg*m) | 0.16333 | 2.29 | --- | --- | --- | --- | UV254 | cm-1 | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NA | NA | --- | --- | --- | --- | UV254 | cm-1 | 0.01 | 0.222 | 2.02 | 1.9373 | 4.0954 | 95.4955 | 0.97424 | 98.9736 | SUVA | L/(mg*m) | NR | 2.775 | --- | --- | --- | --- | UV254 | cm-1 | BMRL | 0.219 | 2.04 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 2.7375 | --- | --- | --- | --- | UV254 | cm-1 | BMRL | 0.22 | 1.97 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 2.75 | --- | --- | --- | ---
Treatment Plant Category | Category II | Feed spacer thickness, T (ft) | 0.0023 | Calculate the Feed Flow Rates at the End of Each Stage | [6 empty] | 1998-10-13 | 1:40 | 27355 | 24 | 127.8 | 66 | 37.6991 | 0 | 1302 | 155 |  | 1457 | 1457 | 0.89362 | 0 | 14.0346 | 14.4556 | 8.736 | 50.4649 | 0.28645 |  | 6.01 | 234 |  | 402 | 1772 | 1813.2 | -2.3251 | 41.791 | 1107.6 | 78.8732 | 127.8 | 98 | 50 | 872 | 585 | 1457 | 1457 | 0.43333 | 0.59849 | 15.9269 | 16.4047 | 4.4331 | 58.4669 | 0.28058 | 6.01 | 6.18 | 148 | 402 | 730 | 780.612 | -6.9331 | 63.1841 | 591.306 | 74.9707 | 98 | 86 | 20 | 310 | 275 | 585 | 585 | 0.365 | 0.52991 | 11.3242 | 11.6639 | 8.6156 | 63.3844 | 0.18402 | 6.18 | 6.25 | 179 | 730 | 1319 | 1351.1273 | -2.4357 | 55.4726 | 1040.5636 | 82.7978 | 86 | 66 | 20 | 120 | 155 | 275 | 275 | 0.46929 | 0.43636 | 11.272 | 11.6102 | 14.9252 | 41.0748 | 0.28266 | 6.25 | 6.29 | 243 | 1319 | 1772 | 2152.0323 | -21.4465 | 39.5522 | 1735.5161 | 85.9984 | SUVA | L/(mg*m) | NR | 2.7889 | 2.8718 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | 2.29 | 2.2889 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NA | NA | NA | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | 2.775 | 2.6579 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | 2.7375 | 2.7568 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | 2.75 | 2.4937 | --- | --- | --- | --- | ---
Process Train Name | Train D | Active membrane area of an equivalent 8" x 40" element (ft2) | 365 | Feed flow rate at the end of stage 1, (QF-s(1))end (gpm) | 861.8056 | [5 empty] | 1998-10-15 | 6:20 | 27381.5 | 24.2 | 132.1 | 71 | 41.5192 | 0 | 1299 | 154 |  | 1453 | 1453 | 0.89401 | 0 | 14.0022 | 14.3373 | 8.2959 | 51.7349 | 0.27713 |  | 6.06 | 238 |  | 397 | 1684 | 1738.1753 | -3.2171 | 40.0504 | 1067.5877 | 77.7067 | 132.1 | 102 | 53 | 871 | 582 | 1453 | 1453 | 0.43185 | 0.59945 | 15.9087 | 16.2894 | 4.3357 | 59.7143 | 0.27279 | 6.06 | 6.13 | 149 | 397 | 722 | 768.1478 | -6.3917 | 62.4685 | 582.5739 | 74.4238 | 102 | 91 | 25 | 308 | 274 | 582 | 582 | 0.3633 | 0.52921 | 11.2511 | 11.5204 | 8.2945 | 63.2055 | 0.18227 | 6.13 | 6.2 | 191 | 722 | 1302 | 1318.8905 | -1.2973 | 51.8892 | 1020.4453 | 81.2827 | 91 | 71 | 25 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.5417 | 13.5487 | 42.4513 | 0.27188 | 6.2 | 6.27 | 327 | 1302 | 1684 | 2061.7403 | -22.4311 | 17.6322 | 1681.8701 | 80.5574 | Bromide | mg/L | 160 | 160 | --- | 160 | --- | 0 | 160 | 0 | [8 empty] | Bromide | mg/L | 170 | 160 | --- | 79.0909 | --- | -6.25 | 124.3341 | -36.7284 | [8 empty] | Bromide | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | 160 | 150 | --- | 69.0909 | --- | -6.6667 | 114.5168 | -39.7175 | [8 empty] | Bromide | mg/L | 170 | 150 | --- | -11.8182 | --- | -13.3333 | 78.6755 | -116.0774 | [8 empty] | Bromide | mg/L | 170 | 150 | --- | -11.8182 | --- | -13.3333 | 78.6755 | -116.0774
ICR Treatment Plant Identification Number | 1092 | Purchase price for an equivalent 8" x 40 " element ($) | 800 | Feed flow rate at the end of stage 2, (QF-s(2))end (gpm) | 382.7431 | [5 empty] | 1998-10-18 | 10:07 | 27449.4 | 24 | 122.6 | 61 | 31.2891 | 0 | 1301 | 154 |  | 1455 | 1455 | 0.89416 | 0 | 14.0238 | 14.4445 | 8.3584 | 52.1525 | 0.27697 |  | 6.05 | 238 |  | 398 | 1708 | 1749.6883 | -2.4408 | 40.201 | 1073.8442 | 77.8366 | 122.6 | 93 | 44 | 873 | 582 | 1455 | 1455 | 0.43227 | 0.6 | 15.9452 | 16.4236 | 4.34 | 59.46 | 0.27621 | 6.05 | 6.25 | 150 | 398 | 715 | 770 | -7.6923 | 62.3116 | 584 | 74.3151 | 93 | 81 | 13 | 308 | 274 | 582 | 582 | 0.3633 | 0.52921 | 11.2511 | 11.5887 | 8.4038 | 65.5962 | 0.17667 | 6.25 | 6.28 | 177 | 715 | 1300 | 1319.7591 | -1.5199 | 55.5276 | 1017.3796 | 82.6024 | 81 | 61 | 13 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.6102 | 13.7988 | 44.2012 | 0.26267 | 6.28 | 6.3 | 307 | 1300 | 1708 | 2073.7662 | -21.4149 | 22.8643 | 1686.8831 | 81.8008 | SDS-Cl2 dose | mg/L | 19 | 29 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 19 | 29 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | NA | NA | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 19 | 28 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 19 | 28 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 19 | 28 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection
PWSID Number of Plant (if assigned) | FL5114069 |  |  | Feed flow rate at the end of stage 3, (QF-s(3))end (gpm) | 181.2326 | [5 empty] | 1998-10-19 | 0:20 | 27463.7 | 23.4 | 122.8 | 60 | 32.2891 | 0 | 1299 | 155 |  | 1454 | 1454 | 0.8934 | 0 | 14.0022 | 14.6804 | 5.7094 | 53.4016 | 0.27491 | 7.09 | 6.03 | 288 | 388 | 398 | 1648 | 1319.871 | 19.9107 | 27.6382 | 858.9355 | 66.4701 | 122.8 | 93 | 45 | 871 | 583 | 1454 | 1454 | 0.43227 | 0.59904 | 15.9087 | 16.6791 | 4.2801 | 58.6199 | 0.28453 | 6.03 | 6.14 | 153 | 398 | 696 | 764.0292 | -9.7743 | 61.5578 | 581.0146 | 73.6668 | 93 | 80 | 14 | 308 | 275 | 583 | 583 | 0.36415 | 0.5283 | 11.2511 | 11.796 | 7.8 | 64.7 | 0.18232 | 6.14 | 6.18 | 196 | 696 | 1268 | 1256 | 0.94637 | 50.7538 | 976 | 79.918 | 80 | 60 | 14 | 120 | 155 | 275 | 275 | 0.46929 | 0.43636 | 11.272 | 11.8179 | 12.5255 | 43.4745 | 0.27184 | 6.18 | 6.19 | 365 | 1268 | 1648 | 1967.0968 | -19.3627 | 8.2915 | 1617.5484 | 77.435 | SDS-Free Cl2 residual | mg/L | 3.28 | 3.51 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.52 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 1.54 | 7.5 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.53 |  |  |  |  | SDS-Free Cl2 residual | mg/L | NA | NA | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | [5 empty] | SDS-Free Cl2 residual | mg/L | 3.2 | 2.2 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.52 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 4.2 | 2.2 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.53 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 3.4 | 2.1 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.53
Historical Minimum Water Temperature (oC) | 22.7 | Additional Information |  |  |  | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | 1998-10-20 | 5:00 | 27489.8 | 24.1 | 124 | 60 | 32.2891 | 0 | 1299 | 154 |  | 1453 | 1453 | 0.89401 | 0 | 14.0022 | 14.3797 | 6.6263 | 53.0846 | 0.27088 |  | 6.01 | 265 |  | 392 | 1626 | 1463.2532 | 10.009 | 32.398 | 927.6266 | 71.4325 | 124 | 92 | 45 | 872 | 581 | 1453 | 1453 | 0.43164 | 0.60014 | 15.9269 | 16.3563 | 4.2185 | 58.7815 | 0.27826 | 6.01 | 6.11 | 151 | 392 | 682 | 753.7074 | -10.5143 | 61.4796 | 572.8537 | 73.6407 | 92 | 80 | 14 | 307 | 274 | 581 | 581 | 0.36288 | 0.5284 | 11.2146 | 11.517 | 7.333 | 64.667 | 0.1781 | 6.11 | 6.21 | 212 | 682 | 1213 | 1208.6058 | 0.36226 | 45.9184 | 945.3029 | 77.5733 | 80 | 60 | 14 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.5759 | 11.9645 | 44.0355 | 0.26288 | 6.21 | 6.23 | 352 | 1213 | 1626 | 1883.9091 | -15.8616 | 10.2041 | 1548.4545 | 77.2677 | SDS-Cl2 demand | mg/L | 15.72 | 25.49 | --- | 104.5382 | --- | 38.3288 | 60.366 | 73.9588 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 294 |  |  |  |  | SDS-Cl2 demand | mg/L | 17.46 | 21.5 | --- | 54.1873 | --- | 18.7907 | 35.909 | 51.3771 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 308 |  |  |  |  | SDS-Cl2 demand | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! |  |  | Stage 2 permeate flow rate during sample collection (gpm) | [5 empty] | SDS-Cl2 demand | mg/L | 15.8 | 25.8 | --- | 106.7091 | --- | 38.7597 | 61.2832 | 74.218 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 308 |  |  |  |  | SDS-Cl2 demand | mg/L | 14.8 | 25.8 | --- | 114.8 | --- | 42.6357 | 65.0285 | 77.2407 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 313 |  |  |  |  | SDS-Cl2 demand | mg/L | 15.6 | 25.9 | --- | 109.2364 | --- | 39.7683 | 62.6321 | 75.0926 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 313
Historical Average Water Temperature (oC) | 25 | Design cross-flow velocity (fps) | 1 | Calculate the Minimum Recycle Flow Rates for Each Stage1 |  | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | 1998-10-22 | 6:40 | 27527.9 | 24 | 120.9 | 61 | 32.1091 | 0 | 1297 | 154 |  | 1451 | 1451 | 0.89387 | 0 | 13.9807 | 14.4001 | 8.7545 | 50.0863 | 0.28751 |  | 6 | 229 |  | 397 | 1732 | 1811.9091 | -4.6137 | 42.3174 | 1104.4545 | 79.2658 | 120.9 | 91 | 44 | 870 | 581 | 1451 | 1451 | 0.43121 | 0.59959 | 15.8904 | 16.3671 | 4.3193 | 57.6307 | 0.284 | 6 | 6.17 | 150 | 397 | 730 | 766.8623 | -5.0496 | 62.2166 | 581.9312 | 74.2238 | 91 | 80 | 15 | 307 | 274 | 581 | 581 | 0.36288 | 0.5284 | 11.2146 | 11.5511 | 8.628 | 61.872 | 0.18669 | 6.17 | 6.28 | 177 | 730 | 1327 | 1349.6022 | -1.7033 | 55.4156 | 1039.8011 | 82.9775 | 80 | 61 | 15 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.6102 | 14.2157 | 41.2843 | 0.28123 | 6.28 | 6.26 | 304 | 1327 | 1732 | 2124.1429 | -22.641 | 23.4257 | 1725.5714 | 82.3826 | SDS-Chlorination temp. | oC | 21.4 | 21.3 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 564 |  |  |  |  | SDS-Chlorination temp. | oC | 21.4 | 21.5 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 583 |  |  |  |  | SDS-Chlorination temp. | oC | NA | NA | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | [5 empty] | SDS-Chlorination temp. | oC | 22.4 | 22.5 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 588 |  |  |  |  | SDS-Chlorination temp. | oC | 21.9 | 21.9 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 591 |  |  |  |  | SDS-Chlorination temp. | oC | 21.9 | 21.9 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 591
State Approved Plant Capacity (MGD) | 12 MGD | Required influent flow to permeate flow rate ratio, QI:Qp | 5:1 | Minimum recycle flow rate for stage 1, (QR-s(1))min (gpm) | 1730.1944 | [5 empty] | 1998-10-23 | 0:08 | 27535.5 | 23 | 120.3 | 60 | 32.6991 | 0 | 1298 | 154 |  | 1452 | 1452 | 0.89394 | 0 | 13.9915 | 14.8435 | 3.7543 | 53.6966 | 0.27643 |  | 6 | 322 |  | 394 | 1685 | 1000.8571 | 40.6019 | 18.2741 | 697.4286 | 53.8304 | 120.3 | 91 | 45 | 870 | 582 | 1452 | 1452 | 0.43164 | 0.59917 | 15.8904 | 16.8581 | 4.1938 | 56.4562 | 0.29861 | 6 | 6.22 | 154 | 394 | 675 | 752.7629 | -11.5204 | 60.9137 | 573.3814 | 73.1418 | 91 | 80 | 15 | 308 | 274 | 582 | 582 | 0.3633 | 0.52921 | 11.2511 | 11.9363 | 7.2323 | 63.2677 | 0.18866 | 6.22 | 6.36 | 212 | 675 | 1274 | 1195.4526 | 6.1654 | 46.1929 | 935.2263 | 77.3317 | 80 | 60 | 15 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.9585 | 12.701 | 42.299 | 0.28271 | 6.36 | 6.31 | 360 | 1274 | 1685 | 1986.2078 | -17.8758 | 8.6294 | 1630.1039 | 77.9155 | SDS-Chlorination pH | --- | 8.3 | 8.17 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.02 | 8.19 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | NA | NA | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.52 | 8.36 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.31 | 8.21 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.3 | 8.2 | --- | --- | --- | --- | --- | ---
|  | Maximum element recovery (%) | 20 | Minimum recycle flow rate for stage 2, (QR-s(2))min (gpm) | 913.2569 | [5 empty] | 1998-10-24 | 7:45 | 27567.1 | 23 | 120.5 | 58 | 30.8791 | 0 | 1299 | 155 |  | 1454 | 1454 | 0.8934 | 0 | 14.0022 | 14.855 | 5.9689 | 52.4021 | 0.28348 |  | 5.93 | 263 |  | 378 | 1702 | 1341.7742 | 21.1649 | 30.4233 | 859.8871 | 69.4146 | 120.5 | 90 | 44 | 867 | 587 | 1454 | 1454 | 0.43312 | 0.59629 | 15.8356 | 16.8 | 3.8073 | 57.4427 | 0.29247 | 5.93 | 6.12 | 159 | 378 | 729 | 701.4634 | 3.7773 | 57.9365 | 539.7317 | 70.5409 | 90 | 78 | 12 | 311 | 276 | 587 | 587 | 0.36628 | 0.52981 | 11.3607 | 12.0526 | 8.0359 | 63.9641 | 0.18843 | 6.12 | 6.15 | 215 | 729 | 1312 | 1308.1812 | 0.29107 | 43.1217 | 1018.5906 | 78.8924 | 78 | 58 | 12 | 121 | 155 | 276 | 276 | 0.47038 | 0.43841 | 11.3659 | 12.0581 | 13.0968 | 42.9032 | 0.28105 | 6.15 | 6.17 | 370 | 1312 | 1702 | 2047.3677 | -20.2919 | 2.1164 | 1679.6839 | 77.972 | SDS-Incubation time | hours | 45 | 45 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 42 | 42 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | NA | NA | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 47.25 | 47.25 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 46 | 46 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 46 | 46 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters
|  | Variability of design flux (%) | 15 +/- | Minimum recycle flow rate for stage 3, (QR-s(3))min (gpm) | 322.7674 | [5 empty] | 1998-10-25 | 9:54 | 27594.3 | 23.7 | 119.4 | 58 | 29.6991 | 0 | 1298 | 156 |  | 1454 | 1454 | 0.89271 | 0 | 13.9915 | 14.5396 | 5.0571 | 53.9438 | 0.26953 |  | 6.11 | 301 |  | 399 | 1645 | 1214.4103 | 26.1757 | 24.5614 | 806.7051 | 62.6877 | 119.4 | 90 | 42 | 872 | 582 | 1454 | 1454 | 0.43206 | 0.59972 | 15.9269 | 16.5509 | 3.7257 | 58.9743 | 0.28065 | 6.11 | 6.36 | 186 | 399 | 705 | 718.134 | -1.863 | 53.3835 | 558.567 | 66.7005 | 90 | 78 | 12 | 307 | 275 | 582 | 582 | 0.36373 | 0.52749 | 11.2146 | 11.6539 | 7.9935 | 64.0065 | 0.18207 | 6.36 | 6.42 | 192 | 705 | 1257 | 1277.6945 | -1.6463 | 51.8797 | 991.3473 | 80.6324 | 78 | 58 | 12 | 119 | 156 | 275 | 275 | 0.47038 | 0.43273 | 11.1781 | 11.616 | 12.709 | 43.291 | 0.26832 | 6.42 | 6.35 | 337 | 1257 | 1645 | 1958.7949 | -19.0757 | 15.5388 | 1607.8974 | 79.041 | SDS-TOX | mg Cl- /L | BMRL | 910 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-22 | CI-s2-22 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | 45 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-24 | CI-s2-24 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-26 | CI-s2-26 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | BMRL | 860 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-28 | CI-s2-28 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | BMRL | 910 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-30 | CI-s2-30 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | BMRL | 1130 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-30 (dup) | CI-s2-30 (dup) | CC(calc) | RF (%) | CB | RB (%)
|  | Rejection of reference solute and conditions of test | 80 | 1: A negative minimum recycle flow rate indicates that recycle is not required to | [6 empty] | 1998-10-26 | 6:00 | 27618.3 | 24.1 | 121 | 57 | 29.6991 | 0 | 1308 | 156 |  | 1464 | 1464 | 0.89344 | 0 | 14.0993 | 14.4794 | 5.2962 | 54.0047 | 0.26811 | 7.01 | 6.08 | 286 | 386 | 388 | 1626 | 1243.2308 | 23.5405 | 26.2887 | 815.6154 | 64.9345 | 121 | 90 | 42 | 873 | 591 | 1464 | 1464 | 0.43609 | 0.59631 | 15.9452 | 16.3751 | 3.5815 | 59.9185 | 0.27329 | 6.08 | 6.18 | 182 | 388 | 712 | 692.2944 | 2.7676 | 53.0928 | 540.1472 | 66.3055 | 90 | 78 | 12 | 313 | 278 | 591 | 591 | 0.36882 | 0.52961 | 11.4338 | 11.742 | 7.7522 | 64.2478 | 0.18276 | 6.18 | 6.28 | 216 | 712 | 1386 | 1270.446 | 8.3372 | 44.3299 | 991.223 | 78.2087 | 78 | 57 | 12 | 122 | 156 | 278 | 278 | 0.47365 | 0.43885 | 11.4599 | 11.7688 | 14.6475 | 40.8525 | 0.28808 | 6.28 | 6.33 | 333 | 1386 | 1626 | 2209.5 | -35.8856 | 14.1753 | 1797.75 | 81.4768 | SDS-CHCl3 | mg/L | 0.7 | 280 | --- | 2539.7909 | --- | 99.75 | 1277.0177 | 99.9452 | Sampling date | MM/DD/YY | 1998-09-08 | 1998-09-08 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 2 | 180 | --- | 1620.1818 | --- | 98.8889 | 814.8534 | 99.7546 | Sampling date | MM/DD/YY | 1998-09-14 | 1998-09-14 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | NA | NA | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 0.6 | 240 | --- | 2176.9636 | --- | 99.75 | 1089.4672 | 99.9449 | Sampling date | MM/DD/YY | 1998-10-12 | 1998-10-12 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 2 | 320 | --- | 2892.9091 | --- | 99.375 | 1454.0592 | 99.8625 | Sampling date | MM/DD/YY | 1998-10-26 | 1998-10-26 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 0.7 | 280 | --- | 2539.7909 | --- | 99.75 | 1276.0463 | 99.9451 | Sampling date | MM/DD/YY | 1998-10-26 | 1998-10-26 | --- | --- | --- | ---
|  | (e.g., solute type and concentration) |  | meet the manufacturer's minimum flow requirement. | [6 empty] | 1998-10-27 | 1:50 | 27628 | 23.7 | 119.7 | 57 | 29.6991 | 0 | 1302 | 158 |  | 1460 | 1460 | 0.89178 | 0 | 14.0346 | 14.5844 | 8.5508 | 50.1001 | 0.2911 |  | 6 | 231 |  | 398 | 1670 | 1774.1646 | -6.2374 | 41.9598 | 1086.0823 | 78.7309 | 119.7 | 89 | 42 | 875 | 585 | 1460 | 1460 | 0.43397 | 0.59932 | 15.9817 | 16.6078 | 4.2997 | 58.0503 | 0.28609 | 6 | 6.21 | 152 | 398 | 718 | 765.9487 | -6.6781 | 61.809 | 581.9744 | 73.882 | 89 | 78 | 12 | 307 | 278 | 585 | 585 | 0.36628 | 0.52479 | 11.2146 | 11.6539 | 8.3196 | 63.1804 | 0.18445 | 6.21 | 6.27 | 182 | 718 | 1292 | 1309.9137 | -1.3865 | 54.2714 | 1013.9568 | 82.0505 | 78 | 57 | 12 | 120 | 158 | 278 | 278 | 0.47584 | 0.43165 | 11.272 | 11.7136 | 13.4801 | 42.0199 | 0.27876 | 6.27 | 6.35 | 315 | 1292 | 1670 | 2034.0253 | -21.7979 | 20.8543 | 1663.0127 | 81.0585 | SDS-BDCM | mg/L | 1 | 62 | --- | 555.5455 | --- | 98.3871 | 279.7518 | 99.6425 | Sampling time | hh:mm | 12:17 | 12:26 | --- | --- | --- | --- | SDS-BDCM | mg/L | 2 | 39 | --- | 338.3636 | --- | 94.8718 | 170.9639 | 98.8302 | Sampling time | hh:mm | 8:15 | 8:31 | --- | --- | --- | --- | SDS-BDCM | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | NA | NA | --- | --- | --- | --- | SDS-BDCM | mg/L | 1.1 | 50 | --- | 445.6455 | --- | 97.8 | 223.5127 | 99.5079 | Sampling time | hh:mm | 7:38 | 7:48 | --- | --- | --- | --- | SDS-BDCM | mg/L | 3.4 | 57 | --- | 490.6727 | --- | 94.0351 | 248.1496 | 98.6299 | Sampling time | hh:mm | 7:17 | 7:36 | --- | --- | --- | --- | SDS-BDCM | mg/L | 1.2 | 58 | --- | 517.5636 | --- | 97.931 | 260.5615 | 99.5395 | Sampling time | hh:mm | 7:17 | 7:36 | --- | --- | --- | ---
|  | Variability of rejection of reference solute (%) | 50 +/- | [7 empty] | 1998-10-29 | 0:37 | 27671.4 | 23.5 | 120.3 | 58 | 30.2891 | 0 | 1299 | 154 |  | 1453 | 1453 | 0.89401 | 0 | 14.0022 | 14.637 | 7.9828 | 50.8781 | 0.28769 |  | 5.99 | 245 |  | 398 | 1662 | 1688.5649 | -1.5984 | 38.4422 | 1043.2825 | 76.5164 | 120.3 | 90 | 43 | 871 | 582 | 1453 | 1453 | 0.43185 | 0.59945 | 15.9087 | 16.6299 | 4.2134 | 57.9366 | 0.28704 | 5.99 | 6.3 | 157 | 398 | 710 | 758.6718 | -6.8552 | 60.5528 | 578.3359 | 72.8531 | 90 | 78 | 12 | 308 | 274 | 582 | 582 | 0.3633 | 0.52921 | 11.2511 | 11.7612 | 8.1382 | 63.8618 | 0.18417 | 6.3 | 6.35 | 189 | 710 | 1276 | 1295.6496 | -1.5399 | 52.5126 | 1002.8248 | 81.1532 | 78 | 58 | 12 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.783 | 13.1457 | 42.8543 | 0.27496 | 6.35 | 6.35 | 330 | 1276 | 1662 | 2013.1429 | -21.1277 | 17.0854 | 1644.5714 | 79.934 | SDS-DBCM | mg/L | 2 | 15 | --- | 120.1818 | --- | 86.6667 | 61.4061 | 96.743 | Operation time | hh.hh | 27020.1 | 27020.3 | --- | --- | --- | --- | SDS-DBCM | mg/L | 2 | 13 | --- | 102 | --- | 84.6154 | 52.2325 | 96.171 | Operation time | hh.hh | 27152.6 | 27152.9 | --- | --- | --- | --- | SDS-DBCM | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | NA | NA | --- | --- | --- | --- | SDS-DBCM | mg/L | 2 | 11 | --- | 83.8182 | --- | 81.8182 | 42.9349 | 95.3418 | Operation time | hh.hh | 27336.8 | 27337 | --- | --- | --- | --- | SDS-DBCM | mg/L | 5.6 | 17 | --- | 109.2364 | --- | 67.0588 | 57.655 | 90.287 | Operation time | hh.hh | 27615.6 | 27616 | --- | --- | --- | --- | SDS-DBCM | mg/L | 2.4 | 18 | --- | 144.2182 | --- | 86.6667 | 73.6331 | 96.7406 | Operation time | hh.hh | 27615.6 | 27616 | --- | --- | --- | ---
|  | Standard testing recovery (%) | 15 | Calculate the Maximum Recycle Flow Rates for Each Stage | [6 empty] | 1998-10-30 | 0:05 | 27694.9 | 22.5 | 120.6 | 60 | 30.2891 | 0 | 1312 | 139 |  | 1451 | 1451 | 0.9042 | 0 | 14.1424 | 15.227 | 3.832 | 56.1789 | 0.27105 |  | 5.99 | 322 |  | 389 | 1528 | 1021.4029 | 33.1543 | 17.2237 | 705.2014 | 54.3393 | 120.6 | 90 | 43 | 878 | 573 | 1451 | 1451 | 0.42951 | 0.6051 | 16.0365 | 17.2665 | 4.0091 | 58.2909 | 0.29621 | 5.99 | 6.21 | 162 | 389 | 697 | 736.829 | -5.7143 | 58.3548 | 562.9145 | 71.2212 | 90 | 78 | 12 | 312 | 261 | 573 | 573 | 0.35397 | 0.5445 | 11.3973 | 12.2714 | 7.8128 | 64.1872 | 0.19118 | 6.21 | 6.31 | 208 | 697 | 1242 | 1281.5517 | -3.1845 | 46.5296 | 989.2759 | 78.9745 | 78 | 60 | 12 | 122 | 139 | 261 | 261 | 0.43655 | 0.46743 | 11.4599 | 12.3388 | 12.518 | 44.482 | 0.27739 | 6.31 | 6.32 | 372 | 1242 | 1528 | 2005.5971 | -31.2564 | 4.3702 | 1623.7986 | 77.0908 | SDS-CHBr3 | mg/L | 1 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 6.02 | 6.25 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | 0.7 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 6.01 | 6.18 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | NA | NA | --- | --- | --- | --- | SDS-CHBr3 | mg/L | 1.2 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 5.99 | 6.21 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | 2.3 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 6.02 | 6.11 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | 1.3 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 6.02 | 6.11 | --- | --- | --- | ---
|  | Standard testing pH | 7.5 to 8.5 | Maximum recycle flow rate for stage 1, (QR-s(1))max (gpm) | 1153.8194 | [5 empty] | 1998-10-31 | 9:58 | 27728.7 | 23.9 | 122.1 | 60 | 31.469 | 0 | 1303 | 154 |  | 1457 | 1457 | 0.8943 | 0 | 14.0454 | 14.5095 | 3.5568 | 56.0242 | 0.25899 |  | 6.14 | 320 |  | 388 | 1568 | 963.3506 | 38.5618 | 17.5258 | 675.6753 | 52.64 | 122.1 | 92 | 45 | 869 | 588 | 1457 | 1457 | 0.43397 | 0.59643 | 15.8721 | 16.3967 | 4.1387 | 57.9113 | 0.28313 | 6.14 | 6.32 | 150 | 388 | 685 | 739.7381 | -7.991 | 61.3402 | 563.869 | 73.3981 | 92 | 80 | 12 | 312 | 276 | 588 | 588 | 0.3667 | 0.53061 | 11.3973 | 11.7739 | 7.56 | 66.44 | 0.17721 | 6.32 | 6.36 | 202 | 685 | 1199 | 1231 | -2.6689 | 47.9381 | 958 | 78.9144 | 80 | 60 | 12 | 122 | 154 | 276 | 276 | 0.46929 | 0.44203 | 11.4599 | 11.8386 | 12.0065 | 45.9935 | 0.2574 | 6.36 | 6.44 | 339 | 1199 | 1568 | 1880.2987 | -19.917 | 12.6289 | 1539.6494 | 77.982 | SDS-THM4 | mg/L | 4.7 | 357 | --- | 3207.4273 | --- | 98.6835 | 1614.6059 | 99.7089 | Temperature | oC | 25.8 | 25.6 | --- | --- | --- | --- | SDS-THM4 | mg/L | 6.7 | 232 | --- | 2054.8818 | --- | 97.1121 | 1035.5532 | 99.353 | Temperature | oC | 25 | 25.1 | --- | --- | --- | --- | SDS-THM4 | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Temperature | oC | NA | NA | --- | --- | --- | --- | SDS-THM4 | mg/L | 4.9 | 301 | --- | 2696.7182 | --- | 98.3721 | 1351.6567 | 99.6375 | Temperature | oC | 25 | 25.1 | --- | --- | --- | --- | SDS-THM4 | mg/L | 13.3 | 394 | --- | 3474.2091 | --- | 96.6244 | 1751.6614 | 99.2407 | Temperature | oC | 24.5 | 24.6 | --- | --- | --- | --- | SDS-THM4 | mg/L | 5.6 | 356 | --- | 3191.0545 | --- | 98.427 | 1605.6048 | 99.6512 | Temperature | oC | 24.5 | 24.6 | --- | --- | --- | ---
|  | Acceptable range of operating pressures | <400psi | Maximum recycle flow rate for stage 2, (QR-s(2))max (gpm) | 625.0694 | [108 empty] | SDS-MCAA* | mg/L | BMRL | 9.1 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 95 | 160 | 230.7778 | 10.3774 | 195.3889 | 51.379 | SDS-MCAA* | mg/L | BMRL | 5.2 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 93 | 134 | 179.92 | -1.087 | 156.96 | 40.7492 | SDS-MCAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | 5.4 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 67 | 122 | 182.5 | 12.987 | 152.25 | 55.9934 | SDS-MCAA* | mg/L | 2.7 | 2.6 | --- | 1.7909 | --- | -3.8462 | 2.2434 | -20.3542 | Alkalinity | mg/L as CaCO3 | 91 | 178 | 275.9532 | 21.5517 | 226.9766 | 59.9078 | SDS-MCAA* | mg/L | BMRL | 2.5 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 91 | 176 | 271.7014 | 21.5517 | 223.8507 | 59.3479
|  | Acceptable range of operating pH values | 2 to 8 | Maximum recycle flow rate for stage 3, (QR-s(3))max (gpm) | 210.6944 | [108 empty] | SDS-DCAA* | mg/L | BMRL | 61 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 246 | 68 | -125.8222 | 59 | -28.9111 | 950.8839 | SDS-DCAA* | mg/L | 1.8 | 82 | --- | 730.8909 | --- | 97.8049 | 368.0407 | 99.5109 | Total dissolved solids | mg/L | 174 | 1164 | 2272.8 | 69.3662 | 1718.4 | 89.8743 | SDS-DCAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | BMRL | 51 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 168 | 1164 | 2259.6 | 68.6567 | 1711.8 | 90.1858 | SDS-DCAA* | mg/L | 1.2 | 59 | --- | 526.6545 | --- | 97.9661 | 265.1277 | 99.5474 | Total dissolved solids | mg/L | 232 | 1108 | 2094.2878 | 58.2734 | 1601.1439 | 85.5104 | SDS-DCAA* | mg/L | BMRL | 58 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 210 | 1098 | 2097.7986 | 61.2546 | 1597.8993 | 86.8577
|  | Typical pressure drop across a single element (psi) | 3 to 4 psi | [110 empty] | SDS-TCAA* | mg/L | BMRL | 85 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 101 | 680 | 1310.4667 | 68.8272 | 995.2333 | 89.8516 | SDS-TCAA* | mg/L | 1.2 | 86 | --- | 772.1091 | --- | 98.6047 | 388.447 | 99.6911 | Total hardness | mg/L as CaCO3 | 93 | 620 | 1210.24 | 69.4079 | 915.12 | 89.8374 | SDS-TCAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | 69 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 86 | 680 | 1333.4 | 73.125 | 1006.7 | 91.4572 | SDS-TCAA* | mg/L | 1.6 | 73 | --- | 650.6909 | --- | 97.8082 | 327.6284 | 99.5116 | Total hardness | mg/L as CaCO3 | 105 | 670 | 1306.1331 | 66.3462 | 988.0665 | 89.3732 | SDS-TCAA* | mg/L | BMRL | 74 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 103 | 700 | 1372.1619 | 66.5584 | 1036.0809 | 90.0587
|  | Maximum permissible SDI | 4 | Select the Design System Recycle Flow Rate2 | [109 empty] | SDS-MBAA* | mg/L | BMRL | 1.1 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 74 | 510 | 984.7556 | 66.3636 | 747.3778 | 90.0987 | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 68 | 500 | 983.84 | 69.6429 | 741.92 | 90.8346 | SDS-MBAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 69 | 520 | 1016.1 | 71.25 | 768.05 | 91.0162 | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 84 | 500 | 968.3741 | 65.2893 | 734.1871 | 88.5588 | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 85 | 510 | 988.5072 | 64.5833 | 749.2536 | 88.6554
|  | Maximum permissible turbidity (ntu) | 1 | Minimum system recycle flow rate, (QR-sys)min (gpm) | 1730.1944 | [108 empty] | SDS-DBAA* | mg/L | BMRL | 2.2 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.06 | 8.4 | 17.4813 | 92.5926 | 12.9407 | 99.5363 | SDS-DBAA* | mg/L | 1.7 | 2.8 | --- | 11.7 | --- | 39.2857 | 6.7233 | 74.7146 | Turbidity | ntu | 0.05 | 11 | 23.264 | 96.1538 | 17.132 | 99.7081 | SDS-DBAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | 2 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.06 | 7.8 | 16.314 | 92.7711 | 12.057 | 99.5024 | SDS-DBAA* | mg/L | 1.4 | 2.3 | --- | 9.5818 | --- | 39.1304 | 5.5096 | 74.5898 | Turbidity | ntu | 0.07 | 5.5 | 11.6136 | 72 | 8.5568 | 99.1819 | SDS-DBAA* | mg/L | BMRL | 2.2 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.06 | 6.2 | 13.113 | 76.9231 | 9.6565 | 99.3787
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | 1 ppm | Maximum system recycle flow rate, (QR-sys)max (gpm) | 210.6944 | [108 empty] | SDS-BCAA* | mg/L | BMRL | 12 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 22 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | 1.4 | 17 | --- | 143.2182 | --- | 91.7647 | 72.6388 | 98.0727 | Total organic carbon | mg/L | 5 | 23 | 43.16 | 50 | 33.08 | 84.8851 | SDS-BCAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | 12 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 20 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | 1.9 | 13 | --- | 102.8091 | --- | 85.3846 | 52.5851 | 96.3868 | Total organic carbon | mg/L | BMRL | 21 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | 13 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 21 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | 1: All of the information requested in this field may not be available, but values for all of the Design |  | Design system recycle flow rate, QR-sys (gpm) | 0 | [108 empty] | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.0112 | 0.669 | 1.3853 | 95.5378 | 1.0271 | 98.9096 | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.0113 | 0.287 | 0.59578 | 95.0655 | 0.44139 | 97.4399 | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.01 | 0.562 | 1.1692 | 95.4955 | 0.8656 | 98.8447 | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.004 | 0.558 | 1.1817 | 98.1735 | 0.86987 | 99.5402 | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.004 | 0.554 | 1.1732 | 98.1818 | 0.86362 | 99.5368
|  | Parameters must be entered in cells E15:E26, since these parameters are used in calculations. |  | System influent flow rate, QI-sys (gpm) | 1546.1806 | [108 empty] | SDS-CDBAA | mg/L | BMRL | 4 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.0409 | --- | --- | --- | --- | SDS-CDBAA | mg/L | BMRL | 2.6 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | 0.226 | 1.2478 | --- | --- | --- | --- | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NA | NA | --- | --- | --- | --- | SDS-CDBAA | mg/L | BMRL | 3.1 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 2.81 | --- | --- | --- | --- | SDS-CDBAA | mg/L | BMRL | 3.6 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 2.6571 | --- | --- | --- | --- | SDS-CDBAA | mg/L | BMRL | 3.3 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 2.6381 | --- | --- | --- | ---
|  |  |  | Recycle ratio, r | 0 | [108 empty] | SDS-DCBAA | mg/L | BMRL | 23 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | 1.3 | 26 | --- | 225.8455 | --- | 95 | 114.0948 | 98.8606 | [8 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | 1 | 17 | --- | 146.4545 | --- | 94.1176 | 73.7731 | 98.6445 | [8 empty] | SDS-DCBAA | mg/L | 1.7 | 19 | --- | 158.9727 | --- | 91.0526 | 80.6957 | 97.8933 | [8 empty] | SDS-DCBAA | mg/L | BMRL | 18 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  |  |  | 2: The design system recycle flow rate must fall between the minimum and | [109 empty] | SDS-HAA5 | mg/L | 0 | 158.4 | --- | 1440 | --- | 100 | 723.8407 | 100 | [8 empty] | SDS-HAA5 | mg/L | 4.7 | 176 | --- | 1561.9727 | --- | 97.3295 | 786.9572 | 99.4028 | [8 empty] | SDS-HAA5 | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-HAA5 | mg/L | 0 | 127.4 | --- | 1158.1818 | --- | 100 | 579.4556 | 100 | [8 empty] | SDS-HAA5 | mg/L | 6.9 | 136.9 | --- | 1188.7182 | --- | 94.9598 | 600.5091 | 98.851 | [8 empty] | SDS-HAA5 | mg/L | 0 | 136.7 | --- | 1242.7273 | --- | 100 | 624.2028 | 100
|  |  |  | maximum system recycle flow rates. | [109 empty] | SDS-HAA6 | mg/L | 0 | 170.4 | --- | 1549.0909 | --- | 100 | 778.6772 | 100 | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | 6.1 | 193 | --- | 1705.1909 | --- | 96.8394 | 859.5961 | 99.2904 | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | 0 | 139.4 | --- | 1267.2727 | --- | 100 | 634.0354 | 100 | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | 8.8 | 149.9 | --- | 1291.5273 | --- | 94.1294 | 653.0942 | 98.6526 | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | 0 | 149.7 | --- | 1360.9091 | --- | 100 | 683.5637 | 100 | Stage 3 Operating Parameters During Sample Collection
[114 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.42 |  |  |  |  | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.44 |  |  |  |  | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | [5 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.43 |  |  |  |  | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.44 |  |  |  |  | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.44
|  |  |  | Summary of the Stage and System Flow Rates | [109 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 114 |  |  |  |  | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 120 |  |  |  |  | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | [5 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 120 |  |  |  |  | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 122 |  |  |  |  | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 122
|  |  |  | Influent flow rate to stage 1, QI-s(1) (gpm) | 1546.1806 | [120 empty] | Stage 3 influent flow rate during sample collection (gpm) | 270 | [16 empty] | Stage 3 influent flow rate during sample collection (gpm) | 275 | [16 empty] | Stage 3 influent flow rate during sample collection (gpm) | [17 empty] | Stage 3 influent flow rate during sample collection (gpm) | 280 | [16 empty] | Stage 3 influent flow rate during sample collection (gpm) | 278 | [16 empty] | Stage 3 influent flow rate during sample collection (gpm) | 278
|  |  |  | Permeate flow rate from stage 1, Qp-s(1) (gpm) | 821.25 | [108 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs
|  |  |  | Concentrate flow rate from stage 1, QC-s(1) (gpm) | 724.9306 | [109 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters
|  |  |  | Influent flow rate to stage 2, QI-s(2) (gpm) | 724.9306 | [109 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-22 | CI-s3-22 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-24 | CI-s3-24 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-26 | CI-s3-26 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-28 | CI-s3-28 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-30 | CI-s3-30 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-30 (dup) | CI-s3-30 (dup) | CC(calc) | RF (%) | CB | RB (%)
|  |  |  | Permeate flow rate from stage 2, Qp-s(2) (gpm) | 410.625 | [108 empty] | Qp/QT (THM4), % | 80.897 | 91.1155 |  | Qp/QT (HAA5), % | 65.9091 | 82.9545 |  |  |  | Sampling date | MM/DD/YY | 1998-09-08 | 1998-09-08 | --- | --- | --- | --- | Qp/QT (THM4), % | 71.0164 | 86.9951 |  | Qp/QT (HAA5), % | 71.2201 | 86.9819 |  |  |  | Sampling date | MM/DD/YY | 1998-09-14 | 1998-09-14 | --- | --- | --- | --- | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | #VALUE! | #VALUE! |  |  |  | Sampling date | MM/DD/YY | NA | NA | --- | --- | --- | --- | Qp/QT (THM4), % | 77.3387 | 89.4968 |  | Qp/QT (HAA5), % | 57.6138 | 78.8069 |  |  |  | Sampling date | MM/DD/YY | 1998-10-12 | 1998-10-12 | --- | --- | --- | --- | Qp/QT (THM4), % | 84.581 | 94.0373 |  | Qp/QT (HAA5), % | 63.7692 | 84.5385 |  |  |  | Sampling date | MM/DD/YY | 1998-10-26 | 1998-10-26 | --- | --- | --- | --- | Qp/QT (THM4), % | 81.0502 | 91.3242 |  | Qp/QT (HAA5), % | 60.4974 | 80.2487 |  |  |  | Sampling date | MM/DD/YY | 1998-10-26 | 1998-10-26 | --- | --- | --- | ---
|  |  |  | Concentrate flow rate from stage 2, QC-s(2) (gpm) | 314.3056 | [108 empty] | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 124.8023 | 64.7511 |  |  |  | Sampling time | hh:mm | 12:20 | 12:29 | --- | --- | --- | --- | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 71.5412 | 36.0298 |  |  |  | Sampling time | hh:mm | 8:18 | 8:35 | --- | --- | --- | --- | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  |  |  | Sampling time | hh:mm | NA | NA | --- | --- | --- | --- | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 130.4055 | 67.6527 |  |  |  | Sampling time | hh:mm | 7:40 | 7:51 | --- | --- | --- | --- | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 151.2305 | 72.1621 |  |  |  | Sampling time | hh:mm | 7:21 | 7:42 | --- | --- | --- | --- | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 144.017 | 74.8085 |  |  |  | Sampling time | hh:mm | 7:21 | 7:42 | --- | --- | --- | ---
|  |  |  | Influent flow rate to stage 3, QI-s(3) (gpm) | 314.3056 | [108 empty] | SDS-HAA5b, mg/L | 30.2592 | 14.073 |  | SDS-HAA5b, mg/L | 54 | 27 |  |  |  | Operation time | hh.hh | 27020.2 | 27020.4 | --- | --- | --- | --- | SDS-HAA5b, mg/L | 54.3489 | 26.9774 |  | SDS-HAA5b, mg/L | 54 | 27 |  |  |  | Operation time | hh.hh | 27152.7 | 27153 | --- | --- | --- | --- | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  |  |  | Operation time | hh.hh | NA | NA | --- | --- | --- | --- | SDS-HAA5b, mg/L | 28.8704 | 13.3811 |  | SDS-HAA5b, mg/L | 54 | 27 |  |  |  | Operation time | hh.hh | 27336.9 | 27337 | --- | --- | --- | --- | SDS-HAA5b, mg/L | 26.9447 | 14.6515 |  | SDS-HAA5b, mg/L | 54 | 27 |  |  |  | Operation time | hh.hh | 27615.7 | 27616.1 | --- | --- | --- | --- | SDS-HAA5b, mg/L | 25.9043 | 11.8598 |  | SDS-HAA5b, mg/L | 54 | 27 |  |  |  | Operation time | hh.hh | 27615.7 | 27616.1 | --- | --- | --- | ---
|  |  |  | Permeate flow rate from stage 3, Qp-s(3) (gpm) | 159.6875 | [108 empty] | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  |  |  | pH | --- | 6.38 | 6.19 | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  |  |  | pH | --- | 6.23 | 6.25 | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  |  |  | pH | --- | NA | NA | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  |  |  | pH | --- | 6.23 | 6.27 | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  |  |  | pH | --- | 6.27 | 6.34 | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  |  |  | pH | --- | 6.27 | 6.34 | --- | --- | --- | ---
|  |  |  | Concentrate flow rate from stage 3, QC-s(3) (gpm) | 154.6181 | [108 empty] | SDS-CDb, mg/L | 17.5864 | 16.588 |  | SDS-CDb, mg/L | 19.0507 | 17.3853 |  |  |  | Temperature | oC | 25.8 | 25.68 | --- | --- | --- | --- | SDS-CDb, mg/L | 18.6309 | 17.9854 |  | SDS-CDb, mg/L | 18.6227 | 17.9859 |  |  |  | Temperature | oC | 25.2 | 25.2 | --- | --- | --- | --- | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | #VALUE! | #VALUE! |  |  |  | Temperature | oC | NA | NA | --- | --- | --- | --- | SDS-CDb, mg/L | 18.0661 | 16.8503 |  | SDS-CDb, mg/L | 20.0386 | 17.9193 |  |  |  | Temperature | oC | 25.2 | 25.2 | --- | --- | --- | --- | SDS-CDb, mg/L | 16.4961 | 15.4559 |  | SDS-CDb, mg/L | 18.7854 | 16.5008 |  |  |  | Temperature | oC | 24.5 | 24.6 | --- | --- | --- | --- | SDS-CDb, mg/L | 17.5518 | 16.4936 |  | SDS-CDb, mg/L | 19.6688 | 17.6344 |  |  |  | Temperature | oC | 24.5 | 24.6 | --- | --- | --- | ---
|  |  |  | System concentrate recycle flow rate, QR-sys (gpm) | 0 | [108 empty] | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! |  |  |  | Alkalinity | mg/L as CaCO3 | 176 | 184 | 189.8462 | -66.0377 | 186.9231 | 5.8436 | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! |  |  |  | Alkalinity | mg/L as CaCO3 | 164 | 164 | 164 | -78.2609 | 164 | 0 | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! |  |  |  | Alkalinity | mg/L as CaCO3 | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! |  |  |  | Alkalinity | mg/L as CaCO3 | 138 | 154 | 166 | -79.2208 | 160 | 13.75 | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! |  |  |  | Alkalinity | mg/L as CaCO3 | 184 | 240 | 283.7949 | -58.6207 | 261.8974 | 29.7435 | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! |  |  |  | Alkalinity | mg/L as CaCO3 | 180 | 242 | 290.4872 | -55.1724 | 266.2436 | 32.3927
|  |  |  | System concentrate waste flow rate, QW-sys (gpm) | 154.6181 | [108 empty] | UV254 b, cm-1 | 0.060488 | 0.036423 |  | UV254 b, cm-1 | 0.095784 | 0.055642 |  |  |  | Total dissolved solids | mg/L | 388 | 2480 | 4008.7692 | 35.3333 | 3244.3846 | 88.0409 | UV254 b, cm-1 | 0.076173 | 0.041787 |  | UV254 b, cm-1 | 0.075734 | 0.041815 |  |  |  | Total dissolved solids | mg/L | 316 | 2472 | 4141.1613 | 44.3662 | 3306.5806 | 90.4433 | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  |  |  | Total dissolved solids | mg/L | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 b, cm-1 | 0.058042 | 0.032267 |  | UV254 b, cm-1 | 0.099859 | 0.054929 |  |  |  | Total dissolved solids | mg/L | 312 | 2540 | 4211 | 41.791 | 3375.5 | 90.7569 | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  |  |  | Total dissolved solids | mg/L | 380 | 2362 | 3912.0256 | 31.6547 | 3137.0128 | 87.8866 | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  |  |  | Total dissolved solids | mg/L | 362 | 2312 | 3837 | 33.2103 | 3074.5 | 88.2257
|  |  |  | System permeate flow rate, Qp-sys (gpm) | 1391.5625 | [108 empty] | Bromideb, mg/L | 160 | 160 |  | Bromideb, mg/L | 160 | 160 |  |  |  | Total hardness | mg/L as CaCO3 | 188 | 1450 | 2372.2308 | 41.9753 | 1911.1154 | 90.1628 | Bromideb, mg/L | 167.1016 | 168.6995 |  | Bromideb, mg/L | 167.122 | 168.6982 |  |  |  | Total hardness | mg/L as CaCO3 | 164 | 1430 | 2410.129 | 46.0526 | 1920.0645 | 91.4586 | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE! |  |  |  | Total hardness | mg/L as CaCO3 | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Bromideb, mg/L | 157.7339 | 158.9497 |  | Bromideb, mg/L | 155.7614 | 157.8807 |  |  |  | Total hardness | mg/L as CaCO3 | 170 | 1430 | 2375 | 46.875 | 1902.5 | 91.0644 | Bromideb, mg/L | 166.9162 | 168.8075 |  | Bromideb, mg/L | 162.7538 | 166.9077 |  |  |  | Total hardness | mg/L as CaCO3 | 206 | 1410 | 2351.5897 | 33.9744 | 1880.7949 | 89.0472 | Bromideb, mg/L | 166.21 | 168.2648 |  | Bromideb, mg/L | 162.0995 | 166.0497 |  |  |  | Total hardness | mg/L as CaCO3 | 206 | 1420 | 2369.4103 | 33.1169 | 1894.7051 | 89.1276
|  |  |  | System feed flow rate, QF-sys (gpm) | 1546.1806 | [108 empty] | Alkb, mg/L CaCO3 | 122.1794 | 124.2231 |  | Alkb, mg/L CaCO3 | 119.1818 | 122.5909 |  |  |  | Calcium hardness | mg/L as CaCO3 | 128 | 1100 | 1810.3077 | 41.8182 | 1455.1538 | 91.2037 | Alkb, mg/L CaCO3 | 117.5659 | 123.3182 |  | Alkb, mg/L CaCO3 | 117.6392 | 123.3135 |  |  |  | Calcium hardness | mg/L as CaCO3 | 123 | 1070 | 1803.1613 | 45.0893 | 1436.5806 | 91.438 | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Calcium hardness | mg/L as CaCO3 | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkb, mg/L CaCO3 | 88.6008 | 90.4245 |  | Alkb, mg/L CaCO3 | 85.6421 | 88.821 |  |  |  | Calcium hardness | mg/L as CaCO3 | 126 | 1140 | 1900.5 | 47.5 | 1520.25 | 91.7119 | Alkb, mg/L CaCO3 | 127.8413 | 129.1652 |  | Alkb, mg/L CaCO3 | 124.9277 | 127.8354 |  |  |  | Calcium hardness | mg/L as CaCO3 | 158 | 990 | 1640.6667 | 34.7107 | 1315.3333 | 87.9878 | Alkb, mg/L CaCO3 | 128.968 | 130.6119 |  | Alkb, mg/L CaCO3 | 125.6796 | 128.8398 |  |  |  | Calcium hardness | mg/L as CaCO3 | 160 | 1010 | 1674.7436 | 33.3333 | 1342.3718 | 88.0808
[114 empty] | T-Hdb, mg/L CaCO3 | 171.9137 | 152.7028 |  | T-Hdb, mg/L CaCO3 | 200.0909 | 168.0455 |  |  |  | Turbidity | ntu | 0.24 | 17.5 | 30.1131 | 70.3704 | 23.8065 | 98.9919 | T-Hdb, mg/L CaCO3 | 173.3298 | 143.929 |  | T-Hdb, mg/L CaCO3 | 172.955 | 143.9533 |  |  |  | Turbidity | ntu | 0.06 | 19 | 33.6632 | 95.3846 | 26.3316 | 99.7721 | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Turbidity | ntu | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | T-Hdb, mg/L CaCO3 | 165.3225 | 141.0064 |  | T-Hdb, mg/L CaCO3 | 204.7724 | 162.3862 |  |  |  | Turbidity | ntu | 0.09 | 17 | 29.6825 | 89.1566 | 23.3412 | 99.6144 | T-Hdb, mg/L CaCO3 | 168.2122 | 152.1366 |  | T-Hdb, mg/L CaCO3 | 203.5923 | 168.2846 |  |  |  | Turbidity | ntu | 0.12 | 18 | 31.9831 | 52 | 24.9915 | 99.5198 | T-Hdb, mg/L CaCO3 | 173.4566 | 156.4018 |  | T-Hdb, mg/L CaCO3 | 207.5743 | 174.7871 |  |  |  | Turbidity | ntu | 0.15 | 16 | 28.3955 | 42.3077 | 22.1978 | 99.3243
|  |  |  | Calculate the Required System Influent Pressure | [109 empty] | Ca-Hdb, mg/L CaCO3 | 122.9236 | 110.6614 |  | Ca-Hdb, mg/L CaCO3 | 140.9091 | 120.4545 |  |  |  | Total organic carbon | mg/L | BMRL | 58 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ca-Hdb, mg/L CaCO3 | 125.9973 | 103.9467 |  | Ca-Hdb, mg/L CaCO3 | 125.7163 | 103.965 |  |  |  | Total organic carbon | mg/L | 6 | 56 | 94.7097 | 40 | 75.3548 | 92.0377 | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Total organic carbon | mg/L | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ca-Hdb, mg/L CaCO3 | 122.4451 | 103.9649 |  | Ca-Hdb, mg/L CaCO3 | 152.427 | 120.2135 |  |  |  | Total organic carbon | mg/L | BMRL | 50 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ca-Hdb, mg/L CaCO3 | 121.8949 | 108.467 |  | Ca-Hdb, mg/L CaCO3 | 151.4477 | 121.9554 |  |  |  | Total organic carbon | mg/L | BMRL | 50 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ca-Hdb, mg/L CaCO3 | 126.5297 | 112.1461 |  | Ca-Hdb, mg/L CaCO3 | 155.3036 | 127.6518 |  |  |  | Total organic carbon | mg/L | BMRL | 43 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  |  |  | Osmotic pressure for stage 13, Dp1 (psi) | 4 | [108 empty] | Notes: | [9 empty] | UV254 | cm-1 | 0.0126 | 1.62 | 2.7946 | 94.9801 | 2.2073 | 99.4292 | Notes: | [9 empty] | UV254 | cm-1 | 0.0198 | 1.398 | 2.465 | 91.3537 | 1.9315 | 98.9749 | Notes: | [9 empty] | UV254 | cm-1 | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Notes: | [9 empty] | UV254 | cm-1 | 0.017 | 1.38 | 2.4022 | 92.3423 | 1.8911 | 99.1011 | Notes: | [9 empty] | UV254 | cm-1 | 0.007 | 1.35 | 2.4003 | 96.8037 | 1.8751 | 99.6267 | Notes: | [9 empty] | UV254 | cm-1 | 0.007 | 1.36 | 2.4181 | 96.8182 | 1.8891 | 99.6294
|  |  |  | Osmotic pressure for stage 23, Dp2 (psi) | 9 | [108 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | NR | 2.7931 | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | 0.33 | 2.4964 | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | NA | NA | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | NR | 2.76 | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | NR | 2.7 | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | NR | 3.1628 | --- | --- | --- | ---
|  |  |  | Osmotic pressure for stage 33, Dp3 (psi) | 16 | [108 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs.
|  |  |  | Pressure losses due to stage hardware, DPs (psi) | 62 | [108 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5.
|  |  |  | Pressure losses in a single element, DPe (psi) | 10.3 | [108 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters.
|  |  |  | Design permeate pressure, Pp (psi) | 18 | [108 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design.
|  |  |  | Mechanical pressure losses per stage, Ls (psi) | 123.8 | [108 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
|  |  |  | Net driving pressure required for permeation, NDP (psi) | 62.5 | [108 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
|  |  |  | Flow weighted system pressure losses, Lsys (psi) | 133.6967 | [108 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio.
|  |  |  | Required influent pressure to the system, PI (psi) | 214.1967 | [108 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL.
|  |  |  | 3: The osmotic pressure can be estimated from Table 6-5 in Part 3 of the | [109 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
"ICR Manual for Bench- and Pilot-Scale Treatment Studies."
Note on A1: TSC_ADM: This utility had trouble with their SDS chlorinations as in their response to EPA review and comments "Overall, all SDS residuals were very inconsistent. Our source water is very stable, but we experienced difficulty in retrieving good residuals on a regular basis. This could be in part to H2S levels in the water since odor removal is not preformed until after production. All SDS residuals below 0.1 were listed as 'NR'"
Note on E23: TSC_ADM: Reviewer entered a more appropriate membrane width
Note on W6: TSC_ADM: System Pp was approximated based on the number of parallel pressure vessels in each stage.
Note on DS16: C. Rice: Utility verified all alkalinity data stating that permeate values may be greater than feed values due to CO2.
Note on DS22: C. Rice: Utility verified the TOC data for week 22.
Note on ED26: TSC_ADM: Data entered by the reviewer since utility did not so do
Note on ED48: TSC_ADM: Data entered by the reviewer since utility did not so do
Note on EP33: C. Rice: Value verified by utility.
Note on EX26: TSC_ADM: Data entered by the reviewer since utility did not so do
Note on EX48: TSC_ADM: Data entered by the reviewer since utility did not so do
Note on FR26: TSC_ADM: Data entered by the reviewer since utility did not so do
Note on FR48: TSC_ADM: Data entered by the reviewer since utility did not so do
Note on GL26: TSC_ADM: Data entered by the reviewer since utility did not so do
Note on GL48: TSC_ADM: Data entered by the reviewer since utility did not so do
Note on HF26: TSC_ADM: Data entered by the reviewer since utility did not so do
Note on HF48: TSC_ADM: Data entered by the reviewer since utility did not so do
Note on HZ26: TSC_ADM: Data entered by the reviewer since utility did not so do
Note on HZ48: TSC_ADM: Data entered by the reviewer since utility did not so do

## Sheet4. Weeks 31-40
FIELD-SET 4: PILOT-SCALE MEMBRANE RESULTS: WEEKS 31-40 (FILE: mempilot.xls)
Field 4-1: PWS And Treatment Plant Data |  | Field 4-2: Manufacturer Reported Membrane Characteristics1 |  | Field 4-3: 3-Stage Membrane Pilot System Design Parameters |  | Field 4-4: Foulants And Fouling Indices1 |  | Field 4-5: Pretreatment Used Prior To Membranes1 |  |  | Field 4-6: Membrane Performance Data During Operation With The Test Water | [18 empty] | Field 4-6: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 4-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 4-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 4-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 4-7: System And Stage Water Quality For Week 32 | [9 empty] | Field 4-7: System And Stage Water Quality For Week 32 (continued) | [7 empty] | Field 4-8: System And Stage Water Quality For Week 34 | [9 empty] | Field 4-8: System And Stage Water Quality For Week 34 (continued) | [7 empty] | Field 4-9: System And Stage Water Quality For Week 36 | [9 empty] | Field 4-9: System And Stage Water Quality For Week 36 (continued) | [7 empty] | Field 4-10: System And Stage Water Quality For Week 38 | [9 empty] | Field 4-10: System And Stage Water Quality For Week 38 (continued) | [7 empty] | Field 4-11: System And Stage Water Quality For Week 40 | [9 empty] | Field 4-11: System And Stage Water Quality For Week 40 (continued) | [7 empty] | Field 4-12: Duplicate Analysis Of System And Stage Water Quality For Week 40 | [9 empty] | Field 4-12: Duplicate Analysis Of System And Stage Water Quality For Week 40 (continued) | [7 empty] | Field 4-13: Membrane Cost Parameters
|  | General Information |  | Calculate Temperature Normalized MTCW |  | Parameters Evaluated Prior to Pretreatment |  |  |  |  | System Operating Parameters | [30 empty] | Stage 1 Operating Parameters | [23 empty] | Stage 2 Operating Parameters | [23 empty] | Stage 3 Operating Parameters | [23 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | General Cost Parameters
PWS Name | Collier County Water Department | Membrane manufacturer | Hydranautics | Average yearly temperature of feed water, TavgoC (oC) | 25 | Alkalinity (mg/L as CaCO3) | 290 | Process | Description | Scale | Date | Time | Operation |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  |  |  | System recovery during sample collection (decimal) | 0.895 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.6 | [6 empty] | System recovery during sample collection (decimal) | 0.89 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.6 | [6 empty] | System recovery during sample collection (decimal) | 0.89 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.6 | [6 empty] | System recovery during sample collection (decimal) | 0.89 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.6 | [6 empty] | System recovery during sample collection (decimal) | 0.89 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.6 | [6 empty] | System recovery during sample collection (decimal) | 0.89 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.6 |  |  |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | FL5114069 | Membrane trade name | PVD 1 | Temperature normalized MTCW (gfd/psi) | 0.24 | Calcium Hardness (mg/L as CaCO3) | 220 | Sulfuric Acid Addition | pH adjustment to 5.8-6.0 | full-scale |  |  | time | Influent | PI | PC | PP | QR | Qp | QW | Cleaning Event | QF | QI | Recovery | Recycle | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) |  |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) |  |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) | [6 empty] | System feed flow rate during sample collection (gpm) | 1447 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 864 | [6 empty] | System feed flow rate during sample collection (gpm) | 1455 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 877 | [6 empty] | System feed flow rate during sample collection (gpm) | 1457 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 872 | [6 empty] | System feed flow rate during sample collection (gpm) | 1454 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 872 | [6 empty] | System feed flow rate during sample collection (gpm) | 1459 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 874 | [6 empty] | System feed flow rate during sample collection (gpm) | 1459 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 874 |  |  |  |  | Capital Recovery Interest Rate (%) | N/A
Water Industry Data Base Number (optional) | NA | Membrane element model number | 8040-LSY-PVD1 |  |  | LSI | 7.26 | Anti-Scalant Addition | Argo Scientific Hyperspearse AS120UL | full-scale | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | Indicate with "X" | (gpm) | (gpm) | (decimal) | ratio | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHF (before acid) | pHF (after acid) | TDSp | TDSF (before acid) | TDSF (after acid) | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) |  |  | System influent flow rate during sample collection (gpm) | 1295 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 1442 | [6 empty] | System influent flow rate during sample collection (gpm) | 1301 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 1455 | [6 empty] | System influent flow rate during sample collection (gpm) | 1300 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 1457 | [6 empty] | System influent flow rate during sample collection (gpm) | 1300 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 1454 | [6 empty] | System influent flow rate during sample collection (gpm) | 1301 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 1459 | [6 empty] | System influent flow rate during sample collection (gpm) | 1301 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 1459 |  |  |  |  | Capital Recovery Period (years) | 25
|  | Molecular weight cutoff (Daltons) | 100-300 | Calculate System Permeate, Feed and Waste Flow Rates |  | Dissolved iron (mg/L) |  | Cartridge Filtration | 5 Micron | full-scale | 1998-11-01 | 10:00 | 27752.6 | 23.7 | 122 | 60 | 30.8791 | 0 | 1300 | 154 |  | 1454 | 1454 | 0.89409 | 0 | 14.013 | 14.562 | 5.7951 | 54.3259 | 0.26805 |  | 6.08 | 280 |  | 391 | 1610 | 1328.013 | 17.5147 | 28.3887 | 859.5065 | 67.4232 | 122 | 92 | 44 | 873 | 581 | 1454 | 1454 | 0.43185 | 0.60041 | 15.9452 | 16.5698 | 4.2556 | 58.7444 | 0.28207 | 6.08 | 6.18 | 148 | 391 | 656 | 756.1274 | -15.2633 | 62.1483 | 573.5637 | 74.1964 | 92 | 81 | 12 | 307 | 274 | 581 | 581 | 0.36288 | 0.5284 | 11.2146 | 11.6539 | 6.9274 | 67.5726 | 0.17247 | 6.18 | 6.29 | 212 | 656 | 1222 | 1153.4745 | 5.6077 | 45.7801 | 904.7372 | 76.5678 | 81 | 60 | 12 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.7136 | 12.3953 | 46.1047 | 0.25407 | 6.29 | 6.37 | 330 | 1222 | 1610 | 1917.0649 | -19.0724 | 15.601 | 1569.5325 | 78.9746 | [108 empty] | Overhead & Profit Factor (% of construction costs) | 10
Official ICR Contact Person |  | Membrane material (e.g., PVD, polyamide, etc.) | Poly Vinyl Derivative | Design system recovery, R (decimal) | 0.9 | Total iron (mg/L) | 0.03 |  |  |  | 1998-11-02 | 6:00 | 27772.1 | 23.5 | 124 | 60 | 31.469 | 0 | 1299 | 153 |  | 1452 | 1452 | 0.89463 | 0 | 14.0022 | 14.637 | 5.6647 | 54.8663 | 0.26678 | 7.02 | 6.11 | 278 | 351 | 386 | 1636 | 1302.9412 | 20.3581 | 27.9793 | 844.4706 | 67.08 | 124 | 92 | 45 | 866 | 586 | 1452 | 1452 | 0.43249 | 0.59642 | 15.8174 | 16.5344 | 4.069 | 58.931 | 0.28057 | 6.11 | 6.19 | 152 | 386 | 624 | 731.8089 | -17.2771 | 60.6218 | 558.9044 | 72.8039 | 92 | 80 | 12 | 312 | 274 | 586 | 586 | 0.365 | 0.53242 | 11.3973 | 11.914 | 6.3088 | 67.6912 | 0.176 | 6.19 | 6.31 | 222 | 624 | 1264 | 1081.7518 | 14.4184 | 42.487 | 852.8759 | 73.9704 | 80 | 60 | 12 | 121 | 153 | 274 | 274 | 0.46601 | 0.44161 | 11.3659 | 11.8812 | 13.0612 | 44.9388 | 0.26439 | 6.31 | 6.34 | 328 | 1264 | 1636 | 2004.2353 | -22.5083 | 15.0259 | 1634.1176 | 79.928 | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | Special Sitework Factor (% of construction costs) | N/A
Mailing Address |  | Membrane construction (e.g., thin-film composite) | Thin Film Composite | Design average system flux, FW (gfd) | 15 | Dissolved aluminum (mg/L) |  |  |  |  | 1998-11-07 | 20:30 | 27815.3 | 23.5 | 122 | 60 | 30.2891 | 0 | 1301 | 160 |  | 1461 | 1461 | 0.89049 | 0 | 14.0238 | 14.6596 | 5.5215 | 55.1894 | 0.26562 |  | 6.09 | 279 |  | 388 | 1624 | 1274.3063 | 21.5329 | 28.0928 | 831.1531 | 66.4322 | 122 | 92 | 43 | 875 | 586 | 1461 | 1461 | 0.4344 | 0.5989 | 15.9817 | 16.7063 | 4.1569 | 59.8431 | 0.27917 | 6.09 | 6.18 | 150 | 388 | 641 | 743.3754 | -15.9712 | 61.3402 | 565.6877 | 73.4836 | 92 | 80 | 12 | 307 | 279 | 586 | 586 | 0.36712 | 0.52389 | 11.2146 | 11.723 | 6.5108 | 67.4892 | 0.1737 | 6.18 | 6.3 | 221 | 641 | 1244 | 1103.1505 | 11.3223 | 43.0412 | 872.0753 | 74.6582 | 80 | 60 | 12 | 119 | 160 | 279 | 279 | 0.47911 | 0.42652 | 11.1781 | 11.6848 | 12.5527 | 45.4473 | 0.25711 | 6.3 | 6.35 | 329 | 1244 | 1624 | 1924.5312 | -18.5056 | 15.2062 | 1584.2656 | 79.2333 | Parameter | Units | Cp-sys-32 | CF-sys-32 | CC-sys-32 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-32 | CI-s1-32 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-34 | CF-sys-34 | CC-sys-34 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-34 | CI-s1-34 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-36 | CF-sys-36 | CC-sys-36 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-36 | CI-s1-36 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-38 | CF-sys-38 | CC-sys-38 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-38 | CI-s1-38 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-40 | CF-sys-40 | CC-sys-40 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-40 | CI-s1-40 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-40 (dup) | CF-sys-40 (dup) | CC-sys-40 (dup) | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-40 (dup) | CI-s1-40 (dup) | CC(calc) | RF (%) | CB | RB (%) | Construction Contingencies (% of construction costs) | NONE
|  | Membrane hydrophobicity | Hydrophillic | Number of elements per pressure vessel, Ne | 6 | Total aluminum (mg/L) | <0.10 |  |  |  | 1998-11-08 | 6:00 | 27825.1 | 23.6 | 122 | 61 | 30.8791 | 0 | 1301 | 155 |  | 1456 | 1456 | 0.89354 | 0 | 14.0238 | 14.6163 | 6.444 | 54.1769 | 0.26979 |  | 6.05 | 258 |  | 382 | 1608 | 1422.8 | 11.5174 | 32.4607 | 902.4 | 71.4096 | 122 | 92 | 44 | 873 | 583 | 1456 | 1456 | 0.4327 | 0.59959 | 15.9452 | 16.6189 | 4.092 | 58.908 | 0.28212 | 6.05 | 6.16 | 148 | 382 | 648 | 732.3979 | -13.0244 | 61.2565 | 557.199 | 73.4386 | 92 | 80 | 12 | 308 | 275 | 583 | 583 | 0.36415 | 0.5283 | 11.2511 | 11.7265 | 6.708 | 67.292 | 0.17426 | 6.16 | 6.28 | 218 | 648 | 1412 | 1129.6 | 20 | 42.9319 | 888.8 | 75.4725 | 80 | 61 | 12 | 120 | 155 | 275 | 275 | 0.46929 | 0.43636 | 11.272 | 11.7483 | 14.9252 | 43.5748 | 0.26961 | 6.28 | 6.33 | 336 | 1412 | 1608 | 2245.0323 | -39.6164 | 12.0419 | 1828.5161 | 81.6244 | Sampling date | MM/DD/YY | 1998-11-10 | 1998-11-10 | 1998-11-10 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-11-10 | 1998-11-10 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-11-23 | 1998-11-23 | 1998-11-23 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-11-23 | 1998-11-23 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-12-07 | 1998-12-07 | 1998-12-07 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-12-07 | 1998-12-07 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-12-21 | 1998-12-21 | 1998-12-21 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-12-21 | 1998-12-21 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-01-04 | 1999-01-04 | 1999-01-04 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-01-04 | 1999-01-04 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-01-04 | 1999-01-04 | 1999-01-04 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-01-04 | 1999-01-04 | --- | --- | --- | --- | Engineering Fee Factor (% of construction costs) | 19
Phone Number |  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Negative | Number of parallel pressure vessels in stage 1, Nv-s(1) | 36 | Fluoride (mg/L) | 0.3 |  |  |  | 1998-11-09 | 6:30 | 27839.3 | 23.8 | 123 | 62 | 31.469 | 0 | 1302 | 155 |  | 1457 | 1457 | 0.89362 | 0 | 14.0346 | 14.5413 | 5.512 | 55.519 | 0.26192 | 7.02 | 5.95 | 262 | 356 | 368 | 1621 | 1258.4 | 22.3689 | 28.8043 | 813.2 | 67.7816 | 123 | 92 | 45 | 870 | 587 | 1457 | 1457 | 0.43376 | 0.59712 | 15.8904 | 16.4642 | 3.7781 | 58.7219 | 0.28038 | 5.95 | 6.09 | 151 | 368 | 652 | 689.6184 | -5.7697 | 58.9674 | 528.8092 | 71.4453 | 92 | 81 | 12 | 311 | 276 | 587 | 587 | 0.36628 | 0.52981 | 11.3607 | 11.7709 | 6.6601 | 67.8399 | 0.17351 | 6.09 | 6.19 | 226 | 652 | 1426 | 1132.0217 | 20.6156 | 38.587 | 892.0109 | 74.664 | 81 | 62 | 12 | 121 | 155 | 276 | 276 | 0.47038 | 0.43841 | 11.3659 | 11.7763 | 15.2657 | 44.2343 | 0.26623 | 6.19 | 6.26 | 328 | 1426 | 1621 | 2283.1484 | -40.8481 | 10.8696 | 1854.5742 | 82.314 | Sampling time | hh:mm | 13:15 | 13:28 | 13:40 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 13:21 | 13:28 | --- | --- | --- | --- | Sampling time | hh:mm | 6:44 | 6:56 | 7:07 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 6:49 | 6:56 | --- | --- | --- | --- | Sampling time | hh:mm | 7:08 | 7:25 | 7:32 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 7:16 | 7:25 | --- | --- | --- | --- | Sampling time | hh:mm | 9:07 | 9:21 | 9:32 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 9:13 | 9:21 | --- | --- | --- | --- | Sampling time | hh:mm | 9:37 | 9:59 | 10:21 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 9:46 | 9:59 | --- | --- | --- | --- | Sampling time | hh:mm | 9:37 | 9:59 | 10:21 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 9:46 | 9:59 | --- | --- | --- | --- | 1998 ENR Construction Cost Index (CCI base year 1913) | 5895.11
FAX Number |  |  |  | Number of parallel pressure vessels in stage 2, Nv-s(2) | 18 | Phosphate (mg/L) | 0.05mg/L as PO4 |  |  |  | 1998-11-10 | 0:13 | 27851.1 | 22.8 | 121.2 | 59 | 31.059 | 0 | 1295 | 152 |  | 1447 | 1447 | 0.89496 | 0 | 13.9591 | 14.897 | 8.4684 | 50.5726 | 0.29457 |  | 5.93 | 241 |  | 402 | 1724 | 1773.6776 | -2.8815 | 40.0498 | 1087.8388 | 77.846 | 121.2 | 90 | 45 | 864 | 583 | 1447 | 1447 | 0.43079 | 0.5971 | 15.7808 | 16.8411 | 4.3351 | 56.2649 | 0.29932 | 5.93 | 6.14 | 153 | 402 | 723 | 771.0154 | -6.6411 | 61.9403 | 586.5077 | 73.9134 | 90 | 78 | 11 | 310 | 273 | 583 | 583 | 0.3633 | 0.53173 | 11.3242 | 12.0851 | 8.4816 | 64.5184 | 0.18731 | 6.14 | 6.28 | 182 | 723 | 1316 | 1337.3223 | -1.6202 | 54.7264 | 1030.1612 | 82.3329 | 78 | 59 | 11 | 121 | 152 | 273 | 273 | 0.46383 | 0.44322 | 11.3659 | 12.1296 | 13.9942 | 43.5058 | 0.27881 | 6.28 | 6.29 | 315 | 1316 | 1724 | 2112.8487 | -22.555 | 21.6418 | 1714.4243 | 81.6265 | Operation time | hh.hh | 27864.1 | 27864 | 27864.5 | --- | --- | --- | --- | --- | Operation time | hh.hh | 27864.2 | 27864.3 | --- | --- | --- | --- | Operation time | hh.hh | 28126.3 | 28126.5 | 28126.6 | --- | --- | --- | --- | --- | Operation time | hh.hh | 28126.3 | 28126.5 | --- | --- | --- | --- | Operation time | hh.hh | 28378.7 | 28378.95 | 28379.1 | --- | --- | --- | --- | --- | Operation time | hh.hh | 28378.8 | 28378.95 | --- | --- | --- | --- | Operation time | hh.hh | 28614.3 | 28614.5 | 28614.7 | --- | --- | --- | --- | --- | Operation time | hh.hh | 28614.4 | 28614.5 | --- | --- | --- | --- | Operation time | hh.hh | 28909.9 | 28910.2 | 28910.6 | --- | --- | --- | --- | --- | Operation time | hh.hh | 28910 | 28910.2 | --- | --- | --- | --- | Operation time | hh.hh | 28909.9 | 28910.2 | 28910.6 | --- | --- | --- | --- | --- | Operation time | hh.hh | 28910 | 28910.2 | --- | --- | --- | --- | 1998 Producers Price Index (PPI base year 1967 = 100) | 123.9
E-Mail Address (optional) |  | Design Parameters |  | Number of parallel pressure vessels in stage 3, Nv-s(3) | 7 | Sulfate (mg/L) | 20 |  |  |  | 1998-11-11 | 1:12 | 27870.2 | 22.2 | 122 | 60 | 30.2891 | 0 | 1299 | 155 |  | 1454 | 1454 | 0.8934 | 0 | 14.0022 | 15.2104 | 6.3841 | 54.3268 | 0.27998 |  | 6.23 | 270 |  | 393 | 1616 | 1423.8194 | 11.8924 | 31.2977 | 908.4097 | 70.2777 | 122 | 90 | 43 | 870 | 584 | 1454 | 1454 | 0.43249 | 0.59835 | 15.8904 | 17.2615 | 3.891 | 59.109 | 0.29203 | 6.23 | 6.4 | 170 | 393 | 665 | 725.2089 | -9.054 | 56.743 | 559.1045 | 69.5942 | 90 | 79 | 12 | 310 | 274 | 584 | 584 | 0.36415 | 0.53082 | 11.3242 | 12.3013 | 6.7168 | 65.7832 | 0.187 | 6.4 | 6.46 | 236 | 665 | 1221 | 1150.365 | 5.785 | 39.9491 | 907.6825 | 73.9997 | 79 | 60 | 12 | 120 | 155 | 275 | 275 | 0.46929 | 0.43636 | 11.272 | 12.2446 | 11.5268 | 45.9732 | 0.26634 | 6.46 | 6.47 | 390 | 1221 | 1616 | 1864.3548 | -15.3685 | 0.76336 | 1542.6774 | 74.7193 | pH | --- | 6.43 | 6.24 | 6.48 | --- | --- | --- | --- | --- | pH | --- | 6.19 | 6.24 | --- | --- | --- | --- | pH | --- | 6.21 | 6.18 | 6.2 | --- | --- | --- | --- | --- | pH | --- | 6.02 | 6.18 | --- | --- | --- | --- | pH | --- | 6.15 | 6.21 | 6.23 | --- | --- | --- | --- | --- | pH | --- | 6.08 | 6.21 | --- | --- | --- | --- | pH | --- | 6.21 | 6.1 | 6.25 | --- | --- | --- | --- | --- | pH | --- | 6.15 | 6.1 | --- | --- | --- | --- | pH | --- | 6.37 | 6.3 | 6.27 | --- | --- | --- | --- | --- | pH | --- | 6.23 | 6.3 | --- | --- | --- | --- | pH | --- | 6.37 | 6.3 | 6.27 | --- | --- | --- | --- | --- | pH | --- | 6.23 | 6.3 | --- | --- | --- | --- | Labor Rate + Fringe ($/work-hour) | 24.39
|  | Element size (e.g., 2.5" x 40", 4" x 40", etc.) | 8" X 40" | Permeate flow rate per element, Qp-e (gpm) | 3.8021 | Calcium (mg/L) | 82 |  |  |  | 1998-11-12 | 0:18 | 27893.2 | 22.9 | 121.8 | 59 | 30.8791 | 0 | 1301 | 154 |  | 1455 | 1455 | 0.89416 | 0 | 14.0238 | 14.9219 | 8.5674 | 50.9535 | 0.29285 |  | 6.02 | 231 |  | 395 | 1670 | 1780.4805 | -6.6156 | 41.519 | 1087.7403 | 78.7633 | 121.8 | 91 | 44 | 871 | 584 | 1455 | 1455 | 0.4327 | 0.59863 | 15.9087 | 16.9275 | 4.2246 | 58.1754 | 0.29097 | 6.02 | 6.22 | 153 | 395 | 703 | 755.9281 | -7.5289 | 61.2658 | 575.464 | 73.4128 | 91 | 79 | 12 | 310 | 274 | 584 | 584 | 0.36415 | 0.53082 | 11.3242 | 12.0494 | 8.1416 | 64.8584 | 0.18578 | 6.22 | 6.33 | 183 | 703 | 1272 | 1291.3212 | -1.519 | 53.6709 | 997.1606 | 81.6479 | 79 | 59 | 12 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.9939 | 13.243 | 43.757 | 0.2741 | 6.33 | 6.32 | 319 | 1272 | 1670 | 2014.5974 | -20.6346 | 19.2405 | 1643.2987 | 80.5878 | Temperature | oC | 24.8 | 25 | 25.2 | --- | --- | --- | --- | --- | Temperature | oC | 24.8 | 25 | --- | --- | --- | --- | Temperature | oC | 24.4 | 24.5 | 24.5 | --- | --- | --- | --- | --- | Temperature | oC | 24.4 | 24.5 | --- | --- | --- | --- | Temperature | oC | 24.4 | 23.9 | 23.9 | --- | --- | --- | --- | --- | Temperature | oC | 23.6 | 23.9 | --- | --- | --- | --- | Temperature | oC | 24.7 | 24.4 | 24.6 | --- | --- | --- | --- | --- | Temperature | oC | 24.4 | 24.4 | --- | --- | --- | --- | Temperature | oC | 23.4 | 23.2 | 23 | --- | --- | --- | --- | --- | Temperature | oC | 23 | 23.2 | --- | --- | --- | --- | Temperature | oC | 23.4 | 23.2 | 23 | --- | --- | --- | --- | --- | Temperature | oC | 23 | 23.2 | --- | --- | --- | --- | Labor Overhead Factor (% of labor) | 10
Technical ICR Contact Person |  | Active membrane area of membrane element used, A (ft2) | 365 | Permeate flow rate per pressure vessel, Qp-v (gpm) | 22.8125 | Barium (mg/L) | 0.008 |  |  |  | 1998-11-13 | 0:01 | 27916.9 | 21.9 | 121.8 | 59 | 30.8791 | 0 | 1294 | 167 | X | 1461 | 1461 | 0.88569 | 0 | 13.9483 | 15.2869 | 5.9953 | 53.5256 | 0.2856 |  | 5.98 | 273 |  | 396 | 1662 | 1349.0659 | 18.8288 | 31.0606 | 872.5329 | 68.7118 | 121.8 | 90 | 44 | 870 | 591 | 1461 | 1461 | 0.43546 | 0.59548 | 15.8904 | 17.4153 | 4.1318 | 57.7682 | 0.30147 | 5.98 | 6.12 | 158 | 396 | 704 | 746.3553 | -6.0164 | 60.101 | 571.1777 | 72.3379 | 90 | 79 | 12 | 305 | 286 | 591 | 591 | 0.37222 | 0.51607 | 11.1416 | 12.2107 | 7.3901 | 65.1099 | 0.18754 | 6.12 | 6.2 | 222 | 704 | 1270 | 1218.021 | 4.0928 | 43.9394 | 961.0105 | 76.8993 | 79 | 59 | 12 | 119 | 167 | 286 | 286 | 0.49439 | 0.41608 | 11.1781 | 12.2508 | 12.7084 | 44.2916 | 0.27659 | 6.2 | 6.23 | 333 | 1270 | 1662 | 1937.6826 | -16.5874 | 15.9091 | 1603.8413 | 79.2373 | Alkalinity | mg/L as CaCO3 | 132 | 116 | 250 | -20.381 | 108.1524 | -13.7931 | 55.8133 | -136.5026 | Alkalinity | mg/L as CaCO3 | 73 | 116 | 180.2768 | 37.069 | 148.1384 | 50.7218 | Alkalinity | mg/L as CaCO3 | 112 | 86 | 140 | -124.3636 | 188.8312 | -30.2326 | -6.7314 | 1763.8452 | Alkalinity | mg/L as CaCO3 | 73 | 86 | 105.7249 | 15.1163 | 95.8625 | 23.8492 | Alkalinity | mg/L as CaCO3 | 126 | 112 | 180 | -1.2727 | 100.7071 | -12.5 | 62.2036 | -102.5607 | Alkalinity | mg/L as CaCO3 | 80 | 112 | 159.6991 | 28.5714 | 135.8496 | 41.1113 | Alkalinity | mg/L as CaCO3 | 122 | 110 | 200 | 12.9091 | 93.5455 | -10.9091 | 67.2053 | -81.5333 | Alkalinity | mg/L as CaCO3 | 79 | 110 | 156.4467 | 28.1818 | 133.2234 | 40.7011 | Alkalinity | mg/L as CaCO3 | 148 | 126 | 180 | -52 | 128.8889 | -17.4603 | 47.8086 | -209.5677 | Alkalinity | mg/L as CaCO3 | 90 | 126 | 179.7846 | 28.5714 | 152.8923 | 41.135 | Alkalinity | mg/L as CaCO3 | 142 | 120 | 180 | -58 | 132.2222 | -18.3333 | 41.8086 | -239.643 | Alkalinity | mg/L as CaCO3 | 90 | 120 | 164.8205 | 25 | 142.4103 | 36.8023 | Electric Rate ($/kW-h) | 0.05
Mailing Address |  | Design flux, FW (gfd) | 30 | Permeate flow rate from stage 1, Qp-s(1) (gpm) | 821.25 | Strontium (mg/L) | 0.6 |  |  |  | 1998-11-15 | 10:15 | 27947.5 | 23.1 | 104 | 52 | 29.1091 | 0 | 1300 | 156 |  | 1456 | 1456 | 0.89286 | 0 | 14.013 | 14.8225 | 6.5617 | 42.3292 | 0.35017 |  | 5.95 | 248 |  | 375 | 1375 | 1433.3333 | -4.2424 | 33.8667 | 904.1667 | 72.5714 | 104 | 83 | 41 | 872 | 584 | 1456 | 1456 | 0.43291 | 0.5989 | 15.9269 | 16.847 | 3.7027 | 48.7973 | 0.34525 | 5.95 | 6.1 | 163 | 375 | 632 | 691.5479 | -9.4221 | 56.5333 | 533.274 | 69.4341 | 83 | 71 | 12 | 308 | 276 | 584 | 584 | 0.365 | 0.5274 | 11.2511 | 11.9011 | 6.6993 | 58.3007 | 0.20413 | 6.1 | 6.19 | 202 | 632 | 1185 | 1111.8551 | 6.1726 | 46.1333 | 871.9275 | 76.8329 | 71 | 52 | 12 | 120 | 156 | 276 | 276 | 0.47147 | 0.43478 | 11.272 | 11.9232 | 11.8662 | 37.6338 | 0.31682 | 6.19 | 6.28 | 328 | 1185 | 1375 | 1844.2308 | -34.1259 | 12.5333 | 1514.6154 | 78.3443 | Total dissolved solids | mg/L | 280 | 552 | 3200 | 2870.4762 | 10.2976 | 49.2754 | 1575.1731 | 82.2242 | Total dissolved solids | mg/L | 182 | 552 | 1105.0796 | 67.029 | 828.5398 | 78.0336 | Total dissolved solids | mg/L | 256 | 576 | 3184 | 3165.0909 | 0.59388 | 55.5556 | 1717.3095 | 85.093 | Total dissolved solids | mg/L | 162 | 576 | 1204.1626 | 71.875 | 890.0813 | 81.7994 | Total dissolved solids | mg/L | 306 | 524 | 3184 | 2287.8182 | 28.1464 | 41.6031 | 1299.4016 | 76.4507 | Total dissolved solids | mg/L | 204 | 524 | 1000.9915 | 61.0687 | 762.4957 | 73.2458 | Total dissolved solids | mg/L | 300 | 548 | 2996 | 2554.5455 | 14.7348 | 45.2555 | 1432.4235 | 79.0565 | Total dissolved solids | mg/L | 208 | 548 | 1057.4158 | 62.0438 | 802.7079 | 74.0877 | Total dissolved solids | mg/L | 304 | 508 | 3008 | 2158.5455 | 28.2398 | 40.1575 | 1233.0474 | 75.3456 | Total dissolved solids | mg/L | 204 | 508 | 962.1812 | 59.8425 | 735.0906 | 72.2483 | Total dissolved solids | mg/L | 278 | 488 | 2996 | 2187.0909 | 26.9996 | 43.0328 | 1234.3724 | 77.4784 | Total dissolved solids | mg/L | 198 | 488 | 921.265 | 59.4262 | 704.6325 | 71.9002 | Fuel Oil Rate ($/gal) | 0.43
|  | Net driving pressure at the design flux, NDP (psi) | 125 | Permeate flow rate from stage 2, Qp-s(2) (gpm) | 410.625 | Reactive silica (mg/L as SiO2) | 18 |  |  |  | 1998-11-16 | 6:15 | 27967.5 | 22.9 | 105 | 53 | 29.6991 | 0 | 1300 | 154 |  | 1454 | 1454 | 0.89409 | 0 | 14.013 | 14.9104 | 7.0481 | 42.2528 | 0.35289 | 6.95 | 5.96 | 246 | 351 | 381 | 1318 | 1520.6104 | -15.3726 | 35.4331 | 950.8052 | 74.1272 | 105 | 84 | 42 | 873 | 581 | 1454 | 1454 | 0.43185 | 0.60041 | 15.9452 | 16.9663 | 3.9054 | 48.5946 | 0.34914 | 5.96 | 6.14 | 158 | 381 | 642 | 716.0757 | -11.5383 | 58.5302 | 548.5379 | 71.1962 | 84 | 72 | 12 | 307 | 274 | 581 | 581 | 0.36288 | 0.5284 | 11.2146 | 11.9328 | 6.9274 | 59.0726 | 0.202 | 6.14 | 6.23 | 198 | 642 | 1196 | 1139.4745 | 4.7262 | 48.0315 | 890.7372 | 77.7712 | 72 | 53 | 12 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.9939 | 12.2842 | 38.2158 | 0.31385 | 6.23 | 6.31 | 312 | 1196 | 1318 | 1884.8312 | -43.0069 | 18.1102 | 1540.4156 | 79.7457 | Total hardness | mg/L as CaCO3 | 156 | 304 | 1900 | 1565.5238 | 17.604 | 48.6842 | 860.7265 | 81.8758 | Total hardness | mg/L as CaCO3 | 89 | 304 | 625.3841 | 70.7237 | 464.692 | 80.8475 | Total hardness | mg/L as CaCO3 | 152 | 304 | 1860 | 1533.8182 | 17.5367 | 50 | 846.122 | 82.0357 | Total hardness | mg/L as CaCO3 | 88 | 304 | 631.737 | 71.0526 | 467.8685 | 81.1913 | Total hardness | mg/L as CaCO3 | 152 | 302 | 1890 | 1515.6364 | 19.8076 | 49.6689 | 835.5332 | 81.808 | Total hardness | mg/L as CaCO3 | 96 | 302 | 609.0632 | 68.2119 | 455.5316 | 78.9257 | Total hardness | mg/L as CaCO3 | 154 | 276 | 1810 | 1263.0909 | 30.216 | 44.2029 | 711.0793 | 78.3428 | Total hardness | mg/L as CaCO3 | 100 | 276 | 539.6976 | 63.7681 | 407.8488 | 75.4811 | Total hardness | mg/L as CaCO3 | 192 | 324 | 1810 | 1392 | 23.0939 | 40.7407 | 793.1483 | 75.7927 | Total hardness | mg/L as CaCO3 | 128 | 324 | 616.8274 | 60.4938 | 470.4137 | 72.7899 | Total hardness | mg/L as CaCO3 | 176 | 304 | 1910 | 1339.6364 | 29.862 | 42.1053 | 758.9317 | 76.8095 | Total hardness | mg/L as CaCO3 | 120 | 304 | 578.8991 | 60.5263 | 441.4496 | 72.8168 | Natural Gas Rate ($/ft3) | N/A
Phone Number |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.24 | Permeate flow rate from stage 3, Qp-s(3) (gpm) | 159.6875 | Turbidity (ntu) | <0.5 |  |  |  | 1998-11-17 | 2:35 | 27981.7 | 23.6 | 103.3 | 51 | 29.1091 | 0 | 1300 | 154 |  | 1454 | 1454 | 0.89409 | 0 | 14.013 | 14.6051 | 8.2488 | 39.792 | 0.36704 |  | 5.96 | 245 |  | 403 | 1670 | 1736.7662 | -3.998 | 39.206 | 1069.8831 | 77.1003 | 103.3 | 82 | 41 | 872 | 582 | 1454 | 1454 | 0.43206 | 0.59972 | 15.9269 | 16.5999 | 4.2154 | 47.4346 | 0.34995 | 5.96 | 6.04 | 162 | 403 | 706 | 764.0859 | -8.2275 | 59.8015 | 583.543 | 72.2385 | 82 | 70 | 12 | 308 | 274 | 582 | 582 | 0.3633 | 0.52921 | 11.2511 | 11.7265 | 8.0289 | 55.9711 | 0.20951 | 6.04 | 6.13 | 192 | 706 | 1275 | 1283.781 | -0.68871 | 52.3573 | 994.8905 | 80.7014 | 70 | 51 | 12 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.7483 | 13.2569 | 35.2431 | 0.33335 | 6.13 | 6.1 | 321 | 1275 | 1670 | 2018.3766 | -20.8609 | 20.3474 | 1646.6883 | 80.5063 | Calcium hardness | mg/L as CaCO3 | 114 | 256 | 1470 | 1466.381 | 0.24619 | 55.4688 | 790.1565 | 85.5725 | Calcium hardness | mg/L as CaCO3 | 71 | 256 | 532.5398 | 72.2656 | 394.2699 | 81.992 | Calcium hardness | mg/L as CaCO3 | 118 | 260 | 1410 | 1408.9091 | 0.077369 | 54.6154 | 766.4561 | 84.6045 | Calcium hardness | mg/L as CaCO3 | 86 | 260 | 524.0104 | 66.9231 | 392.0052 | 78.0615 | Calcium hardness | mg/L as CaCO3 | 140 | 244 | 1410 | 1085.4545 | 23.0174 | 42.623 | 613.9164 | 77.1956 | Calcium hardness | mg/L as CaCO3 | 94 | 244 | 467.5897 | 61.4754 | 355.7949 | 73.5803 | Calcium hardness | mg/L as CaCO3 | 142 | 242 | 1380 | 1051.0909 | 23.834 | 41.3223 | 598.6224 | 76.2789 | Calcium hardness | mg/L as CaCO3 | 96 | 242 | 460.7491 | 60.3306 | 351.3746 | 72.6787 | Calcium hardness | mg/L as CaCO3 | 150 | 244 | 1330 | 1004.5455 | 24.4703 | 38.5246 | 578.0905 | 74.0525 | Calcium hardness | mg/L as CaCO3 | 102 | 244 | 456.1504 | 58.1967 | 350.0752 | 70.8634 | Calcium hardness | mg/L as CaCO3 | 144 | 246 | 1430 | 1071.2727 | 25.0858 | 41.4634 | 608.5237 | 76.3362 | Calcium hardness | mg/L as CaCO3 | 102 | 246 | 461.1385 | 58.5366 | 353.5692 | 71.1513 | Current Process Water Rate ($/1000 gal) | 1.8
FAX Number |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | Permeate flow rate from system, Qp-sys (gpm) | 1391.5625 | SDI | 1.0-1.5 |  |  |  | 1998-11-18 | 5:40 | 28007.1 | 22.8 | 103.3 | 51 | 29.6991 | 0 | 1300 | 154 |  | 1454 | 1454 | 0.89409 | 0 | 14.013 | 14.9546 | 6.3694 | 41.0815 | 0.36402 |  | 6.3 | 262 |  | 384 | 1512 | 1413.8701 | 6.4901 | 31.7708 | 898.9351 | 70.8544 | 103.3 | 82 | 42 | 872 | 582 | 1454 | 1454 | 0.43206 | 0.59972 | 15.9269 | 16.9971 | 4.1455 | 46.5045 | 0.36549 | 6.3 | 6.45 | 147 | 384 | 649 | 739.0928 | -13.8818 | 61.7188 | 561.5464 | 73.8223 | 82 | 70 | 12 | 308 | 274 | 582 | 582 | 0.3633 | 0.52921 | 11.2511 | 12.0071 | 6.7793 | 57.2207 | 0.20984 | 6.45 | 6.5 | 215 | 649 | 1138 | 1136.854 | 0.1007 | 44.0104 | 892.927 | 75.9219 | 70 | 51 | 12 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 12.0294 | 10.8251 | 37.6749 | 0.31929 | 6.5 | 6.5 | 359 | 1138 | 1512 | 1745.013 | -15.4109 | 6.5104 | 1441.5065 | 75.0955 | Turbidity | ntu | 0.05 | 0.2 | 18 | 1.4786 | 91.7857 | 75 | 0.76425 | 93.4576 | Turbidity | ntu | 0.07 | 0.2 | 0.39433 | 65 | 0.29716 | 76.4439 | Turbidity | ntu | 0.08 | 0.21 | 24 | 1.2618 | 94.7424 | 61.9048 | 0.67366 | 88.1245 | Turbidity | ntu | 0.07 | 0.21 | 0.42242 | 66.6667 | 0.31621 | 77.8629 | Turbidity | ntu | 0.07 | 0.2 | 20 | 1.2518 | 93.7409 | 65 | 0.6624 | 89.4323 | Turbidity | ntu | 0.07 | 0.2 | 0.39378 | 65 | 0.29689 | 76.4222 | Turbidity | ntu | 0.07 | 0.18 | 17 | 1.07 | 93.7059 | 61.1111 | 0.57228 | 87.7683 | Turbidity | ntu | 0.06 | 0.18 | 0.35979 | 66.6667 | 0.2699 | 77.7693 | Turbidity | ntu | 0.08 | 0.25 | 21 | 1.6255 | 92.2597 | 68 | 0.85421 | 90.6346 | Turbidity | ntu | 0.08 | 0.25 | 0.50398 | 68 | 0.37699 | 78.7794 | Turbidity | ntu | 0.08 | 0.23 | 21 | 1.4436 | 93.1255 | 65.2174 | 0.76312 | 89.5168 | Turbidity | ntu | 0.07 | 0.23 | 0.46904 | 69.5652 | 0.34952 | 79.9726 | Modifications to Existing Plant (% of construction costs) | N/A
E-Mail Address (optional) |  | Maximum flow rate to the element, QI, max (gpm) | 75 | Feed flow rate to system, QF-sys (gpm) | 1546.1806 | MFI |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | 1998-11-19 | 0:34 | 28024.1 | 23.3 | 103.6 | 51 | 29.6991 | 0 | 1301 | 154 |  | 1455 | 1455 | 0.89416 | 0 | 14.0238 | 14.7465 | 5.5897 | 42.0112 | 0.35101 |  | 5.95 | 293 |  | 400 | 1558 | 1303.9416 | 16.3067 | 26.75 | 851.9708 | 65.6091 | 103.6 | 81 | 42 | 873 | 582 | 1455 | 1455 | 0.43227 | 0.6 | 15.9452 | 16.7669 | 3.92 | 46.38 | 0.36151 | 5.95 | 6.07 | 176 | 400 | 689 | 736 | -6.8215 | 56 | 568 | 69.0141 | 81 | 70 | 12 | 308 | 274 | 582 | 582 | 0.3633 | 0.52921 | 11.2511 | 11.831 | 7.2479 | 56.2521 | 0.21032 | 6.07 | 6.13 | 225 | 689 | 1169 | 1210.5766 | -3.5566 | 43.75 | 949.7883 | 76.3105 | 70 | 51 | 12 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.8529 | 10.9501 | 37.5499 | 0.31566 | 6.13 | 6.13 | 381 | 1169 | 1558 | 1783.026 | -14.4433 | 4.75 | 1476.013 | 74.1872 | Ammonia | mg NH3-N / L | 0.392 | 0.415 | 0.896 | 0.61105 | 31.8027 | 5.5422 | 0.50152 | 21.8374 | Total organic carbon | mg/L | BMRL | 8 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | 0.19 | 0.23 | 0.79 | 0.55364 | 29.9194 | 17.3913 | 0.37266 | 49.0157 | Total organic carbon | mg/L | BMRL | 8 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | 0.23 | 0.3 | 0.81 | 0.86636 | -6.9585 | 23.3333 | 0.54898 | 58.1043 | Total organic carbon | mg/L | BMRL | 8 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | 0.16 | 0.18 | 0.58 | 0.34182 | 41.0658 | 11.1111 | 0.25132 | 36.3373 | Total organic carbon | mg/L | BMRL | 8 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | 0.22 | 0.31 | 0.66 | 1.0382 | -57.3003 | 29.0323 | 0.62987 | 65.0724 | Total organic carbon | mg/L | BMRL | 8 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | 0.24 | 0.24 | 0.69 | 0.24 | 65.2174 | 0 | 0.24 | 0 | Total organic carbon | mg/L | BMRL | 8 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | Minimum flow rate to the element, QI, min (gpm) | 72 | Concentrate-waste flow rate from system, QW-sys (gpm) | 154.6181 | MPFI |  | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | 1998-11-20 | 0:37 | 28048.2 | 23.5 | 104 | 51 | 29.1091 | 0 | 1303 | 154 |  | 1457 | 1457 | 0.8943 | 0 | 14.0454 | 14.6821 | 7.6366 | 40.7543 | 0.36026 |  | 5.94 | 255 |  | 401 | 1636 | 1636.3117 | -0.019052 | 36.409 | 1018.6558 | 74.967 | 104 | 82 | 41 | 873 | 584 | 1457 | 1457 | 0.43312 | 0.59918 | 15.9452 | 16.6681 | 4.1239 | 47.8761 | 0.34815 | 5.94 | 6.1 | 165 | 401 | 697 | 753.7877 | -8.1474 | 58.8529 | 577.3938 | 71.4233 | 82 | 71 | 12 | 310 | 274 | 584 | 584 | 0.36415 | 0.53082 | 11.3242 | 11.8376 | 7.8285 | 56.6715 | 0.20888 | 6.1 | 6.19 | 197 | 697 | 1261 | 1262.6934 | -0.13429 | 50.8728 | 979.8467 | 79.8948 | 71 | 51 | 12 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.783 | 12.9929 | 36.0071 | 0.32724 | 6.19 | 6.16 | 326 | 1261 | 1636 | 1989.5714 | -21.6119 | 18.7032 | 1625.2857 | 79.942 | Total organic carbon | mg/L | BMRL | 8 | 76 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.005 | 0.22 | 0.54138 | 97.7273 | 0.38069 | 98.6866 | Total organic carbon | mg/L | 1 | 8 | 71 | 64.6364 | 8.9629 | 87.5 | 32.9661 | 96.9666 | UV254 | cm-1 | 0.018 | 0.235 | 0.56425 | 92.3404 | 0.39963 | 95.4958 | Total organic carbon | mg/L | BMRL | 8 | 69 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.014 | 0.228 | 0.54699 | 93.8596 | 0.38749 | 96.387 | Total organic carbon | mg/L | BMRL | 8 | 13 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.017 | 0.24 | 0.57412 | 92.9167 | 0.40706 | 95.8237 | Total organic carbon | mg/L | BMRL | 8 | 14 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.017 | 0.222 | 0.52827 | 92.3423 | 0.37514 | 95.4683 | Total organic carbon | mg/L | BMRL | 8 | 14 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.014 | 0.222 | 0.53276 | 93.6937 | 0.37738 | 96.2902
Plant Name | Collier Co. North Regional Water Plant | Total width of all membrane envelopes in the element, w (ft) | 63.4 |  |  |  |  | is to list the pretreatment processes used in this particular pilot-scale run. |  |  | 1998-11-21 | 9:00 | 28080.7 | 23.5 | 103.4 | 50 | 29.1091 | 0 | 1301 | 154 |  | 1455 | 1455 | 0.89416 | 0 | 14.0238 | 14.6596 | 5.6419 | 41.9489 | 0.34946 |  | 6.05 | 293 |  | 401 | 1610 | 1313.3896 | 18.423 | 26.9327 | 857.1948 | 65.8187 | 103.4 | 82 | 41 | 874 | 581 | 1455 | 1455 | 0.43206 | 0.60069 | 15.9635 | 16.6872 | 3.9248 | 47.7752 | 0.34929 | 6.05 | 6.16 | 177 | 401 | 690 | 737.9639 | -6.9513 | 55.8603 | 569.4819 | 68.9191 | 82 | 70 | 12 | 307 | 274 | 581 | 581 | 0.36288 | 0.5284 | 11.2146 | 11.723 | 7.411 | 56.589 | 0.20716 | 6.16 | 6.14 | 215 | 690 | 1238 | 1222.208 | 1.2756 | 46.384 | 956.104 | 77.5129 | 70 | 50 | 12 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.783 | 12.2703 | 35.7297 | 0.32978 | 6.14 | 6.13 | 355 | 1238 | 1610 | 1926.0519 | -19.6306 | 11.4713 | 1582.026 | 77.5604 | UV254 | cm-1 | BMRL | 0.22 | 2.02 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 2.75 | --- | --- | --- | --- | UV254 | cm-1 | 0.016 | 0.235 | 2.16 | 2.0069 | 7.0875 | 93.1915 | 1.0161 | 98.4253 | SUVA | L/(mg*m) | NR | 2.9375 | --- | --- | --- | --- | UV254 | cm-1 | 0.016 | 0.228 | 2.06 | 1.9433 | 5.6664 | 92.9825 | 0.98206 | 98.3708 | SUVA | L/(mg*m) | NR | 2.85 | --- | --- | --- | --- | UV254 | cm-1 | 0.032 | 0.24 | 2.22 | 1.9229 | 13.3825 | 86.6667 | 0.98177 | 96.7406 | SUVA | L/(mg*m) | NR | 3 | --- | --- | --- | --- | UV254 | cm-1 | 0.018 | 0.222 | 2.01 | 1.8725 | 6.8385 | 91.8919 | 0.94705 | 98.0994 | SUVA | L/(mg*m) | NR | 2.775 | --- | --- | --- | --- | UV254 | cm-1 | 0.019 | 0.222 | 2.07 | 1.8645 | 9.9297 | 91.4414 | 0.94349 | 97.9862 | SUVA | L/(mg*m) | NR | 2.775 | --- | --- | --- | ---
Treatment Plant Category | Category II | Feed spacer thickness, T (ft) | 0.0023 | Calculate the Feed Flow Rates at the End of Each Stage | [6 empty] | 1998-11-22 | 10:08 | 28105.6 | 23.8 | 103.5 | 51 | 29.1091 | 0 | 1303 | 154 |  | 1457 | 1457 | 0.8943 | 0 | 14.0454 | 14.5525 | 8.1596 | 39.9812 | 0.36398 |  | 5.98 | 246 |  | 402 | 1639 | 1721.9221 | -5.0593 | 38.806 | 1061.961 | 76.8353 | 103.5 | 82 | 41 | 872 | 585 | 1457 | 1457 | 0.43333 | 0.59849 | 15.9269 | 16.502 | 4.1364 | 47.6136 | 0.34658 | 5.98 | 6.1 | 165 | 402 | 698 | 755.2718 | -8.2051 | 58.9552 | 578.6359 | 71.4847 | 82 | 70 | 12 | 310 | 275 | 585 | 585 | 0.365 | 0.52991 | 11.3242 | 11.7331 | 7.8025 | 56.1975 | 0.20878 | 6.1 | 6.17 | 199 | 698 | 1265 | 1260.5091 | 0.35501 | 50.4975 | 979.2545 | 79.6784 | 70 | 51 | 12 | 121 | 154 | 275 | 275 | 0.4682 | 0.44 | 11.3659 | 11.7763 | 13.1068 | 35.3932 | 0.33273 | 6.17 | 6.15 | 324 | 1265 | 1639 | 2004.3571 | -22.2915 | 19.403 | 1634.6786 | 80.1796 | SUVA | L/(mg*m) | NR | 2.75 | 2.6579 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | 1.6 | 2.9375 | 3.0423 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | 2.85 | 2.9855 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | 3 | 17.0769 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | 2.775 | 14.3571 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | 2.775 | 14.7857 | --- | --- | --- | --- | ---
Process Train Name | Train D | Active membrane area of an equivalent 8" x 40" element (ft2) | 365 | Feed flow rate at the end of stage 1, (QF-s(1))end (gpm) | 861.8056 | [5 empty] | 1998-11-23 | 0:38 | 28120.1 | 23.2 | 103.4 | 51 | 28.5192 | 0 | 1301 | 154 |  | 1455 | 1455 | 0.89416 | 0 | 14.0238 | 14.7902 | 7.4704 | 41.2105 | 0.35889 | 7.04 | 6.05 | 259 | 385 | 402 | 1602 | 1610.0714 | -0.50383 | 35.5721 | 1006.0357 | 74.2554 | 103.4 | 81 | 40 | 877 | 578 | 1455 | 1455 | 0.43142 | 0.60275 | 16.0183 | 16.8936 | 4.0977 | 48.1023 | 0.3512 | 6.05 | 6.2 | 169 | 402 | 686 | 755.5311 | -10.1357 | 57.9602 | 578.7656 | 70.7999 | 81 | 70 | 12 | 305 | 273 | 578 | 578 | 0.36118 | 0.52768 | 11.1416 | 11.7504 | 7.5125 | 55.9875 | 0.20988 | 6.2 | 6.22 | 204 | 686 | 1235 | 1224.4982 | 0.85035 | 49.2537 | 955.2491 | 78.6443 | 70 | 51 | 12 | 119 | 154 | 273 | 273 | 0.46601 | 0.4359 | 11.1781 | 11.7889 | 12.505 | 35.995 | 0.32752 | 6.22 | 6.21 | 333 | 1235 | 1602 | 1932 | -20.5993 | 17.1642 | 1583.5 | 78.9706 | Bromide | mg/L | 170 | 160 | --- | 74.7619 | --- | -6.25 | 122.3833 | -38.9078 | [8 empty] | Bromide | mg/L | 180 | 180 | --- | 180 | --- | 0 | 180 | 0 | [8 empty] | Bromide | mg/L | 160 | 160 | --- | 160 | --- | 0 | 160 | 0 | [8 empty] | Bromide | mg/L | 170 | 160 | --- | 79.0909 | --- | -6.25 | 124.3378 | -36.7244 | [8 empty] | Bromide | mg/L | 160 | 160 | --- | 160 | --- | 0 | 160 | 0 | [8 empty] | Bromide | mg/L | 160 | 160 | --- | 160 | --- | 0 | 160 | 0
ICR Treatment Plant Identification Number | 1092 | Purchase price for an equivalent 8" x 40 " element ($) | 800 | Feed flow rate at the end of stage 2, (QF-s(2))end (gpm) | 382.7431 | [5 empty] | 1998-11-24 | 5:30 | 28133.8 | 23.3 | 103 | 51 | 28.5192 | 0 | 1300 | 158 |  | 1458 | 1458 | 0.89163 | 0 | 14.013 | 14.7352 | 7.8754 | 40.6054 | 0.36289 |  | 6.02 | 242 |  | 396 | 1622 | 1663.0886 | -2.5332 | 38.8889 | 1029.5443 | 76.4945 | 103 | 80 | 40 | 874 | 584 | 1458 | 1458 | 0.43333 | 0.59945 | 15.9635 | 16.7861 | 4.1609 | 47.3391 | 0.35459 | 6.02 | 6.13 | 158 | 396 | 692 | 752.1849 | -8.6972 | 60.101 | 574.0925 | 72.4783 | 80 | 70 | 12 | 307 | 277 | 584 | 584 | 0.36543 | 0.52568 | 11.2146 | 11.7925 | 7.7397 | 55.2603 | 0.2134 | 6.13 | 6.21 | 194 | 692 | 1262 | 1243.935 | 1.4315 | 51.0101 | 967.9675 | 79.958 | 70 | 51 | 12 | 119 | 158 | 277 | 277 | 0.47475 | 0.4296 | 11.1781 | 11.7541 | 12.8297 | 35.6703 | 0.32952 | 6.21 | 6.28 | 330 | 1262 | 1622 | 1963.9494 | -21.082 | 16.6667 | 1612.9747 | 79.5409 | SDS-Cl2 dose | mg/L | 18.5 | 28 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 19 | 28 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 19 | 28 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 19 | 28 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 19 | 28 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 19 | 28 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection
PWSID Number of Plant (if assigned) | Fl5114069 |  |  | Feed flow rate at the end of stage 3, (QF-s(3))end (gpm) | 181.2326 | [5 empty] | 1998-11-25 | 6:00 | 28153.7 | 22.5 | 102.9 | 50 | 28.5192 | 0 | 1305 | 144 |  | 1449 | 1449 | 0.90062 | 0 | 14.0669 | 15.1458 | 7.1906 | 40.7402 | 0.37177 |  | 6.12 | 262 |  | 392 | 1563 | 1570.125 | -0.45585 | 33.1633 | 981.0625 | 73.2943 | 102.9 | 81 | 40 | 875 | 574 | 1449 | 1449 | 0.4293 | 0.60386 | 15.9817 | 17.2075 | 3.7711 | 48.1789 | 0.35716 | 6.12 | 6.2 | 178 | 392 | 588 | 718.2195 | -22.1462 | 54.5918 | 555.1098 | 67.9343 | 81 | 69 | 12 | 310 | 264 | 574 | 574 | 0.35567 | 0.54007 | 11.3242 | 12.1927 | 5.5232 | 57.4768 | 0.21213 | 6.2 | 6.25 | 240 | 588 | 1014 | 996.6364 | 1.7124 | 38.7755 | 792.3182 | 69.7091 | 69 | 50 | 12 | 120 | 144 | 264 | 264 | 0.44528 | 0.45455 | 11.272 | 12.1365 | 8.4292 | 39.0708 | 0.31063 | 6.25 | 6.26 | 419 | 1014 | 1563 | 1509.8333 | 3.4016 | -6.8878 | 1261.9167 | 66.7965 | SDS-Free Cl2 residual | mg/L | 0.15 | 10.5 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.53 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 1.35 | 1.3 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.53 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 0.75 | 10.25 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.53 |  |  |  |  | SDS-Free Cl2 residual | mg/L | NR | NR | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.53 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 1.25 | 4.5 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.53 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 1.25 | 4.5 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.53
Historical Minimum Water Temperature (oC) | 22.7 | Additional Information |  |  |  | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | 1998-11-26 | 6:20 | 28177.7 | 23.2 | 104 | 52 | 29.6991 | 0 | 1296 | 155 |  | 1451 | 1451 | 0.89318 | 0 | 13.9699 | 14.7333 | 6.7348 | 41.566 | 0.35446 |  | 5.99 | 256 |  | 386 | 1610 | 1472.9677 | 8.5113 | 33.6788 | 929.4839 | 72.4578 | 104 | 82 | 42 | 865 | 586 | 1451 | 1451 | 0.43227 | 0.59614 | 15.7991 | 16.6625 | 3.789 | 47.211 | 0.35294 | 5.99 | 6.11 | 168 | 386 | 612 | 707.7918 | -15.6523 | 56.4767 | 546.8959 | 69.2812 | 82 | 70 | 12 | 310 | 276 | 586 | 586 | 0.36585 | 0.52901 | 11.3242 | 11.943 | 5.528 | 58.472 | 0.20425 | 6.11 | 6.25 | 258 | 612 | 1182 | 1009.6087 | 14.5847 | 33.1606 | 810.8043 | 68.1797 | 70 | 52 | 12 | 121 | 155 | 276 | 276 | 0.47038 | 0.43841 | 11.3659 | 11.9871 | 10.9835 | 38.0165 | 0.31531 | 6.25 | 6.29 | 392 | 1182 | 1610 | 1798.7097 | -11.7211 | -1.5544 | 1490.3548 | 73.6975 | SDS-Cl2 demand | mg/L | 18.35 | 17.5 | --- | 10.2548 | --- | -4.8571 | 14.3026 | -28.2985 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 310 |  |  |  |  | SDS-Cl2 demand | mg/L | 17.65 | 26.7 | --- | 99.9227 | --- | 33.8951 | 58.9777 | 70.0734 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 305 |  |  |  |  | SDS-Cl2 demand | mg/L | 18.25 | 17.75 | --- | 13.7045 | --- | -2.8169 | 15.9716 | -14.2656 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 308 |  |  |  |  | SDS-Cl2 demand | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 307 |  |  |  |  | SDS-Cl2 demand | mg/L | 17.75 | 23.5 | --- | 70.0227 | --- | 24.4681 | 43.9364 | 59.6007 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 309 |  |  |  |  | SDS-Cl2 demand | mg/L | 17.75 | 23.5 | --- | 70.0227 | --- | 24.4681 | 43.9364 | 59.6007 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 309
Historical Average Water Temperature (oC) | 25 | Design cross-flow velocity (fps) | 1 | Calculate the Minimum Recycle Flow Rates for Each Stage1 |  | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | 1998-11-28 | 9:15 | 28202.2 | 22.8 | 100.7 | 50 | 27.9292 | 0 | 1300 | 153 |  | 1453 | 1453 | 0.8947 | 0 | 14.013 | 14.9546 | 5.8257 | 41.5951 | 0.35953 |  | 6.17 | 286 |  | 397 | 1423 | 1340.1373 | 5.8231 | 27.9597 | 868.5686 | 67.0723 | 100.7 | 80 | 39 | 869 | 584 | 1453 | 1453 | 0.43227 | 0.59807 | 15.8721 | 16.9386 | 3.1043 | 48.2457 | 0.35109 | 6.17 | 6.36 | 219 | 397 | 662 | 661.8664 | 0.020175 | 44.8363 | 529.4332 | 58.635 | 80 | 68 | 12 | 310 | 274 | 584 | 584 | 0.36415 | 0.53082 | 11.3242 | 12.0851 | 6.8891 | 55.1109 | 0.21929 | 6.36 | 6.41 | 222 | 662 | 1118 | 1159.8102 | -3.7397 | 44.0806 | 910.9051 | 75.6286 | 68 | 50 | 12 | 121 | 153 | 274 | 274 | 0.46601 | 0.44161 | 11.3659 | 12.1296 | 10.5773 | 36.4227 | 0.33302 | 6.41 | 6.4 | 360 | 1118 | 1423 | 1717.4641 | -20.6932 | 9.3199 | 1417.732 | 74.6073 | SDS-Chlorination temp. | oC | 21.1 | 20.9 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 583 |  |  |  |  | SDS-Chlorination temp. | oC | 22.2 | 22.1 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 578 |  |  |  |  | SDS-Chlorination temp. | oC | 20.3 | 20.3 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 585 |  |  |  |  | SDS-Chlorination temp. | oC | NR | NR | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 581 |  |  |  |  | SDS-Chlorination temp. | oC | 23.3 | 23.3 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 584 |  |  |  |  | SDS-Chlorination temp. | oC | 23.4 | 23.4 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 584
State Approved Plant Capacity (MGD) | 12 MGD | Required influent flow to permeate flow rate ratio, QI:Qp | 5:1 | Minimum recycle flow rate for stage 1, (QR-s(1))min (gpm) | 1730.1944 | [5 empty] | 1998-11-29 | 9:30 | 28226.3 | 23.1 | 101 | 51 | 27.9292 | 0 | 1300 | 154 |  | 1454 | 1454 | 0.89409 | 0 | 14.013 | 14.8225 | 6.1083 | 41.9625 | 0.35323 |  | 6.05 | 268 |  | 385 | 1610 | 1372.6623 | 14.7415 | 30.3896 | 878.8312 | 69.505 | 101 | 80 | 39 | 872 | 582 | 1454 | 1454 | 0.43206 | 0.59972 | 15.9269 | 16.847 | 3.6207 | 47.8793 | 0.35186 | 6.05 | 6.16 | 178 | 385 | 686 | 695.1443 | -1.333 | 53.7662 | 540.0722 | 67.0414 | 80 | 67 | 12 | 308 | 274 | 582 | 582 | 0.3633 | 0.52921 | 11.2511 | 11.9011 | 7.2635 | 54.2365 | 0.21943 | 6.16 | 6.27 | 221 | 686 | 1228 | 1208.7007 | 1.5716 | 42.5974 | 947.3504 | 76.6718 | 67 | 51 | 12 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.9232 | 12.2286 | 34.7714 | 0.3429 | 6.27 | 6.31 | 348 | 1228 | 1610 | 1913.7143 | -18.8642 | 9.6104 | 1570.8571 | 77.8465 | SDS-Chlorination pH | --- | 8.24 | 8.27 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.4 | 8.45 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.28 | 8.2 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | NR | NR | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.3 | 8.09 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.36 | 8.14 | --- | --- | --- | --- | --- | ---
|  | Maximum element recovery (%) | 20 | Minimum recycle flow rate for stage 2, (QR-s(2))min (gpm) | 913.2569 | [5 empty] | 1998-12-01 | 1:30 | 28255.6 | 23.6 | 101.3 | 50 | 27.9292 | 0 | 1299 | 154 |  | 1453 | 1453 | 0.89401 | 0 | 14.0022 | 14.5938 | 5.1132 | 42.6076 | 0.34252 |  | 6.01 | 298 |  | 396 | 1567 | 1222.6364 | 21.976 | 24.7475 | 809.3182 | 63.1789 | 101.3 | 79 | 39 | 871 | 582 | 1453 | 1453 | 0.43185 | 0.59945 | 15.9087 | 16.5808 | 3.7064 | 47.4436 | 0.34948 | 6.01 | 6.11 | 184 | 396 | 687 | 713.2715 | -3.8241 | 53.5354 | 554.6357 | 66.8251 | 79 | 68 | 12 | 308 | 274 | 582 | 582 | 0.3633 | 0.52921 | 11.2511 | 11.7265 | 7.5759 | 53.9241 | 0.21746 | 6.11 | 6.22 | 202 | 687 | 1227 | 1232.1825 | -0.42237 | 48.9899 | 959.5912 | 78.9494 | 68 | 50 | 12 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.7483 | 12.3953 | 34.6047 | 0.3395 | 6.22 | 6.2 | 335 | 1227 | 1567 | 1922.0649 | -22.6589 | 15.404 | 1574.5325 | 78.7238 | SDS-Incubation time | hours | 43.5 | 43.5 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 47.5 | 47.5 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 46.25 | 46.25 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | NR | NR | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 44 | 44 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 44 | 44 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters
|  | Variability of design flux (%) | 15 +/- | Minimum recycle flow rate for stage 3, (QR-s(3))min (gpm) | 322.7674 | [5 empty] | 1998-12-02 | 1:22 | 28278.9 | 23.2 | 101.4 | 49 | 27.9292 | 0 | 1302 | 155 |  | 1457 | 1457 | 0.89362 | 0 | 14.0346 | 14.8015 | 7.956 | 39.3148 | 0.37649 |  | 5.99 | 252 |  | 405 | 1620 | 1690.2 | -4.3333 | 37.7778 | 1047.6 | 75.945 | 101.4 | 79 | 39 | 874 | 583 | 1457 | 1457 | 0.43291 | 0.59986 | 15.9635 | 16.8358 | 4.1115 | 47.0885 | 0.35754 | 5.99 | 6.19 | 170 | 405 | 695 | 757.2985 | -8.9638 | 58.0247 | 581.1492 | 70.7476 | 79 | 68 | 12 | 308 | 275 | 583 | 583 | 0.36415 | 0.5283 | 11.2511 | 11.866 | 7.722 | 53.778 | 0.22065 | 6.19 | 6.19 | 200 | 695 | 1274 | 1249.4 | 1.9309 | 50.6173 | 972.2 | 79.4281 | 68 | 49 | 12 | 120 | 155 | 275 | 275 | 0.46929 | 0.43636 | 11.272 | 11.888 | 13.1635 | 33.3365 | 0.35661 | 6.19 | 6.17 | 325 | 1274 | 1620 | 2008.7097 | -23.9944 | 19.7531 | 1641.3548 | 80.1993 | SDS-TOX | mg Cl- /L | BMRL | 455 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-32 | CI-s2-32 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | 88 | 1000 | --- | 8378.9091 | --- | 91.2 | 4252.732 | 97.9307 | Parameter | Units | Cp-s2-34 | CI-s2-34 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | 58 | 460 | --- | 3712.5455 | --- | 87.3913 | 1889.869 | 96.931 | Parameter | Units | Cp-s2-36 | CI-s2-36 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-38 | CI-s2-38 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-40 | CI-s2-40 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-40 (dup) | CI-s2-40 (dup) | CC(calc) | RF (%) | CB | RB (%)
|  | Rejection of reference solute and conditions of test | 80 | 1: A negative minimum recycle flow rate indicates that recycle is not required to | [6 empty] | 1998-12-03 | 0:08 | 28301.7 | 21.3 | 102 | 49 | 28.5192 | 0 | 1299 | 154 |  | 1453 | 1453 | 0.89401 | 0 | 14.0022 | 15.6205 | 4.4349 | 42.5459 | 0.36714 |  | 5.95 | 316 |  | 401 | 1620 | 1117.9805 | 30.9889 | 21.197 | 759.4903 | 58.3931 | 102 | 80 | 40 | 869 | 584 | 1453 | 1453 | 0.43227 | 0.59807 | 15.8721 | 17.7065 | 3.9938 | 47.0062 | 0.37668 | 5.95 | 6.05 | 172 | 401 | 704 | 741.7551 | -5.3629 | 57.1072 | 571.3776 | 69.8973 | 80 | 68 | 12 | 310 | 274 | 584 | 584 | 0.36415 | 0.53082 | 11.3242 | 12.633 | 7.7972 | 54.2028 | 0.23307 | 6.05 | 6.05 | 206 | 704 | 1238 | 1267.4307 | -2.3773 | 48.6284 | 985.7153 | 79.1015 | 68 | 49 | 12 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 12.5747 | 12.2008 | 34.2992 | 0.36662 | 6.05 | 6.04 | 360 | 1238 | 1620 | 1922.1558 | -18.6516 | 10.2244 | 1580.0779 | 77.2163 | SDS-CHCl3 | mg/L | BMRL | 180 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1998-11-10 | 1998-11-10 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 3 | 230 | --- | 2066.6364 | --- | 98.6957 | 1039.6164 | 99.7114 | Sampling date | MM/DD/YY | 1998-11-23 | 1998-11-23 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 3 | 170 | --- | 1521.1818 | --- | 98.2353 | 764.0003 | 99.6073 | Sampling date | MM/DD/YY | 1998-12-07 | 1998-12-07 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1998-12-21 | 1998-12-21 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1999-01-04 | 1999-01-04 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1999-01-04 | 1999-01-04 | --- | --- | --- | ---
|  | (e.g., solute type and concentration) |  | meet the manufacturer's minimum flow requirement. | [6 empty] | 1998-12-04 | 0:26 | 28310.7 | 22.9 | 101.2 | 49 | 27.3392 | 0 | 1306 | 156 |  | 1462 | 1462 | 0.8933 | 0 | 14.0777 | 14.9792 | 6.3787 | 41.3821 | 0.36197 |  | 6.14 | 278 |  | 401 | 1531 | 1430.7308 | 6.5493 | 30.6733 | 915.8654 | 69.6462 | 101.2 | 80 | 38 | 876 | 586 | 1462 | 1462 | 0.43461 | 0.59918 | 16 | 17.0246 | 3.7919 | 48.8081 | 0.34881 | 6.14 | 6.28 | 184 | 401 | 685 | 725.3891 | -5.8962 | 54.1147 | 563.1945 | 67.3292 | 80 | 68 | 12 | 310 | 276 | 586 | 586 | 0.36585 | 0.52901 | 11.3242 | 12.0494 | 7.3083 | 54.6917 | 0.22031 | 6.28 | 6.32 | 217 | 685 | 1204 | 1210.6522 | -0.55251 | 45.8853 | 947.8261 | 77.1055 | 68 | 49 | 12 | 120 | 156 | 276 | 276 | 0.47147 | 0.43478 | 11.272 | 11.9939 | 11.6723 | 34.8277 | 0.34438 | 6.32 | 6.32 | 361 | 1204 | 1531 | 1852.4615 | -20.9968 | 9.9751 | 1528.2308 | 76.3779 | SDS-BDCM | mg/L | BMRL | 37 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 13:24 | 13:34 | --- | --- | --- | --- | SDS-BDCM | mg/L | 8 | 59 | --- | 471.6364 | --- | 86.4407 | 240.8962 | 96.6791 | Sampling time | hh:mm | 6:52 | 7:01 | --- | --- | --- | --- | SDS-BDCM | mg/L | 5 | 37 | --- | 295.9091 | --- | 86.4865 | 150.8204 | 96.6848 | Sampling time | hh:mm | 7:19 | 7:28 | --- | --- | --- | --- | SDS-BDCM | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 9:16 | 9:26 | --- | --- | --- | --- | SDS-BDCM | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 9:50 | 10:09 | --- | --- | --- | --- | SDS-BDCM | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 9:50 | 10:09 | --- | --- | --- | ---
|  | Variability of rejection of reference solute (%) | 50 +/- | [7 empty] | 1998-12-05 | 4:00 | 28335.1 | 22.7 | 102 | 48 | 27.5192 | 0 | 1298 | 155 |  | 1453 | 1453 | 0.89332 | 0 | 13.9915 | 14.9758 | 4.8759 | 42.605 | 0.3515 |  | 6.09 | 310 |  | 404 | 1536 | 1191.1742 | 22.4496 | 23.2673 | 797.5871 | 61.1328 | 102 | 78 | 39 | 872 | 581 | 1453 | 1453 | 0.43164 | 0.60014 | 15.9269 | 17.0474 | 3.7634 | 47.2366 | 0.36089 | 6.09 | 6.2 | 189 | 404 | 669 | 726.685 | -8.6226 | 53.2178 | 565.3425 | 66.5689 | 78 | 68 | 11 | 307 | 274 | 581 | 581 | 0.36288 | 0.5284 | 11.2146 | 12.0036 | 7.0834 | 54.9166 | 0.21858 | 6.2 | 6.3 | 215 | 669 | 1197 | 1177.6788 | 1.6141 | 46.7822 | 923.3394 | 76.715 | 68 | 48 | 11 | 119 | 155 | 274 | 274 | 0.4682 | 0.43431 | 11.1781 | 11.9645 | 11.5968 | 35.4032 | 0.33795 | 6.3 | 6.3 | 359 | 1197 | 1536 | 1840.3677 | -19.8156 | 11.1386 | 1518.6839 | 76.3611 | SDS-DBCM | mg/L | 0.5 | 10 | --- | 90.9762 | --- | 95 | 45.7358 | 98.9068 | Operation time | hh.hh | 27864.3 | 27864.4 | --- | --- | --- | --- | SDS-DBCM | mg/L | 15 | 12 | --- | -12.2727 | --- | -25 | 1.3002 | -1053.6477 | Operation time | hh.hh | 28126.4 | 28126.5 | --- | --- | --- | --- | SDS-DBCM | mg/L | 12 | 9 | --- | -15.2727 | --- | -33.3333 | -1.6707 | 818.2771 | Operation time | hh.hh | 28378.9 | 28379 | --- | --- | --- | --- | SDS-DBCM | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 28614.4 | 28614.6 | --- | --- | --- | --- | SDS-DBCM | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 28910.1 | 28910.4 | --- | --- | --- | --- | SDS-DBCM | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 28910.1 | 28910.4 | --- | --- | --- | ---
|  | Standard testing recovery (%) | 15 | Calculate the Maximum Recycle Flow Rates for Each Stage | [6 empty] | 1998-12-06 | 9:00 | 28355.1 | 23.1 | 101 | 47 | 27.3392 | 0 | 1301 | 154 |  | 1455 | 1455 | 0.89416 | 0 | 14.0238 | 14.8339 | 5.433 | 41.2278 | 0.3598 |  | 6.05 | 288 |  | 392 | 1612 | 1270.5974 | 21.1788 | 26.5306 | 831.2987 | 65.3554 | 101 | 76 | 38 | 869 | 586 | 1455 | 1455 | 0.43312 | 0.59725 | 15.8721 | 16.7891 | 3.7616 | 46.7384 | 0.35921 | 6.05 | 6.11 | 176 | 392 | 682 | 712.314 | -4.4449 | 55.102 | 552.157 | 68.125 | 76 | 67 | 12 | 311 | 275 | 586 | 586 | 0.36543 | 0.53072 | 11.3607 | 12.017 | 7.2011 | 52.2989 | 0.22978 | 6.11 | 6.23 | 222 | 682 | 1182 | 1202.2182 | -1.7105 | 43.3673 | 942.1091 | 76.4358 | 67 | 47 | 12 | 121 | 154 | 275 | 275 | 0.4682 | 0.44 | 11.3659 | 12.0225 | 11.6164 | 33.3836 | 0.36013 | 6.23 | 6.28 | 348 | 1182 | 1612 | 1837.2857 | -13.9755 | 11.2245 | 1509.6429 | 76.9482 | SDS-CHBr3 | mg/L | 0.9 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 6.19 | 6.4 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | 13 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 6.09 | 6.2 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | 15 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 6.01 | 6.3 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 6.01 | 6.27 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 6.22 | 6.29 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 6.22 | 6.29 | --- | --- | --- | ---
|  | Standard testing pH | 7.5 to 8.5 | Maximum recycle flow rate for stage 1, (QR-s(1))max (gpm) | 1153.8194 | [5 empty] | 1998-12-07 | 6:10 | 28377.5 | 23 | 102.2 | 50 | 27.9292 | 0 | 1300 | 157 |  | 1457 | 1457 | 0.89224 | 0 | 14.013 | 14.8664 | 7.6074 | 40.5634 | 0.3665 | 7.18 | 6.01 | 256 | 392 | 404 | 1606 | 1629.4777 | -1.4619 | 36.6337 | 1016.7389 | 74.8215 | 102.2 | 79 | 39 | 872 | 585 | 1457 | 1457 | 0.43333 | 0.59849 | 15.9269 | 16.8969 | 4.084 | 47.516 | 0.3556 | 6.01 | 6.08 | 170 | 404 | 692 | 752.8 | -8.7861 | 57.9208 | 578.4 | 70.6086 | 79 | 69 | 12 | 308 | 277 | 585 | 585 | 0.36585 | 0.5265 | 11.2511 | 11.9363 | 7.6553 | 54.3447 | 0.21964 | 6.08 | 6.14 | 200 | 692 | 1244 | 1239.0614 | 0.397 | 50.495 | 965.5307 | 79.286 | 69 | 50 | 12 | 120 | 157 | 277 | 277 | 0.47365 | 0.43321 | 11.272 | 11.9585 | 12.7297 | 34.7703 | 0.34393 | 6.14 | 6.16 | 323 | 1244 | 1606 | 1947.949 | -21.292 | 20.0495 | 1595.9745 | 79.7616 | SDS-THM4 | mg/L | 1.4 | 227 | --- | 2149.9714 | --- | 99.3833 | 1075.6318 | 99.8698 | Temperature | oC | 25 | 25 | --- | --- | --- | --- | SDS-THM4 | mg/L | 39 | 301 | --- | 2420.8182 | --- | 87.0432 | 1235.4471 | 96.8432 | Temperature | oC | 24.4 | 24.3 | --- | --- | --- | --- | SDS-THM4 | mg/L | 35 | 216 | --- | 1680.4545 | --- | 83.7963 | 859.7967 | 95.9293 | Temperature | oC | 23.1 | 23.7 | --- | --- | --- | --- | SDS-THM4 | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Temperature | oC | 24.4 | 24.4 | --- | --- | --- | --- | SDS-THM4 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | 0 | #DIV/0! | Temperature | oC | 230 | 22.9 | --- | --- | --- | --- | SDS-THM4 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | 0 | #DIV/0! | Temperature | oC | 23 | 22.9 | --- | --- | --- | ---
|  | Acceptable range of operating pressures | <400psi | Maximum recycle flow rate for stage 2, (QR-s(2))max (gpm) | 625.0694 | [5 empty] | 1998-12-08 | 3:30 | 28393.2 | 22.8 | 101.7 | 48 | 16.1298 | 0 | 1302 | 155 |  | 1457 | 1457 | 0.89362 | 0 | 14.0346 | 14.9776 | 6.448 | 52.2722 | 0.28653 |  | 5.96 | 267 |  | 391 | 1611 | 1432.6 | 11.0739 | 31.7136 | 911.8 | 70.7173 | 101.7 | 80 | 19 | 875 | 582 | 1457 | 1457 | 0.4327 | 0.60055 | 15.9817 | 17.0556 | 3.9063 | 67.9437 | 0.25102 | 5.96 | 6.06 | 168 | 391 | 680 | 726.2663 | -6.8039 | 57.0332 | 558.6332 | 69.9266 | 80 | 68 | 12 | 307 | 275 | 582 | 582 | 0.36373 | 0.52749 | 11.2146 | 11.9681 | 7.5728 | 54.4272 | 0.21989 | 6.06 | 6.09 | 194 | 680 | 1232 | 1222.5527 | 0.76682 | 50.3836 | 951.2764 | 79.6063 | 68 | 48 | 12 | 120 | 155 | 275 | 275 | 0.46929 | 0.43636 | 11.272 | 12.0294 | 12.5948 | 33.4052 | 0.36011 | 6.09 | 6.14 | 324 | 1232 | 1611 | 1934.9677 | -20.1097 | 17.1355 | 1583.4839 | 79.5388 | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 92 | 184 | 288.4689 | 20.6897 | 236.2344 | 61.0556 | SDS-MCAA* | mg/L | BMRL | 6 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 89 | 114 | 141.9304 | -3.4884 | 127.9652 | 30.4498 | SDS-MCAA* | mg/L | BMRL | 4.6 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 77 | 132 | 193.1552 | 31.25 | 162.5776 | 52.638 | SDS-MCAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 95 | 150 | 211.6241 | 13.6364 | 180.812 | 47.4593 | SDS-MCAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 109 | 158 | 213.0582 | 13.4921 | 185.5291 | 41.2491 | SDS-MCAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 110 | 150 | 194.9455 | 8.3333 | 172.4727 | 36.2218
|  | Acceptable range of operating pH values | 2 to 8 | Maximum recycle flow rate for stage 3, (QR-s(3))max (gpm) | 210.6944 | [5 empty] | 1998-12-09 | 6:30 | 28411.5 | 23.1 | 102 | 51 | 27.9292 | 0 | 1300 | 155 |  | 1455 | 1455 | 0.89347 | 0 | 14.013 | 14.8225 | 5.4013 | 43.1695 | 0.34336 |  | 6.05 | 282 |  | 386 | 1612 | 1258.2581 | 21.9443 | 26.943 | 822.129 | 65.6988 | 102 | 80 | 39 | 872 | 583 | 1455 | 1455 | 0.43249 | 0.59931 | 15.9269 | 16.847 | 3.8103 | 48.1897 | 0.3496 | 6.05 | 6.12 | 168 | 386 | 682 | 712.0652 | -4.4084 | 56.4767 | 549.0326 | 69.4007 | 80 | 68 | 12 | 308 | 275 | 583 | 583 | 0.36415 | 0.5283 | 11.2511 | 11.9011 | 7.332 | 54.668 | 0.2177 | 6.12 | 6.23 | 212 | 682 | 1186 | 1208.4 | -1.8887 | 45.0777 | 945.2 | 77.5709 | 68 | 51 | 12 | 120 | 155 | 275 | 275 | 0.46929 | 0.43636 | 11.272 | 11.9232 | 11.3603 | 36.1397 | 0.32992 | 6.23 | 6.28 | 367 | 1186 | 1612 | 1820.0645 | -12.9072 | 4.9223 | 1503.0323 | 75.5827 | SDS-DCAA* | mg/L | BMRL | 76 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 214 | 1092 | 2088.9963 | 61.2319 | 1590.4982 | 86.5451 | SDS-DCAA* | mg/L | 1.4 | 54 | --- | 479.5818 | --- | 97.4074 | 241.6027 | 99.4205 | Total dissolved solids | mg/L | 214 | 1104 | 2098.3223 | 62.8472 | 1601.1612 | 86.6347 | SDS-DCAA* | mg/L | 1.1 | 47 | --- | 418.3727 | --- | 97.6596 | 210.2612 | 99.4768 | Total dissolved solids | mg/L | 232 | 1064 | 1989.1119 | 55.7252 | 1526.556 | 84.8024 | SDS-DCAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 218 | 1024 | 1927.073 | 60.219 | 1475.5365 | 85.2257 | SDS-DCAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 232 | 1032 | 1930.9091 | 54.3307 | 1481.4545 | 84.3397 | SDS-DCAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 246 | 1024 | 1898.1891 | 49.5902 | 1461.0945 | 83.1633
|  | Typical pressure drop across a single element (psi) | 3 to 4 psi | [7 empty] | 1998-12-10 | 0:05 | 28423.6 | 22.2 | 103.3 | 50 | 29.1091 | 0 | 1298 | 153 |  | 1451 | 1451 | 0.89456 | 0 | 13.9915 | 15.1987 | 7.3386 | 40.2023 | 0.37806 |  | 5.96 | 258 |  | 398 | 1595 | 1585.7124 | 0.58229 | 35.1759 | 991.8562 | 73.9882 | 103.3 | 80 | 41 | 867 | 584 | 1451 | 1451 | 0.43185 | 0.59752 | 15.8356 | 17.202 | 3.9202 | 46.7298 | 0.36812 | 5.96 | 6.16 | 173 | 398 | 697 | 732.0325 | -5.0262 | 56.5327 | 565.0163 | 69.3814 | 80 | 69 | 12 | 310 | 274 | 584 | 584 | 0.36415 | 0.53082 | 11.3242 | 12.3013 | 7.7032 | 54.7968 | 0.22449 | 6.16 | 6.19 | 205 | 697 | 1245 | 1253.6423 | -0.69416 | 48.4925 | 975.3212 | 78.9813 | 69 | 50 | 12 | 121 | 153 | 274 | 274 | 0.46601 | 0.44161 | 11.3659 | 12.3467 | 12.824 | 34.676 | 0.35606 | 6.19 | 6.18 | 326 | 1245 | 1595 | 1971.7908 | -23.6233 | 18.0905 | 1608.3954 | 79.7314 | SDS-TCAA* | mg/L | BMRL | 79 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 111 | 630 | 1219.3407 | 63.4868 | 924.6703 | 87.9957 | SDS-TCAA* | mg/L | BMRL | 54 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 113 | 670 | 1292.2894 | 62.8289 | 981.1447 | 88.4828 | SDS-TCAA* | mg/L | 1.1 | 60 | --- | 536.5545 | --- | 98.1667 | 269.5007 | 99.5918 | Total hardness | mg/L as CaCO3 | 110 | 800 | 1567.2202 | 63.5762 | 1183.6101 | 90.7064 | SDS-TCAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 113 | 580 | 1103.2445 | 59.058 | 841.6223 | 86.5735 | SDS-TCAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 138 | 700 | 1331.4836 | 57.4074 | 1015.7418 | 86.4139 | SDS-TCAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 141 | 670 | 1264.4036 | 53.6184 | 967.2018 | 85.4219
|  | Maximum permissible SDI | 4 | Select the Design System Recycle Flow Rate2 | [6 empty] | 1998-12-11 | 0:10 | 28445.6 | 23 | 102.7 | 50 | 28.5192 | 0 | 1298 | 154 |  | 1452 | 1452 | 0.89394 | 0 | 13.9915 | 14.8435 | 7.0914 | 40.7394 | 0.36435 |  | 5.95 | 268 |  | 404 | 1572 | 1550.2857 | 1.3813 | 33.6634 | 977.1429 | 72.5731 | 102.7 | 80 | 40 | 870 | 582 | 1452 | 1452 | 0.43164 | 0.59917 | 15.8904 | 16.8581 | 3.9317 | 47.4183 | 0.35552 | 5.95 | 6.14 | 179 | 404 | 677 | 740.3402 | -9.356 | 55.6931 | 572.1701 | 68.7156 | 80 | 69 | 12 | 308 | 274 | 582 | 582 | 0.3633 | 0.52921 | 11.2511 | 11.9363 | 7.0292 | 55.4708 | 0.21518 | 6.14 | 6.32 | 227 | 677 | 1145 | 1182.8394 | -3.3048 | 43.8119 | 929.9197 | 75.5893 | 69 | 50 | 12 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.9585 | 10.8668 | 36.6332 | 0.32644 | 6.32 | 6.2 | 363 | 1145 | 1572 | 1754.3506 | -11.5999 | 10.1485 | 1449.6753 | 74.9599 | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 97 | 474 | 902.0952 | 62.1094 | 688.0476 | 85.9021 | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 97 | 500 | 950.2381 | 62.6923 | 725.119 | 86.6229 | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 98 | 550 | 1052.5848 | 59.8361 | 801.2924 | 87.7698 | SDS-MBAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 108 | 530 | 1002.8248 | 55.3719 | 766.4124 | 85.9084 | SDS-MBAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 130 | 520 | 958.2182 | 46.7213 | 739.1091 | 82.4113 | SDS-MBAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 124 | 520 | 964.96 | 49.5935 | 742.48 | 83.2992
|  | Maximum permissible turbidity (ntu) | 1 | Minimum system recycle flow rate, (QR-sys)min (gpm) | 1730.1944 | [5 empty] | 1998-12-12 | 9:30 | 28478 | 23.1 | 103 | 48 | 29.1091 | 0 | 1298 | 154 |  | 1452 | 1452 | 0.89394 | 0 | 13.9915 | 14.7997 | 6.7786 | 39.6123 | 0.37361 |  | 5.98 | 258 |  | 388 | 1612 | 1483.7143 | 7.9582 | 33.5052 | 935.8571 | 72.4317 | 103 | 80 | 41 | 870 | 582 | 1452 | 1452 | 0.43164 | 0.59917 | 15.8904 | 16.8084 | 3.7744 | 46.7256 | 0.35973 | 5.98 | 6.11 | 172 | 388 | 682 | 710.8866 | -4.2356 | 55.6701 | 549.4433 | 68.6956 | 80 | 70 | 12 | 308 | 274 | 582 | 582 | 0.3633 | 0.52921 | 11.2511 | 11.9011 | 7.1854 | 55.8146 | 0.21323 | 6.11 | 6.23 | 222 | 682 | 1212 | 1199.0803 | 1.066 | 42.7835 | 940.5401 | 76.3965 | 70 | 48 | 12 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.9232 | 12.0062 | 34.9938 | 0.34072 | 6.23 | 6.25 | 348 | 1212 | 1612 | 1885.2468 | -16.9508 | 10.3093 | 1548.6234 | 77.5284 | SDS-DBAA* | mg/L | BMRL | 3.1 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.06 | 3.8 | 8.0469 | 70 | 5.9234 | 98.9871 | SDS-DBAA* | mg/L | 4.5 | 2.5 | --- | -13.6818 | --- | -80 | -4.6332 | 197.1254 | Turbidity | ntu | 0.09 | 7.5 | 15.7786 | 57.1429 | 11.6393 | 99.2268 | SDS-DBAA* | mg/L | 4.1 | 2.6 | --- | -9.5364 | --- | -57.6923 | -2.7353 | 249.8904 | Turbidity | ntu | 0.08 | 5.25 | 10.9986 | 60 | 8.1243 | 99.0153 | SDS-DBAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.06 | 2 | 4.1736 | 66.6667 | 3.0868 | 98.0563 | SDS-DBAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.1 | 6.6 | 13.9036 | 60 | 10.2518 | 99.0246 | SDS-DBAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.07 | 6 | 12.6632 | 69.5652 | 9.3316 | 99.2499
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | 1 ppm | Maximum system recycle flow rate, (QR-sys)max (gpm) | 210.6944 | [5 empty] | 1998-12-13 | 10:00 | 28502.5 | 23.1 | 103 | 48 | 28.5192 | 0 | 1296 | 154 |  | 1450 | 1450 | 0.89379 | 0 | 13.9699 | 14.7769 | 7.0305 | 39.9503 | 0.36988 |  | 5.95 | 261 |  | 396 | 1596 | 1532.1039 | 4.0035 | 34.0909 | 964.0519 | 72.9268 | 103 | 80 | 40 | 875 | 575 | 1450 | 1450 | 0.42973 | 0.60345 | 15.9817 | 16.905 | 3.7154 | 47.7846 | 0.35377 | 5.95 | 6.06 | 185 | 396 | 712 | 717.087 | -0.71446 | 53.2828 | 556.5435 | 66.7591 | 80 | 69 | 12 | 303 | 272 | 575 | 575 | 0.35949 | 0.52696 | 11.0685 | 11.7079 | 8.2053 | 54.2947 | 0.21564 | 6.06 | 6.13 | 185 | 712 | 1254 | 1299.0625 | -3.5935 | 53.2828 | 1005.5312 | 81.6018 | 69 | 48 | 12 | 118 | 154 | 272 | 272 | 0.46492 | 0.43382 | 11.0841 | 11.7245 | 12.4757 | 34.0243 | 0.34459 | 6.13 | 6.21 | 352 | 1254 | 1596 | 1945.1429 | -21.8761 | 11.1111 | 1599.5714 | 77.9941 | SDS-BCAA* | mg/L | BMRL | 14 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 20 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | 2.4 | 13 | --- | 98.7636 | --- | 81.5385 | 50.8059 | 95.2761 | Total organic carbon | mg/L | BMRL | 19 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | 1.7 | 11 | --- | 86.2455 | --- | 84.5455 | 44.0791 | 96.1433 | Total organic carbon | mg/L | BMRL | 20 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 18 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 19 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 19 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | 1: All of the information requested in this field may not be available, but values for all of the Design |  | Design system recycle flow rate, QR-sys (gpm) | 0 | [5 empty] | 1998-12-14 | 2:15 | 28518.7 | 23.6 | 103.1 | 50 | 28.6991 | 0 | 1298 | 154 |  | 1452 | 1452 | 0.89394 | 0 | 13.9915 | 14.5826 | 8.4993 | 39.3516 | 0.37057 | 7.23 | 5.89 | 232 | 388 | 395 | 1630 | 1768.8571 | -8.5188 | 41.2658 | 1081.9286 | 78.5568 | 103.1 | 80 | 41 | 867 | 585 | 1452 | 1452 | 0.43227 | 0.59711 | 15.8356 | 16.5047 | 3.9695 | 46.5805 | 0.35433 | 5.89 | 5.96 | 167 | 395 | 694 | 732.9077 | -5.6063 | 57.7215 | 563.9538 | 70.3876 | 80 | 69 | 11 | 310 | 275 | 585 | 585 | 0.365 | 0.52991 | 11.3242 | 11.8027 | 7.8964 | 55.6036 | 0.21226 | 5.96 | 6.05 | 189 | 694 | 1274 | 1263.2727 | 0.84202 | 52.1519 | 978.6364 | 80.6874 | 69 | 50 | 11 | 121 | 154 | 275 | 275 | 0.4682 | 0.44 | 11.3659 | 11.8462 | 13.6639 | 34.8361 | 0.34005 | 6.05 | 6.09 | 293 | 1274 | 1630 | 2044.7857 | -25.447 | 25.8228 | 1659.3929 | 82.3429 | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.01 | 0.558 | 1.1803 | 95.4545 | 0.86914 | 98.8494 | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.024 | 0.572 | 1.1842 | 89.7872 | 0.87812 | 97.2669 | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.021 | 0.564 | 1.1678 | 90.7895 | 0.86588 | 97.5747 | SDS-TBAA | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.023 | 0.588 | 1.221 | 90.4167 | 0.90452 | 97.4572 | SDS-TBAA | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.017 | 0.53 | 1.1064 | 92.3423 | 0.81821 | 97.9223 | SDS-TBAA | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.018 | 0.542 | 1.1308 | 91.8919 | 0.83639 | 97.8479
|  | Parameters must be entered in cells E15:E26, since these parameters are used in calculations. |  | System influent flow rate, QI-sys (gpm) | 1546.1806 | [5 empty] | 1998-12-15 | 1:13 | 28527.8 | 22.6 | 103.6 | 50 | 29.1091 | 0 | 1304 | 154 |  | 1458 | 1458 | 0.89438 | 0 | 14.0561 | 15.0895 | 7.903 | 39.7879 | 0.37925 |  | 5.96 | 244 |  | 395 | 1637 | 1673.5974 | -2.2356 | 38.2278 | 1034.2987 | 76.4091 | 103.6 | 80 | 41 | 874 | 584 | 1458 | 1458 | 0.43333 | 0.59945 | 15.9635 | 17.1371 | 3.9861 | 46.8139 | 0.36607 | 5.96 | 6.01 | 167 | 395 | 683 | 736.2192 | -7.792 | 57.7215 | 565.6096 | 70.4743 | 80 | 68 | 12 | 310 | 274 | 584 | 584 | 0.36415 | 0.53082 | 11.3242 | 12.1567 | 7.7189 | 54.2811 | 0.22396 | 6.01 | 6.05 | 190 | 683 | 1246 | 1240.7737 | 0.41944 | 51.8987 | 961.8869 | 80.2472 | 68 | 50 | 12 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 12.1007 | 12.7288 | 34.2712 | 0.35309 | 6.05 | 6.01 | 330 | 1246 | 1637 | 1959.7662 | -19.7169 | 16.4557 | 1602.8831 | 79.4121 | SDS-CDBAA | mg/L | BMRL | 21 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 2.79 | --- | --- | --- | --- | SDS-CDBAA | mg/L | 2.2 | 2.3 | --- | 3.1091 | --- | 4.3478 | 2.6567 | 17.1892 | SUVA | L/(mg*m) | NR | 3.0105 | --- | --- | --- | --- | SDS-CDBAA | mg/L | 2.1 | 5.1 | --- | 29.3727 | --- | 58.8235 | 15.7707 | 86.6841 | SUVA | L/(mg*m) | NR | 2.82 | --- | --- | --- | --- | SDS-CDBAA | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | #VALUE! | NR | --- | --- | --- | --- | SDS-CDBAA | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 2.7895 | --- | --- | --- | --- | SDS-CDBAA | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 2.8526 | --- | --- | --- | ---
|  |  |  | Recycle ratio, r | 0 | [5 empty] | 1998-12-16 | 6:30 | 28540.9 | 22.8 | 104 | 48 | 29.1091 | 0 | 1301 | 153 |  | 1454 | 1454 | 0.89477 | 0 | 14.0238 | 14.9661 | 7.7199 | 39.171 | 0.38207 |  | 5.97 | 245 |  | 392 | 1611 | 1641.9804 | -1.9231 | 37.5 | 1016.9902 | 75.9093 | 104 | 80 | 41 | 878 | 576 | 1454 | 1454 | 0.43079 | 0.60385 | 16.0365 | 17.114 | 4.1234 | 46.8766 | 0.36509 | 5.97 | 6.03 | 158 | 392 | 668 | 748.6875 | -12.079 | 59.6939 | 570.3438 | 72.2974 | 80 | 68 | 12 | 305 | 271 | 576 | 576 | 0.35949 | 0.52951 | 11.1416 | 11.8902 | 7.1573 | 54.8427 | 0.2168 | 6.03 | 6.09 | 210 | 668 | 1210 | 1183.4613 | 2.1933 | 46.4286 | 925.7306 | 77.3152 | 68 | 48 | 12 | 118 | 153 | 271 | 271 | 0.46274 | 0.43542 | 11.0841 | 11.8289 | 12.2212 | 33.7788 | 0.35019 | 6.09 | 6.13 | 328 | 1210 | 1611 | 1890.2353 | -17.333 | 16.3265 | 1550.1176 | 78.8403 | SDS-DCBAA | mg/L | BMRL | 27 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | 1.9 | 11 | --- | 84.6273 | --- | 82.7273 | 43.456 | 95.6278 | [8 empty] | SDS-DCBAA | mg/L | 1.5 | 20 | --- | 169.6818 | --- | 92.5 | 85.8024 | 98.2518 | [8 empty] | SDS-DCBAA | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  |  |  | 2: The design system recycle flow rate must fall between the minimum and | [6 empty] | 1998-12-17 | 6:15 | 28558.3 | 19.5 | 104 | 50 | 28.1091 | 0 | 1296 | 153 |  | 1449 | 1449 | 0.89441 | 0 | 13.9699 | 16.4361 | 5.8635 | 43.0273 | 0.38199 |  | 6.17 | 284 |  | 396 | 1512 | 1344.7059 | 11.0644 | 28.2828 | 870.3529 | 67.3696 | 104 | 80 | 40 | 869 | 580 | 1449 | 1449 | 0.43058 | 0.59972 | 15.8721 | 18.6741 | 3.7432 | 48.2568 | 0.38697 | 6.17 | 6.29 | 182 | 396 | 667 | 716.631 | -7.4409 | 54.0404 | 556.3155 | 67.2848 | 80 | 68 | 11 | 307 | 273 | 580 | 580 | 0.36203 | 0.52931 | 11.2146 | 13.1944 | 7.0302 | 55.9698 | 0.23574 | 6.29 | 6.29 | 217 | 667 | 1170 | 1173.044 | -0.26017 | 45.202 | 920.022 | 76.4136 | 68 | 50 | 11 | 120 | 153 | 273 | 273 | 0.46492 | 0.43956 | 11.272 | 13.2619 | 11.4296 | 36.5704 | 0.36264 | 6.29 | 6.25 | 349 | 1170 | 1512 | 1813.9216 | -19.9684 | 11.8687 | 1491.9608 | 76.608 | SDS-HAA5 | mg/L | 0 | 158.1 | --- | 1505.7143 | --- | 100 | 752.8194 | 100 | [8 empty] | SDS-HAA5 | mg/L | 5.9 | 116.5 | --- | 1011.3545 | --- | 94.9356 | 510.9651 | 98.8453 | [8 empty] | SDS-HAA5 | mg/L | 6.3 | 114.2 | --- | 987.2091 | --- | 94.4834 | 497.9882 | 98.7349 | [8 empty] | SDS-HAA5 | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-HAA5 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | 0 | #DIV/0! | [8 empty] | SDS-HAA5 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | 0 | #DIV/0!
|  |  |  | maximum system recycle flow rates. | [6 empty] | 1998-12-18 | 0:10 | 28576 | 19.8 | 104.3 | 49 | 28.6991 | 0 | 1297 | 152 |  | 1449 | 1449 | 0.8951 | 0 | 13.9807 | 16.3035 | 4.9505 | 43.0004 | 0.37915 |  | 5.95 | 287 |  | 381 | 1528 | 1183.0921 | 22.5725 | 24.6719 | 782.0461 | 63.3014 | 104.3 | 80 | 41 | 869 | 580 | 1449 | 1449 | 0.43058 | 0.59972 | 15.8721 | 18.5093 | 3.4458 | 47.7042 | 0.388 | 5.95 | 6.09 | 184 | 381 | 666 | 676.1603 | -1.5256 | 51.706 | 528.5802 | 65.1898 | 80 | 70 | 11 | 308 | 272 | 580 | 580 | 0.36161 | 0.53103 | 11.2511 | 13.1205 | 6.7815 | 57.2185 | 0.22931 | 6.09 | 6.24 | 233 | 666 | 1156 | 1156.3088 | -0.026715 | 38.8451 | 911.1544 | 74.428 | 70 | 49 | 11 | 120 | 152 | 272 | 272 | 0.46274 | 0.44118 | 11.272 | 13.1448 | 11.0463 | 37.4537 | 0.35096 | 6.24 | 6.21 | 364 | 1156 | 1528 | 1781.2632 | -16.5748 | 4.4619 | 1468.6316 | 75.215 | SDS-HAA6 | mg/L | 0 | 172.1 | --- | 1639.0476 | --- | 100 | 819.4827 | 100 | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | 8.3 | 129.5 | --- | 1110.1182 | --- | 93.5907 | 561.771 | 98.5225 | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | 8 | 125.2 | --- | 1073.4545 | --- | 93.6102 | 542.0673 | 98.5242 | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | 0 | #DIV/0! | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | 0 | #DIV/0! | Stage 3 Operating Parameters During Sample Collection
[11 empty] | 1998-12-20 | 16:35 | 28599.2 | 23.6 | 102.8 | 49 | 28.5192 | 0 | 1304 | 155 |  | 1459 | 1459 | 0.89376 | 0 | 14.0561 | 14.65 | 7.0287 | 40.3521 | 0.36305 |  | 6.01 | 269 |  | 404 | 1586 | 1539.7419 | 2.9166 | 33.4158 | 971.871 | 72.3214 | 102.8 | 81 | 40 | 873 | 586 | 1459 | 1459 | 0.43397 | 0.59836 | 15.9452 | 16.6189 | 3.926 | 47.974 | 0.34641 | 6.01 | 6.13 | 179 | 404 | 695 | 739.1962 | -6.3592 | 55.6931 | 571.5981 | 68.6843 | 81 | 69 | 12 | 310 | 276 | 586 | 586 | 0.36585 | 0.52901 | 11.3242 | 11.8027 | 7.5893 | 55.4107 | 0.213 | 6.13 | 6.21 | 209 | 695 | 1218 | 1240.8696 | -1.8776 | 48.2673 | 967.9348 | 78.4076 | 69 | 49 | 12 | 121 | 155 | 276 | 276 | 0.47038 | 0.43841 | 11.3659 | 11.8462 | 12.1792 | 34.8208 | 0.3402 | 6.21 | 6.2 | 342 | 1218 | 1586 | 1901.8452 | -19.9146 | 15.3465 | 1559.9226 | 78.0758 | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.44 |  |  |  |  | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.44 |  |  |  |  | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.43 |  |  |  |  | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.44 |  |  |  |  | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.44 |  |  |  |  | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.44
|  |  |  | Summary of the Stage and System Flow Rates | [6 empty] | 1998-12-21 | 5:45 | 28609 | 23.5 | 103.5 | 49 | 28.5192 | 0 | 1299 | 154 |  | 1453 | 1453 | 0.89401 | 0 | 14.0022 | 14.637 | 6.8871 | 40.8437 | 0.35837 | 7.27 | 6.17 | 261 | 395 | 393 | 1501 | 1506.4286 | -0.36166 | 33.5878 | 949.7143 | 72.5181 | 103.5 | 80 | 40 | 872 | 581 | 1453 | 1453 | 0.43164 | 0.60014 | 15.9269 | 16.649 | 3.7284 | 48.0216 | 0.3467 | 6.17 | 6.2 | 180 | 393 | 668 | 712.6833 | -6.6891 | 54.1985 | 552.8417 | 67.4409 | 80 | 68 | 12 | 307 | 274 | 581 | 581 | 0.36288 | 0.5284 | 11.2146 | 11.723 | 7.1614 | 54.8386 | 0.21377 | 6.2 | 6.23 | 209 | 668 | 1180 | 1182.281 | -0.19331 | 46.8193 | 925.1405 | 77.4088 | 68 | 49 | 12 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.783 | 11.6866 | 34.8134 | 0.33846 | 6.23 | 6.29 | 339 | 1180 | 1501 | 1835.3247 | -22.2735 | 13.7405 | 1507.6623 | 77.5149 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 121 |  |  |  |  | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 119 |  |  |  |  | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 120 |  |  |  |  | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 120 |  |  |  |  | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 120 |  |  |  |  | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 120
|  |  |  | Influent flow rate to stage 1, QI-s(1) (gpm) | 1546.1806 | [5 empty] | 1998-12-22 | 0:05 | 28629.3 | 22.9 | 103.5 | 49 | 29.1091 | 0 | 1301 | 155 |  | 1456 | 1456 | 0.89354 | 0 | 14.0238 | 14.9219 | 6.5999 | 40.541 | 0.36807 |  | 5.94 | 274 |  | 401 | 1552 | 1466.9806 | 5.4781 | 31.6708 | 933.9903 | 70.6635 | 103.5 | 80 | 41 | 874 | 582 | 1456 | 1456 | 0.43249 | 0.60027 | 15.9635 | 16.9858 | 3.8519 | 46.8981 | 0.36218 | 5.94 | 6.22 | 181 | 401 | 683 | 731.378 | -7.0832 | 54.8628 | 566.189 | 68.0319 | 80 | 69 | 12 | 307 | 275 | 582 | 582 | 0.36373 | 0.52749 | 11.2146 | 11.9328 | 7.339 | 55.161 | 0.21633 | 6.22 | 6.27 | 212 | 683 | 1212 | 1208.8073 | 0.26343 | 47.1322 | 945.9036 | 77.5876 | 69 | 49 | 12 | 120 | 155 | 275 | 275 | 0.46929 | 0.43636 | 11.272 | 11.9939 | 12.0955 | 34.9045 | 0.34362 | 6.27 | 6.22 | 340 | 1212 | 1552 | 1887.0968 | -21.5913 | 15.212 | 1549.5484 | 78.0581 | [12 empty] | Stage 3 influent flow rate during sample collection (gpm) | 273 | [16 empty] | Stage 3 influent flow rate during sample collection (gpm) | 273 | [16 empty] | Stage 3 influent flow rate during sample collection (gpm) | 277 | [16 empty] | Stage 3 influent flow rate during sample collection (gpm) | 274 | [16 empty] | Stage 3 influent flow rate during sample collection (gpm) | 275 | [16 empty] | Stage 3 influent flow rate during sample collection (gpm) | 275
|  |  |  | Permeate flow rate from stage 1, Qp-s(1) (gpm) | 821.25 | [5 empty] | 1998-12-23 | 1:00 | 28654.4 | 22.9 | 104 | 48 | 28.5192 | 0 | 1301 | 154 |  | 1455 | 1455 | 0.89416 | 0 | 14.0238 | 14.9219 | 6.3733 | 41.1075 | 0.363 |  | 6.01 | 264 |  | 386 | 1612 | 1416.6623 | 12.1177 | 31.6062 | 901.3312 | 70.71 | 104 | 80 | 40 | 872 | 583 | 1455 | 1455 | 0.43249 | 0.59931 | 15.9269 | 16.9469 | 3.7055 | 48.2945 | 0.35091 | 6.01 | 6.11 | 174 | 386 | 668 | 703.0909 | -5.2531 | 54.9223 | 544.5455 | 68.0467 | 80 | 70 | 12 | 309 | 274 | 583 | 583 | 0.36373 | 0.53002 | 11.2877 | 12.0105 | 7.1625 | 55.8375 | 0.2151 | 6.11 | 6.18 | 210 | 668 | 1302 | 1184.5036 | 9.0243 | 45.5959 | 926.2518 | 77.328 | 70 | 48 | 12 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.9939 | 13.4236 | 33.5764 | 0.35721 | 6.18 | 6.19 | 336 | 1302 | 1612 | 2054.7273 | -27.4645 | 12.9534 | 1678.3636 | 79.9805 | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs
|  |  |  | Concentrate flow rate from stage 1, QC-s(1) (gpm) | 724.9306 | [5 empty] | 1998-12-25 | 0:17 | 28696.4 | 22.9 | 103.6 | 49 | 29.1091 | 0 | 1303 | 154 |  | 1457 | 1457 | 0.8943 | 0 | 14.0454 | 14.9448 | 8.2119 | 38.9789 | 0.38341 |  | 5.83 | 242 |  | 399 | 1674 | 1727.3831 | -3.189 | 39.3484 | 1063.1916 | 77.2383 | 103.6 | 81 | 41 | 873 | 584 | 1457 | 1457 | 0.43312 | 0.59918 | 15.9452 | 16.9663 | 4.089 | 47.211 | 0.35937 | 5.83 | 5.97 | 165 | 399 | 706 | 748.7979 | -6.062 | 58.6466 | 573.899 | 71.2493 | 81 | 69 | 12 | 310 | 274 | 584 | 584 | 0.36415 | 0.53082 | 11.3242 | 12.0494 | 8.032 | 54.968 | 0.21921 | 5.97 | 6.01 | 193 | 706 | 1292 | 1286.4015 | 0.43332 | 51.6291 | 996.2007 | 80.6264 | 69 | 49 | 12 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.9939 | 13.7294 | 33.2706 | 0.36049 | 6.01 | 5.96 | 304 | 1292 | 1674 | 2061.8701 | -23.1703 | 23.8095 | 1676.9351 | 81.8717 |  | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters
|  |  |  | Influent flow rate to stage 2, QI-s(2) (gpm) | 724.9306 | [5 empty] | 1998-12-26 | 6:30 | 28717 | 22.6 | 102.9 | 50 | 29.1091 | 0 | 1297 | 157 |  | 1454 | 1454 | 0.89202 | 0 | 13.9807 | 15.0085 | 4.0532 | 43.2877 | 0.34672 |  | 6.07 | 278 |  | 357 | 1483 | 1009.6306 | 31.9197 | 22.1289 | 683.3153 | 59.316 | 102.9 | 80 | 41 | 868 | 586 | 1454 | 1454 | 0.43291 | 0.59697 | 15.8539 | 17.0194 | 3.0113 | 47.4387 | 0.35877 | 6.07 | 6.16 | 184 | 357 | 658 | 613.2526 | 6.8005 | 48.4594 | 485.1263 | 62.0717 | 80 | 68 | 12 | 309 | 277 | 586 | 586 | 0.36628 | 0.5273 | 11.2877 | 12.1175 | 6.9788 | 55.0212 | 0.22023 | 6.16 | 6.22 | 210 | 658 | 1150 | 1157.7545 | -0.67431 | 41.1765 | 907.8773 | 76.8691 | 68 | 50 | 12 | 120 | 157 | 277 | 277 | 0.47365 | 0.43321 | 11.272 | 12.1007 | 11.1679 | 35.8321 | 0.33771 | 6.22 | 6.29 | 342 | 1150 | 1483 | 1767.5796 | -19.1895 | 4.2017 | 1458.7898 | 76.5559 |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-32 | CI-s3-32 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-34 | CI-s3-34 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-36 | CI-s3-36 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-38 | CI-s3-38 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-40 | CI-s3-40 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-40 (dup) | CI-s3-40 (dup) | CC(calc) | RF (%) | CB | RB (%)
|  |  |  | Permeate flow rate from stage 2, Qp-s(2) (gpm) | 410.625 | [5 empty] | 1998-12-27 | 4:30 | 28739.1 | 23.1 | 104 | 48 | 28.5192 | 0 | 1300 | 156 |  | 1456 | 1456 | 0.89286 | 0 | 14.013 | 14.8225 | 5.115 | 42.3658 | 0.34987 |  | 6.04 | 269 |  | 368 | 1512 | 1193 | 21.0979 | 26.9022 | 780.5 | 65.5349 | 104 | 80 | 40 | 872 | 584 | 1456 | 1456 | 0.43291 | 0.5989 | 15.9269 | 16.847 | 3.2661 | 48.7339 | 0.34569 | 6.04 | 6.11 | 181 | 368 | 682 | 647.2192 | 5.0998 | 50.8152 | 507.6096 | 64.3427 | 80 | 70 | 12 | 308 | 276 | 584 | 584 | 0.365 | 0.5274 | 11.2511 | 11.9011 | 7.338 | 55.662 | 0.21381 | 6.11 | 6.19 | 211 | 682 | 1192 | 1207.6087 | -1.3095 | 42.663 | 944.8043 | 77.6673 | 70 | 48 | 12 | 120 | 156 | 276 | 276 | 0.47147 | 0.43478 | 11.272 | 11.9232 | 11.8246 | 35.1754 | 0.33896 | 6.19 | 6.25 | 338 | 1192 | 1512 | 1848.9231 | -22.2833 | 8.1522 | 1520.4615 | 77.7699 | Qp/QT (THM4), % | 68.7057 | 84.6631 |  | Qp/QT (HAA5), % | 65.8444 | 82.9222 |  |  |  | Sampling date | MM/DD/YY | 1998-11-10 | 1998-11-10 | --- | --- | --- | --- | Qp/QT (THM4), % | 87.4046 | 101.145 |  | Qp/QT (HAA5), % | 56.5099 | 80.9222 |  |  |  | Sampling date | MM/DD/YY | 1998-11-23 | 1998-11-23 | --- | --- | --- | --- | Qp/QT (THM4), % | 79.558 | 99.4475 |  | Qp/QT (HAA5), % | 55.7924 | 80.8156 |  |  |  | Sampling date | MM/DD/YY | 1998-12-07 | 1998-12-07 | --- | --- | --- | --- | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | #VALUE! | #VALUE! |  |  |  | Sampling date | MM/DD/YY | 1998-12-21 | 1998-12-21 | --- | --- | --- | --- | Qp/QT (THM4), % | #DIV/0! | #DIV/0! |  | Qp/QT (HAA5), % | #DIV/0! | #DIV/0! |  |  |  | Sampling date | MM/DD/YY | 1999-01-04 | 1999-01-04 | --- | --- | --- | --- | Qp/QT (THM4), % | #DIV/0! | #DIV/0! |  | Qp/QT (HAA5), % | #DIV/0! | #DIV/0! |  |  |  | Sampling date | MM/DD/YY | 1999-01-04 | 1999-01-04 | --- | --- | --- | ---
|  |  |  | Concentrate flow rate from stage 2, QC-s(2) (gpm) | 314.3056 | [5 empty] | 1998-12-29 | 0:10 | 28770.5 | 23.4 | 103.3 | 48 | 28.6991 | 0 | 1305 | 154 |  | 1459 | 1459 | 0.89445 | 0 | 14.0669 | 14.7482 | 8.7458 | 38.2051 | 0.38603 |  | 6.03 | 247 |  | 414 | 1548 | 1829.1623 | -18.1629 | 40.3382 | 1121.5812 | 77.9775 | 103.3 | 80 | 41 | 873 | 586 | 1459 | 1459 | 0.43397 | 0.59836 | 15.9452 | 16.7174 | 3.9085 | 46.7415 | 0.35766 | 6.03 | 6.11 | 190 | 414 | 682 | 747.7065 | -9.6344 | 54.1063 | 580.8532 | 67.2895 | 80 | 68 | 11 | 311 | 275 | 586 | 586 | 0.36543 | 0.53072 | 11.3607 | 11.9109 | 7.4829 | 55.5171 | 0.21455 | 6.11 | 6.1 | 204 | 682 | 1230 | 1222.5745 | 0.6037 | 50.7246 | 952.2873 | 78.5779 | 68 | 48 | 11 | 121 | 154 | 275 | 275 | 0.4682 | 0.44 | 11.3659 | 11.9164 | 12.7029 | 34.2971 | 0.34745 | 6.1 | 6.13 | 318 | 1230 | 1548 | 1946.5714 | -25.7475 | 23.1884 | 1588.2857 | 79.9784 | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 78.455 | 39.9275 |  |  |  | Sampling time | hh:mm | 13:26 | 13:36 | --- | --- | --- | --- | SDS-THM4b, mg/L | 72 | NA |  | SDS-THM4b, mg/L | 152.9439 | 88.9837 |  |  |  | Sampling time | hh:mm | 6:54 | 7:04 | --- | --- | --- | --- | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 115.0158 | 69.7238 |  |  |  | Sampling time | hh:mm | 7:23 | 7:30 | --- | --- | --- | --- | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  |  |  | Sampling time | hh:mm | 9:18 | 9:30 | --- | --- | --- | --- | SDS-THM4b, mg/L | #DIV/0! | #DIV/0! |  | SDS-THM4b, mg/L | #DIV/0! | #DIV/0! |  |  |  | Sampling time | hh:mm | 9:55 | 10:15 | --- | --- | --- | --- | SDS-THM4b, mg/L | #DIV/0! | #DIV/0! |  | SDS-THM4b, mg/L | #DIV/0! | #DIV/0! |  |  |  | Sampling time | hh:mm | 9:55 | 10:15 | --- | --- | --- | ---
|  |  |  | Influent flow rate to stage 3, QI-s(3) (gpm) | 314.3056 | [5 empty] | 1998-12-30 | 0:12 | 28794.4 | 22.9 | 103.4 | 50 | 28.5192 | 0 | 1300 | 158 |  | 1458 | 1458 | 0.89163 | 0 | 14.013 | 14.9104 | 7.8243 | 40.3565 | 0.36947 |  | 5.93 | 247 |  | 400 | 1640 | 1658.8608 | -1.15 | 38.25 | 1029.4304 | 76.0061 | 103.4 | 80 | 40 | 870 | 588 | 1458 | 1458 | 0.43418 | 0.59671 | 15.8904 | 16.908 | 3.9841 | 47.7159 | 0.35435 | 5.93 | 6.1 | 171 | 400 | 698 | 738.8265 | -5.8491 | 57.25 | 569.4133 | 69.9691 | 80 | 69 | 12 | 310 | 278 | 588 | 588 | 0.36755 | 0.52721 | 11.3242 | 12.0494 | 7.7722 | 54.7278 | 0.22017 | 6.1 | 6.12 | 199 | 698 | 1270 | 1254.4388 | 1.2253 | 50.25 | 976.2194 | 79.6152 | 69 | 50 | 12 | 120 | 158 | 278 | 278 | 0.47584 | 0.43165 | 11.272 | 11.9939 | 13.1214 | 34.3786 | 0.34888 | 6.12 | 6.07 | 319 | 1270 | 1640 | 1992.2785 | -21.4804 | 20.25 | 1631.1392 | 80.4431 | SDS-HAA5b, mg/L | 49.4763 | 24.2476 |  | SDS-HAA5b, mg/L | 54 | 27 |  |  |  | Operation time | hh.hh | 27864.3 | 27864.5 | --- | --- | --- | --- | SDS-HAA5b, mg/L | 19.8305 | NA |  | SDS-HAA5b, mg/L | 54 | 27 |  |  |  | Operation time | hh.hh | 28126.4 | 28126.6 | --- | --- | --- | --- | SDS-HAA5b, mg/L | 28.3569 | 6.8961 |  | SDS-HAA5b, mg/L | 54 | 27 |  |  |  | Operation time | hh.hh | 28378.9 | 28379 | --- | --- | --- | --- | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  |  |  | Operation time | hh.hh | 28614.5 | 28614.7 | --- | --- | --- | --- | SDS-HAA5b, mg/L | #DIV/0! | #DIV/0! |  | SDS-HAA5b, mg/L | #DIV/0! | #DIV/0! |  |  |  | Operation time | hh.hh | 28910.2 | 28910.5 | --- | --- | --- | --- | SDS-HAA5b, mg/L | #DIV/0! | #DIV/0! |  | SDS-HAA5b, mg/L | #DIV/0! | #DIV/0! |  |  |  | Operation time | hh.hh | 28910.2 | 28910.5 | --- | --- | --- | ---
|  |  |  | Permeate flow rate from stage 3, Qp-s(3) (gpm) | 159.6875 | [5 empty] | 1998-12-31 | 0:15 | 28815.8 | 19.2 | 104.2 | 49 | 29.1091 | 0 | 1300 | 156 |  | 1456 | 1456 | 0.89286 | 0 | 14.013 | 16.6337 | 6.5617 | 40.9292 | 0.4064 |  | 5.88 | 263 |  | 390 | 1505 | 1448.3333 | 3.7652 | 32.5641 | 919.1667 | 71.3871 | 104.2 | 80 | 41 | 875 | 581 | 1456 | 1456 | 0.43227 | 0.60096 | 15.9817 | 18.9705 | 3.6112 | 47.4888 | 0.39947 | 5.88 | 6.06 | 184 | 390 | 669 | 700.241 | -4.6698 | 52.8205 | 545.1205 | 66.246 | 80 | 70 | 12 | 306 | 275 | 581 | 581 | 0.3633 | 0.52668 | 11.1781 | 13.2685 | 6.6924 | 56.3076 | 0.23564 | 6.06 | 6.09 | 239 | 669 | 1166 | 1147.4727 | 1.589 | 38.7179 | 908.2364 | 73.6853 | 70 | 49 | 12 | 119 | 156 | 275 | 275 | 0.47038 | 0.43273 | 11.1781 | 13.2685 | 11.0927 | 36.4073 | 0.36445 | 6.09 | 6.08 | 363 | 1166 | 1505 | 1778.5449 | -18.1757 | 6.9231 | 1472.2724 | 75.3442 | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  |  |  | pH | --- | 6.39 | 6.45 | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | 202.8702 | NA |  | SDS-TOXb, mg Cl- /L | 484.6293 | 261.9892 |  |  |  | pH | --- | 6.29 | 6.2 | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | 140.1768 | 60.221 |  | SDS-TOXb, mg Cl- /L | 235.7146 | 135.1214 |  |  |  | pH | --- | 6.25 | 6.25 | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  |  |  | pH | --- | 6.2 | 6.23 | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | #DIV/0! | #DIV/0! |  | SDS-TOXb, mg Cl- /L | #DIV/0! | #DIV/0! |  |  |  | pH | --- | 6.43 | 6.31 | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | #DIV/0! | #DIV/0! |  | SDS-TOXb, mg Cl- /L | #DIV/0! | #DIV/0! |  |  |  | pH | --- | 6.43 | 6.31 | --- | --- | --- | ---
|  |  |  | Concentrate flow rate from stage 3, QC-s(3) (gpm) | 154.6181 | [5 empty] | 1999-01-01 | 0:46 | 28840.3 | 23 | 103.4 | 55 | 29.6991 | 0 | 1292 | 147 |  | 1439 | 1439 | 0.89785 | 0 | 13.9268 | 14.7749 | 8.0379 | 41.463 | 0.35634 |  | 5.98 | 253 |  | 402 | 1653 | 1711.5782 | -3.5438 | 37.0647 | 1056.7891 | 76.0596 | 103.4 | 80 | 42 | 863 | 576 | 1439 | 1439 | 0.4276 | 0.59972 | 15.7626 | 16.7225 | 3.988 | 45.712 | 0.36582 | 5.98 | 6.14 | 174 | 402 | 699 | 743.6042 | -6.3811 | 56.7164 | 572.8021 | 69.623 | 80 | 70 | 12 | 309 | 267 | 576 | 576 | 0.35779 | 0.53646 | 11.2877 | 11.9751 | 8.0038 | 54.9962 | 0.21774 | 6.14 | 6.19 | 192 | 699 | 1281 | 1285.7528 | -0.37102 | 52.2388 | 992.3764 | 80.6525 | 70 | 55 | 12 | 120 | 147 | 267 | 267 | 0.45183 | 0.44944 | 11.272 | 11.9585 | 13.5324 | 36.9676 | 0.32349 | 6.19 | 6.08 | 320 | 1281 | 1653 | 2065.4898 | -24.954 | 20.398 | 1673.2449 | 80.8755 | SDS-CDb, mg/L | 18.084 | 18.2196 |  | SDS-CDb, mg/L | 18.0597 | 18.2048 |  |  |  | Temperature | oC | 25.1 | 25.1 | --- | --- | --- | --- | SDS-CDb, mg/L | 18.7899 | NA |  | SDS-CDb, mg/L | 21.5858 | 19.3765 |  |  |  | Temperature | oC | 24.6 | 24.2 | --- | --- | --- | --- | SDS-CDb, mg/L | 18.1478 | 18.2472 |  | SDS-CDb, mg/L | 18.029 | 18.1541 |  |  |  | Temperature | oC | 23.3 | 23.7 | --- | --- | --- | --- | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | #VALUE! | #VALUE! |  |  |  | Temperature | oC | 24.4 | 24.5 | --- | --- | --- | --- | SDS-CDb, mg/L | #DIV/0! | #DIV/0! |  | SDS-CDb, mg/L | #DIV/0! | #DIV/0! |  |  |  | Temperature | oC | 22.9 | 22.8 | --- | --- | --- | --- | SDS-CDb, mg/L | #DIV/0! | #DIV/0! |  | SDS-CDb, mg/L | #DIV/0! | #DIV/0! |  |  |  | Temperature | oC | 22.9 | 22.8 | --- | --- | --- | ---
|  |  |  | System concentrate recycle flow rate, QR-sys (gpm) | 0 | [5 empty] | 1999-01-02 | 0:54 | 28856.5 | 23.2 | 103.6 | 50 | 26.3392 | 0 | 1302 | 156 |  | 1458 | 1458 | 0.893 | 0 | 14.0346 | 14.8015 | 8.07 | 42.3908 | 0.34917 |  | 5.9 | 244 |  | 400 | 1586 | 1702 | -7.314 | 39 | 1051 | 76.784 | 103.6 | 80 | 37 | 879 | 579 | 1458 | 1458 | 0.43227 | 0.60288 | 16.0548 | 16.9321 | 4.081 | 50.719 | 0.33384 | 5.9 | 6.05 | 168 | 400 | 680 | 752.2073 | -10.6187 | 58 | 576.1036 | 70.8386 | 80 | 68 | 11 | 305 | 274 | 579 | 579 | 0.36203 | 0.52677 | 11.1416 | 11.7504 | 7.4093 | 55.5907 | 0.21137 | 6.05 | 6.07 | 204 | 680 | 1208 | 1209.854 | -0.15348 | 49 | 944.927 | 78.411 | 68 | 50 | 11 | 118 | 156 | 274 | 274 | 0.46929 | 0.43066 | 11.0841 | 11.6899 | 12.0731 | 35.9269 | 0.32538 | 6.07 | 5.99 | 332 | 1208 | 1586 | 1870.6154 | -17.9455 | 17 | 1539.3077 | 78.4319 | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! |  |  |  | Alkalinity | mg/L as CaCO3 | 188 | 232 | 267.0263 | -62.069 | 249.5132 | 24.6533 | TOCb, mg/L | 1.8817 | NA |  | TOCb, mg/L | 4.0443 | 2.3354 |  |  |  | Alkalinity | mg/L as CaCO3 | 150 | 142 | 135.8182 | -74.4186 | 138.9091 | -7.9843 | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! |  |  |  | Alkalinity | mg/L as CaCO3 | 154 | 152 | 150.4713 | -37.5 | 151.2357 | -1.8278 | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! |  |  |  | Alkalinity | mg/L as CaCO3 | 164 | 178 | 188.9091 | -49.0909 | 183.4545 | 10.6046 | TOCb, mg/L | #DIV/0! | #DIV/0! |  | TOCb, mg/L | #DIV/0! | #DIV/0! |  |  |  | Alkalinity | mg/L as CaCO3 | 192 | 178 | 167.1613 | -52.381 | 172.5806 | -11.2523 | TOCb, mg/L | #DIV/0! | #DIV/0! |  | TOCb, mg/L | #DIV/0! | #DIV/0! |  |  |  | Alkalinity | mg/L as CaCO3 | 204 | 178 | 157.871 | -70 | 167.9355 | -21.4752
|  |  |  | System concentrate waste flow rate, QW-sys (gpm) | 154.6181 | [5 empty] | 1999-01-03 | 10:10 | 28886.6 | 23.1 | 103 | 50 | 28.1091 | 0 | 1301 | 158 |  | 1459 | 1459 | 0.89171 | 0 | 14.0238 | 14.8339 | 7.8803 | 40.5105 | 0.36617 |  | 6.02 | 238 |  | 392 | 1608 | 1660.0633 | -3.2378 | 39.2857 | 1026.0316 | 76.8038 | 103 | 82 | 40 | 873 | 586 | 1459 | 1459 | 0.43397 | 0.59836 | 15.9452 | 16.8663 | 3.9783 | 48.5217 | 0.3476 | 6.02 | 6.13 | 164 | 392 | 686 | 731.6655 | -6.6568 | 58.1633 | 561.8328 | 70.8098 | 82 | 70 | 11 | 308 | 278 | 586 | 586 | 0.3667 | 0.5256 | 11.2511 | 11.9011 | 7.3968 | 57.6032 | 0.20661 | 6.13 | 6.23 | 210 | 686 | 1212 | 1213.3669 | -0.11278 | 46.4286 | 949.6835 | 77.8874 | 70 | 50 | 11 | 120 | 158 | 278 | 278 | 0.47584 | 0.43165 | 11.272 | 11.9232 | 12.0866 | 36.9134 | 0.323 | 6.23 | 6.24 | 336 | 1212 | 1608 | 1877.3165 | -16.7485 | 14.2857 | 1544.6582 | 78.2476 | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  |  |  | Total dissolved solids | mg/L | 396 | 2232 | 3693.5526 | 28.2609 | 2962.7763 | 86.6342 | UV254 b, cm-1 | 0.043584 | NA |  | UV254 b, cm-1 | 0.11124 | 0.05778 |  |  |  | Total dissolved solids | mg/L | 360 | 2208 | 3636 | 37.5 | 2922 | 87.6797 | UV254 b, cm-1 | 0.059337 | 0.017171 |  | UV254 b, cm-1 | 0.10972 | 0.056671 |  |  |  | Total dissolved solids | mg/L | 400 | 2296 | 3745.172 | 23.6641 | 3020.586 | 86.7575 | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  |  |  | Total dissolved solids | mg/L | 420 | 2156 | 3508.7273 | 23.3577 | 2832.3636 | 85.1714 | UV254 b, cm-1 | #DIV/0! | #DIV/0! |  | UV254 b, cm-1 | #DIV/0! | #DIV/0! |  |  |  | Total dissolved solids | mg/L | 422 | 2160 | 3505.5484 | 16.9291 | 2832.7742 | 85.1029 | UV254 b, cm-1 | #DIV/0! | #DIV/0! |  | UV254 b, cm-1 | #DIV/0! | #DIV/0! |  |  |  | Total dissolved solids | mg/L | 410 | 2188 | 3564.5161 | 15.9836 | 2876.2581 | 85.7454
|  |  |  | System permeate flow rate, Qp-sys (gpm) | 1391.5625 | [5 empty] | 1999-01-04 | 6:25 | 28906.7 | 20.9 | 103.8 | 49 | 29.1091 | 0 | 1299 | 155 |  | 1454 | 1454 | 0.8934 | 0 | 14.0022 | 15.8063 | 4.0485 | 43.2424 | 0.36553 | 7.12 | 6.07 | 313 | 390 | 391 | 1512 | 1044.6903 | 30.9067 | 19.9488 | 717.8452 | 56.3973 | 103.8 | 80 | 41 | 870 | 584 | 1454 | 1454 | 0.43249 | 0.59835 | 15.8904 | 17.9377 | 3.5421 | 47.3579 | 0.37877 | 6.07 | 6.31 | 188 | 391 | 676 | 693.4144 | -2.5761 | 51.9182 | 542.2072 | 65.3269 | 80 | 69 | 12 | 309 | 275 | 584 | 584 | 0.36458 | 0.52911 | 11.2877 | 12.742 | 7.1531 | 55.3469 | 0.23022 | 6.31 | 6.33 | 218 | 676 | 1184 | 1190.6255 | -0.55958 | 44.2455 | 933.3127 | 76.6423 | 69 | 49 | 12 | 120 | 155 | 275 | 275 | 0.46929 | 0.43636 | 11.272 | 12.7243 | 11.5406 | 35.4594 | 0.35884 | 6.33 | 6.35 | 352 | 1184 | 1512 | 1828.129 | -20.908 | 9.9744 | 1506.0645 | 76.6278 | Bromideb, mg/L | 166.8706 | 168.4663 |  | Bromideb, mg/L | 166.5844 | 168.2922 |  |  |  | Total hardness | mg/L as CaCO3 | 202 | 1280 | 2138.1447 | 33.5526 | 1709.0724 | 88.1807 | Bromideb, mg/L | 180 | NA |  | Bromideb, mg/L | 180 | 180 |  |  |  | Total hardness | mg/L as CaCO3 | 214 | 1310 | 2156.9091 | 29.6053 | 1733.4545 | 87.6547 | Bromideb, mg/L | 160 | 160 |  | Bromideb, mg/L | 160 | 160 |  |  |  | Total hardness | mg/L as CaCO3 | 184 | 1420 | 2364.7134 | 39.0728 | 1892.3567 | 90.2767 | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE! |  |  |  | Total hardness | mg/L as CaCO3 | 214 | 1230 | 2021.6883 | 22.4638 | 1625.8442 | 86.8376 | Bromideb, mg/L | #DIV/0! | #DIV/0! |  | Bromideb, mg/L | #DIV/0! | #DIV/0! |  |  |  | Total hardness | mg/L as CaCO3 | 246 | 1330 | 2169.2258 | 24.0741 | 1749.6129 | 85.9397 | Bromideb, mg/L | #DIV/0! | #DIV/0! |  | Bromideb, mg/L | #DIV/0! | #DIV/0! |  |  |  | Total hardness | mg/L as CaCO3 | 252 | 1350 | 2200.0645 | 17.1053 | 1775.0323 | 85.8031
|  |  |  | System feed flow rate, QF-sys (gpm) | 1546.1806 | [5 empty] | 1999-01-05 | 0:39 | 28924.9 | 21.8 | 104.2 | 49 | 28.6991 | 0 | 1302 | 154 |  | 1456 | 1456 | 0.89423 | 0 | 14.0346 | 15.4269 | 6.9 | 41.0009 | 0.37626 |  | 6.03 | 259 |  | 391 | 1542 | 1507 | 2.2698 | 33.7596 | 949 | 72.7081 | 104.2 | 80 | 41 | 872 | 584 | 1456 | 1456 | 0.43291 | 0.5989 | 15.9269 | 17.507 | 3.6678 | 47.4322 | 0.3691 | 6.03 | 6.18 | 181 | 391 | 673 | 704.5616 | -4.6897 | 53.7084 | 547.7808 | 66.9576 | 80 | 68 | 11 | 310 | 274 | 584 | 584 | 0.36415 | 0.53082 | 11.3242 | 12.4476 | 6.8421 | 56.1579 | 0.22165 | 6.18 | 6.19 | 236 | 673 | 1202 | 1167.4161 | 2.8772 | 39.6419 | 920.208 | 74.3536 | 68 | 49 | 11 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 12.3903 | 12.0757 | 35.4243 | 0.34977 | 6.19 | 6.2 | 333 | 1202 | 1542 | 1879.1429 | -21.864 | 14.8338 | 1540.5714 | 78.3846 | Alkb, mg/L CaCO3 | 126.9929 | 129.5461 |  | Alkb, mg/L CaCO3 | 126.5351 | 129.2676 |  |  |  | Calcium hardness | mg/L as CaCO3 | 170 | 1120 | 1876.25 | 33.5938 | 1498.125 | 88.6525 | Alkb, mg/L CaCO3 | 108.7252 | NA |  | Alkb, mg/L CaCO3 | 100.6926 | 107.0398 |  |  |  | Calcium hardness | mg/L as CaCO3 | 174 | 1010 | 1656 | 33.0769 | 1333 | 86.9467 | Alkb, mg/L CaCO3 | 123.1381 | 125.9227 |  | Alkb, mg/L CaCO3 | 119.8109 | 123.3142 |  |  |  | Calcium hardness | mg/L as CaCO3 | 160 | 1110 | 1836.1146 | 34.4262 | 1473.0573 | 89.1382 | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Calcium hardness | mg/L as CaCO3 | 178 | 1040 | 1711.6883 | 26.4463 | 1375.8442 | 87.0625 | Alkb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | Alkb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  |  |  | Calcium hardness | mg/L as CaCO3 | 186 | 1030 | 1683.4194 | 23.7705 | 1356.7097 | 86.2904 | Alkb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | Alkb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  |  |  | Calcium hardness | mg/L as CaCO3 | 194 | 1030 | 1677.2258 | 21.1382 | 1353.6129 | 85.668
[11 empty] | 1999-01-06 | 0:13 | 28948.5 | 19.2 | 104.8 | 49 | 29.1091 | 0 | 1296 | 154 |  | 1450 | 1450 | 0.89379 | 0 | 13.9699 | 16.5825 | 6.7181 | 41.0728 | 0.40373 |  | 6.03 | 268 |  | 397 | 1643 | 1482.6104 | 9.762 | 32.4937 | 939.8052 | 71.4835 | 104.8 | 79 | 41 | 870 | 580 | 1450 | 1450 | 0.43079 | 0.6 | 15.8904 | 18.8621 | 3.7975 | 47.1025 | 0.40045 | 6.03 | 6.21 | 180 | 397 | 702 | 722.5 | -2.9202 | 54.6599 | 559.75 | 67.8428 | 79 | 69 | 12 | 307 | 273 | 580 | 580 | 0.36203 | 0.52931 | 11.2146 | 13.3119 | 7.6395 | 54.3605 | 0.24488 | 6.21 | 6.23 | 213 | 702 | 1252 | 1251.9011 | 0.0078994 | 46.3476 | 976.9505 | 78.1975 | 69 | 49 | 12 | 119 | 154 | 273 | 273 | 0.46601 | 0.4359 | 11.1781 | 13.2685 | 12.7407 | 34.2593 | 0.3873 | 6.23 | 6.19 | 333 | 1252 | 1643 | 1962.1364 | -19.424 | 16.1209 | 1607.0682 | 79.279 | T-Hdb, mg/L CaCO3 | 202.3156 | 178.6986 |  | T-Hdb, mg/L CaCO3 | 206.5503 | 181.2751 |  |  |  | Turbidity | ntu | 0.11 | 14 | 25.0572 | 45 | 19.5286 | 99.4367 | T-Hdb, mg/L CaCO3 | 171.145 | NA |  | T-Hdb, mg/L CaCO3 | 218.1049 | 180.9982 |  |  |  | Turbidity | ntu | 0.08 | 24 | 42.4836 | 61.9048 | 33.2418 | 99.7593 | T-Hdb, mg/L CaCO3 | 182.663 | 152.8287 |  | T-Hdb, mg/L CaCO3 | 218.3114 | 180.7766 |  |  |  | Turbidity | ntu | 0.18 | 16 | 28.0917 | 10 | 22.0459 | 99.1835 | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Turbidity | ntu | 0.11 | 15 | 26.6026 | 38.8889 | 20.8013 | 99.4712 | T-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | T-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  |  |  | Turbidity | ntu | 0.1 | 15 | 26.5355 | 60 | 20.7677 | 99.5185 | T-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | T-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  |  |  | Turbidity | ntu | 0.11 | 15 | 26.5277 | 52.1739 | 20.7639 | 99.4702
|  |  |  | Calculate the Required System Influent Pressure | [6 empty] | 1999-01-07 | 2:00 | 28974.4 | 20 | 104.9 | 50 | 29.1091 | 0 | 1299 | 154 |  | 1453 | 1453 | 0.89401 | 0 | 14.0022 | 16.2324 | 7.0958 | 41.245 | 0.39356 |  | 5.94 | 254 |  | 390 | 1638 | 1537.1688 | 6.1557 | 34.8718 | 963.5844 | 73.6401 | 104.9 | 81 | 41 | 874 | 579 | 1453 | 1453 | 0.43121 | 0.60151 | 15.9635 | 18.506 | 3.8254 | 48.1246 | 0.38454 | 5.94 | 6.1 | 172 | 390 | 690 | 719.0708 | -4.2132 | 55.8974 | 554.5354 | 68.983 | 81 | 70 | 12 | 306 | 273 | 579 | 579 | 0.36161 | 0.5285 | 11.1781 | 12.9585 | 7.8022 | 55.6978 | 0.23266 | 6.1 | 6.22 | 190 | 690 | 1258 | 1250.4396 | 0.60099 | 51.2821 | 970.2198 | 80.4168 | 70 | 50 | 12 | 119 | 154 | 273 | 273 | 0.46601 | 0.4359 | 11.1781 | 12.9585 | 12.9348 | 35.0652 | 0.36955 | 6.22 | 6.15 | 325 | 1258 | 1638 | 1978.9545 | -20.8153 | 16.6667 | 1618.4773 | 79.9194 | Ca-Hdb, mg/L CaCO3 | 158.4379 | 135.7784 |  | Ca-Hdb, mg/L CaCO3 | 162.5009 | 138.2505 |  |  |  | Total organic carbon | mg/L | BMRL | 49 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ca-Hdb, mg/L CaCO3 | 135.8855 | NA |  | Ca-Hdb, mg/L CaCO3 | 179.7559 | 145.0904 |  |  |  | Total organic carbon | mg/L | BMRL | 47 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ca-Hdb, mg/L CaCO3 | 161.2597 | 140.5746 |  | Ca-Hdb, mg/L CaCO3 | 185.9759 | 159.9518 |  |  |  | Total organic carbon | mg/L | 1 | 50 | 87.4522 | 87.5 | 68.7261 | 98.5449 | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Total organic carbon | mg/L | BMRL | 9 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ca-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | Ca-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  |  |  | Total organic carbon | mg/L | BMRL | 10 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ca-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | Ca-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  |  |  | Total organic carbon | mg/L | BMRL | 9 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  |  |  | Osmotic pressure for stage 13, Dp1 (psi) | 4 | [5 empty] | 1999-01-08 | 2:00 | 28998.4 | 23 | 105.2 | 50 | 29.6991 | 0 | 1302 | 154 |  | 1456 | 1456 | 0.89423 | 0 | 14.0346 | 14.8893 | 7.5273 | 40.3736 | 0.36879 |  | 5.95 | 254 |  | 398 | 1647 | 1615.4545 | 1.9153 | 36.1809 | 1006.7273 | 74.7697 | 105.2 | 81 | 42 | 875 | 581 | 1456 | 1456 | 0.43227 | 0.60096 | 15.9817 | 16.955 | 3.9618 | 47.1382 | 0.35969 | 5.95 | 6.1 | 172 | 398 | 692 | 738.3614 | -6.6996 | 56.7839 | 568.1807 | 69.7279 | 81 | 70 | 12 | 307 | 274 | 581 | 581 | 0.36288 | 0.5284 | 11.2146 | 11.8976 | 7.7387 | 55.7613 | 0.21337 | 6.1 | 6.19 | 196 | 692 | 1261 | 1247.7372 | 1.0518 | 50.7538 | 969.8686 | 79.7911 | 70 | 50 | 12 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.9585 | 12.9373 | 35.0627 | 0.34106 | 6.19 | 6.1 | 330 | 1261 | 1647 | 1986.4545 | -20.6105 | 17.0854 | 1623.7273 | 79.6764 | Notes: | [9 empty] | UV254 | cm-1 | 0.015 | 1.36 | 2.4307 | 93.1818 | 1.8953 | 99.2086 | Notes: | [9 empty] | UV254 | cm-1 | 0.027 | 1.43 | 2.5141 | 88.5106 | 1.9721 | 98.6309 | Notes: | [9 empty] | UV254 | cm-1 | 0.017 | 1.41 | 2.4747 | 92.5439 | 1.9424 | 99.1248 | Notes: | [9 empty] | UV254 | cm-1 | 0.031 | 1.47 | 2.5913 | 87.0833 | 2.0306 | 98.4734 | Notes: | [9 empty] | UV254 | cm-1 | 0.015 | 1.39 | 2.4545 | 93.2432 | 1.9223 | 99.2197 | Notes: | [9 empty] | UV254 | cm-1 | 0.016 | 1.35 | 2.3828 | 92.7928 | 1.8664 | 99.1427
|  |  |  | Osmotic pressure for stage 23, Dp2 (psi) | 9 | [5 empty] | 1999-01-09 | 0:30 | 29021.6 | 22.9 | 105.1 | 50 | 29.1091 | 0 | 1300 | 154 |  | 1454 | 1454 | 0.89409 | 0 | 14.013 | 14.9104 | 7.2569 | 41.184 | 0.36204 |  | 6.15 | 264 |  | 403 | 1564 | 1576.3766 | -0.79134 | 34.4913 | 989.6883 | 73.3249 | 105.1 | 80 | 41 | 872 | 582 | 1454 | 1454 | 0.43206 | 0.59972 | 15.9269 | 16.9469 | 3.0085 | 48.5415 | 0.34912 | 6.15 | 6.2 | 231 | 403 | 679 | 660.7045 | 2.6945 | 42.6799 | 531.8522 | 56.5669 | 80 | 70 | 12 | 308 | 274 | 582 | 582 | 0.3633 | 0.52921 | 11.2511 | 11.9717 | 7.1698 | 55.8302 | 0.21443 | 6.2 | 6.25 | 220 | 679 | 1213 | 1194.9562 | 1.4875 | 45.4094 | 936.9781 | 76.5203 | 70 | 50 | 12 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.9939 | 12.1869 | 35.8131 | 0.3349 | 6.25 | 6.28 | 336 | 1213 | 1564 | 1896.3766 | -21.2517 | 16.6253 | 1554.6883 | 78.388 | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | NR | 2.7755 | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | NR | 3.0426 | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | 1.7 | 2.82 | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | NR | 16.3333 | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | NR | 13.9 | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | NR | 15 | --- | --- | --- | ---
|  |  |  | Osmotic pressure for stage 33, Dp3 (psi) | 16 | [108 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs.
|  |  |  | Pressure losses due to stage hardware, DPs (psi) | 62 | [108 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5.
|  |  |  | Pressure losses in a single element, DPe (psi) | 10.3 | [108 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters.
|  |  |  | Design permeate pressure, Pp (psi) | 18 | [108 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design.
|  |  |  | Mechanical pressure losses per stage, Ls (psi) | 123.8 | [108 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
|  |  |  | Net driving pressure required for permeation, NDP (psi) | 62.5 | [108 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
|  |  |  | Flow weighted system pressure losses, Lsys (psi) | 133.6967 | [108 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio.
|  |  |  | Required influent pressure to the system, PI (psi) | 214.1967 | [108 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL.
|  |  |  | 3: The osmotic pressure can be estimated from Table 6-5 in Part 3 of the | [109 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
"ICR Manual for Bench- and Pilot-Scale Treatment Studies."
Note on A1: TSC_ADM: This utility had trouble with their SDS chlorinations as in their response to EPA review and comments "Overall, all SDS residuals were very inconsistent. Our source water is very stable, but we experienced difficulty in retrieving good residuals on a regular basis. This could be in part to H2S levels in the water since odor removal is not preformed until after production. All SDS residuals below 0.1 were listed as 'NR'"
Note on E23: TSC_ADM: Reviewer entered a more appropriate membrane width
Note on W6: TSC_ADM: System Pp was approximated based on the number of parallel pressure vessels in each stage.
Note on DS16: C. Rice: Utility verified all alkalinity data stating that permeate values may be greater than feed values due to CO2.
Note on ED26: TSC_ADM: Data entered by the reviewer since utility did not so do
Note on ED48: TSC_ADM: Data entered by the reviewer since utility did not so do
Note on EX26: TSC_ADM: Data entered by the reviewer since utility did not so do
Note on EX48: TSC_ADM: Data entered by the reviewer since utility did not so do
Note on FR26: TSC_ADM: Data entered by the reviewer since utility did not so do
Note on FR48: TSC_ADM: Data entered by the reviewer since utility did not so do
Note on GA23: C. Rice: Utility verified week 38 UV data.
Note on GL26: TSC_ADM: Data entered by the reviewer since utility did not so do
Note on GL48: TSC_ADM: Data entered by the reviewer since utility did not so do
Note on GN43: TSC_ADM: Reviewer changed reported permeate and feed TOC concentrations because they were obviously switched
Note on GO43: TSC_ADM: Reviewer changed reported permeate and feed TOC concentrations because they were obviously switched
Note on HF26: TSC_ADM: Data entered by the reviewer since utility did not so do
Note on HF48: TSC_ADM: Data entered by the reviewer since utility did not so do
Note on HZ26: TSC_ADM: Data entered by the reviewer since utility did not so do
Note on HZ48: TSC_ADM: Data entered by the reviewer since utility did not so do

## Sheet5. Weeks 41-50
FIELD-SET 5: PILOT-SCALE MEMBRANE RESULTS: WEEKS 41-50 (FILE: mempilot.xls)
Field 5-1: PWS And Treatment Plant Data |  | Field 5-2: Manufacturer Reported Membrane Characteristics1 |  | Field 5-3: 3-Stage Membrane Pilot System Design Parameters |  | Field 5-4: Foulants And Fouling Indices1 |  | Field 5-5: Pretreatment Used Prior To Membranes1 |  |  | Field 5-6: Membrane Performance Data During Operation With The Test Water | [18 empty] | Field 5-6: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 5-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 5-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 5-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 5-7: System And Stage Water Quality For Week 42 | [9 empty] | Field 5-7: System And Stage Water Quality For Week 42 (continued) | [7 empty] | Field 5-8: System And Stage Water Quality For Week 44 | [9 empty] | Field 5-8: System And Stage Water Quality For Week 44 (continued) | [7 empty] | Field 5-9: System And Stage Water Quality For Week 46 | [9 empty] | Field 5-9: System And Stage Water Quality For Week 46 (continued) | [7 empty] | Field 5-10: System And Stage Water Quality For Week 48 | [9 empty] | Field 5-10: System And Stage Water Quality For Week 48 (continued) | [7 empty] | Field 5-11: System And Stage Water Quality For Week 50 | [9 empty] | Field 5-11: System And Stage Water Quality For Week 50 (continued) | [7 empty] | Field 5-12: Duplicate Analysis Of System And Stage Water Quality For Week 50 | [9 empty] | Field 5-12: Duplicate Analysis Of System And Stage Water Quality For Week 50 (continued) | [7 empty] | Field 5-13: Membrane Cost Parameters
|  | General Information |  | Calculate Temperature Normalized MTCW |  | Parameters Evaluated Prior to Pretreatment |  |  |  |  | System Operating Parameters | [30 empty] | Stage 1 Operating Parameters | [23 empty] | Stage 2 Operating Parameters | [23 empty] | Stage 3 Operating Parameters | [23 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | General Cost Parameters
PWS Name | Collier County Water Department | Membrane manufacturer | Hydranautics | Average yearly temperature of feed water, TavgoC (oC) | 25 | Alkalinity (mg/L as CaCO3) | 290 | Process | Description | Scale | Date | Time | Operation |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  |  |  | System recovery during sample collection (decimal) | 0.89 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.6 | [6 empty] | System recovery during sample collection (decimal) | 0.89 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.6 | [6 empty] | System recovery during sample collection (decimal) | 0.89 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.6 | [6 empty] | System recovery during sample collection (decimal) | 0.89 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.6 | [6 empty] | System recovery during sample collection (decimal) | 0.9 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.6 | [6 empty] | System recovery during sample collection (decimal) | 0.9 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.6 |  |  |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | FL5114069 | Membrane trade name | PVD 1 | Temperature normalized MTCW (gfd/psi) | 0.24 | Calcium Hardness (mg/L as CaCO3) | 220 | Sulfuric Acid Addition | pH adjustment to 5.8-6.0 | full-scale |  |  | time | Influent | PI | PC | PP | QR | Qp | QW | Cleaning Event | QF | QI | Recovery | Recycle | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) |  |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) |  |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) | [6 empty] | System feed flow rate during sample collection (gpm) | 1459 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 871 | [6 empty] | System feed flow rate during sample collection (gpm) | 1457 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 872 | [6 empty] | System feed flow rate during sample collection (gpm) | 1460 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 874 | [6 empty] | System feed flow rate during sample collection (gpm) | 1455 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 873 | [6 empty] | System feed flow rate during sample collection (gpm) | 1542 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 925 | [6 empty] | System feed flow rate during sample collection (gpm) | 1542 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 925 |  |  |  |  | Capital Recovery Interest Rate (%) | N/A
Water Industry Data Base Number (optional) | NA | Membrane element model number | 8040-LSY-PVD1 |  |  | LSI | 7.26 | Anti-Scalant Addition | Argo Scientific Hyperspearse AS120UL | full-scale | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | Indicate with "X" | (gpm) | (gpm) | (decimal) | ratio | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHF (before acid) | pHF (after acid) | TDSp | TDSF (before acid) | TDSF (after acid) | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) |  |  | System influent flow rate during sample collection (gpm) | 1301 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 1459 | [6 empty] | System influent flow rate during sample collection (gpm) | 1303 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 1457 | [6 empty] | System influent flow rate during sample collection (gpm) | 1304 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 1460 | [6 empty] | System influent flow rate during sample collection (gpm) | 1301 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 1455 | [6 empty] | System influent flow rate during sample collection (gpm) | 1388 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 1542 | [6 empty] | System influent flow rate during sample collection (gpm) | 1388 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 1542 |  |  |  |  | Capital Recovery Period (years) | 25
|  | Molecular weight cutoff (Daltons) | 100-300 | Calculate System Permeate, Feed and Waste Flow Rates |  | Dissolved iron (mg/L) |  | Cartridge Filtration | 5 Micron | full-scale | 1999-01-10 | 8:50 | 29053.1 | 23.1 | 105 | 50 | 29.6991 | 0 | 1298 | 154 |  | 1452 | 1452 | 0.89394 | 0 | 13.9915 | 14.7997 | 6.7786 | 41.0223 | 0.36077 |  | 6.04 | 258 |  | 388 | 1608 | 1483.7143 | 7.7292 | 33.5052 | 935.8571 | 72.4317 | 105 | 80 | 42 | 870 | 582 | 1452 | 1452 | 0.43164 | 0.59917 | 15.8904 | 16.8084 | 3.5298 | 46.9702 | 0.35785 | 6.04 | 6.16 | 186 | 388 | 681 | 689.9588 | -1.3155 | 52.0619 | 538.9794 | 65.4903 | 80 | 70 | 12 | 308 | 274 | 582 | 582 | 0.3633 | 0.52921 | 11.2511 | 11.9011 | 7.1385 | 55.8615 | 0.21305 | 6.16 | 6.27 | 224 | 681 | 1216 | 1194.708 | 1.751 | 42.268 | 937.854 | 76.1157 | 70 | 50 | 12 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.9232 | 12.3397 | 35.6603 | 0.33435 | 6.27 | 6.29 | 328 | 1216 | 1608 | 1907.9481 | -18.6535 | 15.4639 | 1561.974 | 79.0009 | [108 empty] | Overhead & Profit Factor (% of construction costs) | 10
Official ICR Contact Person |  | Membrane material (e.g., PVD, polyamide, etc.) | Poly Vinyl Derivative | Design system recovery, R (decimal) | 0.9 | Total iron (mg/L) | 0.03 |  |  |  | 1999-01-13 | 0:20 | 29109.4 | 21.8 | 105 | 50 | 29.1091 | 0 | 1306 | 154 |  | 1460 | 1460 | 0.89452 | 0 | 14.0777 | 15.4743 | 7.2316 | 41.1593 | 0.37596 |  | 5.98 | 256 |  | 394 | 1586 | 1564.3117 | 1.3675 | 35.0254 | 979.1558 | 73.855 | 105 | 81 | 41 | 874 | 586 | 1460 | 1460 | 0.43418 | 0.59863 | 15.9635 | 17.5471 | 3.8406 | 48.1594 | 0.36436 | 5.98 | 6.14 | 174 | 394 | 686 | 722.1229 | -5.2657 | 55.8376 | 558.0614 | 68.8206 | 81 | 69 | 12 | 311 | 275 | 586 | 586 | 0.36543 | 0.53072 | 11.3607 | 12.4878 | 7.5455 | 55.4545 | 0.22519 | 6.14 | 6.18 | 204 | 686 | 1236 | 1231.0982 | 0.39659 | 48.2234 | 958.5491 | 78.7178 | 69 | 50 | 12 | 121 | 154 | 275 | 275 | 0.4682 | 0.44 | 11.3659 | 12.4935 | 12.6889 | 34.8111 | 0.3589 | 6.18 | 6.14 | 325 | 1236 | 1586 | 1951.7857 | -23.0634 | 17.5127 | 1593.8929 | 79.6097 | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | Special Sitework Factor (% of construction costs) | N/A
Mailing Address |  | Membrane construction (e.g., thin-film composite) | Thin Film Composite | Design average system flux, FW (gfd) | 15 | Dissolved aluminum (mg/L) |  |  |  |  | 1999-01-14 | 0:43 | 29133.8 | 22.1 | 105.7 | 50 | 29.6991 | 0 | 1299 | 154 |  | 1453 | 1453 | 0.89401 | 0 | 14.0022 | 15.2555 | 7.5132 | 40.6376 | 0.3754 |  | 5.93 | 252 |  | 396 | 1602 | 1610.6494 | -0.53991 | 36.3636 | 1003.3247 | 74.8835 | 105.7 | 81 | 42 | 871 | 582 | 1453 | 1453 | 0.43185 | 0.59945 | 15.9087 | 17.3325 | 3.9162 | 47.4338 | 0.3654 | 5.93 | 6.04 | 172 | 396 | 685 | 731.2302 | -6.7489 | 56.5657 | 563.6151 | 69.4827 | 81 | 70 | 12 | 308 | 274 | 582 | 582 | 0.3633 | 0.52921 | 11.2511 | 12.2581 | 7.4822 | 56.0178 | 0.21883 | 6.04 | 6.13 | 206 | 685 | 1235 | 1223.438 | 0.9362 | 47.9798 | 954.219 | 78.4117 | 70 | 50 | 12 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 12.2809 | 12.6455 | 35.3545 | 0.34736 | 6.13 | 6.13 | 325 | 1235 | 1602 | 1944.0909 | -21.354 | 17.9293 | 1589.5455 | 79.5539 | Parameter | Units | Cp-sys-42 | CF-sys-42 | CC-sys-42 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-42 | CI-s1-42 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-44 | CF-sys-44 | CC-sys-44 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-44 | CI-s1-44 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-46 | CF-sys-46 | CC-sys-46 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-46 | CI-s1-46 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-48 | CF-sys-48 | CC-sys-48 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-48 | CI-s1-48 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-50 | CF-sys-50 | CC-sys-50 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-50 | CI-s1-50 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-50 (dup) | CF-sys-50 (dup) | CC-sys-50 (dup) | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-50 (dup) | CI-s1-50 (dup) | CC(calc) | RF (%) | CB | RB (%) | Construction Contingencies (% of construction costs) | N/A
|  | Membrane hydrophobicity | Hydrophillic | Number of elements per pressure vessel, Ne | 6 | Total aluminum (mg/L) | <0.10 |  |  |  | 1999-01-15 | 0:33 | 29146.1 | 22.3 | 105.7 | 50 | 29.6991 | 0 | 1306 | 143 |  | 1449 | 1449 | 0.90131 | 0 | 14.0777 | 15.2473 | 7.96 | 40.1909 | 0.37937 |  | 5.99 | 255 |  | 398 | 1617 | 1704 | -5.3803 | 35.9296 | 1051 | 75.7374 | 105.7 | 81 | 42 | 872 | 577 | 1449 | 1449 | 0.42994 | 0.60179 | 15.9269 | 17.2501 | 3.9853 | 47.3647 | 0.3642 | 5.99 | 6.06 | 171 | 398 | 700 | 741.0572 | -5.8653 | 57.0352 | 569.5286 | 69.9752 | 81 | 70 | 12 | 312 | 265 | 577 | 577 | 0.35736 | 0.54073 | 11.3973 | 12.3441 | 7.9434 | 55.5566 | 0.22219 | 6.06 | 6.1 | 200 | 700 | 1242 | 1288.6792 | -3.7584 | 49.7487 | 994.3396 | 79.8861 | 70 | 50 | 12 | 122 | 143 | 265 | 265 | 0.44528 | 0.46038 | 11.4599 | 12.412 | 13.1245 | 34.8755 | 0.35589 | 6.1 | 6.1 | 322 | 1242 | 1617 | 2026.8951 | -25.3491 | 19.0955 | 1634.4476 | 80.2992 | Sampling date | MM/DD/YY | 1999-01-19 | 1999-01-19 | 1999-01-19 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-01-19 | 1999-01-19 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-02-01 | 1999-02-01 | 1999-02-01 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-02-01 | 1999-02-01 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-02-16 | 1999-02-16 | 1999-02-16 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-02-16 | 1999-02-16 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-03-01 | 1999-03-01 | 1999-03-01 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-03-01 | 1999-03-01 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-03-15 | 1999-03-15 | 1999-03-15 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-03-15 | 1999-03-15 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-03-15 | 1999-03-15 | 1999-03-15 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-03-15 | 1999-03-15 | --- | --- | --- | --- | Engineering Fee Factor (% of construction costs) | 19
Phone Number |  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Negative | Number of parallel pressure vessels in stage 1, Nv-s(1) | 36 | Fluoride (mg/L) | 0.3 |  |  |  | 1999-01-16 | 1:47 | 29166 | 23 | 105.3 | 49 | 29.1091 | 0 | 1298 | 145 |  | 1443 | 1443 | 0.89951 | 0 | 13.9915 | 14.8435 | 5.7497 | 42.2912 | 0.35098 |  | 6.02 | 296 |  | 401 | 1522 | 1340.931 | 11.8968 | 26.1845 | 870.9655 | 66.0147 | 105.3 | 81 | 41 | 873 | 570 | 1443 | 1443 | 0.42718 | 0.60499 | 15.9452 | 16.9163 | 3.8671 | 48.2829 | 0.35036 | 6.02 | 6.25 | 182 | 401 | 684 | 736.4158 | -7.6631 | 54.6135 | 568.7079 | 67.9976 | 81 | 69 | 12 | 306 | 264 | 570 | 570 | 0.35397 | 0.53684 | 11.1781 | 11.8588 | 7.4713 | 55.5288 | 0.21356 | 6.25 | 6.28 | 211 | 684 | 1195 | 1232.25 | -3.1172 | 47.3815 | 958.125 | 77.9778 | 69 | 49 | 12 | 119 | 145 | 264 | 264 | 0.44637 | 0.45076 | 11.1781 | 11.8588 | 11.9597 | 35.0403 | 0.33843 | 6.28 | 6.26 | 347 | 1195 | 1522 | 1890.9448 | -24.2408 | 13.4663 | 1542.9724 | 77.5109 | Sampling time | hh:mm | 8:37 | 9:01 | 9:13 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 8:43 | 9:01 | --- | --- | --- | --- | Sampling time | hh:mm | 8:07 | 8:22 | 8:33 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 8:13 | 8:22 | --- | --- | --- | --- | Sampling time | hh:mm | 9:30 | 9:48 | 10:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 9:34 | 9:48 | --- | --- | --- | --- | Sampling time | hh:mm | 8:36 | 8:49 | 9:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 8:42 | 8:49 | --- | --- | --- | --- | Sampling time | hh:mm | 8:41 | 9:02 | 9:18 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 8:50 | 9:02 | --- | --- | --- | --- | Sampling time | hh:mm | 8:41 | 9:02 | 9:18 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 8:50 | 9:02 | --- | --- | --- | --- | 1998 ENR Construction Cost Index (CCI base year 1913) | 5895.11
FAX Number |  |  |  | Number of parallel pressure vessels in stage 2, Nv-s(2) | 18 | Phosphate (mg/L) | 0.05mg/L as PO4 |  |  |  | 1999-01-17 | 3:30 | 29191.9 | 22.6 | 104.9 | 50 | 29.1091 | 0 | 1300 | 154 |  | 1454 | 1454 | 0.89409 | 0 | 14.013 | 15.0432 | 8.04 | 40.3009 | 0.37327 |  | 5.98 | 266 |  | 420 | 1508 | 1720 | -14.0584 | 36.6667 | 1070 | 75.1402 | 104.9 | 80 | 41 | 872 | 682 | 1554 | 1554 | 0.4745 | 0.56113 | 15.9269 | 17.0979 | 3.8523 | 47.5977 | 0.35922 | 5.98 | 6.23 | 185 | 420 | 673 | 720.4692 | -7.0534 | 55.9524 | 570.2346 | 67.5572 | 80 | 70 | 12 | 308 | 374 | 682 | 682 | 0.44819 | 0.45161 | 11.2511 | 12.0783 | 6.4376 | 56.5624 | 0.21354 | 6.23 | 6.28 | 217 | 673 | 1234 | 1048.5294 | 15.03 | 48.3333 | 860.7647 | 74.7899 | 70 | 50 | 12 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 12.1007 | 12.2008 | 35.7992 | 0.33802 | 6.28 | 6.23 | 356 | 1234 | 1508 | 1918.1558 | -27.1987 | 15.2381 | 1576.0779 | 77.4123 | Operation time | hh.hh | 29244.8 | 29245.2 | 29245.4 | --- | --- | --- | --- | --- | Operation time | hh.hh | 29244.9 | 29245.2 | --- | --- | --- | --- | Operation time | hh.hh | 29516 | 29516.2 | 29516.4 | --- | --- | --- | --- | --- | Operation time | hh.hh | 29516.1 | 29516.2 | --- | --- | --- | --- | Operation time | hh.hh | 29859.7 | 29860 | 29860.2 | --- | --- | --- | --- | --- | Operation time | hh.hh | 29859.7 | 29860 | --- | --- | --- | --- | Operation time | hh.hh | 30145.2 | 30145.4 | 30145.6 | --- | --- | --- | --- | --- | Operation time | hh.hh | 30145.3 | 30145.4 | --- | --- | --- | --- | Operation time | hh.hh | 30456.8 | 30457.2 | 30457.5 | --- | --- | --- | --- | --- | Operation time | hh.hh | 30457 | 30457.2 | --- | --- | --- | --- | Operation time | hh.hh | 30456.8 | 30457.2 | 30457.5 | --- | --- | --- | --- | --- | Operation time | hh.hh | 30457 | 30457.2 | --- | --- | --- | --- | 1998 Producers Price Index (PPI base year 1967 = 100) | 123.9
E-Mail Address (optional) |  | Design Parameters |  | Number of parallel pressure vessels in stage 3, Nv-s(3) | 7 | Sulfate (mg/L) | 20 |  |  |  | 1999-01-18 | 0:00 | 29212.5 | 22.9 | 105.2 | 50 | 29.1091 | 0 | 1300 | 152 |  | 1452 | 1452 | 0.89532 | 0 | 14.013 | 14.9104 | 7.8089 | 40.6819 | 0.36651 | 6.99 | 6.02 | 255 | 394 | 403 | 1636 | 1668.7895 | -2.0042 | 36.7246 | 1035.8947 | 75.3836 | 105.2 | 80 | 41 | 871 | 581 | 1452 | 1452 | 0.43142 | 0.59986 | 15.9087 | 16.9275 | 3.4292 | 48.1708 | 0.35141 | 6.02 | 6.24 | 207 | 403 | 692 | 696.8313 | -0.69817 | 48.6352 | 549.9157 | 62.3579 | 80 | 70 | 12 | 309 | 272 | 581 | 581 | 0.36203 | 0.53184 | 11.2877 | 12.0105 | 7.1188 | 55.8812 | 0.21493 | 6.24 | 6.17 | 238 | 692 | 1228 | 1207.7574 | 1.6484 | 40.9429 | 949.8787 | 74.9442 | 70 | 50 | 12 | 120 | 152 | 272 | 272 | 0.46274 | 0.44118 | 11.272 | 11.9939 | 12.2039 | 35.7961 | 0.33506 | 6.17 | 6.21 | 353 | 1228 | 1636 | 1918.7895 | -17.2854 | 12.4069 | 1573.3947 | 77.5644 | pH | --- | 6.11 | 5.95 | 6.23 | --- | --- | --- | --- | --- | pH | --- | 6.13 | 5.95 | --- | --- | --- | --- | pH | --- | 6.24 | 6.23 | 6.11 | --- | --- | --- | --- | --- | pH | --- | 6.03 | 6.23 | --- | --- | --- | --- | pH | --- | 6.3 | 6.2 | 6.3 | --- | --- | --- | --- | --- | pH | --- | 6.1 | 6.2 | --- | --- | --- | --- | pH | --- | 6.19 | 6.07 | 6.11 | --- | --- | --- | --- | --- | pH | --- | 5.99 | 6.07 | --- | --- | --- | --- | pH | --- | 6.22 | 6.21 | 6.21 | --- | --- | --- | --- | --- | pH | --- | 6.05 | 6.21 | --- | --- | --- | --- | pH | --- | 6.22 | 6.21 | 6.21 | --- | --- | --- | --- | --- | pH | --- | 6.05 | 6.21 | --- | --- | --- | --- | Labor Rate + Fringe ($/work-hour) | 24.39
|  | Element size (e.g., 2.5" x 40", 4" x 40", etc.) | 8" X 40" | Permeate flow rate per element, Qp-e (gpm) | 3.8021 | Calcium (mg/L) | 82 |  |  |  | 1999-01-19 | 0:28 | 29236.7 | 23.3 | 105.3 | 50 | 29.1091 | 0 | 1298 | 159 |  | 1457 | 1457 | 0.89087 | 0 | 13.9915 | 14.7125 | 7.8767 | 40.6641 | 0.36181 |  | 5.93 | 250 |  | 405 | 1639 | 1670.3459 | -1.9125 | 38.2716 | 1037.673 | 75.9076 | 105.3 | 81 | 41 | 872 | 585 | 1457 | 1457 | 0.43333 | 0.59849 | 15.9269 | 16.7477 | 4.0665 | 48.0835 | 0.34831 | 5.93 | 6.08 | 172 | 405 | 702 | 752.3094 | -7.1666 | 57.5309 | 578.6547 | 70.2759 | 81 | 70 | 12 | 307 | 278 | 585 | 585 | 0.36628 | 0.52479 | 11.2146 | 11.7925 | 7.7608 | 55.7392 | 0.21157 | 6.08 | 6.11 | 202 | 702 | 1272 | 1254.1583 | 1.4027 | 50.1235 | 978.0791 | 79.3473 | 70 | 50 | 12 | 119 | 159 | 278 | 278 | 0.47693 | 0.42806 | 11.1781 | 11.7541 | 13.0825 | 34.9175 | 0.33663 | 6.11 | 6.06 | 320 | 1272 | 1639 | 1984.5031 | -21.0801 | 20.9877 | 1628.2516 | 80.347 | Temperature | oC | 24.4 | 24.3 | 24.4 | --- | --- | --- | --- | --- | Temperature | oC | 24.6 | 24.3 | --- | --- | --- | --- | Temperature | oC | 24.1 | 24 | 23.3 | --- | --- | --- | --- | --- | Temperature | oC | 23.1 | 24 | --- | --- | --- | --- | Temperature | oC | 23 | 23 | 23 | --- | --- | --- | --- | --- | Temperature | oC | 23 | 23 | --- | --- | --- | --- | Temperature | oC | 23.7 | 23.5 | 22.6 | --- | --- | --- | --- | --- | Temperature | oC | 23.3 | 23.5 | --- | --- | --- | --- | Temperature | oC | 24.1 | 23.6 | 23.5 | --- | --- | --- | --- | --- | Temperature | oC | 24.1 | 23.6 | --- | --- | --- | --- | Temperature | oC | 24.1 | 23.6 | 23.5 | --- | --- | --- | --- | --- | Temperature | oC | 24.1 | 23.6 | --- | --- | --- | --- | Labor Overhead Factor (% of labor) | 10
Technical ICR Contact Person |  | Active membrane area of membrane element used, A (ft2) | 365 | Permeate flow rate per pressure vessel, Qp-v (gpm) | 22.8125 | Barium (mg/L) | 0.008 |  |  |  | 1999-01-21 | 2:09 | 29286.4 | 23.2 | 106 | 50 | 29.6991 | 0 | 1310 | 136 |  | 1446 | 1446 | 0.90595 | 0 | 14.1208 | 14.8925 | 8.0263 | 40.2746 | 0.36977 |  | 6.23 | 253 |  | 391 | 1541 | 1720.2647 | -11.633 | 35.2941 | 1055.6324 | 76.0333 | 106 | 81 | 42 | 872 | 574 | 1446 | 1446 | 0.42867 | 0.60304 | 15.9269 | 16.7973 | 3.8535 | 47.6465 | 0.35254 | 6.23 | 6.34 | 172 | 391 | 675 | 723.6969 | -7.2144 | 56.0102 | 557.3484 | 69.1396 | 81 | 70 | 12 | 315 | 259 | 574 | 574 | 0.35354 | 0.54878 | 11.5068 | 12.1357 | 7.6224 | 55.8776 | 0.21718 | 6.34 | 6.3 | 201 | 675 | 1201 | 1251.4865 | -4.2037 | 48.5934 | 963.2432 | 79.133 | 70 | 50 | 12 | 123 | 136 | 259 | 259 | 0.43109 | 0.4749 | 11.5538 | 12.1852 | 12.7939 | 35.2061 | 0.34611 | 6.3 | 6.26 | 320 | 1201 | 1541 | 1997.7868 | -29.6422 | 18.1586 | 1599.3934 | 79.9924 | Alkalinity | mg/L as CaCO3 | 138 | 84 | 36 | -352.9091 | 1080.303 | -64.2857 | -107.9243 | 227.8674 | Alkalinity | mg/L as CaCO3 | 83 | 84 | 85.4813 | 1.1905 | 84.7406 | 2.0541 | Alkalinity | mg/L as CaCO3 | 118 | 98 | 36 | -63.8182 | 277.2727 | -20.4082 | 26.6535 | -342.7193 | Alkalinity | mg/L as CaCO3 | 78 | 98 | 127.812 | 20.4082 | 112.906 | 30.916 | Alkalinity | mg/L as CaCO3 | 104 | 90 | 130 | -23.2727 | 117.9021 | -15.5556 | 40.1392 | -159.0986 | Alkalinity | mg/L as CaCO3 | 69 | 90 | 121.3208 | 23.3333 | 105.6604 | 34.6964 | Alkalinity | mg/L as CaCO3 | 100 | 78 | 140 | -100 | 171.4286 | -28.2051 | -0.46503 | 21604.1322 | Alkalinity | mg/L as CaCO3 | 65 | 78 | 97.5 | 16.6667 | 87.75 | 25.9259 | Alkalinity | mg/L as CaCO3 | 110 | 92 | 160 | -70 | 143.75 | -19.5652 | 19.987 | -450.3569 | Alkalinity | mg/L as CaCO3 | 69 | 92 | 126.4814 | 25 | 109.2407 | 36.8367 | Alkalinity | mg/L as CaCO3 | 112 | 94 | 160 | -68 | 142.5 | -19.1489 | 21.987 | -409.3912 | Alkalinity | mg/L as CaCO3 | 70 | 94 | 129.9806 | 25.5319 | 111.9903 | 37.4946 | Electric Rate ($/kW-h) | 0.05
Mailing Address |  | Design flux, FW (gfd) | 30 | Permeate flow rate from stage 1, Qp-s(1) (gpm) | 821.25 | Strontium (mg/L) | 0.6 |  |  |  | 1999-01-23 | 0:43 | 29329.6 | 23.6 | 105.3 | 49 | 29.1091 | 0 | 1298 | 153 |  | 1451 | 1451 | 0.89456 | 0 | 13.9915 | 14.5826 | 7.9676 | 40.0733 | 0.3639 |  | 6.04 | 247 |  | 399 | 1625 | 1688.5163 | -3.9087 | 38.0952 | 1043.7582 | 76.3355 | 105.3 | 81 | 41 | 870 | 581 | 1451 | 1451 | 0.43121 | 0.59959 | 15.8904 | 16.5618 | 3.9871 | 48.1629 | 0.34387 | 6.04 | 6.16 | 171 | 399 | 697 | 740.4114 | -6.2283 | 57.1429 | 569.7057 | 69.9845 | 81 | 69 | 12 | 308 | 273 | 581 | 581 | 0.36246 | 0.53012 | 11.2511 | 11.7265 | 7.8049 | 55.1951 | 0.21246 | 6.16 | 6.1 | 198 | 697 | 1259 | 1259.9744 | -0.077391 | 50.3759 | 978.4872 | 79.7647 | 69 | 49 | 12 | 120 | 153 | 273 | 273 | 0.46492 | 0.43956 | 11.272 | 11.7483 | 13.2116 | 33.7884 | 0.3477 | 6.1 | 6.06 | 310 | 1259 | 1625 | 2003.3137 | -23.2808 | 22.3058 | 1631.1569 | 80.9951 | Total dissolved solids | mg/L | 290 | 572 | 3184 | 2853.6364 | 10.3757 | 49.3007 | 1574.2715 | 81.5788 | Total dissolved solids | mg/L | 194 | 572 | 1131.9286 | 66.0839 | 851.9643 | 77.2291 | Total dissolved solids | mg/L | 270 | 572 | 3148 | 3015.4545 | 4.2105 | 52.7972 | 1649.3328 | 83.6297 | Total dissolved solids | mg/L | 186 | 572 | 1147.3709 | 67.4825 | 859.6855 | 78.3642 | Total dissolved solids | mg/L | 282 | 544 | 3436 | 2663.8182 | 22.4733 | 48.1618 | 1477.1102 | 80.9087 | Total dissolved solids | mg/L | 186 | 544 | 1077.9454 | 65.8088 | 810.9727 | 77.0646 | Total dissolved solids | mg/L | 268 | 528 | 3312 | 2631.6364 | 20.5424 | 49.2424 | 1455.314 | 81.5847 | Total dissolved solids | mg/L | 180 | 528 | 1050 | 65.9091 | 789 | 77.1863 | Total dissolved solids | mg/L | 278 | 504 | 3336 | 2538 | 23.9209 | 44.8413 | 1408.1628 | 80.258 | Total dissolved solids | mg/L | 186 | 504 | 980.7423 | 63.0952 | 742.3712 | 74.9451 | Total dissolved solids | mg/L | 266 | 496 | 3388 | 2566 | 24.2621 | 46.371 | 1416.1657 | 81.2169 | Total dissolved solids | mg/L | 188 | 496 | 957.7504 | 62.0968 | 726.8752 | 74.1359 | Fuel Oil Rate ($/gal) | 0.43
|  | Net driving pressure at the design flux, NDP (psi) | 125 | Permeate flow rate from stage 2, Qp-s(2) (gpm) | 410.625 | Reactive silica (mg/L as SiO2) | 18 |  |  |  | 1999-01-24 | 0:50 | 29353.7 | 23.7 | 107 | 50 | 29.1091 | 0 | 1297 | 154 |  | 1451 | 1451 | 0.89387 | 0 | 13.9807 | 14.5284 | 8.025 | 41.3659 | 0.35122 |  | 6.02 | 234 |  | 388 | 1612 | 1685 | -4.5285 | 39.6907 | 1036.5 | 77.424 | 107 | 81 | 41 | 868 | 583 | 1451 | 1451 | 0.43164 | 0.59821 | 15.8539 | 16.4749 | 3.8377 | 49.1623 | 0.33511 | 6.02 | 6.11 | 168 | 388 | 686 | 715.5472 | -4.3072 | 56.701 | 551.7736 | 69.5527 | 81 | 70 | 12 | 309 | 274 | 583 | 583 | 0.36373 | 0.53002 | 11.2877 | 11.7299 | 7.5535 | 55.9465 | 0.20966 | 6.11 | 6.18 | 203 | 686 | 1260 | 1230.6971 | 2.3256 | 47.6804 | 958.3485 | 78.8177 | 70 | 50 | 12 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.7136 | 13.3958 | 34.6042 | 0.3385 | 6.18 | 6.19 | 296 | 1260 | 1612 | 2011.1688 | -24.7623 | 23.7113 | 1635.5844 | 81.9025 | Total hardness | mg/L as CaCO3 | 164 | 302 | 1920 | 1418.5455 | 26.1174 | 45.6954 | 792.4733 | 79.3053 | Total hardness | mg/L as CaCO3 | 98 | 302 | 604.1837 | 67.5497 | 453.0918 | 78.3708 | Total hardness | mg/L as CaCO3 | 140 | 301 | 1860 | 1603.6364 | 13.783 | 53.4884 | 875.3397 | 84.0062 | Total hardness | mg/L as CaCO3 | 90 | 301 | 615.5162 | 70.0997 | 458.2581 | 80.3604 | Total hardness | mg/L as CaCO3 | 130 | 306 | 1920 | 1730 | 9.8958 | 57.5163 | 932.8221 | 86.0638 | Total hardness | mg/L as CaCO3 | 83 | 306 | 638.5973 | 72.8758 | 472.2986 | 82.4264 | Total hardness | mg/L as CaCO3 | 132 | 296 | 1940 | 1622.9091 | 16.3449 | 55.4054 | 880.9211 | 85.0157 | Total hardness | mg/L as CaCO3 | 83 | 296 | 615.5 | 71.9595 | 455.75 | 81.7883 | Total hardness | mg/L as CaCO3 | 148 | 300 | 1820 | 1668 | 8.3516 | 50.6667 | 908.1095 | 83.7024 | Total hardness | mg/L as CaCO3 | 91 | 300 | 613.3306 | 69.6667 | 456.6653 | 80.0729 | Total hardness | mg/L as CaCO3 | 152 | 302 | 1850 | 1652 | 10.7027 | 49.6689 | 902.1081 | 83.1506 | Total hardness | mg/L as CaCO3 | 92 | 302 | 616.8298 | 69.5364 | 459.4149 | 79.9745 | Natural Gas Rate ($/ft3) | N/A
Phone Number |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.24 | Permeate flow rate from stage 3, Qp-s(3) (gpm) | 159.6875 | Turbidity (ntu) | <0.5 |  |  |  | 1999-01-25 | 6:40 | 29370.6 | 21.5 | 103.3 | 50 | 29.6991 | 0 | 1303 | 154 |  | 1457 | 1457 | 0.8943 | 0 | 14.0454 | 15.5763 | 4.289 | 42.6619 | 0.36511 |  | 6.38 | 278 |  | 360 | 938 | 1053.8052 | -12.346 | 22.7778 | 706.9026 | 60.6735 | 103.3 | 82 | 42 | 873 | 584 | 1457 | 1457 | 0.43312 | 0.59918 | 15.9452 | 17.6832 | 2.9182 | 47.7318 | 0.37047 | 6.38 | 6.37 | 193 | 360 | 498 | 609.6421 | -22.4181 | 46.3889 | 484.8211 | 60.1915 | 82 | 70 | 12 | 310 | 274 | 584 | 584 | 0.36415 | 0.53082 | 11.3242 | 12.5585 | 4.337 | 59.663 | 0.21049 | 6.37 | 6.4 | 221 | 498 | 730 | 811.3942 | -11.1499 | 38.6111 | 654.6971 | 66.2439 | 70 | 50 | 12 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 12.5006 | 6.4756 | 41.5244 | 0.30104 | 6.4 | 6.59 | 264 | 730 | 938 | 1093.1169 | -16.537 | 26.6667 | 911.5584 | 71.0386 | Calcium hardness | mg/L as CaCO3 | 126 | 260 | 1390 | 1344.1818 | 3.2963 | 51.5385 | 736.2567 | 82.8864 | Calcium hardness | mg/L as CaCO3 | 80 | 260 | 526.6327 | 69.2308 | 393.3163 | 79.6601 | Calcium hardness | mg/L as CaCO3 | 106 | 234 | 1470 | 1269.6364 | 13.6302 | 54.7009 | 690.6179 | 84.6514 | Calcium hardness | mg/L as CaCO3 | 72 | 234 | 475.4769 | 69.2308 | 354.7385 | 79.7034 | Calcium hardness | mg/L as CaCO3 | 114 | 246 | 1550 | 1314 | 15.2258 | 53.6585 | 716.1166 | 84.0808 | Calcium hardness | mg/L as CaCO3 | 73 | 246 | 504.0239 | 70.3252 | 375.0119 | 80.534 | Calcium hardness | mg/L as CaCO3 | 126 | 248 | 1540 | 1235.0909 | 19.7993 | 49.1935 | 683.1242 | 81.5553 | Calcium hardness | mg/L as CaCO3 | 82 | 248 | 497 | 66.9355 | 372.5 | 77.9866 | Calcium hardness | mg/L as CaCO3 | 126 | 246 | 1550 | 1326 | 14.4516 | 48.7805 | 726.0865 | 82.6467 | Calcium hardness | mg/L as CaCO3 | 84 | 246 | 488.8687 | 65.8537 | 367.4344 | 77.1388 | Calcium hardness | mg/L as CaCO3 | 130 | 254 | 1560 | 1370 | 12.1795 | 48.8189 | 750.0893 | 82.6687 | Calcium hardness | mg/L as CaCO3 | 86 | 254 | 505.8639 | 66.1417 | 379.9319 | 77.3644 | Current Process Water Rate ($/1000 gal) | 1.9
FAX Number |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | Permeate flow rate from system, Qp-sys (gpm) | 1391.5625 | SDI | 1.0-1.5 |  |  |  | 1999-01-27 | 2:37 | 29390.4 | 22.9 | 104.1 | 50 | 27.9292 | 0 | 1314 | 154 |  | 1468 | 1468 | 0.8951 | 0 | 14.1639 | 15.071 | 7.2674 | 41.8534 | 0.36009 |  | 6.04 | 255 |  | 393 | 1626 | 1570.4805 | 3.4145 | 35.1145 | 981.7403 | 74.0257 | 104.1 | 81 | 39 | 885 | 583 | 1468 | 1468 | 0.43524 | 0.60286 | 16.1644 | 17.1996 | 4.0633 | 49.4867 | 0.34756 | 6.04 | 6.13 | 162 | 393 | 691 | 743.6604 | -7.6209 | 58.7786 | 568.3302 | 71.4954 | 81 | 70 | 12 | 309 | 274 | 583 | 583 | 0.36373 | 0.53002 | 11.2877 | 12.0105 | 7.8193 | 55.6807 | 0.2157 | 6.13 | 6.16 | 191 | 691 | 1258 | 1254.8686 | 0.24892 | 51.3995 | 972.9343 | 80.3687 | 70 | 50 | 12 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.9939 | 13.2569 | 34.7431 | 0.34522 | 6.16 | 6.08 | 304 | 1258 | 1626 | 2001.3766 | -23.0859 | 22.6463 | 1629.6883 | 81.3461 | Turbidity | ntu | 0.08 | 0.22 | 23 | 1.3527 | 94.1186 | 63.6364 | 0.71758 | 88.8514 | Turbidity | ntu | 0.07 | 0.22 | 0.44219 | 68.1818 | 0.3311 | 78.8582 | Turbidity | ntu | 0.08 | 0.23 | 19 | 1.4436 | 92.4019 | 65.2174 | 0.7651 | 89.5438 | Turbidity | ntu | 0.08 | 0.23 | 0.45359 | 65.2174 | 0.34179 | 76.5941 | Turbidity | ntu | 0.08 | 0.25 | 18 | 1.6255 | 90.9697 | 68 | 0.85545 | 90.6482 | Turbidity | ntu | 0.18 | 0.25 | 0.3544 | 28 | 0.3022 | 40.4371 | Turbidity | ntu | 0.06 | 0.21 | 18 | 1.4236 | 92.0909 | 71.4286 | 0.74499 | 91.9462 | Turbidity | ntu | 0.08 | 0.21 | 0.405 | 61.9048 | 0.3075 | 73.9837 | Turbidity | ntu | 0.11 | 0.21 | 17 | 1.11 | 93.4706 | 47.619 | 0.61007 | 81.9693 | Turbidity | ntu | 0.08 | 0.21 | 0.40489 | 61.9048 | 0.30745 | 73.9793 | Turbidity | ntu | 0.11 | 0.21 | 18 | 1.11 | 93.8333 | 47.619 | 0.61007 | 81.9693 | Turbidity | ntu | 0.06 | 0.21 | 0.43488 | 71.4286 | 0.32244 | 81.3918 | Modifications to Existing Plant (% of construction costs) | N/A
E-Mail Address (optional) |  | Maximum flow rate to the element, QI, max (gpm) | 75 | Feed flow rate to system, QF-sys (gpm) | 1546.1806 | MFI |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | 1999-01-29 | 0:35 | 29436.4 | 23.4 | 104.5 | 50 | 29.6991 | 0 | 1298 | 154 |  | 1452 | 1452 | 0.89394 | 0 | 13.9915 | 14.6691 | 8.1343 | 39.4166 | 0.37215 |  | 5.95 | 239 |  | 395 | 1643 | 1709.8571 | -4.0692 | 39.4937 | 1052.4286 | 77.2906 | 104.5 | 82 | 42 | 869 | 583 | 1452 | 1452 | 0.43185 | 0.59848 | 15.8721 | 16.6408 | 4.1014 | 47.1486 | 0.35294 | 5.95 | 6.04 | 160 | 395 | 694 | 745.283 | -7.3895 | 59.4937 | 570.1415 | 71.9368 | 82 | 70 | 12 | 309 | 274 | 583 | 583 | 0.36373 | 0.53002 | 11.2877 | 11.8343 | 7.8975 | 56.1025 | 0.21094 | 6.04 | 6.06 | 189 | 694 | 1273 | 1263.5073 | 0.7457 | 52.1519 | 978.7536 | 80.6897 | 70 | 50 | 12 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.8179 | 13.4931 | 34.5069 | 0.34248 | 6.06 | 6.02 | 302 | 1273 | 1643 | 2029.6234 | -23.5316 | 23.5443 | 1651.3117 | 81.7115 | Ammonia | mg NH3-N / L | 0.23 | 0.23 | 0.75 | 0.23 | 69.3333 | 0 | 0.23 | 0 | Total organic carbon | mg/L | BMRL | 8 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | 0.21 | 0.22 | 0.68 | 0.30091 | 55.7487 | 4.5455 | 0.25567 | 17.8639 | Total organic carbon | mg/L | BMRL | 8 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | 0.32 | 0.29 | 0.9 | 0.047273 | 94.7475 | -10.3448 | 0.18316 | -74.7151 | Total organic carbon | mg/L | BMRL | 8 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | 0.15 | 0.19 | 0.64 | 0.51364 | 19.7443 | 21.0526 | 0.33266 | 54.9094 | Total organic carbon | mg/L | BMRL | 7 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | 0.32 | 0.32 | 0.94 | 0.32 | 65.9574 | 0 | 0.32 | 0 | Total organic carbon | mg/L | BMRL | 7 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | 0.32 | 0.32 | 0.94 | 0.32 | 65.9574 | 0 | 0.32 | 0 | Total organic carbon | mg/L | BMRL | 7 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | Minimum flow rate to the element, QI, min (gpm) | 72 | Concentrate-waste flow rate from system, QW-sys (gpm) | 154.6181 | MPFI |  | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | 1999-01-30 | 0:29 | 29460.3 | 23.4 | 103.8 | 49 | 29.1091 | 0 | 1298 | 153 |  | 1451 | 1451 | 0.89456 | 0 | 13.9915 | 14.6691 | 7.4958 | 39.795 | 0.36862 |  | 6.16 | 249 |  | 392 | 1572 | 1605.1634 | -2.1096 | 36.4796 | 998.5817 | 75.0646 | 103.8 | 81 | 41 | 875 | 576 | 1451 | 1451 | 0.43015 | 0.60303 | 15.9817 | 16.7557 | 3.9062 | 47.4938 | 0.3528 | 6.16 | 6.26 | 170 | 392 | 676 | 729.2396 | -7.8757 | 56.6327 | 560.6198 | 69.6764 | 81 | 69 | 12 | 305 | 271 | 576 | 576 | 0.35949 | 0.52951 | 11.1416 | 11.6811 | 7.4699 | 55.5301 | 0.21036 | 6.26 | 6.22 | 198 | 676 | 1220 | 1213.9705 | 0.49422 | 49.4898 | 944.9852 | 79.0473 | 69 | 49 | 12 | 118 | 153 | 271 | 271 | 0.46274 | 0.43542 | 11.0841 | 11.621 | 12.4706 | 34.5294 | 0.33655 | 6.22 | 6.17 | 320 | 1220 | 1572 | 1914.1176 | -21.7632 | 18.3673 | 1567.0588 | 79.5796 | Total organic carbon | mg/L | BMRL | 8 | 68 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.017 | 0.227 | 0.53807 | 92.511 | 0.38254 | 95.556 | Total organic carbon | mg/L | 1 | 8 | 72 | 64.6364 | 10.2273 | 87.5 | 32.9713 | 96.9671 | UV254 | cm-1 | 0.013 | 0.248 | 0.59829 | 94.7581 | 0.42315 | 96.9278 | Total organic carbon | mg/L | 1 | 8 | 73 | 64.6364 | 11.457 | 87.5 | 32.9304 | 96.9633 | UV254 | cm-1 | 0.012 | 0.225 | 0.54268 | 94.6667 | 0.38384 | 96.8737 | Total organic carbon | mg/L | BMRL | 7 | 68 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.013 | 0.225 | 0.543 | 94.2222 | 0.384 | 96.6146 | Total organic carbon | mg/L | 1 | 7 | 81 | 61 | 24.6914 | 85.7143 | 31.0043 | 96.7746 | UV254 | cm-1 | 0.013 | 0.223 | 0.53783 | 94.1704 | 0.38041 | 96.5827 | Total organic carbon | mg/L | BMRL | 7 | 74 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.014 | 0.226 | 0.54383 | 93.8053 | 0.38491 | 96.3628
Plant Name | Collier Co. North Regional Water Plant | Total width of all membrane envelopes in the element, w (ft) | 63.4 |  |  |  |  | is to list the pretreatment processes used in this particular pilot-scale run. |  |  | 1999-01-31 | 0:40 | 29484.4 | 23.6 | 105 | 50 | 29.6991 | 0 | 1301 | 153 |  | 1454 | 1454 | 0.89477 | 0 | 14.0238 | 14.6163 | 7.5624 | 40.2385 | 0.36324 |  | 6.1 | 244 |  | 388 | 1614 | 1612.4706 | 0.094759 | 37.1134 | 1000.2353 | 75.6057 | 105 | 80 | 42 | 872 | 582 | 1454 | 1454 | 0.43206 | 0.59972 | 15.9269 | 16.5999 | 3.8481 | 46.6519 | 0.35582 | 6.1 | 6.19 | 168 | 388 | 692 | 717.622 | -3.7026 | 56.701 | 552.811 | 69.6099 | 80 | 70 | 12 | 309 | 273 | 582 | 582 | 0.36288 | 0.53093 | 11.2877 | 11.7646 | 7.6731 | 55.3269 | 0.21264 | 6.19 | 6.23 | 202 | 692 | 1240 | 1246.6154 | -0.5335 | 47.9381 | 969.3077 | 79.1604 | 70 | 50 | 12 | 120 | 153 | 273 | 273 | 0.46492 | 0.43956 | 11.272 | 11.7483 | 12.6965 | 35.3035 | 0.33278 | 6.23 | 6.24 | 328 | 1240 | 1614 | 1955.2941 | -21.1459 | 15.4639 | 1597.6471 | 79.4698 | UV254 | cm-1 | 0.03 | 0.227 | 2.03 | 1.8209 | 10.3 | 86.7841 | 0.92717 | 96.7643 | SUVA | L/(mg*m) | NR | 2.8375 | --- | --- | --- | --- | UV254 | cm-1 | 0.029 | 0.248 | 2.11 | 2.0199 | 4.2697 | 88.3065 | 1.0292 | 97.1824 | SUVA | L/(mg*m) | NR | 3.1 | --- | --- | --- | --- | UV254 | cm-1 | 0.026 | 0.225 | 2.12 | 1.8351 | 13.4391 | 88.4444 | 0.93374 | 97.2155 | SUVA | L/(mg*m) | NR | 2.8125 | --- | --- | --- | --- | UV254 | cm-1 | 0.027 | 0.225 | 2.07 | 1.827 | 11.7391 | 88 | 0.93119 | 97.1005 | SUVA | L/(mg*m) | NR | 3.2143 | --- | --- | --- | --- | UV254 | cm-1 | 0.027 | 0.223 | 2.19 | 1.987 | 9.2694 | 87.8924 | 1.0071 | 97.3191 | SUVA | L/(mg*m) | NR | 3.1857 | --- | --- | --- | --- | UV254 | cm-1 | 0.027 | 0.226 | 2.31 | 2.017 | 12.684 | 88.0531 | 1.0221 | 97.3585 | SUVA | L/(mg*m) | NR | 3.2286 | --- | --- | --- | ---
Treatment Plant Category | Category II | Feed spacer thickness, T (ft) | 0.0023 | Calculate the Feed Flow Rates at the End of Each Stage | [6 empty] | 1999-02-02 | 0:30 | 29536.1 | 23.3 | 104 | 50 | 29.1091 | 0 | 1299 | 153 |  | 1452 | 1452 | 0.89463 | 0 | 14.0022 | 14.7238 | 9.1265 | 38.7644 | 0.37983 |  | 6.02 | 224 |  | 398 | 1622 | 1875.2941 | -15.6162 | 43.7186 | 1136.6471 | 80.2929 | 104 | 81 | 41 | 878 | 574 | 1452 | 1452 | 0.42994 | 0.60468 | 16.0365 | 16.863 | 4.0591 | 47.4409 | 0.35545 | 6.02 | 6.11 | 168 | 398 | 672 | 749.8118 | -11.5791 | 57.7889 | 573.9059 | 70.7269 | 81 | 70 | 12 | 303 | 271 | 574 | 574 | 0.35864 | 0.52787 | 11.0685 | 11.6389 | 7.3275 | 56.1725 | 0.2072 | 6.11 | 6.17 | 202 | 672 | 1282 | 1197.4982 | 6.5914 | 49.2462 | 934.7491 | 78.3899 | 70 | 50 | 12 | 118 | 153 | 271 | 271 | 0.46274 | 0.43542 | 11.0841 | 11.6554 | 13.6345 | 34.3655 | 0.33916 | 6.17 | 6.18 | 298 | 1282 | 1622 | 2040.902 | -25.8263 | 25.1256 | 1661.451 | 82.0639 | SUVA | L/(mg*m) | NR | 2.8375 | 2.9853 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | 2.9 | 3.1 | 2.9306 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | 2.6 | 2.8125 | 2.9041 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | 3.2143 | 3.0441 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | 2.7 | 3.1857 | 2.7037 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | 3.2286 | 3.1216 | --- | --- | --- | --- | ---
Process Train Name | Train D | Active membrane area of an equivalent 8" x 40" element (ft2) | 365 | Feed flow rate at the end of stage 1, (QF-s(1))end (gpm) | 861.8056 | [5 empty] | 1999-02-03 | 12:20 | 29550.8 | 21.8 | 104.7 | 53 | 29.6991 | 0 | 1303 | 154 |  | 1457 | 1457 | 0.8943 | 0 | 14.0454 | 15.4387 | 4.3413 | 44.8096 | 0.34454 |  | 6.18 | 299 |  | 382 | 1545 | 1084.2662 | 29.821 | 21.7277 | 733.1331 | 59.2161 | 104.7 | 82 | 42 | 876 | 581 | 1457 | 1457 | 0.43249 | 0.60124 | 16 | 17.5873 | 3.8059 | 47.5441 | 0.36992 | 6.18 | 6.28 | 165 | 382 | 641 | 709.1807 | -10.6366 | 56.8063 | 545.5904 | 69.7575 | 82 | 71 | 12 | 307 | 274 | 581 | 581 | 0.36288 | 0.5284 | 11.2146 | 12.3272 | 7.0054 | 57.4946 | 0.21441 | 6.28 | 6.27 | 192 | 641 | 1213 | 1144.0766 | 5.6821 | 49.7382 | 892.5383 | 78.4883 | 71 | 53 | 12 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 12.3903 | 12.0201 | 37.9799 | 0.32623 | 6.27 | 6.24 | 348 | 1213 | 1545 | 1887.026 | -22.1376 | 8.9005 | 1550.013 | 77.5486 | Bromide | mg/L | 170 | 170 | --- | 170 | --- | 0 | 170 | 0 | [8 empty] | Bromide | mg/L | 160 | 150 | --- | 69.0909 | --- | -6.6667 | 114.3267 | -39.9498 | [8 empty] | Bromide | mg/L | 160 | 160 | --- | 160 | --- | 0 | 160 | 0 | [8 empty] | Bromide | mg/L | 170 | 160 | --- | 79.0909 | --- | -6.25 | 124.3341 | -36.7284 | [8 empty] | Bromide | mg/L | 160 | 150 | --- | 60 | --- | -6.6667 | 109.9928 | -45.4641 | [8 empty] | Bromide | mg/L | 160 | 160 | --- | 160 | --- | 0 | 160 | 0
ICR Treatment Plant Identification Number | 1092 | Purchase price for an equivalent 8" x 40 " element ($) | 800 | Feed flow rate at the end of stage 2, (QF-s(2))end (gpm) | 382.7431 | [5 empty] | 1999-02-04 | 0:33 | 29570.6 | 23.4 | 104 | 51 | 29.1091 | 0 | 1301 | 155 |  | 1456 | 1456 | 0.89354 | 0 | 14.0238 | 14.703 | 8.003 | 40.3878 | 0.36404 |  | 6.02 | 240 |  | 394 | 1665 | 1686.6065 | -1.2977 | 39.0863 | 1040.3032 | 76.9298 | 104 | 82 | 41 | 872 | 584 | 1456 | 1456 | 0.43291 | 0.5989 | 15.9269 | 16.6983 | 4.1219 | 47.8781 | 0.34877 | 6.02 | 6.09 | 158 | 394 | 702 | 746.3836 | -6.3224 | 59.8985 | 570.1918 | 72.29 | 82 | 70 | 12 | 309 | 275 | 584 | 584 | 0.36458 | 0.52911 | 11.2877 | 11.8343 | 8.0746 | 55.9254 | 0.21161 | 6.09 | 6.12 | 185 | 702 | 1285 | 1282.92 | 0.16187 | 53.0457 | 992.46 | 81.3595 | 70 | 51 | 12 | 120 | 155 | 275 | 275 | 0.46929 | 0.43636 | 11.272 | 11.8179 | 13.7739 | 34.7261 | 0.34032 | 6.12 | 6.04 | 292 | 1285 | 1665 | 2053.7742 | -23.3498 | 25.8883 | 1669.3871 | 82.5086 | SDS-Cl2 dose | mg/L | 19 | 28 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 19.1 | NR | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 19 | 28 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 19 | 28 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 19 | 28 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 19 | 28 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection
PWSID Number of Plant (if assigned) | FL5114069 |  |  | Feed flow rate at the end of stage 3, (QF-s(3))end (gpm) | 181.2326 | [5 empty] | 1999-02-05 | 12:30 | 29594.6 | 22.4 | 103.2 | 50 | 29.1091 | 0 | 1301 | 155 |  | 1456 | 1456 | 0.89354 | 0 | 14.0238 | 15.1441 | 6.7038 | 40.787 | 0.3713 |  | 6.16 | 248 |  | 377 | 1635 | 1459.7677 | 10.7176 | 34.2175 | 918.3839 | 72.996 | 103.2 | 81 | 41 | 872 | 584 | 1456 | 1456 | 0.43291 | 0.5989 | 15.9269 | 17.1992 | 3.825 | 47.275 | 0.36381 | 6.16 | 6.32 | 158 | 377 | 659 | 704 | -6.8285 | 58.0902 | 540.5 | 70.7678 | 81 | 70 | 12 | 309 | 275 | 584 | 584 | 0.36458 | 0.52911 | 11.2877 | 12.1894 | 7.3562 | 56.1438 | 0.21711 | 6.32 | 6.34 | 188 | 659 | 1247 | 1188.2327 | 4.7127 | 50.1326 | 923.6164 | 79.6452 | 70 | 50 | 12 | 120 | 155 | 275 | 275 | 0.46929 | 0.43636 | 11.272 | 12.1725 | 13.011 | 34.989 | 0.34789 | 6.34 | 6.17 | 309 | 1247 | 1635 | 1973.1935 | -20.6846 | 18.0371 | 1610.0968 | 80.8086 | SDS-Free Cl2 residual | mg/L | 5.5 | 15 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.52 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 0.1 | NR | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.53 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 4.35 | 3.65 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.53 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 3.35 | 3.6 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.53 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 3.35 | 3.5 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.54 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 0.75 | 2.55 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.54
Historical Minimum Water Temperature (oC) | 22.7 | Additional Information |  |  |  | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | 1999-02-06 | 3:36 | 29670.8 | 23.6 | 103.5 | 50 | 29.9292 | 0 | 1307 | 143 |  | 1450 | 1450 | 0.90138 | 0 | 14.0885 | 14.6837 | 5.4585 | 41.3623 | 0.355 |  | 6.48 | 290 |  | 388 | 1360 | 1283.7063 | 5.6098 | 25.2577 | 835.8531 | 65.3049 | 103.5 | 81 | 41 | 871 | 579 | 1450 | 1450 | 0.43058 | 0.60069 | 15.9087 | 16.5808 | 3.3641 | 47.8859 | 0.34626 | 6.48 | 6.62 | 196 | 388 | 636 | 676.829 | -6.4197 | 49.4845 | 532.4145 | 63.1866 | 81 | 70 | 14 | 314 | 265 | 579 | 579 | 0.35821 | 0.54231 | 11.4703 | 11.9549 | 6.4176 | 55.0824 | 0.21704 | 6.62 | 6.61 | 233 | 636 | 1070 | 1113.517 | -4.067 | 39.9485 | 874.7585 | 73.3641 | 70 | 50 | 14 | 122 | 143 | 265 | 265 | 0.44528 | 0.46038 | 11.4599 | 11.9441 | 9.8719 | 36.1281 | 0.3306 | 6.61 | 6.62 | 378 | 1070 | 1360 | 1660.3776 | -22.0866 | 2.5773 | 1365.1888 | 72.3115 | SDS-Cl2 demand | mg/L | 13.5 | 13 | --- | 8.9545 | --- | -3.8462 | 11.2229 | -20.2895 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 307 |  |  |  |  | SDS-Cl2 demand | mg/L | 19 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 305 |  |  |  |  | SDS-Cl2 demand | mg/L | 14.65 | 24.35 | --- | 102.8318 | --- | 39.8357 | 58.8964 | 75.1258 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 307 |  |  |  |  | SDS-Cl2 demand | mg/L | 15.65 | 24.4 | --- | 95.1955 | --- | 35.8607 | 55.6077 | 71.8564 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 306 |  |  |  |  | SDS-Cl2 demand | mg/L | 15.65 | 24.5 | --- | 104.15 | --- | 36.1224 | 59.9064 | 73.8759 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 333 |  |  |  |  | SDS-Cl2 demand | mg/L | 18.25 | 25.45 | --- | 90.25 | --- | 28.2908 | 54.2552 | 66.3627 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 333
Historical Average Water Temperature (oC) | 25 | Design cross-flow velocity (fps) | 1 | Calculate the Minimum Recycle Flow Rates for Each Stage1 |  | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | 1999-02-07 | 3:00 | 29644.2 | 23.5 | 104 | 50 | 28.9292 | 0 | 1300 | 154 |  | 1454 | 1454 | 0.89409 | 0 | 14.013 | 14.6483 | 5.0642 | 43.0066 | 0.34061 |  | 6.01 | 265 |  | 362 | 1312 | 1180.8312 | 9.9976 | 26.7956 | 771.4156 | 65.6476 | 104 | 80 | 40 | 872 | 582 | 1454 | 1454 | 0.43206 | 0.59972 | 15.9269 | 16.649 | 3.0435 | 48.9565 | 0.34008 | 6.01 | 6.13 | 188 | 362 | 682 | 622.701 | 8.6949 | 48.0663 | 492.3505 | 61.8158 | 80 | 70 | 13 | 308 | 274 | 582 | 582 | 0.3633 | 0.52921 | 11.2511 | 11.7612 | 7.1854 | 54.8146 | 0.21456 | 6.13 | 6.21 | 222 | 682 | 1190 | 1199.0803 | -0.76305 | 38.674 | 940.5401 | 76.3965 | 70 | 50 | 13 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.783 | 11.506 | 35.494 | 0.33197 | 6.21 | 6.22 | 362 | 1190 | 1312 | 1835.1948 | -39.8777 | 0 | 1512.5974 | 76.0677 | SDS-Chlorination temp. | oC | 22.6 | 22.5 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 585 |  |  |  |  | SDS-Chlorination temp. | oC | 23.1 | NR | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 577 |  |  |  |  | SDS-Chlorination temp. | oC | 23.6 | 23.6 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 582 |  |  |  |  | SDS-Chlorination temp. | oC | 23.2 | 23.2 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 580 |  |  |  |  | SDS-Chlorination temp. | oC | 23.7 | 23.7 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 618 |  |  |  |  | SDS-Chlorination temp. | oC | 23.7 | 23.7 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 618
State Approved Plant Capacity (MGD) | 12 MGD | Required influent flow to permeate flow rate ratio, QI:Qp | 5:1 | Minimum recycle flow rate for stage 1, (QR-s(1))min (gpm) | 1730.1944 | [5 empty] | 1999-02-08 | 0:28 | 29665.7 | 22.1 | 103.8 | 50 | 27.9292 | 0 | 1317 | 154 |  | 1471 | 1471 | 0.89531 | 0 | 14.1963 | 15.4669 | 7.5974 | 41.3734 | 0.37384 | 7.21 | 5.99 | 241 | 378 | 385 | 1678 | 1616.4805 | 3.6662 | 37.4026 | 1000.7403 | 75.9178 | 103.8 | 82 | 39 | 892 | 579 | 1471 | 1471 | 0.43503 | 0.60639 | 16.2922 | 17.7504 | 4.0717 | 49.8283 | 0.35623 | 5.99 | 6.02 | 155 | 385 | 696 | 739.3351 | -6.2263 | 59.7403 | 562.1675 | 72.4281 | 82 | 70 | 12 | 306 | 273 | 579 | 579 | 0.36161 | 0.5285 | 11.1781 | 12.1785 | 7.8958 | 56.1042 | 0.21707 | 6.02 | 6.03 | 190 | 696 | 1290 | 1263.1648 | 2.0802 | 50.6494 | 979.5824 | 80.604 | 70 | 50 | 12 | 119 | 154 | 273 | 273 | 0.46601 | 0.4359 | 11.1781 | 12.1785 | 13.7111 | 34.2889 | 0.35517 | 6.03 | 5.97 | 301 | 1290 | 1678 | 2054.2273 | -22.4212 | 21.8182 | 1672.1136 | 81.9988 | SDS-Chlorination pH | --- | 8.2 | 8.33 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.3 | NR | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.41 | 8.35 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.35 | 8.29 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.44 | 8.42 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.47 | 8.41 | --- | --- | --- | --- | --- | ---
|  | Maximum element recovery (%) | 20 | Minimum recycle flow rate for stage 2, (QR-s(2))min (gpm) | 913.2569 | [5 empty] | 1999-02-09 | 0:05 | 29689.2 | 22.9 | 104.2 | 50 | 29.1091 | 0 | 1291 | 154 |  | 1445 | 1445 | 0.89343 | 0 | 13.916 | 14.8072 | 7.0605 | 40.9303 | 0.36177 |  | 6.05 | 251 |  | 387 | 1654 | 1527.1039 | 7.6721 | 35.1421 | 957.0519 | 73.7736 | 104.2 | 82 | 41 | 870 | 575 | 1445 | 1445 | 0.42867 | 0.60208 | 15.8904 | 16.908 | 4.0576 | 48.0424 | 0.35194 | 6.05 | 6.19 | 156 | 387 | 686 | 736.513 | -7.3634 | 59.6899 | 561.7565 | 72.23 | 82 | 70 | 12 | 303 | 272 | 575 | 575 | 0.35949 | 0.52696 | 11.0685 | 11.7773 | 7.8005 | 56.1995 | 0.20956 | 6.19 | 6.22 | 185 | 686 | 1252 | 1244.0993 | 0.63105 | 52.1964 | 965.0496 | 80.83 | 70 | 50 | 12 | 118 | 154 | 272 | 272 | 0.46492 | 0.43382 | 11.0841 | 11.794 | 13.0151 | 34.9849 | 0.33712 | 6.22 | 6.11 | 311 | 1252 | 1654 | 1973.026 | -19.2881 | 19.6382 | 1612.513 | 80.7133 | SDS-Incubation time | hours | 41.5 | 41.5 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 44 | NR | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 44 | 44 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 46 | 46 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 44.5 | 44.5 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 44.5 | 44.5 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters
|  | Variability of design flux (%) | 15 +/- | Minimum recycle flow rate for stage 3, (QR-s(3))min (gpm) | 322.7674 | [5 empty] | 1999-02-10 | 0:25 | 29713.6 | 23.2 | 104.4 | 50 | 29.6991 | 0 | 1301 | 154 |  | 1455 | 1455 | 0.89416 | 0 | 14.0238 | 14.7902 | 8.0972 | 39.4036 | 0.37535 |  | 5.92 | 237 |  | 392 | 1641 | 1701.4481 | -3.6836 | 39.5408 | 1046.724 | 77.3579 | 104.4 | 82 | 42 | 872 | 583 | 1455 | 1455 | 0.43249 | 0.59931 | 15.9269 | 16.7973 | 4.09 | 47.11 | 0.35655 | 5.92 | 6.07 | 158 | 392 | 693 | 741.9966 | -7.0702 | 59.6939 | 566.9983 | 72.134 | 82 | 70 | 12 | 309 | 274 | 583 | 583 | 0.36373 | 0.53002 | 11.2877 | 11.9045 | 7.9601 | 56.0399 | 0.21243 | 6.07 | 6.09 | 184 | 693 | 1268 | 1267.0182 | 0.077425 | 53.0612 | 980.0091 | 81.2247 | 70 | 50 | 12 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.888 | 13.5209 | 34.4791 | 0.34479 | 6.09 | 6.01 | 295 | 1268 | 1641 | 2026.1818 | -23.4724 | 24.7449 | 1647.0909 | 82.0896 | SDS-TOX | mg Cl- /L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-42 | CI-s2-42 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | 56 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-44 | CI-s2-44 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | 56 | 695 | --- | 5865.0909 | --- | 91.9424 | 2970.7916 | 98.115 | Parameter | Units | Cp-s2-46 | CI-s2-46 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | BMRL | 845 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-48 | CI-s2-48 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | 62 | 815 | --- | 7592 | --- | 92.3926 | 3827.5425 | 98.3802 | Parameter | Units | Cp-s2-50 | CI-s2-50 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | 57 | 740 | --- | 6887 | --- | 92.2973 | 3472.4921 | 98.3585 | Parameter | Units | Cp-s2-50 (dup) | CI-s2-50 (dup) | CC(calc) | RF (%) | CB | RB (%)
|  | Rejection of reference solute and conditions of test | 80 | 1: A negative minimum recycle flow rate indicates that recycle is not required to | [6 empty] | 1999-02-11 | 0:10 | 29737.4 | 22 | 104.9 | 50 | 30.2891 | 0 | 1297 | 156 |  | 1453 | 1453 | 0.89264 | 0 | 13.9807 | 15.2771 | 5.9822 | 41.1787 | 0.37099 |  | 6.1 | 264 |  | 380 | 1632 | 1344.4359 | 17.6203 | 30.5263 | 862.2179 | 69.3813 | 104.9 | 82 | 43 | 868 | 585 | 1453 | 1453 | 0.43249 | 0.59738 | 15.8539 | 17.324 | 3.867 | 46.583 | 0.37189 | 6.1 | 6.14 | 158 | 380 | 669 | 709.3949 | -6.0381 | 58.4211 | 544.6974 | 70.9931 | 82 | 70 | 12 | 309 | 276 | 585 | 585 | 0.36543 | 0.52821 | 11.2877 | 12.3343 | 7.487 | 56.513 | 0.21826 | 6.14 | 6.17 | 189 | 669 | 1168 | 1206.3913 | -3.2869 | 50.2632 | 937.6957 | 79.8442 | 70 | 50 | 12 | 120 | 156 | 276 | 276 | 0.47147 | 0.43478 | 11.272 | 12.3172 | 11.7554 | 36.2446 | 0.33984 | 6.17 | 6.07 | 319 | 1168 | 1632 | 1821.0769 | -11.5856 | 16.0526 | 1494.5385 | 78.6556 | SDS-CHCl3 | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1999-01-19 | 1999-01-19 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 2.4 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1999-02-01 | 1999-02-01 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 4 | 200 | --- | 1785.8182 | --- | 98 | 898.0519 | 99.5546 | Sampling date | MM/DD/YY | 1999-02-16 | 1999-02-16 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 5 | 230 | --- | 2050.4545 | --- | 97.8261 | 1032.4832 | 99.5157 | Sampling date | MM/DD/YY | 1999-03-01 | 1999-03-01 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 4.4 | 260 | --- | 2560.4 | --- | 98.3077 | 1282.5841 | 99.6569 | Sampling date | MM/DD/YY | 1999-03-15 | 1999-03-15 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 3.2 | 280 | --- | 2771.2 | --- | 98.8571 | 1387.3994 | 99.7694 | Sampling date | MM/DD/YY | 1999-03-15 | 1999-03-15 | --- | --- | --- | ---
|  | (e.g., solute type and concentration) |  | meet the manufacturer's minimum flow requirement. | [6 empty] | 1999-02-12 | 0:24 | 29761.6 | 23.1 | 104.6 | 50 | 29.6991 | 0 | 1297 | 155 |  | 1452 | 1452 | 0.89325 | 0 | 13.9807 | 14.7883 | 7.9832 | 39.6177 | 0.37328 |  | 5.9 | 230 |  | 384 | 1654 | 1672.6323 | -1.1265 | 40.1042 | 1028.3161 | 77.6333 | 104.6 | 82 | 42 | 869 | 583 | 1452 | 1452 | 0.43185 | 0.59848 | 15.8721 | 16.7891 | 4.084 | 47.216 | 0.35558 | 5.9 | 6.06 | 150 | 384 | 682 | 732.7925 | -7.4476 | 60.9375 | 558.3962 | 73.1374 | 82 | 70 | 12 | 308 | 275 | 583 | 583 | 0.36415 | 0.5283 | 11.2511 | 11.9011 | 7.8936 | 56.1064 | 0.21212 | 6.06 | 6.01 | 176 | 682 | 1272 | 1248.72 | 1.8302 | 54.1667 | 965.36 | 81.7685 | 70 | 50 | 12 | 120 | 155 | 275 | 275 | 0.46929 | 0.43636 | 11.272 | 11.9232 | 13.7877 | 34.2123 | 0.34851 | 6.01 | 5.95 | 278 | 1272 | 1654 | 2041.5484 | -23.431 | 27.6042 | 1656.7742 | 83.2204 | SDS-BDCM | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 8:49 | 9:05 | --- | --- | --- | --- | SDS-BDCM | mg/L | 4.6 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 8:16 | 8:27 | --- | --- | --- | --- | SDS-BDCM | mg/L | 10 | 59 | --- | 455.4545 | --- | 83.0508 | 233.513 | 95.7176 | Sampling time | hh:mm | 9:38 | 9:52 | --- | --- | --- | --- | SDS-BDCM | mg/L | 11 | 70 | --- | 547.3636 | --- | 84.2857 | 280.4289 | 96.0774 | Sampling time | hh:mm | 8:44 | 8:53 | --- | --- | --- | --- | SDS-BDCM | mg/L | 10 | 85 | --- | 760 | --- | 88.2353 | 385.054 | 97.403 | Sampling time | hh:mm | 8:54 | 9:09 | --- | --- | --- | --- | SDS-BDCM | mg/L | 7 | 70 | --- | 637 | --- | 90 | 322.0454 | 97.8264 | Sampling time | hh:mm | 8:54 | 9:09 | --- | --- | --- | ---
|  | Variability of rejection of reference solute (%) | 50 +/- | [7 empty] | 1999-02-13 | 0:21 | 29785.5 | 23.2 | 105 | 51 | 29.6991 | 0 | 1304 | 155 |  | 1459 | 1459 | 0.89376 | 0 | 14.0561 | 14.8243 | 7.7576 | 40.5433 | 0.36564 |  | 6.02 | 243 |  | 392 | 1634 | 1645.5226 | -0.70518 | 38.0102 | 1018.7613 | 76.1475 | 105 | 82 | 42 | 876 | 583 | 1459 | 1459 | 0.43333 | 0.60041 | 16 | 16.8743 | 4.063 | 47.437 | 0.35572 | 6.02 | 6.15 | 160 | 392 | 687 | 740.5969 | -7.8016 | 59.1837 | 566.2985 | 71.7463 | 82 | 71 | 12 | 308 | 275 | 583 | 583 | 0.36415 | 0.5283 | 11.2511 | 11.866 | 7.8312 | 56.6688 | 0.20939 | 6.15 | 6.11 | 185 | 687 | 1259 | 1249.24 | 0.77522 | 52.8061 | 968.12 | 80.8908 | 71 | 51 | 12 | 120 | 155 | 275 | 275 | 0.46929 | 0.43636 | 11.272 | 11.888 | 13.3161 | 35.6839 | 0.33315 | 6.11 | 6.03 | 299 | 1259 | 1634 | 2002.2258 | -22.5352 | 23.7245 | 1630.6129 | 81.6633 | SDS-DBCM | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 29245 | 29245.3 | --- | --- | --- | --- | SDS-DBCM | mg/L | 13 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 29516.1 | 29516.3 | --- | --- | --- | --- | SDS-DBCM | mg/L | 19 | 16 | --- | -8.2727 | --- | -18.75 | 5.3155 | -257.443 | Operation time | hh.hh | 29859.8 | 29860 | --- | --- | --- | --- | SDS-DBCM | mg/L | 18 | 18 | --- | 18 | --- | 0 | 18 | 0 | Operation time | hh.hh | 30145.3 | 30145.5 | --- | --- | --- | --- | SDS-DBCM | mg/L | 23 | 24 | --- | 33 | --- | 4.1667 | 28.0007 | 17.8593 | Operation time | hh.hh | 30457.1 | 30457.3 | --- | --- | --- | --- | SDS-DBCM | mg/L | 23 | 20 | --- | -7 | --- | -15 | 7.9978 | -187.5777 | Operation time | hh.hh | 30457.1 | 30457.3 | --- | --- | --- | ---
|  | Standard testing recovery (%) | 15 | Calculate the Maximum Recycle Flow Rates for Each Stage | [6 empty] | 1999-02-14 | 0:30 | 29809.6 | 23.3 | 105 | 50 | 29.6991 | 0 | 1297 | 156 |  | 1453 | 1453 | 0.89264 | 0 | 13.9807 | 14.7012 | 7.5293 | 40.2716 | 0.36505 |  | 6.01 | 238 |  | 384 | 1614 | 1597.859 | 1.0001 | 38.0208 | 990.9295 | 75.9821 | 105 | 81 | 42 | 870 | 583 | 1453 | 1453 | 0.43206 | 0.59876 | 15.8904 | 16.7093 | 3.8415 | 47.1585 | 0.35432 | 6.01 | 6.12 | 164 | 384 | 692 | 712.3019 | -2.9338 | 57.2917 | 548.1509 | 70.0812 | 81 | 71 | 12 | 307 | 276 | 583 | 583 | 0.36458 | 0.52659 | 11.2146 | 11.7925 | 7.7341 | 56.2659 | 0.20959 | 6.12 | 6.19 | 195 | 692 | 1226 | 1244.8225 | -1.5353 | 49.2188 | 968.4112 | 79.8639 | 71 | 50 | 12 | 120 | 156 | 276 | 276 | 0.47147 | 0.43478 | 11.272 | 11.8529 | 12.7938 | 35.7062 | 0.33196 | 6.19 | 6.19 | 302 | 1226 | 1614 | 1936.7692 | -19.9981 | 21.3542 | 1581.3846 | 80.9028 | SDS-CHBr3 | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 5.96 | 6.02 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | 20 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 6.01 | 6.23 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | 9 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 6 | 6.2 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | 7 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 5.95 | 6.19 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | 11 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 6.04 | 6.3 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | 23 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 6.04 | 6.3 | --- | --- | --- | ---
|  | Standard testing pH | 7.5 to 8.5 | Maximum recycle flow rate for stage 1, (QR-s(1))max (gpm) | 1153.8194 | [5 empty] | 1999-02-15 | 0:10 | 29826.5 | 20.3 | 104.9 | 50 | 29.6991 | 0 | 1299 | 155 |  | 1454 | 1454 | 0.8934 | 0 | 14.0022 | 16.0891 | 4.7751 | 42.9758 | 0.37438 | 7.26 | 6.1 | 292 | 395 | 384 | 1635 | 1155.0194 | 29.3566 | 23.9583 | 769.5097 | 62.0538 | 104.9 | 82 | 42 | 872 | 582 | 1454 | 1454 | 0.43206 | 0.59972 | 15.9269 | 18.3007 | 3.8481 | 47.6019 | 0.38445 | 6.1 | 6.26 | 164 | 384 | 687 | 713.622 | -3.8751 | 57.2917 | 548.811 | 70.1172 | 82 | 70 | 12 | 307 | 275 | 582 | 582 | 0.36373 | 0.52749 | 11.2146 | 12.886 | 7.6507 | 56.3493 | 0.22868 | 6.26 | 6.15 | 196 | 687 | 1260 | 1235.1345 | 1.9734 | 48.9583 | 961.0673 | 79.606 | 70 | 50 | 12 | 120 | 155 | 275 | 275 | 0.46929 | 0.43636 | 11.272 | 12.952 | 13.011 | 34.989 | 0.37017 | 6.15 | 6.1 | 322 | 1260 | 1635 | 1986.1935 | -21.4797 | 16.1458 | 1623.0968 | 80.1614 | SDS-THM4 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | 0 | #DIV/0! | Temperature | oC | 24.3 | 24.4 | --- | --- | --- | --- | SDS-THM4 | mg/L | 40 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Temperature | oC | 23.9 | 23.8 | --- | --- | --- | --- | SDS-THM4 | mg/L | 42 | 275 | --- | 2160.1818 | --- | 84.7273 | 1104.827 | 96.1985 | Temperature | oC | 23 | 23 | --- | --- | --- | --- | SDS-THM4 | mg/L | 41 | 318 | --- | 2559.1818 | --- | 87.1069 | 1305.946 | 96.8605 | Temperature | oC | 22.8 | 232 | --- | --- | --- | --- | SDS-THM4 | mg/L | 48.4 | 369 | --- | 3254.4 | --- | 86.8835 | 1651.631 | 97.0696 | Temperature | oC | 23.4 | 23.5 | --- | --- | --- | --- | SDS-THM4 | mg/L | 56.2 | 370 | --- | 3194.2 | --- | 84.8108 | 1625.4261 | 96.5424 | Temperature | oC | 23.4 | 23.5 | --- | --- | --- | ---
|  | Acceptable range of operating pressures | <400psi | Maximum recycle flow rate for stage 2, (QR-s(2))max (gpm) | 625.0694 | [5 empty] | 1999-02-16 | 0:59 | 29851.2 | 22 | 105.3 | 51 | 30.2891 | 0 | 1298 | 155 |  | 1453 | 1453 | 0.89332 | 0 | 13.9915 | 15.2889 | 8.1437 | 39.7172 | 0.38494 |  | 5.97 | 240 |  | 397 | 1654 | 1711.7484 | -3.4914 | 39.5466 | 1054.3742 | 77.2377 | 105.3 | 82 | 43 | 871 | 582 | 1453 | 1453 | 0.43185 | 0.59945 | 15.9087 | 17.3838 | 4.1784 | 46.4716 | 0.37407 | 5.97 | 6.07 | 158 | 397 | 698 | 754.6787 | -8.1202 | 60.2015 | 575.8393 | 72.5618 | 82 | 71 | 12 | 307 | 275 | 582 | 582 | 0.36373 | 0.52749 | 11.2146 | 12.2545 | 8.0246 | 56.4754 | 0.21699 | 6.07 | 6.05 | 183 | 698 | 1280 | 1272.9273 | 0.55256 | 53.9043 | 985.4636 | 81.4301 | 71 | 51 | 12 | 120 | 155 | 275 | 275 | 0.46929 | 0.43636 | 11.272 | 12.3172 | 13.6074 | 35.3926 | 0.34802 | 6.05 | 6.02 | 299 | 1280 | 1654 | 2039.4839 | -23.3062 | 24.6851 | 1659.7419 | 81.9852 | SDS-MCAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 93 | 136 | 183.4856 | -10.7143 | 159.7428 | 41.7814 | SDS-MCAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 91 | 122 | 156.761 | 7.1429 | 139.3805 | 34.7111 | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 75 | 110 | 149.0727 | 16.6667 | 129.5364 | 42.1012 | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 71 | 112 | 157.7883 | 8.9744 | 134.8942 | 47.3661 | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 85 | 132 | 186.9158 | 7.6087 | 159.4579 | 46.6944 | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 84 | 128 | 179.4105 | 10.6383 | 153.7053 | 45.35
|  | Acceptable range of operating pH values | 2 to 8 | Maximum recycle flow rate for stage 3, (QR-s(3))max (gpm) | 210.6944 | [5 empty] | 1999-02-17 | 0:10 | 29874.3 | 22.8 | 105.5 | 54 | 29.6991 | 0 | 1293 | 154 |  | 1447 | 1447 | 0.89357 | 0 | 13.9376 | 14.874 | 8.1609 | 41.8899 | 0.35507 |  | 5.94 | 236 |  | 393 | 1638 | 1711.1883 | -4.4682 | 39.9491 | 1052.0942 | 77.5685 | 105.5 | 82 | 42 | 868 | 579 | 1447 | 1447 | 0.42994 | 0.59986 | 15.8539 | 16.9191 | 4.059 | 47.691 | 0.35477 | 5.94 | 6.14 | 161 | 393 | 683 | 740.7997 | -8.4626 | 59.0331 | 566.8998 | 71.5999 | 82 | 70 | 12 | 306 | 273 | 579 | 579 | 0.36161 | 0.5285 | 11.1781 | 11.9291 | 7.7398 | 56.2602 | 0.21204 | 6.14 | 6.1 | 187 | 683 | 1271 | 1238.956 | 2.5212 | 52.4173 | 960.978 | 80.5407 | 70 | 54 | 12 | 119 | 154 | 273 | 273 | 0.46601 | 0.4359 | 11.1781 | 11.9291 | 13.5864 | 36.4136 | 0.3276 | 6.1 | 6.05 | 291 | 1271 | 1638 | 2028.2727 | -23.8262 | 25.9542 | 1649.6364 | 82.3597 | SDS-DCAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 228 | 1108 | 2079.7986 | 60.1399 | 1593.8993 | 85.6955 | SDS-DCAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 214 | 1064 | 2017.125 | 62.5874 | 1540.5625 | 86.109 | SDS-DCAA* | mg/L | 1.7 | 56 | --- | 495.3364 | --- | 96.9643 | 249.3889 | 99.3183 | Total dissolved solids | mg/L | 208 | 1116 | 2129.6582 | 61.7647 | 1622.8291 | 87.1829 | SDS-DCAA* | mg/L | 2.2 | 56 | --- | 491.2909 | --- | 96.0714 | 247.8827 | 99.1125 | Total dissolved solids | mg/L | 196 | 1084 | 2075.708 | 62.8788 | 1579.854 | 87.5938 | SDS-DCAA* | mg/L | 1.1 | 51 | --- | 500.1 | --- | 97.8431 | 250.636 | 99.5611 | Total dissolved solids | mg/L | 218 | 1040 | 2000.4421 | 56.746 | 1520.2211 | 85.66 | SDS-DCAA* | mg/L | BMRL | 48 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 230 | 1072 | 2055.8105 | 53.629 | 1563.9053 | 85.2932
|  | Typical pressure drop across a single element (psi) | 3 to 4 psi | [7 empty] | 1999-02-18 | 0:20 | 29897 | 21.4 | 104.6 | 51 | 29.6991 | 0 | 1295 | 155 |  | 1450 | 1450 | 0.8931 | 0 | 13.9591 | 15.5265 | 8.3356 | 39.7652 | 0.39045 |  | 5.91 | 234 |  | 395 | 1660 | 1740.129 | -4.8271 | 40.7595 | 1067.5645 | 78.081 | 104.6 | 82 | 42 | 870 | 580 | 1450 | 1450 | 0.43079 | 0.6 | 15.8904 | 17.6746 | 4.1475 | 47.1525 | 0.37484 | 5.91 | 6.08 | 158 | 395 | 699 | 750.5 | -7.3677 | 60 | 572.75 | 72.4138 | 82 | 71 | 12 | 306 | 274 | 580 | 580 | 0.36246 | 0.52759 | 11.1781 | 12.4332 | 8.0569 | 56.4431 | 0.22028 | 6.08 | 6.03 | 182 | 699 | 1290 | 1276.3796 | 1.0558 | 53.9241 | 987.6898 | 81.5732 | 71 | 51 | 12 | 119 | 155 | 274 | 274 | 0.4682 | 0.43431 | 11.1781 | 12.4332 | 13.728 | 35.272 | 0.35249 | 6.03 | 5.99 | 298 | 1290 | 1660 | 2051.6 | -23.5904 | 24.557 | 1670.8 | 82.1642 | SDS-TCAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 118 | 690 | 1321.6691 | 60.9272 | 1005.8345 | 88.2684 | SDS-TCAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 108 | 646 | 1249.2721 | 64.1196 | 947.636 | 88.6032 | SDS-TCAA* | mg/L | 1.3 | 70 | --- | 625.8455 | --- | 98.1429 | 314.6743 | 99.5869 | Total hardness | mg/L as CaCO3 | 100 | 602 | 1162.4145 | 67.3203 | 882.2073 | 88.6648 | SDS-TCAA* | mg/L | 2 | 74 | --- | 656.5455 | --- | 97.2973 | 330.7946 | 99.3954 | Total hardness | mg/L as CaCO3 | 105 | 680 | 1322.1533 | 64.527 | 1001.0766 | 89.5113 | SDS-TCAA* | mg/L | 1.4 | 65 | --- | 637.4 | --- | 97.8462 | 319.4458 | 99.5617 | Total hardness | mg/L as CaCO3 | 113 | 620 | 1212.3895 | 62.3333 | 916.1947 | 87.6664 | SDS-TCAA* | mg/L | 1.1 | 64 | --- | 630.1 | --- | 98.2812 | 315.6453 | 99.6515 | Total hardness | mg/L as CaCO3 | 113 | 620 | 1212.3895 | 62.5828 | 916.1947 | 87.6664
|  | Maximum permissible SDI | 4 | Select the Design System Recycle Flow Rate2 | [6 empty] | 1999-02-19 | 0:30 | 29920.2 | 23.6 | 104.4 | 50 | 29.6991 | 0 | 1302 | 155 |  | 1457 | 1457 | 0.89362 | 0 | 14.0346 | 14.6276 | 6.344 | 41.1569 | 0.35541 |  | 6.05 | 268 |  | 390 | 1518 | 1414.8 | 6.7984 | 31.2821 | 902.4 | 70.3014 | 104.4 | 82 | 42 | 872 | 585 | 1457 | 1457 | 0.43333 | 0.59849 | 15.9269 | 16.5999 | 3.9793 | 47.2207 | 0.35154 | 6.05 | 6.17 | 162 | 390 | 683 | 729.8564 | -6.8604 | 58.4615 | 559.9282 | 71.0677 | 82 | 70 | 12 | 310 | 275 | 585 | 585 | 0.365 | 0.52991 | 11.3242 | 11.8027 | 7.6305 | 56.3695 | 0.20938 | 6.17 | 6.17 | 195 | 683 | 1257 | 1233.1091 | 1.9006 | 50 | 958.0545 | 79.6463 | 70 | 50 | 12 | 120 | 155 | 275 | 275 | 0.46929 | 0.43636 | 11.272 | 11.7483 | 13.0248 | 34.9752 | 0.3359 | 6.17 | 6.15 | 318 | 1257 | 1518 | 1983.9677 | -30.6962 | 18.4615 | 1620.4839 | 80.3762 | SDS-MBAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 102 | 500 | 939.518 | 60.7692 | 719.759 | 85.8286 | SDS-MBAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 88 | 500 | 961.9853 | 62.3932 | 730.9926 | 87.9616 | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 88 | 530 | 1023.4327 | 64.2276 | 776.7164 | 88.6703 | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 94 | 570 | 1101.5912 | 62.0968 | 835.7956 | 88.7532 | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 101 | 520 | 1009.5684 | 58.9431 | 764.7842 | 86.7937 | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 101 | 540 | 1052.9368 | 60.2362 | 796.4684 | 87.319
|  | Maximum permissible turbidity (ntu) | 1 | Minimum system recycle flow rate, (QR-sys)min (gpm) | 1730.1944 | [5 empty] | 1999-02-20 | 0:20 | 29930.7 | 23.6 | 105.4 | 52 | 29.6991 | 0 | 1295 | 159 |  | 1454 | 1454 | 0.89065 | 0 | 13.9591 | 14.5489 | 7.7607 | 41.2402 | 0.35278 |  | 5.94 | 259 |  | 412 | 1757 | 1658.1321 | 5.6271 | 37.1359 | 1035.066 | 74.9774 | 105.4 | 83 | 42 | 874 | 580 | 1454 | 1454 | 0.43164 | 0.6011 | 15.9635 | 16.6379 | 4.3661 | 47.8339 | 0.34783 | 5.94 | 6.06 | 163 | 412 | 717 | 787.2172 | -9.7932 | 60.4369 | 599.6086 | 72.8156 | 83 | 71 | 12 | 303 | 277 | 580 | 580 | 0.36373 | 0.52241 | 11.0685 | 11.5361 | 8.075 | 56.925 | 0.20266 | 6.06 | 6.05 | 195 | 717 | 1327 | 1287.9964 | 2.9392 | 52.6699 | 1002.4982 | 80.5486 | 71 | 52 | 12 | 118 | 159 | 277 | 277 | 0.47584 | 0.42599 | 11.0841 | 11.5525 | 13.9301 | 35.5699 | 0.32478 | 6.05 | 6 | 311 | 1327 | 1757 | 2081.0126 | -18.4412 | 24.5146 | 1704.0063 | 81.7489 | SDS-DBAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.07 | 2 | 4.1313 | 68.1818 | 3.0657 | 97.7166 | SDS-DBAA* | mg/L | 4.8 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.05 | 4 | 8.4292 | 78.2609 | 6.2146 | 99.1954 | SDS-DBAA* | mg/L | 3.8 | 2.6 | --- | -7.1091 | --- | -46.1538 | -1.6738 | 327.0301 | Turbidity | ntu | 0.2 | 3.7 | 7.6073 | 20 | 5.6536 | 96.4625 | SDS-DBAA* | mg/L | 3.5 | 2.6 | --- | -4.6818 | --- | -34.6154 | -0.60993 | 673.8336 | Turbidity | ntu | 0.05 | 1.4 | 2.9077 | 76.1905 | 2.1538 | 97.6786 | SDS-DBAA* | mg/L | 3.8 | 2.7 | --- | -7.2 | --- | -40.7407 | -1.7008 | 323.4253 | Turbidity | ntu | 0.11 | 1.4 | 2.9073 | 47.619 | 2.1536 | 94.8923 | SDS-DBAA* | mg/L | 4.4 | 2.3 | --- | -16.6 | --- | -91.3043 | -6.1015 | 172.1133 | Turbidity | ntu | 0.09 | 1.5 | 3.1475 | 57.1429 | 2.3237 | 96.1269
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | 1 ppm | Maximum system recycle flow rate, (QR-sys)max (gpm) | 210.6944 | [5 empty] | 1999-02-21 | 9:00 | 29963.1 | 23.4 | 105 | 51 | 30.2891 | 0 | 1298 | 154 |  | 1452 | 1452 | 0.89394 | 0 | 13.9915 | 14.6691 | 7.5086 | 40.2023 | 0.36488 |  | 5.95 | 252 |  | 396 | 1691 | 1609.7143 | 4.807 | 36.3636 | 1002.8571 | 74.8718 | 105 | 82 | 43 | 870 | 582 | 1452 | 1452 | 0.43164 | 0.59917 | 15.8904 | 16.66 | 4.054 | 46.446 | 0.3587 | 5.95 | 6.04 | 164 | 396 | 692 | 742.8041 | -7.3416 | 58.5859 | 569.4021 | 71.1979 | 82 | 71 | 12 | 308 | 274 | 582 | 582 | 0.3633 | 0.52921 | 11.2511 | 11.796 | 7.7321 | 56.7679 | 0.20779 | 6.04 | 6.11 | 197 | 692 | 1312 | 1248.4234 | 4.8458 | 50.2525 | 970.2117 | 79.6952 | 71 | 51 | 12 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.8179 | 13.9795 | 35.0205 | 0.33746 | 6.11 | 6.08 | 306 | 1312 | 1691 | 2095.8961 | -23.9442 | 22.7273 | 1703.9481 | 82.0417 | SDS-BCAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 20 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | 1.9 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 20 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | 2.8 | 13 | --- | 95.5273 | --- | 78.4615 | 49.3272 | 94.3236 | Total organic carbon | mg/L | BMRL | 19 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | 2.9 | 13 | --- | 94.7182 | --- | 77.6923 | 49.0226 | 94.0844 | Total organic carbon | mg/L | BMRL | 19 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | 2.7 | 13 | --- | 105.7 | --- | 79.2308 | 54.2074 | 95.0191 | Total organic carbon | mg/L | BMRL | 18 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | 1.9 | 13 | --- | 112.9 | --- | 85.3846 | 57.408 | 96.6904 | Total organic carbon | mg/L | BMRL | 18 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | 1: All of the information requested in this field may not be available, but values for all of the Design |  | Design system recycle flow rate, QR-sys (gpm) | 0 | [5 empty] | 1999-02-22 | 5:20 | 29981.6 | 23.2 | 105.2 | 51 | 29.6991 | 0 | 1298 | 154 |  | 1452 | 1452 | 0.89394 | 0 | 13.9915 | 14.7561 | 7.5086 | 40.8923 | 0.36085 | 7.19 | 6.12 | 249 | 380 | 393 | 1608 | 1606.7143 | 0.079957 | 36.6412 | 999.8571 | 75.0964 | 105.2 | 83 | 42 | 870 | 582 | 1452 | 1452 | 0.43164 | 0.59917 | 15.8904 | 16.7588 | 4.0715 | 48.0285 | 0.34893 | 6.12 | 6.21 | 160 | 393 | 688 | 741.299 | -7.7469 | 59.2875 | 567.1495 | 71.7887 | 83 | 71 | 12 | 308 | 274 | 582 | 582 | 0.3633 | 0.52921 | 11.2511 | 11.866 | 7.7634 | 57.2366 | 0.20731 | 6.21 | 6.2 | 191 | 688 | 1245 | 1246.6715 | -0.13426 | 51.3995 | 967.3358 | 80.255 | 71 | 51 | 12 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.888 | 12.8956 | 36.1044 | 0.32927 | 6.2 | 6.15 | 317 | 1245 | 1608 | 1968.1169 | -22.3953 | 19.3384 | 1606.5584 | 80.2684 | SDS-TBAA | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.0226 | 0.56 | 1.1535 | 90.0441 | 0.85673 | 97.3621 | SDS-TBAA | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.019 | 0.594 | 1.2388 | 92.3387 | 0.91638 | 97.9266 | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.018 | 0.56 | 1.1651 | 92 | 0.86253 | 97.9131 | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.019 | 0.562 | 1.1684 | 91.5556 | 0.86521 | 97.804 | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.019 | 0.56 | 1.1921 | 91.4798 | 0.87606 | 97.8312 | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.019 | 0.56 | 1.1921 | 91.5929 | 0.87606 | 97.8312
|  | Parameters must be entered in cells E15:E26, since these parameters are used in calculations. |  | System influent flow rate, QI-sys (gpm) | 1546.1806 | [5 empty] | 1999-02-23 | 0:25 | 30000.7 | 20.5 | 105.1 | 50 | 29.6991 | 0 | 1297 | 156 |  | 1453 | 1453 | 0.89264 | 0 | 13.9807 | 15.9697 | 6.4979 | 41.353 | 0.38618 |  | 6.18 | 253 |  | 379 | 1551 | 1426.5769 | 8.0221 | 33.2454 | 902.7885 | 71.9757 | 105.1 | 82 | 42 | 869 | 584 | 1453 | 1453 | 0.43227 | 0.59807 | 15.8721 | 18.1302 | 3.6275 | 47.9225 | 0.37832 | 6.18 | 6.28 | 171 | 379 | 670 | 688.5068 | -2.7622 | 54.8813 | 533.7534 | 67.9627 | 82 | 70 | 12 | 308 | 276 | 584 | 584 | 0.365 | 0.5274 | 11.2511 | 12.8518 | 7.4471 | 56.5529 | 0.22725 | 6.28 | 6.3 | 192 | 670 | 1210 | 1203.4203 | 0.54378 | 49.3404 | 936.7101 | 79.5027 | 70 | 50 | 12 | 120 | 156 | 276 | 276 | 0.47147 | 0.43478 | 11.272 | 12.8756 | 12.2123 | 35.7877 | 0.35978 | 6.3 | 6.26 | 328 | 1210 | 1551 | 1888.4615 | -21.7577 | 13.4565 | 1549.2308 | 78.8282 | SDS-CDBAA | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 2.8 | --- | --- | --- | --- | SDS-CDBAA | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 2.97 | --- | --- | --- | --- | SDS-CDBAA | mg/L | 2.7 | 3.3 | --- | 8.1545 | --- | 18.1818 | 5.4369 | 50.3393 | SUVA | L/(mg*m) | NR | 2.9474 | --- | --- | --- | --- | SDS-CDBAA | mg/L | 3.2 | 4 | --- | 10.4727 | --- | 20 | 6.8533 | 53.307 | SUVA | L/(mg*m) | NR | 2.9579 | --- | --- | --- | --- | SDS-CDBAA | mg/L | 3.7 | 4.8 | --- | 14.7 | --- | 22.9167 | 9.2008 | 59.7861 | SUVA | L/(mg*m) | NR | 3.1111 | --- | --- | --- | --- | SDS-CDBAA | mg/L | 2.6 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.1111 | --- | --- | --- | ---
|  |  |  | Recycle ratio, r | 0 | [5 empty] | 1999-02-24 | 0:21 | 30023.7 | 21.9 | 105.2 | 51 | 29.6991 | 0 | 1301 | 156 |  | 1457 | 1457 | 0.89293 | 0 | 14.0238 | 15.3696 | 7.7548 | 40.6461 | 0.37813 |  | 6 | 246 |  | 396 | 1620 | 1646.9615 | -1.6643 | 37.8788 | 1021.4808 | 75.9173 | 105.2 | 82 | 42 | 873 | 584 | 1457 | 1457 | 0.43312 | 0.59918 | 15.9452 | 17.4753 | 4.1065 | 47.4935 | 0.36795 | 6 | 6.12 | 161 | 396 | 690 | 747.2928 | -8.3033 | 59.3434 | 571.6464 | 71.8357 | 82 | 71 | 12 | 308 | 276 | 584 | 584 | 0.365 | 0.5274 | 11.2511 | 12.3308 | 7.7899 | 56.7101 | 0.21744 | 6.12 | 6.14 | 190 | 690 | 1254 | 1247.971 | 0.48078 | 52.0202 | 968.9855 | 80.3919 | 71 | 51 | 12 | 120 | 156 | 276 | 276 | 0.47147 | 0.43478 | 11.272 | 12.3537 | 13.0985 | 35.9015 | 0.3441 | 6.14 | 6.07 | 308 | 1254 | 1620 | 1981.6923 | -22.3267 | 22.2222 | 1617.8462 | 80.9623 | SDS-DCBAA | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | 2.6 | 18 | --- | 142.6 | --- | 85.5556 | 72.8469 | 96.4309 | [8 empty] | SDS-DCBAA | mg/L | 3 | 19 | --- | 148.4545 | --- | 84.2105 | 76.0655 | 96.056 | [8 empty] | SDS-DCBAA | mg/L | 2.8 | 18 | --- | 154.8 | --- | 84.4444 | 78.811 | 96.4472 | [8 empty] | SDS-DCBAA | mg/L | 1.9 | 16 | --- | 142.9 | --- | 88.125 | 72.4102 | 97.3761
|  |  |  | 2: The design system recycle flow rate must fall between the minimum and | [6 empty] | 1999-02-25 | 0:10 | 30040.8 | 21.8 | 105.1 | 50 | 29.6991 | 0 | 1303 | 155 |  | 1458 | 1458 | 0.89369 | 0 | 14.0454 | 15.4387 | 6.1918 | 41.659 | 0.3706 |  | 6.09 | 258 |  | 377 | 1615 | 1377.3677 | 14.7141 | 31.565 | 877.1839 | 70.5877 | 105.1 | 82 | 42 | 874 | 584 | 1458 | 1458 | 0.43333 | 0.59945 | 15.9635 | 17.5471 | 3.7588 | 47.7912 | 0.36716 | 6.09 | 6.26 | 162 | 377 | 679 | 698.7637 | -2.9107 | 57.0292 | 537.8818 | 69.8819 | 82 | 70 | 12 | 309 | 275 | 584 | 584 | 0.36458 | 0.52911 | 11.2877 | 12.4075 | 7.4343 | 56.5657 | 0.21935 | 6.26 | 6.27 | 203 | 679 | 1197 | 1213.8509 | -1.4078 | 46.1538 | 946.4255 | 78.5509 | 70 | 50 | 12 | 120 | 155 | 275 | 275 | 0.46929 | 0.43636 | 11.272 | 12.3903 | 11.9706 | 36.0294 | 0.34389 | 6.27 | 6.2 | 334 | 1197 | 1615 | 1865.129 | -15.4879 | 11.4058 | 1531.0645 | 78.1851 | SDS-HAA5 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | 0 | #DIV/0! | [8 empty] | SDS-HAA5 | mg/L | 4.8 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-HAA5 | mg/L | 6.8 | 128.6 | --- | 1114.0727 | --- | 94.7123 | 562.3894 | 98.7909 | [8 empty] | SDS-HAA5 | mg/L | 7.7 | 132.6 | --- | 1143.1545 | --- | 94.1931 | 578.0674 | 98.668 | [8 empty] | SDS-HAA5 | mg/L | 6.3 | 118.7 | --- | 1130.3 | --- | 94.6925 | 568.381 | 98.8916 | [8 empty] | SDS-HAA5 | mg/L | 5.5 | 114.3 | --- | 1093.5 | --- | 95.1881 | 549.5784 | 98.9992
|  |  |  | maximum system recycle flow rates. | [6 empty] | 1999-02-26 | 2:16 | 30066.9 | 21.5 | 105.6 | 51 | 29.6991 | 0 | 1303 | 155 |  | 1458 | 1458 | 0.89369 | 0 | 14.0454 | 15.5763 | 7.3886 | 41.2123 | 0.37795 |  | 5.96 | 248 |  | 390 | 1618 | 1583.7161 | 2.1189 | 36.4103 | 986.8581 | 74.8697 | 105.6 | 81 | 42 | 874 | 584 | 1458 | 1458 | 0.43333 | 0.59945 | 15.9635 | 17.7034 | 4.0735 | 47.2265 | 0.37486 | 5.96 | 6.15 | 157 | 390 | 690 | 738.7021 | -7.0583 | 59.7436 | 564.351 | 72.1804 | 81 | 71 | 12 | 309 | 275 | 584 | 584 | 0.36458 | 0.52911 | 11.2877 | 12.518 | 7.8091 | 56.1909 | 0.22278 | 6.15 | 6.13 | 190 | 690 | 1251 | 1251.8182 | -0.065402 | 51.2821 | 970.9091 | 80.4307 | 71 | 51 | 12 | 120 | 155 | 275 | 275 | 0.46929 | 0.43636 | 11.272 | 12.5006 | 13.1081 | 35.8919 | 0.34829 | 6.13 | 6.08 | 306 | 1251 | 1618 | 1982.6129 | -22.5348 | 21.5385 | 1616.8065 | 81.0738 | SDS-HAA6 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | 0 | #DIV/0! | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | 6.7 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | 9.6 | 141.6 | --- | 1209.6 | --- | 93.2203 | 611.7166 | 98.4306 | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | 10.6 | 145.6 | --- | 1237.8727 | --- | 92.7198 | 627.0899 | 98.3097 | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | 9 | 131.7 | --- | 1236 | --- | 93.1663 | 622.5884 | 98.5544 | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | 7.4 | 127.3 | --- | 1206.4 | --- | 94.187 | 606.9864 | 98.7809 | Stage 3 Operating Parameters During Sample Collection
[11 empty] | 1999-02-27 | 2:00 | 30090.6 | 22.3 | 106 | 50 | 29.6991 | 0 | 1299 | 155 |  | 1454 | 1454 | 0.8934 | 0 | 14.0022 | 15.1656 | 8.6159 | 39.6849 | 0.38215 |  | 5.95 | 232 |  | 398 | 1610 | 1789.1871 | -11.1296 | 41.7085 | 1093.5935 | 78.7855 | 106 | 81 | 42 | 875 | 579 | 1454 | 1454 | 0.43142 | 0.60179 | 15.9817 | 17.3095 | 4.1432 | 47.3568 | 0.36551 | 5.95 | 6.04 | 162 | 398 | 686 | 754.6494 | -10.0072 | 59.2965 | 576.3247 | 71.8908 | 81 | 71 | 12 | 305 | 274 | 579 | 579 | 0.36203 | 0.52677 | 11.1416 | 12.0672 | 7.5961 | 56.4039 | 0.21394 | 6.04 | 6.13 | 198 | 686 | 1280 | 1229.2117 | 3.9678 | 50.2513 | 957.6058 | 79.3234 | 71 | 50 | 12 | 119 | 155 | 274 | 274 | 0.4682 | 0.43431 | 11.1781 | 12.1068 | 12.5794 | 35.9206 | 0.33704 | 6.13 | 6.14 | 371 | 1280 | 1610 | 1977.8774 | -22.8495 | 6.7839 | 1628.9387 | 77.2244 | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.43 |  |  |  |  | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.44 |  |  |  |  | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.44 |  |  |  |  | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.44 |  |  |  |  | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.46 |  |  |  |  | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.46
|  |  |  | Summary of the Stage and System Flow Rates | [6 empty] | 1999-02-28 | 0:20 | 30113 | 22.4 | 105.5 | 52 | 29.1091 | 0 | 1299 | 156 |  | 1455 | 1455 | 0.89278 | 0 | 14.0022 | 15.1208 | 4.7504 | 44.8905 | 0.33684 |  | 6.17 | 297 |  | 389 | 1548 | 1155.0769 | 25.3826 | 23.6504 | 772.0385 | 61.5304 | 105.5 | 82 | 41 | 876 | 579 | 1455 | 1455 | 0.43164 | 0.60206 | 16 | 17.2781 | 3.9345 | 48.8155 | 0.35395 | 6.17 | 6.26 | 165 | 389 | 670 | 727.9016 | -8.642 | 57.5835 | 558.4508 | 70.454 | 82 | 70 | 12 | 305 | 274 | 579 | 579 | 0.36203 | 0.52677 | 11.1416 | 12.0316 | 7.1758 | 56.8242 | 0.21173 | 6.26 | 6.19 | 209 | 670 | 1243 | 1183.1569 | 4.8144 | 46.2725 | 926.5785 | 77.4439 | 70 | 52 | 12 | 118 | 156 | 274 | 274 | 0.46929 | 0.43066 | 11.0841 | 11.9696 | 12.5692 | 36.4308 | 0.32856 | 6.19 | 6.23 | 331 | 1243 | 1548 | 1932.8462 | -24.8609 | 14.91 | 1587.9231 | 79.1552 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 119 |  |  |  |  | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 272 |  |  |  |  | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 275 |  |  |  |  | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 275 |  |  |  |  | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 130 |  |  |  |  | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 130
|  |  |  | Influent flow rate to stage 1, QI-s(1) (gpm) | 1546.1806 | [5 empty] | 1999-03-02 | 5:00 | 30165.7 | 23.1 | 106 | 50 | 29.6991 | 0 | 1301 | 155 |  | 1456 | 1456 | 0.89354 | 0 | 14.0238 | 14.8339 | 7.1715 | 41.1293 | 0.36067 |  | 5.97 | 248 |  | 386 | 1640 | 1544.3097 | 5.8348 | 35.7513 | 965.1548 | 74.3046 | 106 | 81 | 42 | 874 | 582 | 1456 | 1456 | 0.43249 | 0.60027 | 15.9635 | 16.8857 | 3.7468 | 47.7532 | 0.3536 | 5.97 | 6.06 | 172 | 386 | 692 | 707.3677 | -2.2208 | 55.4404 | 546.6838 | 68.5376 | 81 | 71 | 12 | 307 | 275 | 582 | 582 | 0.36373 | 0.52749 | 11.2146 | 11.8625 | 7.7286 | 56.2714 | 0.21081 | 6.06 | 6.17 | 196 | 692 | 1242 | 1245.7164 | -0.29922 | 49.2228 | 968.8582 | 79.77 | 71 | 50 | 12 | 120 | 155 | 275 | 275 | 0.46929 | 0.43636 | 11.272 | 11.9232 | 12.9277 | 35.5723 | 0.33518 | 6.17 | 6.19 | 310 | 1242 | 1640 | 1963.5484 | -19.7286 | 19.6891 | 1602.7742 | 80.6585 | [12 empty] | Stage 3 influent flow rate during sample collection (gpm) | 278 | [16 empty] | Stage 3 influent flow rate during sample collection (gpm) | 119 | [16 empty] | Stage 3 influent flow rate during sample collection (gpm) | 120 | [16 empty] | Stage 3 influent flow rate during sample collection (gpm) | 119 | [16 empty] | Stage 3 influent flow rate during sample collection (gpm) | 285 | [16 empty] | Stage 3 influent flow rate during sample collection (gpm) | 285
|  |  |  | Permeate flow rate from stage 1, Qp-s(1) (gpm) | 821.25 | [5 empty] | 1999-03-03 | 5:20 | 30189.9 | 23.2 | 106 | 51 | 29.6991 | 0 | 1301 | 154 |  | 1455 | 1455 | 0.89416 | 0 | 14.0238 | 14.7902 | 7.3136 | 41.4872 | 0.3565 |  | 5.98 | 252 |  | 392 | 1660 | 1574.7273 | 5.1369 | 35.7143 | 983.3636 | 74.3737 | 106 | 81 | 42 | 874 | 581 | 1455 | 1455 | 0.43206 | 0.60069 | 15.9635 | 16.8358 | 3.8197 | 47.6803 | 0.3531 | 5.98 | 6.07 | 174 | 392 | 701 | 719.938 | -2.7016 | 55.6122 | 555.969 | 68.7033 | 81 | 70 | 12 | 307 | 274 | 581 | 581 | 0.36288 | 0.5284 | 11.2146 | 11.8275 | 7.6607 | 55.8393 | 0.21181 | 6.07 | 6.16 | 210 | 701 | 1228 | 1251.135 | -1.884 | 46.4286 | 976.0675 | 78.4851 | 70 | 51 | 12 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.888 | 12.7844 | 35.7156 | 0.33285 | 6.16 | 6.18 | 308 | 1228 | 1660 | 1944.8831 | -17.1616 | 21.4286 | 1586.4416 | 80.5855 | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs
|  |  |  | Concentrate flow rate from stage 1, QC-s(1) (gpm) | 724.9306 | [5 empty] | 1999-03-04 | 0:41 | 30206.5 | 22.9 | 105.6 | 52 | 29.6991 | 0 | 1301 | 155 |  | 1456 | 1456 | 0.89354 | 0 | 14.0238 | 14.9219 | 7.6393 | 41.4616 | 0.3599 |  | 5.97 | 244 |  | 391 | 1620 | 1624.8516 | -0.29948 | 37.5959 | 1007.9258 | 75.7919 | 105.6 | 83 | 42 | 874 | 582 | 1456 | 1456 | 0.43249 | 0.60027 | 15.9635 | 16.9858 | 4.0445 | 48.2555 | 0.352 | 5.97 | 6.09 | 160 | 391 | 688 | 737.8969 | -7.2525 | 59.0793 | 564.4485 | 71.6537 | 83 | 71 | 12 | 307 | 275 | 582 | 582 | 0.36373 | 0.52749 | 11.2146 | 11.9328 | 7.7286 | 57.2714 | 0.20836 | 6.09 | 6.13 | 192 | 688 | 1245 | 1241.7164 | 0.26375 | 50.8951 | 964.8582 | 80.1007 | 71 | 52 | 12 | 120 | 155 | 275 | 275 | 0.46929 | 0.43636 | 11.272 | 11.9939 | 12.9416 | 36.5584 | 0.32807 | 6.13 | 6.12 | 312 | 1245 | 1620 | 1967.3226 | -21.4397 | 20.2046 | 1606.1613 | 80.5748 |  | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters
|  |  |  | Influent flow rate to stage 2, QI-s(2) (gpm) | 724.9306 | [5 empty] | 1999-03-05 | 0:30 | 30224 | 23.1 | 106 | 50 | 30.2891 | 0 | 1302 | 154 |  | 1456 | 1456 | 0.89423 | 0 | 14.0346 | 14.8453 | 7.2136 | 40.4973 | 0.36658 |  | 5.97 | 248 |  | 386 | 1640 | 1552.7273 | 5.3215 | 35.7513 | 969.3636 | 74.4162 | 106 | 82 | 43 | 869 | 587 | 1456 | 1456 | 0.43355 | 0.59684 | 15.8721 | 16.7891 | 3.724 | 47.276 | 0.35513 | 5.97 | 6.06 | 172 | 386 | 690 | 702.8075 | -1.8562 | 55.4404 | 544.4037 | 68.4058 | 82 | 70 | 12 | 312 | 275 | 587 | 587 | 0.36585 | 0.53152 | 11.3973 | 12.0557 | 7.7423 | 56.2577 | 0.21429 | 6.06 | 6.17 | 196 | 690 | 1242 | 1250.4655 | -0.6816 | 49.2228 | 970.2327 | 79.7987 | 70 | 50 | 12 | 121 | 154 | 275 | 275 | 0.4682 | 0.44 | 11.3659 | 12.0225 | 12.9814 | 35.0186 | 0.34332 | 6.17 | 6.19 | 310 | 1242 | 1640 | 1974.2857 | -20.3833 | 19.6891 | 1608.1429 | 80.7231 |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-42 | CI-s3-42 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-44 | CI-s3-44 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-46 | CI-s3-46 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-48 | CI-s3-48 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-50 | CI-s3-50 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-50 (dup) | CI-s3-50 (dup) | CC(calc) | RF (%) | CB | RB (%)
|  |  |  | Permeate flow rate from stage 2, Qp-s(2) (gpm) | 410.625 | [5 empty] | 1999-03-06 | 0:15 | 30246.3 | 21.5 | 105.6 | 50 | 29.6991 | 0 | 1301 | 154 |  | 1455 | 1455 | 0.89416 | 0 | 14.0238 | 15.5524 | 6.2166 | 41.8843 | 0.37132 |  | 5.97 | 248 |  | 367 | 1618 | 1372.3182 | 15.1843 | 32.4251 | 869.6591 | 71.4831 | 105.6 | 82 | 42 | 872 | 583 | 1455 | 1455 | 0.43249 | 0.59931 | 15.9269 | 17.6629 | 3.0937 | 48.7063 | 0.36264 | 5.97 | 6.07 | 190 | 367 | 690 | 631.741 | 8.4433 | 48.2289 | 499.3705 | 61.9521 | 82 | 71 | 12 | 309 | 274 | 583 | 583 | 0.36373 | 0.53002 | 11.2877 | 12.518 | 7.8193 | 56.6807 | 0.22085 | 6.07 | 6.19 | 190 | 690 | 1251 | 1253.8686 | -0.22931 | 48.2289 | 971.9343 | 80.4514 | 71 | 50 | 12 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 12.5006 | 13.1318 | 35.3682 | 0.35344 | 6.19 | 6.19 | 306 | 1251 | 1618 | 1987.3636 | -22.8284 | 16.6213 | 1619.1818 | 81.1016 | Qp/QT (THM4), % | #DIV/0! | #DIV/0! |  | Qp/QT (HAA5), % | #DIV/0! | #DIV/0! |  |  |  | Sampling date | MM/DD/YY | 1999-01-19 | 1999-01-19 | --- | --- | --- | --- | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | #VALUE! | #VALUE! |  |  |  | Sampling date | MM/DD/YY | 1999-02-01 | 1999-02-01 | --- | --- | --- | --- | Qp/QT (THM4), % | 87.1245 | 102.5751 |  | Qp/QT (HAA5), % | 61.2479 | 83.4154 |  |  |  | Sampling date | MM/DD/YY | 1999-02-16 | 1999-02-16 | --- | --- | --- | --- | Qp/QT (THM4), % | 88.8087 | 101.8051 |  | Qp/QT (HAA5), % | 62.9303 | 84.5476 |  |  |  | Sampling date | MM/DD/YY | 1999-03-01 | 1999-03-01 | --- | --- | --- | --- | Qp/QT (THM4), % | 92.6388 | 103.8677 |  | Qp/QT (HAA5), % | 57.5623 | 81.5836 |  |  |  | Sampling date | MM/DD/YY | 1999-03-15 | 1999-03-15 | --- | --- | --- | --- | Qp/QT (THM4), % | 94.9649 | 106.4372 |  | Qp/QT (HAA5), % | 55.4228 | 80.239 |  |  |  | Sampling date | MM/DD/YY | 1999-03-15 | 1999-03-15 | --- | --- | --- | ---
|  |  |  | Concentrate flow rate from stage 2, QC-s(2) (gpm) | 314.3056 | [5 empty] | 1999-03-07 | 0:15 | 30271.1 | 23.1 | 105.6 | 50 | 29.6991 | 0 | 1301 | 154 |  | 1455 | 1455 | 0.89416 | 0 | 14.0238 | 14.8339 | 5.5897 | 42.5112 | 0.34894 |  | 6.07 | 281 |  | 388 | 1559 | 1291.9416 | 17.1301 | 27.5773 | 839.9708 | 66.5465 | 105.6 | 82 | 42 | 873 | 582 | 1455 | 1455 | 0.43227 | 0.6 | 15.9452 | 16.8663 | 3.885 | 47.915 | 0.35201 | 6.07 | 6.24 | 166 | 388 | 675 | 721 | -6.8148 | 57.2165 | 554.5 | 70.0631 | 82 | 70 | 12 | 308 | 274 | 582 | 582 | 0.3633 | 0.52921 | 11.2511 | 11.9011 | 7.4197 | 56.5803 | 0.21034 | 6.24 | 6.27 | 200 | 675 | 1239 | 1208.9416 | 2.426 | 48.4536 | 941.9708 | 78.7679 | 70 | 50 | 12 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.9232 | 12.5482 | 35.4518 | 0.33632 | 6.27 | 6.25 | 336 | 1239 | 1559 | 1942.6364 | -24.6078 | 13.4021 | 1590.8182 | 78.8788 | SDS-THM4b, mg/L | #DIV/0! | #DIV/0! |  | SDS-THM4b, mg/L | #DIV/0! | #DIV/0! |  |  |  | Sampling time | hh:mm | 8:55 | 9:10 | --- | --- | --- | --- | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  |  |  | Sampling time | hh:mm | 8:19 | 8:30 | --- | --- | --- | --- | SDS-THM4b, mg/L | 72 | NA |  | SDS-THM4b, mg/L | 132.2923 | 80.642 |  |  |  | Sampling time | hh:mm | 9:42 | 9:56 | --- | --- | --- | --- | SDS-THM4b, mg/L | 72 | NA |  | SDS-THM4b, mg/L | 143.6829 | 83.803 |  |  |  | Sampling time | hh:mm | 8:47 | 8:55 | --- | --- | --- | --- | SDS-THM4b, mg/L | 72 | NA |  | SDS-THM4b, mg/L | 184.4553 | 107.4429 |  |  |  | Sampling time | hh:mm | 8:58 | 9:12 | --- | --- | --- | --- | SDS-THM4b, mg/L | 72 | NA |  | SDS-THM4b, mg/L | 196.0833 | 118.2101 |  |  |  | Sampling time | hh:mm | 8:58 | 9:12 | --- | --- | --- | ---
|  |  |  | Influent flow rate to stage 3, QI-s(3) (gpm) | 314.3056 | [5 empty] | 1999-03-08 | 4:10 | 30299 | 22.6 | 105.7 | 50 | 29.6991 | 0 | 1300 | 154 |  | 1454 | 1454 | 0.89409 | 0 | 14.013 | 15.0432 | 8.0922 | 40.0587 | 0.37553 | 7.24 | 5.97 | 238 | 382 | 393 | 1590 | 1701.4416 | -7.0089 | 39.4402 | 1047.2208 | 77.2732 | 105.7 | 82 | 42 | 875 | 579 | 1454 | 1454 | 0.43142 | 0.60179 | 15.9817 | 17.1567 | 4.0204 | 47.8296 | 0.3587 | 5.97 | 6.17 | 164 | 393 | 677 | 739.0708 | -9.1685 | 58.2697 | 566.0354 | 71.0265 | 82 | 70 | 12 | 306 | 273 | 579 | 579 | 0.36161 | 0.5285 | 11.1781 | 11.9999 | 7.5681 | 56.4319 | 0.21264 | 6.17 | 6.1 | 192 | 677 | 1228 | 1220.6264 | 0.60046 | 51.145 | 948.8132 | 79.7642 | 70 | 50 | 12 | 119 | 154 | 273 | 273 | 0.46601 | 0.4359 | 11.1781 | 11.9999 | 12.81 | 35.19 | 0.341 | 6.1 | 6.22 | 304 | 1228 | 1590 | 1942 | -22.1384 | 22.6463 | 1585 | 80.8202 | SDS-HAA5b, mg/L | #DIV/0! | #DIV/0! |  | SDS-HAA5b, mg/L | #DIV/0! | #DIV/0! |  |  |  | Operation time | hh.hh | 29245.1 | 29245.3 | --- | --- | --- | --- | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  |  |  | Operation time | hh.hh | 29516.2 | 29516.4 | --- | --- | --- | --- | SDS-HAA5b, mg/L | 22.4824 | NA |  | SDS-HAA5b, mg/L | 54 | 27 |  |  |  | Operation time | hh.hh | 29859.9 | 29860.1 | --- | --- | --- | --- | SDS-HAA5b, mg/L | 21.678 | NA |  | SDS-HAA5b, mg/L | 54 | 27 |  |  |  | Operation time | hh.hh | 30145.4 | 30145.5 | --- | --- | --- | --- | SDS-HAA5b, mg/L | 14.574 | NA |  | SDS-HAA5b, mg/L | 54 | 27 |  |  |  | Operation time | hh.hh | 30457.1 | 30457.4 | --- | --- | --- | --- | SDS-HAA5b, mg/L | 10.9781 | NA |  | SDS-HAA5b, mg/L | 54 | 27 |  |  |  | Operation time | hh.hh | 30457.1 | 30457.4 | --- | --- | --- | ---
|  |  |  | Permeate flow rate from stage 3, Qp-s(3) (gpm) | 159.6875 | [5 empty] | 1999-03-09 | 5:05 | 30323.9 | 23 | 105.6 | 51 | 29.6991 | 0 | 1298 | 154 |  | 1452 | 1452 | 0.89394 | 0 | 13.9915 | 14.8435 | 7.5086 | 41.0923 | 0.36122 |  | 5.98 | 246 |  | 390 | 1618 | 1603.7143 | 0.88292 | 36.9231 | 996.8571 | 75.3224 | 105.6 | 82 | 42 | 871 | 581 | 1452 | 1452 | 0.43142 | 0.59986 | 15.9087 | 16.8775 | 4.0065 | 47.7935 | 0.35313 | 5.98 | 6.03 | 161 | 390 | 680 | 733.3029 | -7.8387 | 58.7179 | 561.6515 | 71.3345 | 82 | 71 | 12 | 307 | 274 | 581 | 581 | 0.36288 | 0.5284 | 11.2146 | 11.8976 | 7.5203 | 56.9797 | 0.2088 | 6.03 | 6.11 | 198 | 680 | 1236 | 1220.0511 | 1.2904 | 49.2308 | 950.0255 | 79.1585 | 71 | 51 | 12 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.9585 | 12.8817 | 36.1183 | 0.33109 | 6.11 | 6.11 | 309 | 1236 | 1618 | 1958.3377 | -21.0345 | 20.7692 | 1597.1688 | 80.6533 | SDS-TOXb, mg Cl- /L | #DIV/0! | #DIV/0! |  | SDS-TOXb, mg Cl- /L | #DIV/0! | #DIV/0! |  |  |  | pH | --- | 6.19 | 6.21 | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  |  |  | pH | --- | 6.21 | 6.14 | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | 138.2747 | NA |  | SDS-TOXb, mg Cl- /L | 303.6256 | 161.9754 |  |  |  | pH | --- | 6.2 | 6.3 | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | #VALUE! | NA |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  |  |  | pH | --- | 6.16 | 6.16 | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | 117.4298 | NA |  | SDS-TOXb, mg Cl- /L | 381.556 | 200.6753 |  |  |  | pH | --- | 6.27 | 6.21 | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | 91.3894 | NA |  | SDS-TOXb, mg Cl- /L | 361.4623 | 191.9678 |  |  |  | pH | --- | 6.27 | 6.21 | --- | --- | --- | ---
|  |  |  | Concentrate flow rate from stage 3, QC-s(3) (gpm) | 154.6181 | [5 empty] | 1999-03-10 | 5:00 | 30336.1 | 23.1 | 106 | 51 | 29.6991 | 0 | 1300 | 154 |  | 1454 | 1454 | 0.89409 | 0 | 14.013 | 14.8225 | 6.6304 | 42.1705 | 0.35149 |  | 5.95 | 258 |  | 385 | 1610 | 1457.0779 | 9.4983 | 32.987 | 921.039 | 71.9882 | 106 | 82 | 42 | 872 | 582 | 1454 | 1454 | 0.43206 | 0.59972 | 15.9269 | 16.847 | 3.9705 | 48.0295 | 0.35076 | 5.95 | 6.04 | 158 | 385 | 692 | 725.11 | -4.7847 | 58.961 | 555.055 | 71.5344 | 82 | 71 | 12 | 308 | 274 | 582 | 582 | 0.3633 | 0.52921 | 11.2511 | 11.9011 | 7.6384 | 56.8616 | 0.2093 | 6.04 | 6.13 | 203 | 692 | 1218 | 1241.6788 | -1.9441 | 47.2727 | 966.8394 | 79.0038 | 71 | 51 | 12 | 120 | 154 | 274 | 274 | 0.46711 | 0.43796 | 11.272 | 11.9232 | 12.7844 | 36.2156 | 0.32923 | 6.13 | 6.12 | 298 | 1218 | 1610 | 1934.8831 | -20.1791 | 22.5974 | 1576.4416 | 81.0967 | SDS-CDb, mg/L | #DIV/0! | #DIV/0! |  | SDS-CDb, mg/L | #DIV/0! | #DIV/0! |  |  |  | Temperature | oC | 24.6 | 24.4 | --- | --- | --- | --- | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | #VALUE! | #VALUE! |  |  |  | Temperature | oC | 23.9 | 23.5 | --- | --- | --- | --- | SDS-CDb, mg/L | 15.8989 | NA |  | SDS-CDb, mg/L | 18.4089 | 16.2587 |  |  |  | Temperature | oC | 23 | 23 | --- | --- | --- | --- | SDS-CDb, mg/L | 16.6292 | NA |  | SDS-CDb, mg/L | 18.8936 | 17.0021 |  |  |  | Temperature | oC | 22.8 | 23.4 | --- | --- | --- | --- | SDS-CDb, mg/L | 16.3015 | NA |  | SDS-CDb, mg/L | 19.4057 | 17.2798 |  |  |  | Temperature | oC | 23.6 | 23.5 | --- | --- | --- | --- | SDS-CDb, mg/L | 18.6125 | NA |  | SDS-CDb, mg/L | 21.4596 | 19.6728 |  |  |  | Temperature | oC | 23.6 | 23.5 | --- | --- | --- | ---
|  |  |  | System concentrate recycle flow rate, QR-sys (gpm) | 0 | [5 empty] | 1999-03-11 | 5:50 | 30360 | 22.8 | 114 | 55 | 32.649 | 0 | 1372 | 154 |  | 1526 | 1526 | 0.89908 | 0 | 14.7891 | 15.7828 | 4.8 | 47.051 | 0.33544 |  | 5.96 | 255 |  | 343 | 1615 | 1127 | 30.2167 | 25.656 | 735 | 65.3061 | 114 | 88 | 47 | 909 | 617 | 1526 | 1526 | 0.45477 | 0.59567 | 16.6027 | 17.7183 | 3.2649 | 50.7351 | 0.34923 | 5.96 | 6.07 | 155 | 343 | 685 | 619.9724 | 9.4931 | 54.8105 | 481.4862 | 67.808 | 88 | 76 | 12 | 333 | 284 | 617 | 617 | 0.3824 | 0.53971 | 12.1644 | 12.9817 | 7.7568 | 62.2432 | 0.20856 | 6.07 | 6.15 | 196 | 685 | 1224 | 1258.3697 | -2.808 | 42.8571 | 971.6849 | 79.8289 | 76 | 55 | 12 | 130 | 154 | 284 | 284 | 0.47802 | 0.45775 | 12.2114 | 13.0318 | 13.1116 | 40.3884 | 0.32266 | 6.15 | 6.16 | 302 | 1224 | 1615 | 2002.3117 | -23.9821 | 11.9534 | 1613.1558 | 81.2789 | TOCb, mg/L | #DIV/0! | #DIV/0! |  | TOCb, mg/L | #DIV/0! | #DIV/0! |  |  |  | Alkalinity | mg/L as CaCO3 | 152 | 150 | 148.5031 | -80.9524 | 149.2516 | -1.8415 | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! |  |  |  | Alkalinity | mg/L as CaCO3 | 142 | 138 | 145.1111 | -44.898 | 141.5556 | -0.31397 | TOCb, mg/L | 1.9013 | NA |  | TOCb, mg/L | 3.7126 | 2.1609 |  |  |  | Alkalinity | mg/L as CaCO3 | 126 | 136 | 118.2581 | -40 | 127.129 | 0.8881 | TOCb, mg/L | #VALUE! | NA |  | TOCb, mg/L | #VALUE! | #VALUE! |  |  |  | Alkalinity | mg/L as CaCO3 | 124 | 130 | 119.4231 | -58.9744 | 124.7115 | 0.57055 | TOCb, mg/L | 1.4417 | NA |  | TOCb, mg/L | 3.5463 | 2.105 |  |  |  | Alkalinity | mg/L as CaCO3 | 150 | 152 | 153.6774 | -63.0435 | 152.8387 | 1.8573 | TOCb, mg/L | #VALUE! | NA |  | TOCb, mg/L | #VALUE! | #VALUE! |  |  |  | Alkalinity | mg/L as CaCO3 | 154 | 152 | 150.3226 | -63.8298 | 151.1613 | -1.8779
|  |  |  | System concentrate waste flow rate, QW-sys (gpm) | 154.6181 | [5 empty] | 1999-03-12 | 0:05 | 30376.2 | 23 | 113 | 56 | 32.649 | 0 | 1368 | 154 |  | 1522 | 1522 | 0.89882 | 0 | 14.746 | 15.644 | 5.9857 | 45.8653 | 0.34109 |  | 6.1 | 281 |  | 391 | 1633 | 1368.1429 | 16.2191 | 28.133 | 879.5714 | 68.0526 | 113 | 88 | 47 | 905 | 617 | 1522 | 1522 | 0.45392 | 0.59461 | 16.5297 | 17.5363 | 3.8655 | 49.6345 | 0.35331 | 6.1 | 6.19 | 168 | 391 | 669 | 718.0908 | -7.3379 | 57.0332 | 554.5454 | 69.7049 | 88 | 75 | 12 | 333 | 284 | 617 | 617 | 0.3824 | 0.53971 | 12.1644 | 12.9052 | 7.3127 | 62.1873 | 0.20752 | 6.19 | 6.28 | 208 | 669 | 1223 | 1209.5387 | 1.1007 | 46.8031 | 939.2694 | 77.8551 | 75 | 56 | 12 | 130 | 154 | 284 | 284 | 0.47802 | 0.45775 | 12.2114 | 12.955 | 12.5996 | 40.9004 | 0.31675 | 6.28 | 6.24 | 337 | 1223 | 1633 | 1970.9221 | -20.6933 | 13.8107 | 1596.961 | 78.8974 | UV254 b, cm-1 | #DIV/0! | #DIV/0! |  | UV254 b, cm-1 | #DIV/0! | #DIV/0! |  |  |  | Total dissolved solids | mg/L | 376 | 2360 | 3844.8805 | 34.2657 | 3102.4403 | 87.8805 | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  |  |  | Total dissolved solids | mg/L | 376 | 2320 | -1136 | 34.2657 | 592 | 36.4865 | UV254 b, cm-1 | 0.051622 | NA |  | UV254 b, cm-1 | 0.10312 | 0.059003 |  |  |  | Total dissolved solids | mg/L | 354 | 2400 | -1230 | 34.9265 | 585 | 39.4872 | UV254 b, cm-1 | 0.049159 | NA |  | UV254 b, cm-1 | 0.1004 | 0.057596 |  |  |  | Total dissolved solids | mg/L | 358 | 2344 | -1156.9615 | 32.197 | 593.5192 | 39.6818 | UV254 b, cm-1 | 0.041428 | NA |  | UV254 b, cm-1 | 0.11018 | 0.063096 |  |  |  | Total dissolved solids | mg/L | 372 | 2272 | 3865.5484 | 26.1905 | 3068.7742 | 87.8779 | UV254 b, cm-1 | 0.03702 | NA |  | UV254 b, cm-1 | 0.11571 | 0.066324 |  |  |  | Total dissolved solids | mg/L | 364 | 2336 | 3989.9355 | 26.6129 | 3162.9677 | 88.4918
|  |  |  | System permeate flow rate, Qp-sys (gpm) | 1391.5625 | [5 empty] | 1999-03-13 | 6:00 | 30405.9 | 23.1 | 113 | 56 | 32.059 | 0 | 1393 | 155 |  | 1548 | 1548 | 0.89987 | 0 | 15.0155 | 15.8829 | 5.8232 | 46.6178 | 0.3407 |  | 6.02 | 276 |  | 382 | 1622 | 1334.6323 | 17.7169 | 27.7487 | 858.3161 | 67.844 | 113 | 87 | 46 | 928 | 620 | 1548 | 1548 | 0.46007 | 0.59948 | 16.9498 | 17.9289 | 3.9164 | 50.0836 | 0.35798 | 6.02 | 6.11 | 158 | 382 | 676 | 717.2774 | -6.1061 | 58.6387 | 549.6387 | 71.2538 | 87 | 76 | 12 | 335 | 285 | 620 | 620 | 0.3841 | 0.54032 | 12.2374 | 12.9444 | 7.5893 | 61.9107 | 0.20908 | 6.11 | 6.19 | 198 | 676 | 1236 | 1237.8596 | -0.15046 | 48.1675 | 956.9298 | 79.3088 | 76 | 56 | 12 | 130 | 155 | 285 | 285 | 0.4802 | 0.45614 | 12.2114 | 12.9168 | 12.8877 | 41.1123 | 0.31418 | 6.19 | 6.22 | 328 | 1236 | 1622 | 1997.5484 | -23.1534 | 14.1361 | 1616.7742 | 79.7127 | Bromideb, mg/L | #DIV/0! | #DIV/0! |  | Bromideb, mg/L | #DIV/0! | #DIV/0! |  |  |  | Total hardness | mg/L as CaCO3 | 198 | 1320 | 2159.7358 | 34.4371 | 1739.8679 | 88.6198 | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE! |  |  |  | Total hardness | mg/L as CaCO3 | 180 | 1430 | -792.2222 | 40.1993 | 318.8889 | 43.554 | Bromideb, mg/L | 160 | NA |  | Bromideb, mg/L | 160 | 160 |  |  |  | Total hardness | mg/L as CaCO3 | 178 | 1430 | -791.2903 | 41.8301 | 319.3548 | 44.2626 | Bromideb, mg/L | 168.8809 | NA |  | Bromideb, mg/L | 166.293 | 168.4548 |  |  |  | Total hardness | mg/L as CaCO3 | 182 | 1370 | -724.2308 | 38.5135 | 322.8846 | 43.6331 | Bromideb, mg/L | 159.2639 | NA |  | Bromideb, mg/L | 155.7562 | 158.1584 |  |  |  | Total hardness | mg/L as CaCO3 | 190 | 1290 | 2212.5806 | 36.6667 | 1751.2903 | 89.1509 | Bromideb, mg/L | 160 | NA |  | Bromideb, mg/L | 160 | 160 |  |  |  | Total hardness | mg/L as CaCO3 | 190 | 1290 | 2212.5806 | 37.0861 | 1751.2903 | 89.1509
|  |  |  | System feed flow rate, QF-sys (gpm) | 1546.1806 | [5 empty] | 1999-03-14 | 1:25 | 30425.8 | 21.9 | 114.2 | 56 | 32.059 | 0 | 1391 | 151 |  | 1542 | 1542 | 0.90208 | 0 | 14.9939 | 16.4328 | 6.559 | 46.482 | 0.35353 |  | 6.09 | 267 |  | 384 | 1606 | 1461.7947 | 8.9792 | 30.4688 | 922.8974 | 71.0694 | 114.2 | 89 | 46 | 928 | 614 | 1542 | 1542 | 0.45753 | 0.60182 | 16.9498 | 18.5763 | 3.8099 | 51.7901 | 0.35868 | 6.09 | 6.22 | 167 | 384 | 676 | 711.9739 | -5.3216 | 56.5104 | 547.987 | 69.5248 | 89 | 76 | 12 | 333 | 281 | 614 | 614 | 0.37986 | 0.54235 | 12.1644 | 13.3317 | 7.6441 | 62.8559 | 0.2121 | 6.22 | 6.31 | 196 | 676 | 1254 | 1244.8256 | 0.73161 | 48.9583 | 960.4128 | 79.5921 | 76 | 56 | 12 | 130 | 151 | 281 | 281 | 0.47147 | 0.46263 | 12.2114 | 13.3832 | 13.4177 | 40.5823 | 0.32978 | 6.31 | 6.28 | 316 | 1254 | 1606 | 2061.5497 | -28.3655 | 17.7083 | 1657.7748 | 80.9383 | Alkb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | Alkb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  |  |  | Calcium hardness | mg/L as CaCO3 | 164 | 1040 | 1695.6226 | 36.9231 | 1367.8113 | 88.01 | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Calcium hardness | mg/L as CaCO3 | 138 | 1150 | -649.1111 | 41.0256 | 250.4444 | 44.898 | Alkb, mg/L CaCO3 | 102.1974 | NA |  | Alkb, mg/L CaCO3 | 98.5747 | 101.6782 |  |  |  | Calcium hardness | mg/L as CaCO3 | 138 | 1110 | -614.5161 | 43.9024 | 247.7419 | 44.2969 | Alkb, mg/L CaCO3 | 97.5379 | NA |  | Alkb, mg/L CaCO3 | 91.8447 | 96.6005 |  |  |  | Calcium hardness | mg/L as CaCO3 | 158 | 1120 | -575.8333 | 36.2903 | 272.0833 | 41.9296 | Alkb, mg/L CaCO3 | 108.675 | NA |  | Alkb, mg/L CaCO3 | 102.3612 | 106.6851 |  |  |  | Calcium hardness | mg/L as CaCO3 | 170 | 1090 | 1861.6129 | 30.8943 | 1475.8065 | 88.4809 | Alkb, mg/L CaCO3 | 111.0937 | NA |  | Alkb, mg/L CaCO3 | 103.9761 | 108.443 |  |  |  | Calcium hardness | mg/L as CaCO3 | 166 | 1160 | 1993.6774 | 34.6457 | 1576.8387 | 89.4726
[11 empty] | 1999-03-15 | 1:36 | 30449.8 | 23.4 | 113.9 | 55 | 32.059 | 0 | 1390 | 155 |  | 1545 | 1545 | 0.89968 | 0 | 14.9832 | 15.7088 | 8.171 | 44.22 | 0.35524 | 7.12 | 5.99 | 245 | 378 | 394 | 1661 | 1730.1935 | -4.1658 | 37.8173 | 1062.0968 | 76.9324 | 113.9 | 89 | 46 | 927 | 618 | 1545 | 1545 | 0.45901 | 0.6 | 16.9315 | 17.7515 | 3.9725 | 51.4775 | 0.34484 | 5.99 | 6.14 | 167 | 394 | 685 | 734.5 | -7.2263 | 57.6142 | 564.25 | 70.4032 | 89 | 76 | 12 | 333 | 285 | 618 | 618 | 0.38325 | 0.53883 | 12.1644 | 12.7535 | 7.7309 | 62.7691 | 0.20318 | 6.14 | 6.16 | 197 | 685 | 1260 | 1255.1895 | 0.38179 | 50 | 970.0947 | 79.6927 | 76 | 55 | 12 | 130 | 155 | 285 | 285 | 0.4802 | 0.45614 | 12.2114 | 12.8027 | 13.3419 | 40.1581 | 0.31881 | 6.16 | 6.14 | 320 | 1260 | 1661 | 2048.3871 | -23.3225 | 18.7817 | 1654.1935 | 80.6552 | T-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | T-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  |  |  | Turbidity | ntu | 0.28 | 21 | 36.5074 | -27.2727 | 28.7537 | 99.0262 | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Turbidity | ntu | 0.07 | 18 | -13.8756 | 69.5652 | 2.0622 | 96.6056 | T-Hdb, mg/L CaCO3 | 152.6609 | NA |  | T-Hdb, mg/L CaCO3 | 198.2036 | 159.1888 |  |  |  | Turbidity | ntu | 0.14 | 16 | -12.1387 | 44 | 1.9306 | 92.7485 | T-Hdb, mg/L CaCO3 | 150.3538 | NA |  | T-Hdb, mg/L CaCO3 | 192.7942 | 157.3419 |  |  |  | Turbidity | ntu | 0.19 | 10.3 | -7.5221 | 9.5238 | 1.3889 | 86.3205 | T-Hdb, mg/L CaCO3 | 159.189 | NA |  | T-Hdb, mg/L CaCO3 | 212.5053 | 175.9929 |  |  |  | Turbidity | ntu | 0.21 | 12 | 21.8884 | 0 | 16.9442 | 98.7606 | T-Hdb, mg/L CaCO3 | 159.5526 | NA |  | T-Hdb, mg/L CaCO3 | 218.8658 | 181.6415 |  |  |  | Turbidity | ntu | 0.21 | 11 | 20.0497 | 0 | 15.5248 | 98.6473
|  |  |  | Calculate the Required System Influent Pressure | [6 empty] | 1999-03-16 | 2:00 | 30468.7 | 23.3 | 115 | 55 | 32.059 | 0 | 1394 | 155 |  | 1549 | 1549 | 0.89994 | 0 | 15.0263 | 15.8006 | 7.1458 | 45.7952 | 0.34503 |  | 6.01 | 252 |  | 382 | 1652 | 1551.1613 | 6.104 | 34.0314 | 966.5806 | 73.9287 | 115 | 89 | 46 | 930 | 619 | 1549 | 1549 | 0.46007 | 0.60039 | 16.9863 | 17.8617 | 3.7476 | 52.2524 | 0.34183 | 6.01 | 6.09 | 168 | 382 | 692 | 703.5186 | -1.6645 | 56.0209 | 542.7593 | 69.0471 | 89 | 75 | 12 | 334 | 285 | 619 | 619 | 0.38368 | 0.53958 | 12.2009 | 12.8297 | 7.8347 | 62.1653 | 0.20638 | 6.09 | 6.17 | 198 | 692 | 1280 | 1270.9333 | 0.70833 | 48.1675 | 981.4667 | 79.8261 | 75 | 55 | 12 | 130 | 155 | 285 | 285 | 0.4802 | 0.45614 | 12.2114 | 12.8406 | 13.6542 | 39.3458 | 0.32635 | 6.17 | 6.19 | 318 | 1280 | 1652 | 2086.8387 | -26.322 | 16.7539 | 1683.4194 | 81.1099 | Ca-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | Ca-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  |  |  | Total organic carbon | mg/L | BMRL | 48 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Total organic carbon | mg/L | BMRL | 50 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ca-Hdb, mg/L CaCO3 | 130.9957 | NA |  | Ca-Hdb, mg/L CaCO3 | 165.1527 | 135.8916 |  |  |  | Total organic carbon | mg/L | 1 | 47 | -34.6129 | 87.5 | 6.1935 | 83.8542 | Ca-Hdb, mg/L CaCO3 | 139.6534 | NA |  | Ca-Hdb, mg/L CaCO3 | 171.225 | 144.8519 |  |  |  | Total organic carbon | mg/L | BMRL | 45 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ca-Hdb, mg/L CaCO3 | 134.8334 | NA |  | Ca-Hdb, mg/L CaCO3 | 176.9253 | 148.0996 |  |  |  | Total organic carbon | mg/L | BMRL | 49 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ca-Hdb, mg/L CaCO3 | 136.2435 | NA |  | Ca-Hdb, mg/L CaCO3 | 185.2757 | 154.5037 |  |  |  | Total organic carbon | mg/L | BMRL | 49 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  |  |  | Osmotic pressure for stage 13, Dp1 (psi) | 4 | [5 empty] | 1999-03-17 | 1:40 | 30491.4 | 23.2 | 114.5 | 56 | 32.649 | 0 | 1386 | 154 |  | 1540 | 1540 | 0.9 | 0 | 14.94 | 15.7565 | 8.195 | 44.406 | 0.35483 |  | 6.16 | 244 |  | 393 | 1647 | 1734 | -5.2823 | 37.9135 | 1063.5 | 77.0569 | 114.5 | 90 | 47 | 923 | 617 | 1540 | 1540 | 0.45774 | 0.59935 | 16.8584 | 17.7797 | 3.898 | 51.352 | 0.34623 | 6.16 | 6.16 | 170 | 393 | 677 | 726.5964 | -7.3259 | 56.743 | 559.7982 | 69.6319 | 90 | 76 | 12 | 333 | 284 | 617 | 617 | 0.3824 | 0.53971 | 12.1644 | 12.8291 | 7.5824 | 63.4176 | 0.2023 | 6.16 | 6.21 | 199 | 677 | 1245 | 1237.4718 | 0.60467 | 49.3639 | 957.2359 | 79.211 | 76 | 56 | 12 | 130 | 154 | 284 | 284 | 0.47802 | 0.45775 | 12.2114 | 12.8787 | 13.14 | 40.86 | 0.31519 | 6.21 | 6.23 | 321 | 1245 | 1647 | 2025 | -22.9508 | 18.3206 | 1635 | 80.367 | Notes: | [9 empty] | UV254 | cm-1 | 0.026 | 1.415 | 2.4546 | 88.5463 | 1.9348 | 98.6562 | Notes: | [9 empty] | UV254 | cm-1 | 0.0276 | 1.48 | -1.102 | 88.871 | 0.18898 | 85.3951 | Notes: | [9 empty] | UV254 | cm-1 | 0.023 | 1.44 | -1.074 | 89.7778 | 0.18298 | 87.4306 | Notes: | [9 empty] | UV254 | cm-1 | 0.025 | 1.41 | -1.0315 | 88.8889 | 0.18925 | 86.7897 | Notes: | [9 empty] | UV254 | cm-1 | 0.019 | 1.42 | 2.595 | 91.4798 | 2.0075 | 99.0536 | Notes: | [9 empty] | UV254 | cm-1 | 0.024 | 1.45 | 2.646 | 89.3805 | 2.048 | 98.8281
|  |  |  | Osmotic pressure for stage 23, Dp2 (psi) | 9 | [5 empty] | 1999-03-19 | 0:33 | 30519.9 | 22.7 | 114.3 | 55 | 32.649 | 0 | 1384 | 159 |  | 1543 | 1543 | 0.89695 | 0 | 14.9185 | 15.968 | 7.4396 | 44.5615 | 0.35834 |  | 6.03 | 252 |  | 391 | 1674 | 1600.9119 | 4.3661 | 35.5499 | 995.956 | 74.6977 | 114.3 | 89 | 47 | 924 | 619 | 1543 | 1543 | 0.4588 | 0.59883 | 16.8767 | 18.064 | 3.8769 | 50.7731 | 0.35578 | 6.03 | 6.16 | 169 | 391 | 679 | 722.3861 | -6.3897 | 56.7775 | 556.6931 | 69.6422 | 89 | 76 | 12 | 331 | 288 | 619 | 619 | 0.38495 | 0.53473 | 12.0913 | 12.9419 | 7.5741 | 62.9259 | 0.20567 | 6.16 | 6.23 | 198 | 679 | 1245 | 1231.816 | 1.059 | 49.3606 | 955.408 | 79.2759 | 76 | 55 | 12 | 129 | 159 | 288 | 288 | 0.48784 | 0.44792 | 12.1174 | 12.9699 | 12.9461 | 40.5539 | 0.31982 | 6.23 | 6.23 | 324 | 1245 | 1674 | 1992.2264 | -19.0099 | 17.1355 | 1618.6132 | 79.9829 | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | NR | 2.9479 | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | NR | 2.96 | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | NR | 3.0638 | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | NR | 3.1333 | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | NR | 2.898 | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | NR | 2.9592 | --- | --- | --- | ---
|  |  |  | Osmotic pressure for stage 33, Dp3 (psi) | 16 | [5 empty] | 1999-03-20 | 8:00 | 30550.5 | 22.9 | 114 | 56 | 32.2389 | 0 | 1388 | 155 |  | 1543 | 1543 | 0.89955 | 0 | 14.9616 | 15.9197 | 7.3945 | 45.3665 | 0.35091 |  | 6.02 | 255 |  | 390 | 1622 | 1598.9032 | 1.424 | 34.6154 | 994.4516 | 74.3577 | 114 | 89 | 47 | 925 | 618 | 1543 | 1543 | 0.45859 | 0.59948 | 16.895 | 17.9769 | 3.8814 | 50.6186 | 0.35515 | 6.02 | 6.13 | 168 | 390 | 681 | 722.2816 | -6.0619 | 56.9231 | 556.1408 | 69.7918 | 89 | 76 | 11 | 333 | 285 | 618 | 618 | 0.38325 | 0.53883 | 12.1644 | 12.9434 | 7.6042 | 63.8958 | 0.20257 | 6.13 | 6.19 | 201 | 681 | 1242 | 1241.8421 | 0.012713 | 48.4615 | 961.4211 | 79.0934 | 76 | 56 | 11 | 130 | 155 | 285 | 285 | 0.4802 | 0.45614 | 12.2114 | 12.9934 | 13.0013 | 41.9987 | 0.30938 | 6.19 | 6.22 | 326 | 1242 | 1622 | 2010.2581 | -23.937 | 16.4103 | 1626.129 | 79.9524 | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs.
|  |  |  | Pressure losses due to stage hardware, DPs (psi) | 62 | [108 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5.
|  |  |  | Pressure losses in a single element, DPe (psi) | 10.3 | [108 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters.
|  |  |  | Design permeate pressure, Pp (psi) | 18 | [108 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design.
|  |  |  | Mechanical pressure losses per stage, Ls (psi) | 123.8 | [108 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
|  |  |  | Net driving pressure required for permeation, NDP (psi) | 62.5 | [108 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
|  |  |  | Flow weighted system pressure losses, Lsys (psi) | 133.6967 | [108 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio.
|  |  |  | Required influent pressure to the system, PI (psi) | 214.1967 | [108 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL.
|  |  |  | 3: The osmotic pressure can be estimated from Table 6-5 in Part 3 of the | [109 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
"ICR Manual for Bench- and Pilot-Scale Treatment Studies."
Note on A1: TSC_ADM: This utility had trouble with their SDS chlorinations as in their response to EPA review and comments "Overall, all SDS residuals were very inconsistent. Our source water is very stable, but we experienced difficulty in retrieving good residuals on a regular basis. This could be in part to H2S levels in the water since odor removal is not preformed until after production. All SDS residuals below 0.1 were listed as 'NR'"
Note on E23: TSC_ADM: Reviewer entered a more appropriate membrane width
Note on W6: TSC_ADM: System Pp was approximated based on the number of parallel pressure vessels in each stage.
Note on DS16: C. Rice: Utility verified all alkalinity data stating that permeate values may be greater than feed values due to CO2.
Note on ED26: TSC_ADM: Data entered by the reviewer since utility did not so do
Note on ED48: TSC_ADM: Data entered by the reviewer since utility did not so do
Note on EP26: 12/23/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '27.6'.
Note on EP27: 12/23/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '0.05'.
Note on EP28: 12/23/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '27.55'.
Note on EP29: 12/23/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '23.1'.
Note on EP30: 12/23/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '8.27'.
Note on EP31: 12/23/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '44'. 12/23/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NR'.
Note on EX26: TSC_ADM: Data entered by the reviewer since utility did not so do
Note on EX48: TSC_ADM: Data entered by the reviewer since utility did not so do
Note on FR26: TSC_ADM: Data entered by the reviewer since utility did not so do
Note on FR48: TSC_ADM: Data entered by the reviewer since utility did not so do
Note on GL26: TSC_ADM: Data entered by the reviewer since utility did not so do
Note on GL48: TSC_ADM: Data entered by the reviewer since utility did not so do
Note on HF26: TSC_ADM: Data entered by the reviewer since utility did not so do
Note on HF48: TSC_ADM: Data entered by the reviewer since utility did not so do
Note on HZ26: TSC_ADM: Data entered by the reviewer since utility did not so do
Note on HZ48: TSC_ADM: Data entered by the reviewer since utility did not so do