## Sheet1. Weeks 1-10
FIELD-SET 1: PILOT-SCALE MEMBRANE RESULTS: WEEKS 1-10 (FILE: mempilot.xls)
Field 1-1: PWS And Treatment Plant Data |  | Field 1-2: Manufacturer Reported Membrane Characteristics1 |  | Field 1-3: 2-Stage Membrane Pilot System Design Parameters |  | Field 1-4: Foulants And Fouling Indices1 |  | Field 1-5: Pretreatment Used Prior To Membranes1 |  |  | Field 1-6: Membrane Performance Data During Operation With The Test Water | [18 empty] | Field 1-6: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 1-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 1-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 1-7: System And Stage Water Quality For 4/9/96 | [9 empty] | Field 1-7: System And Stage Water Quality For 4/9/96 (continued) | [7 empty] | Field 1-8: System And Stage Water Quality For 4/15/96 | [9 empty] | Field 1-8: System And Stage Water Quality For 4/15/96 (continued) | [7 empty] | Field 1-9: System And Stage Water Quality For 4/26/96 | [9 empty] | Field 1-9: System And Stage Water Quality For 4/26/96 (continued) | [7 empty] | Field 1-10: System And Stage Water Quality For 5/14/96 | [9 empty] | Field 1-10: System And Stage Water Quality For 5/14/96 (continued) | [7 empty] | Field 1-11: System And Stage Water Quality For 5/21/96 | [9 empty] | Field 1-11: System And Stage Water Quality For 5/21/96 (continued) | [7 empty] | Field 1-12: Analysis Of System And Stage Water Quality For 5/29/96 | [9 empty] | Field 1-12: Analysis Of System And Stage Water Quality For 5/29/96 (continued) | [7 empty] | Field 1-13: Membrane Cost Parameters
|  | General Information |  | Calculate Temperature Normalized MTCW |  | Parameters Evaluated Prior to Pretreatment |  |  |  |  | System Operating Parameters | [30 empty] | Stage 1 Operating Parameters | [23 empty] | Stage 2 Operating Parameters | [23 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | General Cost Parameters
PWS Name | Fairfax County Water Authority | Membrane manufacturer | FilmTec Corp. | Average yearly temperature of feed water, TavgoC (oC) | 17.9 | Alkalinity (mg/L as CaCO3) | 46 | Process | Description | Scale | Date | Time | Operation |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  |  |  | System recovery during sample collection (decimal) | 0.78 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.56 | [6 empty] | System recovery during sample collection (decimal) | 0.83 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.58 | [6 empty] | System recovery during sample collection (decimal) | 0.83 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.58 | [6 empty] | System recovery during sample collection (decimal) | 0.83 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.62 | [6 empty] | System recovery during sample collection (decimal) | 0.83 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.61 | [6 empty] | System recovery during sample collection (decimal) | 0.84 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.61 |  |  |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | VA6059501 | Membrane trade name | FilmTec NF70 | Temperature normalized MTCW (gfd/psi) | 0.28953 | Calcium Hardness (mg/L as CaCO3) | 49 | Microfiltration | 0.2 micron nominal pore size | pilot-scale |  |  | time | Influent | PI | PC | PP | QR | Qp | QW | Cleaning Event | QF | QI | Recovery | Recycle | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) |  |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) | [6 empty] | System feed flow rate during sample collection (gpm) | 14.7 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 8.2 | [6 empty] | System feed flow rate during sample collection (gpm) | 13.9 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 8 | [6 empty] | System feed flow rate during sample collection (gpm) | 14.4 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 8.4 | [6 empty] | System feed flow rate during sample collection (gpm) | 18.1 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 11.3 | [6 empty] | System feed flow rate during sample collection (gpm) | 18.3 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 11.2 | [6 empty] | System feed flow rate during sample collection (gpm) | 19.2 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 11.8 |  |  |  |  | Capital Recovery Interest Rate (real discount rate) (%) | 3
Water Industry Data Base Number (optional) | NA | Membrane element model number | NF70-4040 |  |  | LSI |  | Sulfuric acid addition | pH = 6.0 | Pilot-scale | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | Indicate with "X" | (gpm) | (gpm) | (decimal) | ratio | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHF (before acid) | pHF (after acid) | TDSp | TDSF (before acid) | TDSF (after acid) | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) |  |  | System influent flow rate during sample collection (gpm) | 14.7 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 14.7 | [6 empty] | System influent flow rate during sample collection (gpm) | 13.9 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 13.9 | [6 empty] | System influent flow rate during sample collection (gpm) | 14.4 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 14.4 | [6 empty] | System influent flow rate during sample collection (gpm) | 18.1 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 18.1 | [6 empty] | System influent flow rate during sample collection (gpm) | 18.3 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 18.3 | [6 empty] | System influent flow rate during sample collection (gpm) | 19.2 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 19.2 |  |  |  |  | Capital Recovery Period (years) | 20
|  | Molecular weight cutoff (Daltons) | 200 | Calculate System Permeate, Feed and Waste Flow Rates |  | Dissolved iron (mg/L) |  | Cartridge filtration | 5 um nominal pore size | pilot-scale | 1996-04-08 | 16:30 | 0 | 9 | 65 | 41 | 3.1 | 0 | 11.4 | 3.3 |  | 14.7 | 14.7 | 0.77551 | 0 | 12.6316 | 16.4327 | 2 | 47.9 | 0.34306 | [11 empty] | 65 | 53 | 3.5 | 8 | 6.7 | 14.7 | 14.7 | 0.35476 | 0.54422 | 13.2964 | 17.2976 | 1.2 | 54.3 | 0.31856 | [10 empty] | 53 | 41 | 3.1 | 3.4 | 3.3 | 6.7 | 6.7 | 0.33155 | 0.50746 | 11.3019 | 14.7029 | 2.2 | 41.7 | 0.35259 | [118 empty] | Overhead & Profit Factor (% of construction costs) | 20
Official ICR Contact Person |  | Membrane material (e.g., PVD, polyamide, etc.) | Crosslinked aromatic polyamide | Design system recovery, R (decimal) | 0.85 | Total iron (mg/L) | 0.91 |  |  |  | 1996-04-09 | 9:00 | 8 | 10 | 66 | 42 | 3.2 | 0 | 11.4 | 3.3 |  | 14.7 | 14.7 | 0.77551 | 0 | 12.6316 | 15.9541 | 1.9759 | 48.8241 | 0.32677 |  |  | 12.55 |  | 85 | 280.5 | 335.2818 | -19.5301 | 85.2353 | 210.1409 | 94.0278 | 66 | 53 | 4.2 | 8.2 | 6.5 | 14.7 | 14.7 | 0.35144 | 0.55782 | 13.6288 | 17.2136 | 1.2174 | 54.0826 | 0.31828 |  |  | 10.35 | 85 | 165.5 | 179.1738 | -8.2621 | 87.8235 | 132.0869 | 92.1643 | 53 | 42 | 3.2 | 3.2 | 3.3 | 6.5 | 6.5 | 0.32492 | 0.49231 | 10.6371 | 13.435 | 2.1909 | 42.1091 | 0.31905 |  |  | 17.95 | 165.5 | 280.5 | 308.5788 | -10.0103 | 78.8824 | 237.0394 | 92.4274 | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | Special Sitework Factor (% of construction costs) | 5
Mailing Address |  | Membrane construction (e.g., thin-film composite) | Thin Film Composite | Design average system flux, FW (gfd) | 18 | Dissolved aluminum (mg/L) |  |  |  |  | 1996-04-09 | 16:00 | 15 | 10.2 | 65 | 41 | 2.8 | 0 | 11.4 | 3.3 |  | 14.7 | 14.7 | 0.77551 | 0 | 12.6316 | 15.86 | 1.9432 | 48.2568 | 0.32866 | 6.4 | 6 | 11.75 |  | 83 | 270 | 329.1364 | -21.9024 | 85.8434 | 206.0682 | 94.298 | 65 | 53 | 3.1 | 8.2 | 6.5 | 14.7 | 14.7 | 0.35144 | 0.55782 | 13.6288 | 17.1121 | 1.1913 | 54.7087 | 0.31279 | 6 | 6.1 | 9.95 | 83 | 163.5 | 175.1554 | -7.1287 | 88.012 | 129.0777 | 92.2915 | 53 | 41 | 2.8 | 3.2 | 3.3 | 6.5 | 6.5 | 0.32492 | 0.49231 | 10.6371 | 13.3558 | 2.1753 | 42.0247 | 0.31781 | 6.1 | 6 | 17 | 163.5 | 270 | 305.5606 | -13.1706 | 79.5181 | 234.5303 | 92.7515 | Parameter | Units | Cp-sys-2 | CF-sys-2 | CC-sys-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-2 | CI-s1-2 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-4 | CF-sys-4 | CC-sys-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-4 | CI-s1-4 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-6 | CF-sys-6 | CC-sys-6 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-6 | CI-s1-6 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-8 | CF-sys-8 | CC-sys-8 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-8 | CI-s1-8 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-10 | CF-sys-10 | CC-sys-10 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-10 | CI-s1-10 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-10 (dup) | CF-sys-10 (dup) | CC-sys-10 (dup) | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-10 (dup) | CI-s1-10 (dup) | CC(calc) | RF (%) | CB | RB (%) | Construction Contingencies (% of construction costs) | 15
|  | Membrane hydrophobicity | Hydrophilic | Number of elements per pressure vessel, Ne | 6 | Total aluminum (mg/L) |  |  |  |  | 1996-04-10 | 11:00 | 23.6 | 10 | 66 | 41 | 2.9 | 0 | 11.4 | 3.3 |  | 14.7 | 14.7 | 0.77551 | 0 | 12.6316 | 15.9541 | 2 | 48.6 | 0.32827 | [11 empty] | 66 | 53 | 3.1 | 8.2 | 6.5 | 14.7 | 14.7 | 0.35144 | 0.55782 | 13.6288 | 17.2136 | 1.2 | 55.2 | 0.31184 |  |  |  |  | 0 | [5 empty] | 53 | 41 | 2.9 | 3.2 | 3.3 | 6.5 | 6.5 | 0.32492 | 0.49231 | 10.6371 | 13.435 | 2.2 | 41.9 | 0.32064 | [10 empty] | Sampling date | MM/DD/YY | 1996-04-09 | 1996-04-09 | 1996-04-09 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1996-04-09 | 1996-04-09 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1996-04-15 | 1996-04-15 | 1996-04-15 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1996-04-15 | 1996-04-15 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1996-04-26 | 1996-04-26 | 1996-04-26 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1996-04-26 | 1996-04-26 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1996-05-14 | 1996-05-14 | 1996-05-14 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1996-05-14 | 1996-05-14 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1996-05-21 | 1996-05-21 | 1996-05-21 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1996-05-21 | 1996-05-21 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1996-05-29 | 1996-05-29 | 1996-05-29 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1996-05-29 | 1996-05-29 | --- | --- | --- | --- | Engineering Fee Factor (% of construction costs) | 12
Phone Number |  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Negative | Number of parallel pressure vessels in stage 1, Nv-s(1) | 2 | Fluoride (mg/L) |  |  |  |  | 1996-04-10 | 12:00 | 24.4 | 10 | 70 | 45 | 3 | 0 | 11.8 | 3.3 |  | 15.1 | 15.1 | 0.78146 | 0 | 13.0748 | 16.5139 | 2 | 52.5 | 0.31455 |  |  | 0 | [8 empty] | 70 | 57 | 2.8 | 8.2 | 6.9 | 15.1 | 15.1 | 0.3647 | 0.54305 | 13.6288 | 17.2136 | 1.2 | 59.5 | 0.2893 |  |  |  |  | 0 | [5 empty] | 57 | 45 | 3 | 3.6 | 3.3 | 6.9 | 6.9 | 0.33818 | 0.52174 | 11.9668 | 15.1144 | 2.2 | 45.8 | 0.33001 | [10 empty] | Sampling time | hh:mm | 11:00 | 11:00 | 11:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 11:00 | 11:00 | --- | --- | --- | --- | Sampling time | hh:mm | 11:00 | 11:00 | 11:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 11:00 | 11:00 | --- | --- | --- | --- | Sampling time | hh:mm | 11:00 | 11:00 | 11:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 11:00 | 11:00 | --- | --- | --- | --- | Sampling time | hh:mm | 11:00 | 11:00 | 11:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 11:00 | 11:00 | --- | --- | --- | --- | Sampling time | hh:mm | 11:00 | 11:00 | 11:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 11:00 | 11:00 | --- | --- | --- | --- | Sampling time | hh:mm | 11:00 | 11:00 | 11:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 11:00 | 11:00 | --- | --- | --- | --- | 1998 ENR Construction Cost Index (CCI base year 1913) | 6081
FAX Number |  |  |  | Number of parallel pressure vessels in stage 2, Nv-s(2) | 1 | Phosphate (mg/L) |  |  |  |  | 1996-04-10 | 15:00 | 27 | 10.1 | 68 | 44 | 2.3 | 0 | 11.8 | 3.3 |  | 15.1 | 15.1 | 0.78146 | 0 | 13.0748 | 16.4651 | 2.0031 | 51.6969 | 0.31849 | 6.4 | 6.1 | 11.15 |  | 83 | 285 | 339.9182 | -19.2695 | 86.5663 | 211.4591 | 94.7271 | 68 | 56 | 3.1 | 8.4 | 6.7 | 15.1 | 15.1 | 0.36139 | 0.55629 | 13.9612 | 17.5814 | 1.1957 | 57.7043 | 0.30468 | 6.1 | 6.2 | 9.5 | 83 | 162.5 | 175.1493 | -7.7842 | 88.5542 | 129.0746 | 92.6399 | 56 | 44 | 2.3 | 3.4 | 3.3 | 6.7 | 6.7 | 0.33155 | 0.50746 | 11.3019 | 14.2326 | 2.2136 | 45.4864 | 0.3129 | 6.2 | 6.1 | 16.4 | 162.5 | 285 | 313.0273 | -9.8341 | 80.241 | 237.7636 | 93.1024 | Operation time | hh.hh | 10 | 10 | 10 | --- | --- | --- | --- | --- | Operation time | hh.hh | 10 | 10 | --- | --- | --- | --- | Operation time | hh.hh | 142 | 142 | 142 | --- | --- | --- | --- | --- | Operation time | hh.hh | 142 | 142 | --- | --- | --- | --- | Operation time | hh.hh | 405 | 405 | 405 | --- | --- | --- | --- | --- | Operation time | hh.hh | 405 | 405 | --- | --- | --- | --- | Operation time | hh.hh | 840 | 840 | 840 | --- | --- | --- | --- | --- | Operation time | hh.hh | 840 | 840 | --- | --- | --- | --- | Operation time | hh.hh | 985 | 985 | 985 | --- | --- | --- | --- | --- | Operation time | hh.hh | 985 | 985 | --- | --- | --- | --- | Operation time | hh.hh | 1097 | 1097 | 1097 | --- | --- | --- | --- | --- | Operation time | hh.hh | 1097 | 1097 | --- | --- | --- | --- | 1998 Producers Price Index (PPI base year 1967 = 100) | 131.8
E-Mail Address (optional) |  | Design Parameters |  | Permeate flow rate per element, Qp-e (gpm) | 0.9025 | Sulfate (mg/L) |  |  |  |  | 1996-04-11 | 8:30 | 44.1 | 9.7 | 69 | 44 | 2.2 | 0 | 11.8 | 3.3 |  | 15.1 | 15.1 | 0.78146 | 0 | 13.0748 | 16.661 | 2.0212 | 52.2788 | 0.31869 | 6.6 | 6.1 | 11 |  | 83.5 | 288.5 | 342.7424 | -18.8015 | 86.8263 | 213.1212 | 94.8386 | 69 | 57 | 2.8 | 8.4 | 6.7 | 15.1 | 15.1 | 0.36139 | 0.55629 | 13.9612 | 17.7905 | 1.2039 | 58.9961 | 0.30155 | 6.1 | 6.1 | 9.5 | 83.5 | 164 | 176.2761 | -7.4854 | 88.6228 | 129.8881 | 92.686 | 57 | 44 | 2.2 | 3.4 | 3.3 | 6.7 | 6.7 | 0.33155 | 0.50746 | 11.3019 | 14.4018 | 2.2462 | 46.0538 | 0.31272 | 6.1 | 6 | 15.75 | 164 | 288.5 | 316.7424 | -9.7894 | 81.1377 | 240.3712 | 93.4476 | pH | --- | 5.5 | 6 | 6 | --- | --- | --- | --- | --- | pH | --- | NA | 6 | --- | --- | --- | --- | pH | --- | 5.7 | 6.2 | 6.2 | --- | --- | --- | --- | --- | pH | --- | NA | 5.7 | --- | --- | --- | --- | pH | --- | 5.4 | 5.9 | 6.3 | --- | --- | --- | --- | --- | pH | --- | NA | 5.9 | --- | --- | --- | --- | pH | --- | 6 | 6.4 | 6.5 | --- | --- | --- | --- | --- | pH | --- | NA | 6.4 | --- | --- | --- | --- | pH | --- | 5.6 | 6 | 6.4 | --- | --- | --- | --- | --- | pH | --- | NA | 6 | --- | --- | --- | --- | pH | --- | NA | NA | NA | --- | --- | --- | --- | --- | pH | --- | NA | NA | --- | --- | --- | --- | Labor Rate + Fringe ($/work-hour) | 28
|  | Element size (e.g., 2.5" x 40", 4" x 40", etc.) | 4" x 40" | Permeate flow rate per pressure vessel, Qp-v (gpm) | 5.415 | Calcium (mg/L) |  |  |  |  | 1996-04-11 | 15:00 | 50.4 | 10.8 | 67 | 43 | 1.9 | 0 | 11.8 | 3.3 |  | 15.1 | 15.1 | 0.78146 | 0 | 13.0748 | 16.1279 | 1.9919 | 51.1081 | 0.31557 | 6.5 | 6.2 | 11.05 |  | 82.5 | 268 | 337.9879 | -26.1149 | 86.6061 | 210.2439 | 94.7442 | 67 | 55 | 2.8 | 8.5 | 6.6 | 15.1 | 15.1 | 0.35973 | 0.56291 | 14.1274 | 17.4264 | 1.2042 | 56.9958 | 0.30575 | 6.2 | 6.2 | 9.25 | 82.5 | 163 | 176.8371 | -8.489 | 88.7879 | 129.6686 | 92.8664 | 55 | 43 | 1.9 | 3.3 | 3.3 | 6.6 | 6.6 | 0.32823 | 0.5 | 10.9695 | 13.5311 | 2.1862 | 44.9138 | 0.30127 | 6.2 | 6.2 | 17.25 | 163 | 268 | 308.75 | -15.2052 | 79.0909 | 235.875 | 92.6868 | Temperature | oC | 11.2 | 10 | 11.6 | --- | --- | --- | --- | --- | Temperature | oC | NA | 10 | --- | --- | --- | --- | Temperature | oC | 12.5 | 11 | 12.8 | --- | --- | --- | --- | --- | Temperature | oC | NA | 11 | --- | --- | --- | --- | Temperature | oC | 15.9 | 14.6 | 16.1 | --- | --- | --- | --- | --- | Temperature | oC | NA | 15.9 | --- | --- | --- | --- | Temperature | oC | 17.4 | 16.4 | 7.6 | --- | --- | --- | --- | --- | Temperature | oC | NA | 16.4 | --- | --- | --- | --- | Temperature | oC | 17.9 | 17 | 18.2 | --- | --- | --- | --- | --- | Temperature | oC | NA | 17 | --- | --- | --- | --- | Temperature | oC | 18.1 | 17.1 | 18.4 | --- | --- | --- | --- | --- | Temperature | oC | NA | 17.1 | --- | --- | --- | --- | Labor Overhead Factor (% of labor) | 50
Technical ICR Contact Person |  | Active membrane area of membrane element used, A (ft2) | 72.2 | Permeate flow rate from stage 1, Qp-s(1) (gpm) | 10.83 | Barium (mg/L) |  |  |  |  | 1996-04-12 | 7:30 | 67.2 | 10.6 | 67 | 43 | 1.9 | 0 | 11.8 | 3.3 |  | 15.1 | 15.1 | 0.78146 | 0 | 13.0748 | 16.2236 | 1.9459 | 51.1541 | 0.31715 | 6.7 | 6 | 11.2 |  | 81 | 269 | 330.5879 | -22.8951 | 86.1728 | 205.7939 | 94.5577 | 67 | 55 | 2.5 | 8.4 | 6.7 | 15.1 | 15.1 | 0.36139 | 0.55629 | 13.9612 | 17.3235 | 1.1722 | 57.3278 | 0.30218 | 6 | 6 | 8.95 | 81 | 154.5 | 171.3313 | -10.8941 | 88.9506 | 126.1657 | 92.9062 | 55 | 43 | 1.9 | 3.4 | 3.3 | 6.7 | 6.7 | 0.33155 | 0.50746 | 11.3019 | 14.0238 | 2.097 | 45.003 | 0.31162 | 6 | 6 | 16.1 | 154.5 | 269 | 297.0939 | -10.4438 | 80.1235 | 225.797 | 92.8697 | Alkalinity | mg/L as CaCO3 | 1 | 9 | 31 | 37.3636 | -20.5279 | 88.8889 | 23.1818 | 95.6863 | Alkalinity | mg/L as CaCO3 | NA | 9 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 1 | 12 | 54 | 65.7059 | -21.6776 | 91.6667 | 38.8529 | 97.4262 | Alkalinity | mg/L as CaCO3 | NA | 12 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 3 | 12 | 59 | 55.9412 | 5.1844 | 75 | 33.9706 | 91.1688 | Alkalinity | mg/L as CaCO3 | NA | 12 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 6 | 18 | 74 | 76.5882 | -3.4976 | 66.6667 | 47.2941 | 87.3134 | Alkalinity | mg/L as CaCO3 | NA | 18 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 3 | 15 | 73 | 73.5882 | -0.8058 | 80 | 44.2941 | 93.2271 | Alkalinity | mg/L as CaCO3 | NA | 15 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 2 | 17 | 81 | 95.75 | -18.2099 | 88.2353 | 56.375 | 96.4523 | Alkalinity | mg/L as CaCO3 | NA | 17 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Electric Rate ($/kW-h) | 0.086
Mailing Address |  | Design flux, FW (gfd) | 25 | Permeate flow rate from stage 2, Qp-s(2) (gpm) | 5.415 | Strontium (mg/L) |  |  |  |  | 1996-04-12 | 14:00 | 73.5 | 10 | 64 | 44 | 2.9 | 0 | 11.5 | 2.4 |  | 13.9 | 13.9 | 0.82734 | 0 | 12.7424 | 16.094 | 2 | 49.1 | 0.32778 | [11 empty] | 64 | 53 | 3.1 | 8 | 5.9 | 13.9 | 13.9 | 0.32823 | 0.57554 | 13.2964 | 16.7938 | 1.2 | 54.2 | 0.30985 | [10 empty] | 53 | 44 | 2.9 | 3.5 | 2.4 | 5.9 | 5.9 | 0.27519 | 0.59322 | 11.6343 | 14.6945 | 2.1 | 43.5 | 0.33781 | [10 empty] | Total dissolved solids | mg/L | 11.8 | 83 | 270 | 335.4364 | -24.2357 | 85.7831 | 209.2182 | 94.36 | Total dissolved solids | mg/L | 10 | 83 | 175.0923 | 87.9518 | 129.0462 | 92.2508 | Total dissolved solids | mg/L | 12 | 82 | 410 | 423.7647 | -3.3572 | 85.3659 | 252.8824 | 95.2547 | Total dissolved solids | mg/L | 9.5 | 82 | 180.3051 | 88.4146 | 131.1525 | 92.7565 | Total dissolved solids | mg/L | 15.55 | 97.5 | 501 | 497.6088 | 0.67688 | 84.0513 | 297.5544 | 94.7741 | Total dissolved solids | mg/L | 11.8 | 97.5 | 217.48 | 87.8974 | 157.49 | 92.5075 | Total dissolved solids | mg/L | 10.4 | 85 | 365 | 449.2235 | -23.0749 | 87.7647 | 267.1118 | 96.1065 | Total dissolved solids | mg/L | 8.2 | 85 | 212.6235 | 90.3529 | 148.8118 | 94.4897 | Total dissolved solids | mg/L | 10.6 | 88 | 372 | 465.8941 | -25.2404 | 87.9545 | 276.9471 | 96.1726 | Total dissolved solids | mg/L | 8.7 | 88 | 213.093 | 90.1136 | 150.5465 | 94.2211 | Total dissolved solids | mg/L | 9.8 | 89 | 419 | 504.8 | -20.4773 | 88.9888 | 296.9 | 96.6992 | Total dissolved solids | mg/L | 7.8 | 89 | 218.4811 | 91.236 | 153.7405 | 94.9265 | Fuel Oil Rate ($/gal) | 0.8
|  | Net driving pressure at the design flux, NDP (psi) | 70 | Permeate flow rate from system, Qp-sys (gpm) | 16.245 | Reactive silica (mg/L as SiO2) |  |  |  |  | 1996-04-14 | 17:30 | 124.9 | 12.1 | 63 | 44 | 2.5 | 0 | 11.5 | 2.7 |  | 14.2 | 14.2 | 0.80986 | 0 | 12.7424 | 15.1254 | 2 | 49 | 0.30868 | [11 empty] | 63 | 52 | 3.2 | 8 | 6.2 | 14.2 | 14.2 | 0.33818 | 0.56338 | 13.2964 | 15.783 | 1.2 | 53.1 | 0.29723 | [10 empty] | 52 | 44 | 2.5 | 3.5 | 2.7 | 6.2 | 6.2 | 0.29508 | 0.56452 | 11.6343 | 13.8101 | 2.1 | 43.4 | 0.31821 | [10 empty] | Total hardness | mg/L as CaCO3 | 13 | 51 | 145 | 185.7273 | -28.0878 | 74.5098 | 118.3636 | 89.0169 | Total hardness | mg/L as CaCO3 | NA | 49 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 1 | 49 | 280 | 283.3529 | -1.1975 | 97.9592 | 166.1765 | 99.3982 | Total hardness | mg/L as CaCO3 | NA | 49 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 22 | 57 | 224.7 | 227.8824 | -1.4163 | 61.4035 | 142.4412 | 84.555 | Total hardness | mg/L as CaCO3 | NA | 86 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 46 | 82 | 282 | 257.7647 | 8.5941 | 43.9024 | 169.8824 | 72.9224 | Total hardness | mg/L as CaCO3 | NA | 82 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 26 | 70 | 250 | 284.8235 | -13.9294 | 62.8571 | 177.4118 | 85.3448 | Total hardness | mg/L as CaCO3 | NA | 70 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 25 | 83 | 308 | 387.5 | -25.8117 | 69.8795 | 235.25 | 89.373 | Total hardness | mg/L as CaCO3 | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Natural Gas Rate ($/ft3) | 0.007
Phone Number |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.35714 | Feed flow rate to system, QF-sys (gpm) | 19.1118 | Turbidity (ntu) | 13 |  |  |  | 1996-04-15 | 8:30 | 139.9 | 11.1 | 64 | 47 | 2.8 | 0 | 11.5 | 2.4 |  | 13.9 | 13.9 | 0.82734 | 0 | 12.7424 | 15.5791 | 2.3601 | 50.3399 | 0.30948 | 6.8 | 6.2 | 12 |  | 81.5 | 410 | 414.5208 | -1.1026 | 85.2761 | 248.0104 | 95.1615 | 64 | 54 | 3.5 | 8 | 5.9 | 13.9 | 13.9 | 0.32823 | 0.57554 | 13.2964 | 16.2565 | 1.2098 | 54.2902 | 0.29944 | 6.2 | 6.2 | 9.4 | 81.5 | 176 | 179.2627 | -1.8538 | 88.4663 | 130.3814 | 92.7904 | 54 | 47 | 2.8 | 3.5 | 2.4 | 5.9 | 5.9 | 0.27519 | 0.59322 | 11.6343 | 14.2244 | 2.7018 | 44.9982 | 0.31611 | 6.2 | 6.2 | 19.75 | 176 | 410 | 403.8646 | 1.4964 | 75.7669 | 289.9323 | 93.1881 | Calcium hardness | mg/L as CaCO3 | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Current Process Water Rate ($/1000 gal) | 1.05
FAX Number |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | Concentrate-waste flow rate from system, QW-sys (gpm) | 2.8668 | SDI |  |  |  |  | 1996-04-15 | 15:00 | 146.6 | 11 | 64 | 47 | 2.2 | 0 | 11.5 | 2.4 |  | 13.9 | 13.9 | 0.82734 | 0 | 12.7424 | 15.6253 | 2.3652 | 50.9348 | 0.30677 | 6.8 | 6.4 | 12.35 |  | 82 | 392.5 | 415.7396 | -5.9209 | 84.939 | 248.8698 | 95.0376 | 64 | 54 | 3 | 8 | 5.9 | 13.9 | 13.9 | 0.32823 | 0.57554 | 13.2964 | 16.3046 | 1.2065 | 54.7935 | 0.29756 | 6.4 | 6.2 | 10.1 | 82 | 181 | 179.4915 | 0.83341 | 87.6829 | 130.7458 | 92.2751 | 54 | 47 | 2.2 | 3.5 | 2.4 | 5.9 | 5.9 | 0.27519 | 0.59322 | 11.6343 | 14.2665 | 2.7935 | 45.5065 | 0.31351 | 6.2 | 6.3 | 19.45 | 181 | 392.5 | 416.5938 | -6.1385 | 76.2805 | 298.7969 | 93.4906 | Turbidity | ntu | 0.08 | 0.1 | 0.16 | 0.17091 | -6.8182 | 20 | 0.13545 | 40.9396 | Turbidity | ntu | NA | 0.1 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.07 | 0.1 | 0.16 | 0.24647 | -54.0441 | 30 | 0.17324 | 59.5925 | Turbidity | ntu | NA | 0.1 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.09 | 0.09 | 0.28 | 0.09 | 67.8571 | 0 | 0.09 | 0 | Turbidity | ntu | NA | 0.09 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | NA | 0.1 | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | NA | 0.12 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.05 | 0.08 | 0.18 | 0.22647 | -25.817 | 37.5 | 0.15324 | 67.3704 | Turbidity | ntu | NA | 0.08 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Modifications to Existing Plant (% of construction costs) | 10
E-Mail Address (optional) |  | Maximum flow rate to the element, QI, max (gpm) | 16 |  |  | MFI (s/mL) | 0.0368 |  |  |  | 1996-04-16 | 7:30 | 163.1 | 11.2 | 64 | 47 | 2.5 | 0 | 11.5 | 2.4 |  | 13.9 | 13.9 | 0.82734 | 0 | 12.7424 | 15.5332 | 2.3533 | 50.6467 | 0.3067 | 6.7 | 6.2 | 12.2 |  | 81.5 | 401.5 | 413.5625 | -3.0044 | 85.0307 | 247.5312 | 95.0713 | 64 | 54 | 3.2 | 8 | 5.9 | 13.9 | 13.9 | 0.32823 | 0.57554 | 13.2964 | 16.2085 | 1.209 | 54.591 | 0.29691 | 6.2 | 5.7 | 9.45 | 81.5 | 173.5 | 179.1949 | -3.2824 | 88.4049 | 130.3475 | 92.7501 | 54 | 47 | 2.5 | 3.5 | 2.4 | 5.9 | 5.9 | 0.27519 | 0.59322 | 11.6343 | 14.1825 | 2.6707 | 45.3293 | 0.31288 | 5.7 | 6.1 | 19.05 | 173.5 | 401.5 | 398.7396 | 0.68753 | 76.6258 | 286.1198 | 93.3419 | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | NA | 5.2 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | NA | 5.7 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | NA | 4.8 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | NA | 6.1 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | NA | 5.6 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | NA | 5.3 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | Minimum flow rate to the element, QI, min (gpm) | 4 | Calculate the Feed Flow Rates at the End of Each Stage |  | MPFI |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | 1996-04-16 | 15:00 | 170.3 | 12 | 62 | 45 | 2.8 | 0 | 11.5 | 2.4 |  | 13.9 | 13.9 | 0.82734 | 0 | 12.7424 | 15.1702 | 2.3041 | 48.3959 | 0.31346 | 6.3 | 6.1 | 12.65 |  | 80.5 | 413 | 405.6146 | 1.7882 | 84.2857 | 243.0573 | 94.7955 | 62 | 52 | 3 | 8 | 5.9 | 13.9 | 13.9 | 0.32823 | 0.57554 | 13.2964 | 15.8297 | 1.1897 | 52.8103 | 0.29975 | 6.1 | 6.4 | 9.6 | 80.5 | 180.5 | 176.6356 | 2.1409 | 88.0745 | 128.5678 | 92.5331 | 52 | 45 | 2.8 | 3.5 | 2.4 | 5.9 | 5.9 | 0.27519 | 0.59322 | 11.6343 | 13.851 | 2.79 | 42.91 | 0.32279 | 6.4 | 6.2 | 19.15 | 180.5 | 413 | 415.8021 | -0.67847 | 76.2112 | 298.151 | 93.5771 | Total organic carbon | mg/L | BMRL | 5.2 | 23 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.005 | 0.177 | 0.39398 | 97.1751 | 0.28549 | 98.2486 | Total organic carbon | mg/L | BMRL | 5.7 | 23 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.003 | 0.178 | 0.41529 | 98.3146 | 0.29664 | 98.9887 | Total organic carbon | mg/L | BMRL | 4.8 | 28 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.002 | 0.111 | 0.2636 | 98.1982 | 0.1873 | 98.9322 | Total organic carbon | mg/L | BMRL | 6.1 | 34.9 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.003 | 0.19 | 0.50075 | 98.4211 | 0.34537 | 99.1314 | Total organic carbon | mg/L | BMRL | 5.6 | 32.4 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.005 | 0.179 | 0.45348 | 97.2067 | 0.31624 | 98.4189 | Total organic carbon | mg/L | BMRL | 5.3 | 31.2 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.003 | 0.163 | 0.41814 | 98.1595 | 0.29057 | 98.9675
Plant Name | Lorton/Occoquan WTP | Total width of all membrane envelopes in the element, w (ft) | 12 | Feed flow rate at the end of stage 1, (QF-s(1))end (gpm) | 10.0868 | TOC | 4.8 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | 1996-04-17 | 8:00 | 187.8 | 12 | 62 | 46 | 2.8 | 0 | 11.5 | 2.4 |  | 13.9 | 13.9 | 0.82734 | 0 | 12.7424 | 15.1702 | 2.3228 | 48.8772 | 0.31037 | 6.4 | 6.1 | 12.1 |  | 80.5 | 408.5 | 408.25 | 0.0612 | 84.9689 | 244.375 | 95.0486 | 62 | 52 | 3.2 | 8 | 5.9 | 13.9 | 13.9 | 0.32823 | 0.57554 | 13.2964 | 15.8297 | 1.1905 | 52.6095 | 0.30089 | 6.1 | 6.3 | 9.55 | 80.5 | 179 | 176.7034 | 1.283 | 88.1366 | 128.6017 | 92.574 | 52 | 46 | 2.8 | 3.5 | 2.4 | 5.9 | 5.9 | 0.27519 | 0.59322 | 11.6343 | 13.851 | 2.7719 | 43.4281 | 0.31894 | 6.3 | 6.2 | 18.7 | 179 | 408.5 | 412.7708 | -1.0455 | 76.7702 | 295.8854 | 93.68 | UV254 | cm-1 | 0.005 | 0.177 | 0.684 | 0.78682 | -15.0319 | 97.1751 | 0.48191 | 98.9625 | SUVA | L/(mg*m) | NA | 3.4038 | --- | --- | --- | --- | UV254 | cm-1 | 0.006 | 0.178 | 1.124 | 1.0178 | 9.4515 | 96.6292 | 0.59788 | 98.9965 | SUVA | L/(mg*m) | NA | 3.1228 | --- | --- | --- | --- | UV254 | cm-1 | BMRL | 0.111 | 0.761 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NA | 2.3125 | --- | --- | --- | --- | UV254 | cm-1 | 0.001 | 0.19 | 1.048 | 1.1128 | -6.1798 | 99.4737 | 0.65138 | 99.8465 | SUVA | L/(mg*m) | NA | 3.1148 | --- | --- | --- | --- | UV254 | cm-1 | 0.001 | 0.179 | 0.978 | 1.0481 | -7.1635 | 99.4413 | 0.61353 | 99.837 | SUVA | L/(mg*m) | NA | 3.1964 | --- | --- | --- | --- | UV254 | cm-1 | 0.006 | 0.163 | 0.974 | 0.98725 | -1.3604 | 96.319 | 0.57512 | 98.9567 | SUVA | L/(mg*m) | NA | 3.0755 | --- | --- | --- | ---
Treatment Plant Category | CONV | Feed spacer thickness, T (ft) | 0.0028 | Feed flow rate at the end of stage 2, (QF-s(2))end (gpm) | 3.7693 |  |  | is to list the pretreatment processes used in this particular pilot-scale run. |  |  | 1996-04-17 | 14:00 | 193.7 | 12 | 62 | 46 | 2.7 | 0 | 11.5 | 2.4 |  | 13.9 | 13.9 | 0.82734 | 0 | 12.7424 | 15.1702 | 2.4518 | 48.8482 | 0.31056 | 6.6 | 6.1 | 12.8 |  | 85 | 433.5 | 430.9583 | 0.58631 | 84.9412 | 257.9792 | 95.0384 | 62 | 52 | 3.3 | 8 | 5.9 | 13.9 | 13.9 | 0.32823 | 0.57554 | 13.2964 | 15.8297 | 1.261 | 52.439 | 0.30187 | 6.1 | 6.3 | 9.85 | 85 | 181 | 186.8983 | -3.2587 | 88.4118 | 135.9492 | 92.7546 | 52 | 46 | 2.7 | 3.5 | 2.4 | 5.9 | 5.9 | 0.27519 | 0.59322 | 11.6343 | 13.851 | 2.7788 | 43.5212 | 0.31826 | 6.3 | 6.2 | 20.3 | 181 | 433.5 | 415.3542 | 4.1859 | 76.1176 | 298.1771 | 93.192 | SUVA | L/(mg*m) | NR | 3.4038 | 2.9739 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | 3.1228 | 4.887 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | 2.3125 | 2.7179 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | 3.1148 | 3.0029 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | 3.1964 | 3.0185 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | 3.0755 | 3.1218 | --- | --- | --- | --- | ---
Process Train Name | Conventional train | Active membrane area of an equivalent 8" x 40" element (ft2) | 400 | [7 empty] | 1996-04-18 | 7:30 | 211.3 | 11.8 | 63 | 47 | 2.8 | 0 | 11.5 | 2.4 |  | 13.9 | 13.9 | 0.82734 | 0 | 12.7424 | 15.2601 | 2.5316 | 49.6684 | 0.30724 | 6.5 | 6.1 | 12.95 |  | 87.5 | 438.5 | 444.7188 | -1.4182 | 85.2 | 266.1094 | 95.1336 | 63 | 54 | 3.5 | 8 | 5.9 | 13.9 | 13.9 | 0.32823 | 0.57554 | 13.2964 | 15.9236 | 1.2962 | 53.7038 | 0.29651 | 6.1 | 6.2 | 10.25 | 87.5 | 188.5 | 192.2458 | -1.9871 | 88.2857 | 139.8729 | 92.6719 | 54 | 47 | 2.8 | 3.5 | 2.4 | 5.9 | 5.9 | 0.27519 | 0.59322 | 11.6343 | 13.9331 | 2.8972 | 44.8028 | 0.31099 | 6.2 | 6.2 | 20.95 | 188.5 | 438.5 | 432.8438 | 1.2899 | 76.0571 | 310.6719 | 93.2566 | Bromide | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
ICR Treatment Plant Identification Number | 685 | Purchase price for an equivalent 8" x 40 " element ($) | 600 | Calculate the Minimum Recycle Flow Rates for Each Stage1 | [6 empty] | 1996-04-18 | 14:30 | 218.4 | 12.1 | 63 | 47 | 2.9 | 0 | 11.5 | 2.4 |  | 13.9 | 13.9 | 0.82734 | 0 | 12.7424 | 15.1254 | 2.5893 | 49.5107 | 0.3055 | 6.5 | 6.1 | 13.25 |  | 89.5 | 446.5 | 454.8646 | -1.8734 | 85.1955 | 272.1823 | 95.1319 | 63 | 54 | 3.9 | 8 | 5.9 | 13.9 | 13.9 | 0.32823 | 0.57554 | 13.2964 | 15.783 | 1.3273 | 53.2727 | 0.29627 | 6.1 | 6.3 | 10.4 | 89.5 | 194.5 | 196.7542 | -1.159 | 88.3799 | 143.1271 | 92.7337 | 54 | 47 | 2.9 | 3.5 | 2.4 | 5.9 | 5.9 | 0.27519 | 0.59322 | 11.6343 | 13.8101 | 2.9897 | 44.6103 | 0.30957 | 6.3 | 6.2 | 21.6 | 194.5 | 446.5 | 446.6458 | -0.032661 | 75.8659 | 320.5729 | 93.2621 | SDS-Cl2 dose | mg/L | 1 | 4 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 1 | 7 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 1 | 4 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | NA | NA | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | NA | NA | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | NA | NA | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection
PWSID Number of Plant (if assigned) | VA6059500 |  |  | Minimum recycle flow rate for stage 1, (QR-s(1))min (gpm) | -2.0868 | [5 empty] | 1996-04-19 | 7:00 | 234.8 | 11.9 | 63 | 46 | 3.2 | 0 | 11.5 | 2.4 |  | 13.9 | 13.9 | 0.82734 | 0 | 12.7424 | 15.2151 | 2.7286 | 48.5714 | 0.31325 | 6.4 | 6.1 | 13.65 |  | 94 | 450.5 | 479.0104 | -6.3286 | 85.4787 | 286.5052 | 95.2357 | 63 | 53 | 3.8 | 8 | 5.9 | 13.9 | 13.9 | 0.32823 | 0.57554 | 13.2964 | 15.8766 | 1.3977 | 52.8023 | 0.30068 | 6.1 | 6.3 | 10.7 | 94 | 206.5 | 206.9492 | -0.21751 | 88.617 | 150.4746 | 92.8892 | 53 | 46 | 3.2 | 3.5 | 2.4 | 5.9 | 5.9 | 0.27519 | 0.59322 | 11.6343 | 13.892 | 3.1799 | 43.1201 | 0.32217 | 6.3 | 6.3 | 22.6 | 206.5 | 450.5 | 474.6875 | -5.369 | 75.9574 | 340.5938 | 93.3645 | SDS-Free Cl2 residual | mg/L | 0.81 | 0.04 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.49 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 0.78 | 1.03 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.59 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 0.8 | 0.61 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.6 |  |  |  |  | SDS-Free Cl2 residual | mg/L | NA | NA | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.54 |  |  |  |  | SDS-Free Cl2 residual | mg/L | NA | NA | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.56 |  |  |  |  | SDS-Free Cl2 residual | mg/L | NA | NA | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.59
Historical Minimum Water Temperature (oC) | 4 | Additional Information |  | Minimum recycle flow rate for stage 2, (QR-s(2))min (gpm) | 0.23074 | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | 1996-04-19 | 16:30 | 243.9 | 12.6 | 62 | 45 | 2.6 | 0 | 11.5 | 2.4 |  | 13.9 | 13.9 | 0.82734 | 0 | 12.7424 | 14.9035 | 2.6674 | 48.2326 | 0.30899 |  |  | 13.45 |  | 92 | 443.5 | 468.3854 | -5.6111 | 85.3804 | 280.1927 | 95.1997 | 62 | 52 | 3.2 | 8 | 5.9 | 13.9 | 13.9 | 0.32823 | 0.57554 | 13.2964 | 15.5515 | 1.3675 | 52.4325 | 0.2966 |  |  | 10.5 | 92 | 202.5 | 202.5085 | -0.004185 | 88.587 | 147.2542 | 92.8695 | 52 | 45 | 2.6 | 3.5 | 2.4 | 5.9 | 5.9 | 0.27519 | 0.59322 | 11.6343 | 13.6075 | 3.1142 | 42.7858 | 0.31804 |  |  | 22.4 | 202.5 | 443.5 | 465.1458 | -4.8807 | 75.6522 | 333.8229 | 93.2899 | SDS-Cl2 demand | mg/L | 0.19 | 3.96 | --- | 17.3264 | --- | 95.202 | 10.6432 | 98.2148 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 3.2 |  |  |  |  | SDS-Cl2 demand | mg/L | 0.22 | 5.97 | --- | 34.0435 | --- | 96.3149 | 20.0068 | 98.9004 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 3.5 |  |  |  |  | SDS-Cl2 demand | mg/L | 0.2 | 3.39 | --- | 18.9647 | --- | 94.1003 | 11.1774 | 98.2107 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 3.6 |  |  |  |  | SDS-Cl2 demand | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 3.7 |  |  |  |  | SDS-Cl2 demand | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 4 |  |  |  |  | SDS-Cl2 demand | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 4.4
Historical Average Water Temperature (oC) | 14.7 | Design cross-flow velocity (fps) |  | 1: A negative minimum recycle flow rate indicates that recycle is not required to |  | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | 1996-04-22 | 7:30 | 307.3 | 13 | 62 | 44 | 2.8 | 0 | 11.5 | 2.4 |  | 13.9 | 13.9 | 0.82734 | 0 | 12.7424 | 14.7283 | 2.7812 | 47.4188 | 0.3106 | 6.4 | 6 | 14.6 |  | 96.5 | 474 | 488.9375 | -3.1514 | 84.8705 | 292.7188 | 95.0123 | 62 | 52 | 3.2 | 8 | 5.9 | 13.9 | 13.9 | 0.32823 | 0.57554 | 13.2964 | 15.3687 | 1.4355 | 52.3645 | 0.29349 | 6 | 6.1 | 10.95 | 96.5 | 207.5 | 212.5 | -2.4096 | 88.6528 | 154.5 | 92.9126 | 52 | 44 | 2.8 | 3.5 | 2.4 | 5.9 | 5.9 | 0.27519 | 0.59322 | 11.6343 | 13.4476 | 3.1626 | 42.0374 | 0.3199 | 6.1 | 6.2 | 24.6 | 207.5 | 474 | 474.2292 | -0.048347 | 74.5078 | 340.8646 | 92.7831 | SDS-Chlorination temp. | oC | 19 | 19 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 6.5 |  |  |  |  | SDS-Chlorination temp. | oC | 19 | 19 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 5.9 |  |  |  |  | SDS-Chlorination temp. | oC | 19 | 19 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 6 |  |  |  |  | SDS-Chlorination temp. | oC | NA | NA | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 6.8 |  |  |  |  | SDS-Chlorination temp. | oC | NA | NA | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 7.1 |  |  |  |  | SDS-Chlorination temp. | oC | NA | NA | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 7.4
State Approved Plant Capacity (MGD) | 112 | Required influent flow to permeate flow rate ratio, QI:Qp | 6:1 | meet the manufacturer's minimum flow requirement. | [6 empty] | 1996-04-22 | 14:30 | 314 | 13.6 | 61 | 44 | 2.4 | 0 | 11.5 | 2.4 |  | 13.9 | 13.9 | 0.82734 | 0 | 12.7424 | 14.4694 | 2.7982 | 47.3018 | 0.3059 | 6.2 | 6 | 16.1 |  | 98.5 | 487 | 493.3333 | -1.3005 | 83.6548 | 295.9167 | 94.5593 | 61 | 51 | 3.1 | 8 | 5.9 | 13.9 | 13.9 | 0.32823 | 0.57554 | 13.2964 | 15.0985 | 1.4414 | 51.4586 | 0.29341 | 6 | 5.9 | 12.6 | 98.5 | 218 | 214.9746 | 1.3878 | 87.2081 | 156.7373 | 91.9611 | 51 | 44 | 2.4 | 3.5 | 2.4 | 5.9 | 5.9 | 0.27519 | 0.59322 | 11.6343 | 13.2112 | 3.3364 | 41.7636 | 0.31633 | 5.9 | 6.2 | 25.05 | 218 | 487 | 499.3854 | -2.5432 | 74.5685 | 358.6927 | 93.0163 | SDS-Chlorination pH | --- | 7.5 | 7.5 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 7.5 | 7.5 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 7.5 | 7.5 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | NA | NA | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | NA | NA | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | NA | NA | --- | --- | --- | --- | --- | ---
|  | Maximum element recovery (%) | 15 | [7 empty] | 1996-04-23 | 7:30 | 331.2 | 13.5 | 60 | 43 | 2.9 | 0 | 11.5 | 2.4 |  | 13.9 | 13.9 | 0.82734 | 0 | 12.7424 | 14.5122 | 2.7965 | 45.8035 | 0.31684 | 6.4 | 6 | 16.15 |  | 98.5 | 492 | 493.0938 | -0.22231 | 83.6041 | 295.7969 | 94.5402 | 60 | 50 | 3.5 | 8 | 5.9 | 13.9 | 13.9 | 0.32823 | 0.57554 | 13.2964 | 15.1432 | 1.4405 | 50.0595 | 0.3025 | 6 | 6.2 | 12.65 | 98.5 | 204.5 | 214.9068 | -5.0889 | 87.1574 | 156.7034 | 91.9274 | 50 | 43 | 2.9 | 3.5 | 2.4 | 5.9 | 5.9 | 0.27519 | 0.59322 | 11.6343 | 13.2503 | 3.084 | 40.516 | 0.32704 | 6.2 | 6.2 | 26.15 | 204.5 | 492 | 464.5938 | 5.5704 | 73.4518 | 334.5469 | 92.1835 | SDS-Incubation time | hours | 72 | 72 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 72 | 72 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 72 | 72 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | NA | NA | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | NA | NA | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | NA | NA | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters
|  | Variability of design flux (%) | 20 | Calculate the Maximum Recycle Flow Rates for Each Stage | [6 empty] | 1996-04-23 | 15:00 | 338.4 | 14.3 | 61 | 44 | 3.2 | 0 | 11.5 | 2.4 |  | 13.9 | 13.9 | 0.82734 | 0 | 12.7424 | 14.1731 | 2.8321 | 46.4679 | 0.30501 |  |  | 16.6 |  | 100 | 475 | 499.625 | -5.1842 | 83.4 | 299.8125 | 94.4632 | 61 | 51 | 3.8 | 8.1 | 5.8 | 13.9 | 13.9 | 0.32658 | 0.58273 | 13.4626 | 14.9742 | 1.4673 | 50.7327 | 0.29516 |  |  | 13.6 | 100 | 204 | 220.6621 | -8.1677 | 86.4 | 160.331 | 91.5175 | 51 | 44 | 3.2 | 3.4 | 2.4 | 5.8 | 5.8 | 0.27187 | 0.58621 | 11.3019 | 12.5709 | 3.0434 | 41.2566 | 0.3047 |  |  | 25.85 | 204 | 475 | 456.3792 | 3.9202 | 74.15 | 330.1896 | 92.1712 | SDS-TOX | mg Cl- /L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-2 | CI-s2-2 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-4 | CI-s2-4 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-6 | CI-s2-6 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-8 | CI-s2-8 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-10 | CI-s2-10 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-10 (dup) | CI-s2-10 (dup) | CC(calc) | RF (%) | CB | RB (%)
|  | Rejection of reference solute and conditions of test | 98% rejection of 2,000 ppm | Maximum recycle flow rate for stage 1, (QR-s(1))max (gpm) | 12.8882 | [5 empty] | 1996-04-24 | 8:30 | 356.2 | 14.8 | 60 | 43 | 3.6 | 0 | 11.5 | 2.4 |  | 13.9 | 13.9 | 0.82734 | 0 | 12.7424 | 13.9652 | 2.7846 | 45.1154 | 0.30954 | 6.4 | 6 | 17 |  | 99 | 482 | 491.9167 | -2.0574 | 82.8283 | 295.4583 | 94.2462 | 60 | 50 | 4.1 | 8.1 | 5.8 | 13.9 | 13.9 | 0.32658 | 0.58273 | 13.4626 | 14.7545 | 1.4401 | 49.4599 | 0.29831 | 6 | 6.1 | 14.2 | 99 | 210.5 | 217.4276 | -3.291 | 85.6566 | 158.2138 | 91.0248 | 50 | 43 | 3.6 | 3.4 | 2.4 | 5.8 | 5.8 | 0.27187 | 0.58621 | 11.3019 | 12.3865 | 3.1339 | 39.7661 | 0.31148 | 6.1 | 6.2 | 27.05 | 210.5 | 482 | 470.3875 | 2.4092 | 72.6768 | 340.4438 | 92.0545 | SDS-CHCl3 | mg/L | BMRL | 81.9 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1996-04-09 | 1996-04-09 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | BMRL | 118.9 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1996-04-15 | 1996-04-15 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | BMRL | 81.9 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1996-04-26 | 1996-04-26 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1996-05-14 | 1996-05-14 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1996-05-21 | 1996-05-21 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1996-05-29 | 1996-05-29 | --- | --- | --- | ---
|  | (e.g., solute type and concentration) | MgSO4 solution | Maximum recycle flow rate for stage 2, (QR-s(2))max (gpm) | 7.7182 | [5 empty] | 1996-04-24 | 14:30 | 361.7 | 15.3 | 59 | 42 | 3.2 | 0 | 11.5 | 2.4 |  | 13.9 | 13.9 | 0.82734 | 0 | 12.7424 | 13.7603 | 2.7846 | 44.5154 | 0.30911 | 6.4 | 6 | 17 |  | 99 | 477.5 | 491.9167 | -3.0192 | 82.8283 | 295.4583 | 94.2462 | 59 | 49 | 4 | 8.2 | 5.7 | 13.9 | 13.9 | 0.32492 | 0.58993 | 13.6288 | 14.7175 | 1.4838 | 48.5162 | 0.30335 | 6 | 6.2 | 12.7 | 99 | 216 | 223.1509 | -3.3106 | 87.1717 | 161.0754 | 92.1155 | 49 | 42 | 3.2 | 3.3 | 2.4 | 5.7 | 5.7 | 0.26855 | 0.57895 | 10.9695 | 11.8458 | 3.159 | 39.141 | 0.30264 | 6.2 | 6.2 | 28.8 | 216 | 477.5 | 473.4 | 0.85864 | 70.9091 | 344.7 | 91.6449 | SDS-BDCM | mg/L | BMRL | 14.4 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 11:00 | 11:00 | --- | --- | --- | --- | SDS-BDCM | mg/L | BMRL | 8.3 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 11:00 | 11:00 | --- | --- | --- | --- | SDS-BDCM | mg/L | BMRL | 14.4 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 11:00 | 11:00 | --- | --- | --- | --- | SDS-BDCM | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 11:00 | 11:00 | --- | --- | --- | --- | SDS-BDCM | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 11:00 | 11:00 | --- | --- | --- | --- | SDS-BDCM | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 11:00 | 11:00 | --- | --- | --- | ---
|  | Variability of rejection of reference solute (%) | < 3% | [7 empty] | 1996-04-25 | 7:30 | 379 | 14.4 | 61 | 44 | 3.8 | 0 | 11.5 | 2.4 |  | 13.9 | 13.9 | 0.82734 | 0 | 12.7424 | 14.1313 | 2.8 | 45.9 | 0.30787 | 6.4 | 6 |  |  | 99 | [6 empty] | 61 | 51 | 4.5 | 8.1 | 5.8 | 13.9 | 13.9 | 0.32658 | 0.58273 | 13.4626 | 14.93 | 1.4 | 50.1 | 0.298 | 6 | 6.2 |  | 99 | [6 empty] | 51 | 44 | 3.8 | 3.4 | 2.4 | 5.8 | 5.8 | 0.27187 | 0.58621 | 11.3019 | 12.5338 | 3.1 | 40.6 | 0.30871 | 6.2 | 6.2 | [8 empty] | SDS-DBCM | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 10 | 10 | --- | --- | --- | --- | SDS-DBCM | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 142 | 142 | --- | --- | --- | --- | SDS-DBCM | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 405 | 405 | --- | --- | --- | --- | SDS-DBCM | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 840 | 840 | --- | --- | --- | --- | SDS-DBCM | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 985 | 985 | --- | --- | --- | --- | SDS-DBCM | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 1097 | 1097 | --- | --- | --- | ---
|  | Standard testing recovery (%) | 15 | Select the Design System Recycle Flow Rate2 | [6 empty] | 1996-04-25 | 16:30 | 388 | 14.6 | 62 | 44 | 2.7 | 0 | 12 | 2.5 |  | 14.5 | 14.5 | 0.82759 | 0 | 13.2964 | 14.6587 | 2.7574 | 47.5426 | 0.30833 |  |  | 16.9 |  | 98 | 497 | 487.28 | 1.9557 | 82.7551 | 292.64 | 94.225 | 62 | 51 | 3.2 | 8.2 | 6.3 | 14.5 | 14.5 | 0.34481 | 0.56552 | 13.6288 | 15.0252 | 1.4048 | 51.8952 | 0.28953 |  |  | 12.9 | 98 | 211 | 208.7651 | 1.0592 | 86.8367 | 153.3825 | 91.5897 | 51 | 44 | 2.7 | 3.8 | 2.5 | 6.3 | 6.3 | 0.29176 | 0.60317 | 12.6316 | 13.9258 | 3.2331 | 41.5669 | 0.33502 |  |  | 27.3 | 211 | 497 | 490.224 | 1.3634 | 72.1429 | 350.612 | 92.2136 | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | NA | 6.1 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | NA | 6.2 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | NA | 6.3 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | NA | 6.4 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | NA | 6.3 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | NA | NA | --- | --- | --- | ---
|  | Standard testing pH | 7 | Minimum system recycle flow rate, (QR-sys)min (gpm) | 0.23074 | [5 empty] | 1996-04-26 | 7:30 | 403 | 14.3 | 62 | 44 | 3.2 | 0 | 12 | 2.4 |  | 14.4 | 14.4 | 0.83333 | 0 | 13.2964 | 14.7893 | 2.8718 | 46.9282 | 0.31515 |  |  | 16.45 |  | 98.5 | 476 | 508.75 | -6.8803 | 83.2995 | 303.625 | 94.5821 | 62 | 52 | 4 | 8.4 | 6 | 14.4 | 14.4 | 0.33818 | 0.58333 | 13.9612 | 15.5288 | 1.468 | 51.532 | 0.30134 |  |  | 12.15 | 98.5 | 211.5 | 219.39 | -3.7305 | 87.665 | 158.945 | 92.3558 | 52 | 44 | 3.2 | 3.6 | 2.4 | 6 | 6 | 0.2785 | 0.6 | 11.9668 | 13.3104 | 3.2314 | 41.5686 | 0.3202 |  |  | 26.85 | 211.5 | 476 | 488.475 | -2.6208 | 72.7411 | 349.9875 | 92.3283 | SDS-THM4 | mg/L | 0 | 96.3 | --- | 437.7273 | --- | 100 | 267.0136 | 100 | Temperature | oC | NA | 11.4 | --- | --- | --- | --- | SDS-THM4 | mg/L | 0 | 127.2 | --- | 748.2353 | --- | 100 | 437.7176 | 100 | Temperature | oC | NA | 12.5 | --- | --- | --- | --- | SDS-THM4 | mg/L | 0 | 96.3 | --- | 566.4706 | --- | 100 | 331.3853 | 100 | Temperature | oC | NA | 16 | --- | --- | --- | --- | SDS-THM4 | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Temperature | oC | NA | 17.5 | --- | --- | --- | --- | SDS-THM4 | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Temperature | oC | NA | 18.1 | --- | --- | --- | --- | SDS-THM4 | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Temperature | oC | NA | 18.2 | --- | --- | --- | ---
|  | Acceptable range of operating pressures | < 250 | Maximum system recycle flow rate, (QR-sys)max (gpm) | 7.7182 | [5 empty] | 1996-04-26 | 14:00 | 410 | 14.6 | 62 | 44 | 3 | 0 | 12 | 2.4 |  | 14.4 | 14.4 | 0.83333 | 0 | 13.2964 | 14.6587 | 2.8 | 47.2 | 0.31057 | 6.5 | 5.9 | 16.75 |  | 97.5 | 499 | 501.25 | -0.4509 | 82.8205 | 299.375 | 94.405 | 62 | 51 | 3.8 | 8.4 | 6 | 14.4 | 14.4 | 0.33818 | 0.58333 | 13.9612 | 15.3917 | 1.4 | 51.3 | 0.30003 | 5.9 | 6.3 | 13.1 |  | 210.5 | -18.34 | 108.7126 | 86.5641 | -9.17 | 242.8571 | 51 | 44 | 3 | 3.6 | 2.4 | 6 | 6 | 0.2785 | 0.6 | 11.9668 | 13.1929 | 3.2043 | 41.2957 | 0.31947 | 6.3 | 6.3 | 27.4 | 210.5 | 499 | 485.15 | 2.7756 | 71.8974 | 347.825 | 92.1225 | SDS-MCAA* | mg/L | BMRL | 3 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | NA | 20 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | 3 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | NA | 24 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | 3 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | NA | 29 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | NA | 37 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | NA | 36 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | NA | 36 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | Acceptable range of operating pH values | 3-9 | Design system recycle flow rate, QR-sys (gpm) | 0 | [5 empty] | 1996-04-29 | 7:30 | 474.9 | 14.7 | 69 | 47 | 2.4 | 0 | 12 | 2.5 |  | 14.5 | 14.5 | 0.82759 | 0 | 13.2964 | 14.6155 | 2.7863 | 52.8137 | 0.27674 | 6.6 | 5.9 | 15.55 |  | 97.5 | 501 | 490.86 | 2.024 | 84.0513 | 294.18 | 94.7141 | 69 | 56 | 3.2 | 8.4 | 6.1 | 14.5 | 14.5 | 0.3415 | 0.57931 | 13.9612 | 15.3463 | 1.4471 | 57.8529 | 0.26526 | 5.9 | 6.3 | 11.8 | 97.5 | 218.5 | 215.5131 | 1.367 | 87.8974 | 156.5066 | 92.4604 | 56 | 47 | 2.4 | 3.6 | 2.5 | 6.1 | 6.1 | 0.28513 | 0.59016 | 11.9668 | 13.1539 | 3.3058 | 45.7942 | 0.28724 | 6.3 | 6.3 | 26.3 | 218.5 | 501 | 495.268 | 1.1441 | 73.0256 | 356.884 | 92.6307 | SDS-DCAA* | mg/L | 1 | 42 | --- | 187.3636 | --- | 97.619 | 114.6818 | 99.128 | Total dissolved solids | mg/L | 17 | 164 | 306.5455 | 79.5181 | 235.2727 | 92.7743 | SDS-DCAA* | mg/L | 1 | 63 | --- | 365.7059 | --- | 98.4127 | 214.3529 | 99.5335 | Total dissolved solids | mg/L | 19.45 | 181 | 416.5938 | 76.2805 | 298.7969 | 93.4906 | SDS-DCAA* | mg/L | 1 | 42 | --- | 242.1765 | --- | 97.619 | 142.0882 | 99.2962 | Total dissolved solids | mg/L | 26.3 | 218.5 | 506.8 | 73.0256 | 362.65 | 92.7478 | SDS-DCAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 16.8 | 187 | 390.1419 | 80.2353 | 288.571 | 94.1782 | SDS-DCAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 16.7 | 192 | 418.1935 | 81.0227 | 305.0968 | 94.5263 | SDS-DCAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 15.3 | 192 | 451.16 | 82.809 | 321.58 | 95.2422
|  | Typical pressure drop across a single element (psi) | 3-5 | System influent flow rate, QI-sys (gpm) | 19.1118 | [5 empty] | 1996-04-29 | 14:30 | 481.7 | 15.5 | 67 | 46 | 1.8 | 0 | 12.5 | 2.5 |  | 15 | 15 | 0.83333 | 0 | 13.8504 | 14.8687 | 2.8893 | 51.8107 | 0.28698 |  |  | 15.45 |  | 98 | 488 | 510.75 | -4.6619 | 84.2347 | 304.375 | 94.924 | 67 | 54 | 2.5 | 9 | 6 | 15 | 15 | 0.34813 | 0.6 | 14.9584 | 16.0582 | 1.505 | 56.495 | 0.28424 |  |  | 12 | 98 | 221 | 227 | -2.7149 | 87.7551 | 162.5 | 92.6154 | 54 | 46 | 1.8 | 3.5 | 2.5 | 6 | 6 | 0.28182 | 0.58333 | 11.6343 | 12.4897 | 3.2955 | 44.9046 | 0.27814 |  |  | 27.15 | 221 | 488 | 492.39 | -0.89959 | 72.2959 | 356.695 | 92.3885 | SDS-TCAA* | mg/L | 1 | 63 | --- | 282.8182 | --- | 98.4127 | 172.9091 | 99.4217 | Total hardness | mg/L as CaCO3 | NA | 116 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | 72 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | NA | 116 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | 1 | 63 | --- | 365.7059 | --- | 98.4127 | 214.3529 | 99.5335 | Total hardness | mg/L as CaCO3 | NA | 173 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | NA | 144 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | NA | 144 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | NA | 165 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | Maximum permissible SDI | 5 | Recycle ratio, r | 0 | [5 empty] | 1996-04-30 | 8:00 | 500.4 | 15.2 | 67 | 46 | 2 | 0 | 12.5 | 2.5 |  | 15 | 15 | 0.83333 | 0 | 13.8504 | 15.0011 | 2.9 | 51.6 | 0.29072 | [11 empty] | 67 | 54 | 2.9 | 9 | 6 | 15 | 15 | 0.34813 | 0.6 | 14.9584 | 16.2012 | 1.5 | 56.1 | 0.28879 | [10 empty] | 54 | 46 | 2 | 3.5 | 2.5 | 6 | 6 | 0.28182 | 0.58333 | 11.6343 | 12.6009 | 3.3 | 44.7 | 0.2819 | [10 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | Maximum permissible turbidity (ntu) | 1 | 2: The design system recycle flow rate must fall between the minimum and | [6 empty] | 1996-04-30 | 14:30 | 506.9 | 15.4 | 67 | 46 | 2 | 0 | 12.5 | 2.5 |  | 15 | 15 | 0.83333 | 0 | 13.8504 | 14.9127 | 2.884 | 51.616 | 0.28892 |  |  | 16.6 |  | 99 | 529 | 511 | 3.4026 | 83.2323 | 305 | 94.5574 | 67 | 54 | 3 | 9 | 6 | 15 | 15 | 0.34813 | 0.6 | 14.9584 | 16.1057 | 1.519 | 55.981 | 0.2877 |  |  | 12.2 | 99 | 228 | 229.2 | -0.52632 | 87.6768 | 164.1 | 92.5655 | 54 | 46 | 2 | 3.5 | 2.5 | 6 | 6 | 0.28182 | 0.58333 | 11.6343 | 12.5267 | 3.3923 | 44.6076 | 0.28082 |  |  | 28.45 | 228 | 529 | 507.37 | 4.0888 | 71.2626 | 367.685 | 92.2624 | SDS-DBAA* | mg/L | BMRL | 8 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | NA | 0.17 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | NA | 0.13 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | 8 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | NA | 0.16 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | NA | 0.14 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | NA | 0.12 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | < 0.1 | maximum system recycle flow rates. | [6 empty] | 1996-05-01 | 9:00 | 524.8 | 15.2 | 67 | 46 | 3 | 0 | 12.5 | 2.5 |  | 15 | 15 | 0.83333 | 0 | 13.8504 | 15.0011 | 2.8683 | 50.6317 | 0.29628 | 6.5 | 6 | 17.05 |  | 99 | 501 | 508.75 | -1.5469 | 82.7778 | 303.875 | 94.3891 | 67 | 54 | 3.5 | 9 | 6 | 15 | 15 | 0.34813 | 0.6 | 14.9584 | 16.2012 | 1.5181 | 55.4819 | 0.29201 | 6 | 6.2 | 12.25 | 99 | 230 | 229.125 | 0.38043 | 87.6263 | 164.0625 | 92.5333 | 54 | 46 | 3 | 3.5 | 2.5 | 6 | 6 | 0.28182 | 0.58333 | 11.6343 | 12.6009 | 3.4263 | 43.5737 | 0.28919 | 6.2 | 6.2 | 28.45 | 230 | 501 | 512.17 | -2.2295 | 71.2626 | 371.085 | 92.3333 | SDS-BCAA* | mg/L | BMRL | 5 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | NA | 9.5 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | 2 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 12.3 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | 5 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | NA | 9.5 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | NA | 12.7 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | NA | 14.6 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | NA | 14 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | 1: All of the information requested in this field may not be available, but values for all of the Design | [8 empty] | 1996-05-01 | 16:00 | 531 | 15.6 | 70 | 47 | 3.8 | 0 | 12.5 | 2.5 |  | 15 | 15 | 0.83333 | 0 | 13.8504 | 14.8248 | 2.9 | 51.8 | 0.28619 | [11 empty] | 70 | 55 | 4.1 | 9.2 | 5.8 | 15 | 15 | 0.34481 | 0.61333 | 15.2909 | 16.3666 | 1.5 | 56.9 | 0.28764 | [10 empty] | 55 | 47 | 3.8 | 3.3 | 2.5 | 5.8 | 5.8 | 0.27519 | 0.56897 | 10.9695 | 11.7412 | 3.4 | 43.8 | 0.26806 | [10 empty] | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.004 | 0.382 | 0.74855 | 97.7401 | 0.56527 | 99.2924 | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.004 | 0.42 | 1.0267 | 97.7528 | 0.72333 | 99.447 | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.001 | 0.284 | 0.7085 | 99.0991 | 0.49625 | 99.7985 | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.003 | 0.471 | 1.0296 | 98.4211 | 0.75029 | 99.6002 | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.003 | 0.445 | 1.0153 | 98.324 | 0.73016 | 99.5891 | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.003 | 0.418 | 1.0267 | 98.1595 | 0.72233 | 99.5847
|  | Parameters must be entered in cells E15:E26, since these parameters are used in calculations. |  | Summary of the Stage and System Flow Rates | [6 empty] | 1996-05-02 | 8:00 | 548 | 16.3 | 72 | 48 | 3.2 | 0 | 12.5 | 1.89 |  | 14.39 | 14.39 | 0.86866 | 0 | 13.8504 | 14.5212 | 2.9 | 53.9 | 0.26941 |  |  |  |  | 96.5 | [6 empty] | 72 | 56 | 3.7 | 9.1 | 5.29 | 14.39 | 14.39 | 0.32624 | 0.63238 | 15.1247 | 15.8571 | 1.5 | 58.8 | 0.26968 |  |  |  | 96.5 | [6 empty] | 56 | 48 | 3.2 | 3.4 | 1.89 | 5.29 | 5.29 | 0.23805 | 0.64272 | 11.3019 | 11.8493 | 3.4 | 45.4 | 0.261 | [10 empty] | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NA | 4.0211 | --- | --- | --- | --- | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.4146 | --- | --- | --- | --- | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NA | 2.9895 | --- | --- | --- | --- | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NA | 3.7087 | --- | --- | --- | --- | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NA | 3.0479 | --- | --- | --- | --- | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NA | 2.9857 | --- | --- | --- | ---
|  |  |  | Influent flow rate to stage 1, QI-s(1) (gpm) | 19.1118 | [5 empty] | 1996-05-02 | 16:00 | 555.6 | 16.5 | 69 | 45 | 3.2 | 0 | 12.5 | 1.89 |  | 14.39 | 14.39 | 0.86866 | 0 | 13.8504 | 14.4356 | 2.9 | 50.9 | 0.28361 |  |  | 15.8 |  | 96.5 | 481 | 630.2302 | -31.025 | 83.6269 | 363.3651 | 95.6518 | 69 | 54 | 3.7 | 9.1 | 5.29 | 14.39 | 14.39 | 0.32624 | 0.63238 | 15.1247 | 15.7637 | 1.5 | 56.3 | 0.27999 |  |  | 11.6 |  | 221.5 | -19.9546 | 109.0089 | 87.9793 | -9.9773 | 216.2637 | 54 | 45 | 3.2 | 3.4 | 1.89 | 5.29 | 5.29 | 0.23805 | 0.64272 | 11.3019 | 11.7795 | 3.6973 | 42.6027 | 0.2765 |  |  | 26.85 | 221.5 | 481 | 571.664 | -18.8491 | 72.1762 | 396.582 | 93.2296 | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  |  |  | Permeate flow rate from stage 1, Qp-s(1) (gpm) | 10.83 | [5 empty] | 1996-05-03 | 7:30 | 571.1 | 15.8 | 70 | 46 | 2.9 | 0 | 12.5 | 1.83 |  | 14.33 | 14.33 | 0.8723 | 0 | 13.8504 | 14.7374 | 3.5212 | 51.5788 | 0.28573 | 6.4 | 6 | 15.25 |  | 95 | 503.5 | 639.7404 | -27.0587 | 83.9474 | 367.3702 | 95.8489 | 70 | 54 | 3.2 | 9.2 | 5.13 | 14.33 | 14.33 | 0.3226 | 0.64201 | 15.2909 | 16.2701 | 1.5989 | 57.2011 | 0.28444 | 6 | 6.3 | 10.7 | 95 | 211.5 | 246.1813 | -16.3978 | 88.7368 | 170.5906 | 93.7277 | 54 | 46 | 2.9 | 3.3 | 1.83 | 5.13 | 5.13 | 0.23076 | 0.64327 | 10.9695 | 11.672 | 3.5294 | 43.5706 | 0.26789 | 6.3 | 6.3 | 25.9 | 211.5 | 503.5 | 546.1885 | -8.4784 | 72.7368 | 378.8443 | 93.1634 | SDS-HAA5 | mg/L | 2 | 116 | --- | 520.1818 | --- | 98.2759 | 318.0909 | 99.3712 | [8 empty] | SDS-HAA5 | mg/L | 1 | 138 | --- | 806.8824 | --- | 99.2754 | 472.4412 | 99.7883 | [8 empty] | SDS-HAA5 | mg/L | 2 | 116 | --- | 672.5882 | --- | 98.2759 | 394.2941 | 99.4928 | [8 empty] | SDS-HAA5 | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-HAA5 | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-HAA5 | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  |  |  | Concentrate flow rate from stage 1, QC-s(1) (gpm) | 8.2818 | [5 empty] | 1996-05-03 | 17:30 | 577 | 16.1 | 71 | 46 | 2.8 | 0 | 12.6 | 1.85 |  | 14.45 | 14.45 | 0.87197 | 0 | 13.9612 | 14.7242 | 3.6785 | 52.0215 | 0.28304 |  |  | 15.5 |  | 99 | 540 | 667.7027 | -23.6486 | 84.3434 | 383.3514 | 95.9567 | 71 | 55 | 3.2 | 9.4 | 5.05 | 14.45 | 14.45 | 0.32326 | 0.65052 | 15.6233 | 16.477 | 1.6855 | 58.1145 | 0.28353 |  |  | 11.7 | 99 | 221.5 | 261.499 | -18.0582 | 88.1818 | 180.2495 | 93.509 | 55 | 46 | 2.8 | 3.2 | 1.85 | 5.05 | 5.05 | 0.22877 | 0.63366 | 10.6371 | 11.2184 | 3.6477 | 44.0523 | 0.25466 |  |  | 25.9 | 221.5 | 540 | 559.8351 | -3.6732 | 73.8384 | 390.6676 | 93.3703 | SDS-HAA6 | mg/L | 2 | 121 | --- | 542.9091 | --- | 98.3471 | 331.9545 | 99.3975 | [8 empty] | SDS-HAA6 | mg/L | 1 | 140 | --- | 818.6471 | --- | 99.2857 | 479.3235 | 99.7914 | [8 empty] | SDS-HAA6 | mg/L | 2 | 121 | --- | 702 | --- | 98.3471 | 411.5 | 99.514 | [8 empty] | SDS-HAA6 | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-HAA6 | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-HAA6 | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  |  |  | Influent flow rate to stage 2, QI-s(2) (gpm) | 8.2818 | [5 empty] | 1996-05-06 | 9:00 | 645 | 16.2 | 72 | 46 | 2.9 | 0 | 12.6 | 1.84 |  | 14.44 | 14.44 | 0.87258 | 0 | 13.9612 | 14.6807 | 3.4551 | 52.6449 | 0.27886 |  |  | 14.9 |  | 93 | 494.5 | 627.8152 | -26.9596 | 83.9785 | 360.4076 | 95.8658 | 72 | 54 | 3.2 | 9.4 | 5.04 | 14.44 | 14.44 | 0.32293 | 0.65097 | 15.6233 | 16.4284 | 1.5885 | 58.2115 | 0.28222 |  |  | 10.8 | 93 | 216 | 246.3095 | -14.0322 | 88.3871 | 169.6548 | 93.6341 | 54 | 46 | 2.9 | 3.2 | 1.84 | 5.04 | 5.04 | 0.22811 | 0.63492 | 10.6371 | 11.1853 | 3.5503 | 43.5497 | 0.25684 |  |  | 26.1 | 216 | 494.5 | 546.2609 | -10.4673 | 71.9355 | 381.1304 | 93.152 | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
|  |  |  | Permeate flow rate from stage 2, Qp-s(2) (gpm) | 5.415 | [5 empty] | 1996-05-06 | 15:00 | 649.9 | 16.5 | 97 | 54 | 2.4 | 0 | 15.7 | 3.1 |  | 18.8 | 18.8 | 0.83511 | 0 | 17.3961 | 18.1311 | 3 | 70.1 | 0.25865 | [11 empty] | 97 | 69 | 3.1 | 11.5 | 7.3 | 18.8 | 18.8 | 0.43267 | 0.6117 | 19.1136 | 19.9211 | 1.6 | 78.3 | 0.25442 | [10 empty] | 69 | 54 | 2.4 | 4.2 | 3.1 | 7.3 | 7.3 | 0.34481 | 0.57534 | 13.9612 | 14.5511 | 3.6 | 55.5 | 0.26218 | [10 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
|  |  |  | Concentrate flow rate from stage 2, QC-s(2) (gpm) | 2.8668 | [5 empty] | 1996-05-07 | 8:30 | 666.2 | 16.2 | 95 | 55 | 3.2 | 0 | 15.8 | 3.1 |  | 18.9 | 18.9 | 0.83598 | 0 | 17.5069 | 18.4091 | 3 | 68.8 | 0.26757 | [11 empty] | 95 | 70 | 4 | 11.5 | 7.4 | 18.9 | 18.9 | 0.43599 | 0.60847 | 19.1136 | 20.0986 | 1.6 | 76.9 | 0.26136 | [10 empty] | 70 | 55 | 3.2 | 4.3 | 3.1 | 7.4 | 7.4 | 0.34813 | 0.58108 | 14.2936 | 15.0302 | 3.6 | 55.7 | 0.26984
|  |  |  | System concentrate recycle flow rate, QR-sys (gpm) | 0 | [5 empty] | 1996-05-07 | 16:00 | 674.2 | 16.8 | 96 | 54 | 2.2 | 0 | 15.8 | 3.1 |  | 18.9 | 18.9 | 0.83598 | 0 | 17.5069 | 18.0855 | 3.1616 | 69.6384 | 0.25971 |  |  | 13.4 |  | 102.5 | 434 | 556.6226 | -28.2541 | 86.9268 | 329.5613 | 95.934 | 96 | 70 | 3.2 | 11.5 | 7.4 | 18.9 | 18.9 | 0.43599 | 0.60847 | 19.1136 | 19.7453 | 1.6135 | 78.1865 | 0.25254 |  |  | 11.7 | 102.5 | 218 | 243.6081 | -11.7468 | 88.5854 | 173.0541 | 93.2391 | 70 | 54 | 2.2 | 4.3 | 3.1 | 7.4 | 7.4 | 0.34813 | 0.58108 | 14.2936 | 14.766 | 3.3253 | 56.4747 | 0.26146 |  |  | 21.65 | 218 | 434 | 490.3565 | -12.9854 | 78.878 | 354.1782 | 93.8873 | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs
|  |  |  | System concentrate waste flow rate, QW-sys (gpm) | 2.8668 | [5 empty] | 1996-05-08 | 15:30 | 697.3 | 16.5 | 94 | 53 | 2 | 0 | 15.6 | 3.1 |  | 18.7 | 18.7 | 0.83422 | 0 | 17.2853 | 18.0156 | 3 | 68.5 | 0.263 | [11 empty] | 94 | 68 | 3.1 | 11.5 | 7.2 | 18.7 | 18.7 | 0.42936 | 0.61497 | 19.1136 | 19.9211 | 1.5 | 76.4 | 0.26075 | [10 empty] | 68 | 53 | 2 | 4.1 | 3.1 | 7.2 | 7.2 | 0.3415 | 0.56944 | 13.6288 | 14.2046 | 3.3 | 55.2 | 0.25733 | [11 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls
|  |  |  | System permeate flow rate, Qp-sys (gpm) | 16.245 | [5 empty] | 1996-05-09 | 8:00 | 714.1 | 16.2 | 96 | 55 | 2.5 | 0 | 15.4 | 3.1 |  | 18.5 | 18.5 | 0.83243 | 0 | 17.0637 | 17.9431 | 3 | 70 | 0.25633 | [11 empty] | 96 | 70 | 3.8 | 11.5 | 7 | 18.5 | 18.5 | 0.42272 | 0.62162 | 19.1136 | 20.0986 | 1.5 | 77.7 | 0.25867 | [10 empty] | 70 | 55 | 2.5 | 3.9 | 3.1 | 7 | 7 | 0.33486 | 0.55714 | 12.964 | 13.6321 | 3.3 | 56.7 | 0.24042 | [11 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2
|  |  |  | System feed flow rate, QF-sys (gpm) | 19.1118 | [5 empty] | 1996-05-09 | 15:30 | 721.2 | 16.7 | 96 | 54 | 2 | 0 | 15.6 | 3.1 |  | 18.7 | 18.7 | 0.83422 | 0 | 17.2853 | 17.9094 | 3 | 70 | 0.25585 | [11 empty] | 96 | 69 | 3.2 | 11.5 | 7.2 | 18.7 | 18.7 | 0.42936 | 0.61497 | 19.1136 | 19.8037 | 1.5 | 77.8 | 0.25455 | [10 empty] | 69 | 54 | 2 | 4.1 | 3.1 | 7.2 | 7.2 | 0.3415 | 0.56944 | 13.6288 | 14.1209 | 3.3 | 56.2 | 0.25126 | [10 empty] | Qp/QT (THM4), % | 25.2336 | 62.6168 |  | Qp/QT (HAA5), % | 54.386 | 78.0702 | [11 empty] | Qp/QT (THM4), % | 43.3962 | 71.6981 |  | Qp/QT (HAA5), % | 61.3139 | 81.0219 | [11 empty] | Qp/QT (THM4), % | 25.2336 | 62.6168 |  | Qp/QT (HAA5), % | 54.386 | 78.0702 | [11 empty] | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | #VALUE! | #VALUE! | [11 empty] | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | #VALUE! | #VALUE! | [11 empty] | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | #VALUE! | #VALUE!
[11 empty] | 1996-05-10 | 8:30 | 738.6 | 16.6 | 97 | 54 | 2.2 | 0 | 15.4 | 3.1 |  | 18.5 | 18.5 | 0.83243 | 0 | 17.0637 | 17.7322 | 2.8672 | 70.4328 | 0.25176 |  |  | 12.2 |  | 94.5 | 420.5 | 503.3452 | -19.7016 | 87.0899 | 298.9226 | 95.9187 | 97 | 69 | 3.2 | 11.5 | 7 | 18.5 | 18.5 | 0.42272 | 0.62162 | 19.1136 | 19.8623 | 1.5027 | 78.2973 | 0.25368 |  |  | 12 | 94.5 | 210.5 | 230.0357 | -9.2806 | 87.3016 | 162.2679 | 92.6048 | 69 | 54 | 2.2 | 3.9 | 3.1 | 7 | 7 | 0.33486 | 0.55714 | 12.964 | 13.4718 | 3.1066 | 56.1934 | 0.23974 |  |  | 19.8 | 210.5 | 420.5 | 450.4129 | -7.1137 | 79.0476 | 330.4565 | 94.0083 | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 43.9263 | 21.1184 | [11 empty] | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 49.2088 | 24.1401 | [11 empty] | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 43.9263 | 21.1184 | [11 empty] | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! | [11 empty] | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! | [11 empty] | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | #VALUE! | #VALUE!
|  |  |  | Calculate the Required System Influent Pressure | [6 empty] | 1996-05-10 | 15:30 | 745.5 | 16.6 | 95 | 53 | 1.8 | 0 | 15.4 | 3.1 |  | 18.5 | 18.5 | 0.83243 | 0 | 17.0637 | 17.7322 | 2.8 | 69.4 | 0.25551 | [11 empty] | 95 | 68 | 3 | 11.5 | 7 | 18.5 | 18.5 | 0.42272 | 0.62162 | 19.1136 | 19.8623 | 1.4 | 77.1 | 0.25762 | [10 empty] | 68 | 53 | 1.8 | 3.9 | 3.1 | 7 | 7 | 0.33486 | 0.55714 | 12.964 | 13.4718 | 3.1 | 55.6 | 0.2423 | [10 empty] | SDS-HAA5b, mg/L | 87.2336 | 44.6168 |  | SDS-HAA5b, mg/L | 54 | 27 | [11 empty] | SDS-HAA5b, mg/L | 78.5472 | 39.7736 |  | SDS-HAA5b, mg/L | 54 | 27 | [11 empty] | SDS-HAA5b, mg/L | 87.2336 | 44.6168 |  | SDS-HAA5b, mg/L | 54 | 27 | [11 empty] | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! | [11 empty] | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! | [11 empty] | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE!
|  |  |  | Osmotic pressure for stage 13, Dp1 (psi) | 1.394 | [5 empty] | 1996-05-11 | 10:30 | 764.5 | 16.5 | 95 | 53 | 0 | 0 | 15.4 | 3.1 |  | 18.5 | 18.5 | 0.83243 | 0 | 17.0637 | 17.7847 | 2.8 | 71.2 | 0.24978 | [11 empty] | 95 | 68 | 3 | 11.5 | 7 | 18.5 | 18.5 | 0.42272 | 0.62162 | 19.1136 | 19.9211 | 1.4 | 77.1 | 0.25838 | [10 empty] | 68 | 53 | 0 | 3.9 | 3.1 | 7 | 7 | 0.33486 | 0.55714 | 12.964 | 13.5117 | 3.1 | 57.4 | 0.2354 | [10 empty] | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! | [11 empty] | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! | [11 empty] | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! | [11 empty] | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! | [11 empty] | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! | [11 empty] | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE!
|  |  |  | Osmotic pressure for stage 23, Dp2 (psi) | 2.9658 | [5 empty] | 1996-05-12 | 14:30 | 792.6 | 16.5 | 98 | 55 | 1.7 | 0 | 15.4 | 3.1 |  | 18.5 | 18.5 | 0.83243 | 0 | 17.0637 | 17.7847 | 2.8 | 72 | 0.24701 | [11 empty] | 98 | 70 | 3 | 11.5 | 7 | 18.5 | 18.5 | 0.42272 | 0.62162 | 19.1136 | 19.9211 | 1.4 | 79.6 | 0.25027 | [10 empty] | 70 | 55 | 1.7 | 3.9 | 3.1 | 7 | 7 | 0.33486 | 0.55714 | 12.964 | 13.5117 | 3.1 | 57.7 | 0.23417 | [10 empty] | SDS-CDb, mg/L | 3.0087 | 1.5993 |  | SDS-CDb, mg/L | 1.9096 | 1.0168 | [11 empty] | SDS-CDb, mg/L | 3.4747 | 1.8474 |  | SDS-CDb, mg/L | 2.4445 | 1.3112 | [11 empty] | SDS-CDb, mg/L | 2.585 | 1.3925 |  | SDS-CDb, mg/L | 1.6551 | 0.89956 | [11 empty] | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | #VALUE! | #VALUE! | [11 empty] | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | #VALUE! | #VALUE! | [11 empty] | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | #VALUE! | #VALUE!
|  |  |  | Pressure losses due to stage hardware, DPs (psi) | 4 | [5 empty] | 1996-05-13 | 8:30 | 810.3 | 16.7 | 98 | 55 | 2.2 | 0 | 15.2 | 3.1 |  | 18.3 | 18.3 | 0.8306 | 0 | 16.8421 | 17.4502 | 2.549 | 71.751 | 0.24321 | 6.6 | 6.2 | 10.65 |  | 84.5 | 370 | 446.6032 | -20.7036 | 87.3964 | 265.5516 | 95.9895 | 98 | 71 | 3 | 11.5 | 6.8 | 18.3 | 18.3 | 0.41609 | 0.62842 | 19.1136 | 19.8037 | 1.4091 | 80.0909 | 0.24727 | 6.2 | 6.3 | 8.15 | 84.5 | 186.5 | 213.6213 | -14.5423 | 90.355 | 149.0607 | 94.5324 | 71 | 55 | 2.2 | 3.7 | 3.1 | 6.8 | 6.8 | 0.32823 | 0.54412 | 12.2992 | 12.7433 | 2.7033 | 58.0967 | 0.21935 | 6.3 | 6.4 | 17.2 | 186.5 | 370 | 388.5677 | -5.0183 | 79.645 | 287.5339 | 94.0181 | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! | [11 empty] | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! | [11 empty] | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! | [11 empty] | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! | [11 empty] | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! | [11 empty] | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE!
|  |  |  | Pressure losses in a single element, DPe (psi) | 2 | [5 empty] | 1996-05-13 | 15:30 | 817.3 | 16.5 | 97 | 54 | 1.8 | 0 | 15.2 | 3.1 |  | 18.3 | 18.3 | 0.8306 | 0 | 16.8421 | 17.5537 | 2.6 | 71.1 | 0.24689 | [11 empty] | 97 | 69 | 2.3 | 11.5 | 6.8 | 18.3 | 18.3 | 0.41609 | 0.62842 | 19.1136 | 19.9211 | 1.4 | 79.3 | 0.25121 | [10 empty] | 69 | 54 | 1.8 | 3.7 | 3.1 | 6.8 | 6.8 | 0.32823 | 0.54412 | 12.2992 | 12.8188 | 2.8 | 56.9 | 0.22529 | [10 empty] | UV254 b, cm-1 | 0.1336 | 0.069299 |  | UV254 b, cm-1 | 0.083456 | 0.042719 | [11 empty] | UV254 b, cm-1 | 0.10336 | 0.054679 |  | UV254 b, cm-1 | 0.07254 | 0.038642 | [11 empty] | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! | [11 empty] | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! | [11 empty] | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! | [11 empty] | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE!
|  |  |  | Design permeate pressure, Pp (psi) | 0 | [5 empty] | 1996-05-14 | 8:00 | 834.2 | 16.4 | 101 | 56 | 1.8 | 0 | 15 | 3.1 |  | 18.1 | 18.1 | 0.82873 | 0 | 16.6205 | 17.374 | 2.5679 | 74.1321 | 0.23437 | 6.9 | 6.4 | 10.4 |  | 85.5 | 364.5 | 448.8871 | -23.1515 | 87.8363 | 267.1935 | 96.1077 | 101 | 72 | 3.1 | 11.3 | 6.8 | 18.1 | 18.1 | 0.41278 | 0.62431 | 18.7812 | 19.6326 | 1.4162 | 81.9838 | 0.23947 | 6.4 | 6.4 | 8.15 | 85.5 | 187 | 214.0375 | -14.4586 | 90.4678 | 149.7688 | 94.5583 | 72 | 56 | 1.8 | 3.7 | 3.1 | 6.8 | 6.8 | 0.32823 | 0.54412 | 12.2992 | 12.8568 | 2.7177 | 59.4823 | 0.21614 | 6.4 | 6.5 | 16.8 | 187 | 364.5 | 390.1419 | -7.0348 | 80.3509 | 288.571 | 94.1782 | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE! | [11 empty] | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE! | [11 empty] | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE! | [11 empty] | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE! | [11 empty] | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE! | [11 empty] | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE!
|  |  |  | Mechanical pressure losses per stage, Ls (psi) | 16 | [5 empty] | 1996-05-14 | 15:00 | 841.1 | 16.5 | 100 | 55 | 1.8 | 0 | 15 | 3.1 |  | 18.1 | 18.1 | 0.82873 | 0 | 16.6205 | 17.3227 | 2.6 | 73.1 | 0.23697 | [11 empty] | 100 | 70 | 2.6 | 11.3 | 6.8 | 18.1 | 18.1 | 0.41278 | 0.62431 | 18.7812 | 19.5747 | 1.4 | 81 | 0.24166 | [10 empty] | 70 | 55 | 1.8 | 3.7 | 3.1 | 6.8 | 6.8 | 0.32823 | 0.54412 | 12.2992 | 12.8188 | 2.8 | 57.9 | 0.2214 | [10 empty] | Alkb, mg/L CaCO3 | 6.9813 | 3.9907 |  | Alkb, mg/L CaCO3 | 4.6491 | 2.7544 | [11 empty] | Alkb, mg/L CaCO3 | 7.2264 | 4.1132 |  | Alkb, mg/L CaCO3 | 5.2555 | 3.0876 | [11 empty] | Alkb, mg/L CaCO3 | 9.729 | 6.3645 |  | Alkb, mg/L CaCO3 | 7.1053 | 4.9737 | [11 empty] | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! | [11 empty] | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! | [11 empty] | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE!
|  |  |  | Net driving pressure required for permeation, NDP (psi) | 62.1691 | [5 empty] | 1996-05-15 | 8:30 | 858.8 | 16.5 | 102 | 56 | 1.9 | 0 | 15.2 | 3.1 |  | 18.3 | 18.3 | 0.8306 | 0 | 16.8421 | 17.5537 | 2.5784 | 74.5216 | 0.23555 | 6.5 | 6.2 | 10.8 |  | 85.5 | 380 | 451.771 | -18.8871 | 87.3684 | 268.6355 | 95.9797 | 102 | 72 | 3.1 | 11.3 | 7 | 18.3 | 18.3 | 0.41941 | 0.61749 | 18.7812 | 19.5747 | 1.3807 | 82.5193 | 0.23721 | 6.2 | 6.2 | 9.1 | 85.5 | 190 | 208.8314 | -9.9113 | 89.3567 | 147.1657 | 93.8165 | 72 | 56 | 1.9 | 3.9 | 3.1 | 7 | 7 | 0.33486 | 0.55714 | 12.964 | 13.5117 | 2.8133 | 59.2867 | 0.2279 | 6.2 | 6.3 | 17.3 | 190 | 380 | 407.2677 | -7.1757 | 79.7661 | 298.6339 | 94.207 | T-Hdb, mg/L CaCO3 | 41.4112 | 27.2056 |  | T-Hdb, mg/L CaCO3 | 30.3333 | 21.3333 | [11 empty] | T-Hdb, mg/L CaCO3 | 28.1698 | 14.5849 |  | T-Hdb, mg/L CaCO3 | 19.5693 | 10.1095 | [11 empty] | T-Hdb, mg/L CaCO3 | 48.1682 | 35.0841 |  | T-Hdb, mg/L CaCO3 | 37.9649 | 29.6754 | [11 empty] | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! | [11 empty] | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! | [11 empty] | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE!
|  |  |  | Flow weighted system pressure losses, Lsys (psi) | 20.5846 | [5 empty] | 1996-05-16 | 16:30 | 869.4 | 16.5 | 97 | 55 | 1.8 | 0 | 15.4 | 3.1 |  | 18.5 | 18.5 | 0.83243 | 0 | 17.0637 | 17.7847 | 2.6 | 71.6 | 0.24839 | [11 empty] | 97 | 70 | 2.8 | 11.4 | 7.1 | 18.5 | 18.5 | 0.42438 | 0.61622 | 18.9474 | 19.7479 | 1.4 | 79.3 | 0.24903 | [10 empty] | 70 | 55 | 1.8 | 4 | 3.1 | 7.1 | 7.1 | 0.33818 | 0.56338 | 13.2964 | 13.8582 | 2.8 | 57.9 | 0.23935 | [10 empty] | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! | [11 empty] | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! | [11 empty] | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! | [11 empty] | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! | [11 empty] | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! | [11 empty] | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE!
|  |  |  | Required influent pressure to the system, PI (psi) | 82.7537 | [5 empty] | 1996-05-17 | 8:00 | 884.8 | 17 | 99 | 56 | 0 | 0 | 15.2 | 3.1 |  | 18.3 | 18.3 | 0.8306 | 0 | 16.8421 | 17.2962 | 2.5594 | 74.9406 | 0.2308 | 6.9 | 6.2 | 9.85 |  | 84 | 360 | 447.5742 | -24.3262 | 88.2738 | 265.7871 | 96.294 | 99 | 72 | 2.2 | 11.2 | 7.1 | 18.3 | 18.3 | 0.42107 | 0.61202 | 18.615 | 19.1168 | 1.3603 | 81.9397 | 0.2333 | 6.2 | 6.3 | 7.95 | 84 | 183.5 | 203.9662 | -11.1532 | 90.5357 | 143.9831 | 94.4785 | 72 | 56 | 0 | 4 | 3.1 | 7.1 | 7.1 | 0.33818 | 0.56338 | 13.2964 | 13.6549 | 2.763 | 61.237 | 0.22298 | 6.3 | 6.3 | 15.55 | 183.5 | 360 | 400.2097 | -11.1694 | 81.4881 | 291.8548 | 94.672 | Notes: | [17 empty] | Notes: | [17 empty] | Notes: | [17 empty] | Notes: | [17 empty] | Notes: | [17 empty] | Notes:
|  |  |  | 3: The osmotic pressure can be estimated from Table 6-5 in Part 3 of the | [6 empty] | 1996-05-17 | 15:30 | 892.2 | 17.2 | 101 | 57 | 2.2 | 0 | 15.2 | 3.1 |  | 18.3 | 18.3 | 0.8306 | 0 | 16.8421 | 17.1942 | 2.6 | 74.2 | 0.23173 | [11 empty] | 101 | 73 | 3.5 | 11.2 | 7.1 | 18.3 | 18.3 | 0.42107 | 0.61202 | 18.615 | 19.0041 | 1.4 | 82.1 | 0.23148 | [10 empty] | 73 | 57 | 2.2 | 4 | 3.1 | 7.1 | 7.1 | 0.33818 | 0.56338 | 13.2964 | 13.5744 | 2.8 | 60 | 0.22624 | [10 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be
|  |  |  | "ICR Manual for Bench- and Pilot-Scale Treatment Studies." | [6 empty] | 1996-05-18 | 16:30 | 915.3 | 17 | 100 | 57 | 2 | 0 | 15.2 | 3.1 |  | 18.3 | 18.3 | 0.8306 | 0 | 16.8421 | 17.2962 | 2.6 | 73.9 | 0.23405 | [11 empty] | 100 | 73 | 3 | 11.1 | 7.2 | 18.3 | 18.3 | 0.42272 | 0.60656 | 18.4488 | 18.9461 | 1.4 | 82.1 | 0.23077 | [10 empty] | 73 | 57 | 2 | 4.1 | 3.1 | 7.2 | 7.2 | 0.3415 | 0.56944 | 13.6288 | 13.9962 | 2.8 | 60.2 | 0.2325 | [10 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs.
[11 empty] | 1996-05-20 | 6:00 | 948.8 | 18 | 99 | 57 | 2 | 0 | 15.2 | 3.1 |  | 18.3 | 18.3 | 0.8306 | 0 | 16.8421 | 16.7924 | 2.6 | 73.4 | 0.22878 | [11 empty] | 99 | 73 | 2.9 | 11.1 | 7.2 | 18.3 | 18.3 | 0.42272 | 0.60656 | 18.4488 | 18.3943 | 1.4 | 81.7 | 0.22514 | [10 empty] | 73 | 57 | 2 | 4.1 | 3.1 | 7.2 | 7.2 | 0.3415 | 0.56944 | 13.6288 | 13.5886 | 2.8 | 60.2 | 0.22572 | [10 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5.
[11 empty] | 1996-05-20 | 14:00 | 962.3 | 18 | 98 | 56 | 1.5 | 0 | 15.2 | 3.1 |  | 18.3 | 18.3 | 0.8306 | 0 | 16.8421 | 16.7924 | 2.6439 | 72.8561 | 0.23049 |  |  | 10.4 |  | 87 | 357.5 | 462.5871 | -29.395 | 88.046 | 274.7935 | 96.2153 | 98 | 72 | 2 | 11.1 | 7.2 | 18.3 | 18.3 | 0.42272 | 0.60656 | 18.4488 | 18.3943 | 1.3866 | 81.6134 | 0.22538 |  |  | 8.7 | 87 | 187 | 207.7125 | -11.0762 | 90 | 147.3562 | 94.0959 | 72 | 56 | 0 | 4.1 | 3.1 | 7.2 | 7.2 | 0.3415 | 0.56944 | 13.6288 | 13.5886 | 2.8333 | 61.1667 | 0.22216 |  |  | 16.45 | 187 | 357.5 | 412.5661 | -15.4031 | 81.092 | 299.7831 | 94.5127 | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters.
[11 empty] | 1996-05-21 | 9:00 | 981.7 | 17.5 | 99 | 57 | 2 | 0 | 15.2 | 3.1 |  | 18.3 | 18.3 | 0.8306 | 0 | 16.8421 | 17.0424 | 2.6 | 73.4 | 0.23219 | [11 empty] | 99 | 73 | 2.1 | 11.2 | 7.1 | 18.3 | 18.3 | 0.42107 | 0.61202 | 18.615 | 18.8364 | 1.4 | 82.5 | 0.22832 | [10 empty] | 73 | 57 | 0 | 4 | 3.1 | 7.1 | 7.1 | 0.33818 | 0.56338 | 13.2964 | 13.4545 | 2.8 | 62.2 | 0.21631 | [10 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design.
[11 empty] | 1996-05-21 | 15:00 | 987.9 | 17.5 | 99 | 56 | 2 | 0 | 15.2 | 3.1 |  | 18.3 | 18.3 | 0.8306 | 0 | 16.8421 | 17.0424 | 2.6 | 72.9 | 0.23378 | [11 empty] | 99 | 71 | 0 | 11.2 | 7.1 | 18.3 | 18.3 | 0.42107 | 0.61202 | 18.615 | 18.8364 | 1.4 | 83.6 | 0.22532 | [10 empty] | 71 | 56 | 0 | 4 | 3.1 | 7.1 | 7.1 | 0.33818 | 0.56338 | 13.2964 | 13.4545 | 2.8 | 60.7 | 0.22166 | [10 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[11 empty] | 1996-05-22 | 8:00 | 1004.1 | 17 | 100 | 58 | 1.8 | 0 | 15.2 | 3.1 |  | 18.3 | 18.3 | 0.8306 | 0 | 16.8421 | 17.2962 | 2.6715 | 74.5285 | 0.23207 | 6.5 | 6 | 10.6 |  | 88 | 372.5 | 467.5097 | -25.506 | 87.9545 | 277.7548 | 96.1837 | 100 | 74 | 2.8 | 11.2 | 7.1 | 18.3 | 18.3 | 0.42107 | 0.61202 | 18.615 | 19.1168 | 1.4185 | 82.7815 | 0.23093 | 6 | 6.3 | 8.7 | 88 | 192.5 | 213.093 | -10.6976 | 90.1136 | 150.5465 | 94.2211 | 74 | 58 | 1.8 | 4 | 3.1 | 7.1 | 7.1 | 0.33818 | 0.56338 | 13.2964 | 13.6549 | 2.8922 | 61.3078 | 0.22273 | 6.3 | 6.4 | 16.7 | 192.5 | 372.5 | 419.3387 | -12.5742 | 81.0227 | 305.9194 | 94.541 | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[11 empty] | 1996-05-22 | 12:00 | 1008.2 | 17.2 | 105 | 62 | 2 | 0 | 16.2 | 2.9 |  | 19.1 | 19.1 | 0.84817 | 0 | 17.9501 | 18.3254 | 2.7 | 78.8 | 0.23256 | [11 empty] | 105 | 77 | 2.9 | 11.8 | 7.3 | 19.1 | 19.1 | 0.43764 | 0.6178 | 19.6122 | 20.0222 | 1.4 | 86.7 | 0.23094 | [10 empty] | 77 | 62 | 2 | 4.4 | 2.9 | 7.3 | 7.3 | 0.33818 | 0.60274 | 14.626 | 14.9318 | 2.8 | 64.7 | 0.23079 | [10 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio.
[11 empty] | 1996-05-22 | 15:00 | 1011.6 | 17.2 | 104 | 62 | 2 | 0 | 16.2 | 2.9 |  | 19.1 | 19.1 | 0.84817 | 0 | 17.9501 | 18.3254 | 2.9643 | 78.0357 | 0.23483 |  |  | 10.35 |  | 88.5 | 407.5 | 525.0621 | -28.8496 | 88.3051 | 306.781 | 96.6263 | 104 | 77 | 2.8 | 11.8 | 7.3 | 19.1 | 19.1 | 0.43764 | 0.6178 | 19.6122 | 20.0222 | 1.4538 | 86.2462 | 0.23215 |  |  | 8.1 | 88.5 | 200.5 | 218.4616 | -8.9584 | 90.8475 | 153.4808 | 94.7225 | 77 | 62 | 2 | 4.4 | 2.9 | 7.3 | 7.3 | 0.33818 | 0.60274 | 14.626 | 14.9318 | 3.242 | 64.258 | 0.23237 |  |  | 16.15 | 200.5 | 407.5 | 480.2034 | -17.8413 | 81.7514 | 340.3517 | 95.2549 | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL.
[11 empty] | 1996-05-23 | 8:30 | 1028.7 | 16.9 | 107 | 64 | 2.5 | 0 | 16.2 | 3 |  | 19.2 | 19.2 | 0.84375 | 0 | 17.9501 | 18.4886 | 2.9249 | 80.0751 | 0.23089 |  |  | 9.95 |  | 89 | 425 | 515.87 | -21.3812 | 88.8202 | 302.435 | 96.71 | 107 | 79 | 3 | 11.75 | 7.45 | 19.2 | 19.2 | 0.44179 | 0.61198 | 19.5291 | 20.115 | 1.4461 | 88.5539 | 0.22715 |  |  | 8.15 | 89 | 195.5 | 216.5151 | -10.7494 | 90.8427 | 152.7576 | 94.6647 | 79 | 64 | 2.5 | 4.45 | 3 | 7.45 | 7.45 | 0.34647 | 0.59732 | 14.7922 | 15.236 | 3.1254 | 65.8746 | 0.23129 |  |  | 16.05 | 195.5 | 425 | 461.6842 | -8.6316 | 81.9663 | 328.5921 | 95.1155 | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[11 empty] | 1996-05-23 | 15:30 | 1035 | 17.1 | 105 | 63 | 2 | 0 | 16.2 | 3 |  | 19.2 | 19.2 | 0.84375 | 0 | 17.9501 | 18.3797 | 2.9 | 79.1 | 0.23236 | [11 empty] | 105 | 77 | 2.5 | 11.8 | 7.4 | 19.2 | 19.2 | 0.44096 | 0.61458 | 19.6122 | 20.0815 | 1.4 | 87.1 | 0.23056 | [10 empty] | 77 | 63 | 2 | 4.4 | 3 | 7.4 | 7.4 | 0.34481 | 0.59459 | 14.626 | 14.976 | 3 | 65 | 0.2304
[11 empty] | 1996-05-24 | 8:00 | 1053 | 17.2 | 106 | 64 | 2.5 | 0 | 16.2 | 3 |  | 19.2 | 19.2 | 0.84375 | 0 | 17.9501 | 18.3254 | 2.9 | 79.6 | 0.23022 | [11 empty] | 106 | 79 | 3 | 11.7 | 7.5 | 19.2 | 19.2 | 0.44262 | 0.60938 | 19.446 | 19.8525 | 1.4 | 88.1 | 0.22534 | [10 empty] | 79 | 64 | 2.5 | 4.5 | 3 | 7.5 | 7.5 | 0.34813 | 0.6 | 14.9584 | 15.2712 | 3 | 66 | 0.23138
[11 empty] | 1996-05-24 | 15:30 | 1059.9 | 17.5 | 104 | 63 | 2 | 0 | 16.2 | 3 |  | 19.2 | 19.2 | 0.84375 | 0 | 17.9501 | 18.1636 | 2.9 | 78.6 | 0.23109 | [11 empty] | 104 | 77 | 2.8 | 11.7 | 7.5 | 19.2 | 19.2 | 0.44262 | 0.60938 | 19.446 | 19.6773 | 1.4 | 86.3 | 0.22801 | [10 empty] | 77 | 63 | 2 | 4.5 | 3 | 7.5 | 7.5 | 0.34813 | 0.6 | 14.9584 | 15.1364 | 3.1 | 64.9 | 0.23323
[11 empty] | 1996-05-28 | 14:00 | 1074.8 | 17.1 | 105 | 66 | 2 | 0 | 16.2 | 3 |  | 19.2 | 19.2 | 0.84375 | 0 | 17.9501 | 18.3797 | 2.9 | 80.6 | 0.22804 |  |  |  |  | 89 | [6 empty] | 105 | 81 | 2.8 | 11.8 | 7.4 | 19.2 | 19.2 | 0.44096 | 0.61458 | 19.6122 | 20.0815 | 1.4 | 88.8 | 0.22614 |  |  |  | 89 | [6 empty] | 81 | 66 | 2 | 4.4 | 3 | 7.4 | 7.4 | 0.34481 | 0.59459 | 14.626 | 14.976 | 3.1 | 68.4 | 0.21895
[11 empty] | 1996-05-29 | 10:00 | 1095.4 | 17.1 | 104 | 66 | 2.2 | 0 | 16.2 | 3 |  | 19.2 | 19.2 | 0.84375 | 0 | 17.9501 | 18.3797 | 2.9 | 79.9 | 0.23003 |  |  | 9.3 |  | 89 | 403 | 519.38 | -28.8784 | 89.5506 | 304.19 | 96.9427 | 104 | 81 | 3 | 11.8 | 7.4 | 19.2 | 19.2 | 0.44096 | 0.61458 | 19.6122 | 20.0815 | 1.4 | 88.1 | 0.22794 |  |  | 7.7 |  | 195 | -12.2784 | 106.2966 | 91.3483 | -6.1392 | 225.4237 | 81 | 66 | 2.2 | 4.4 | 3 | 7.4 | 7.4 | 0.34481 | 0.59459 | 14.626 | 14.976 | 3.1217 | 68.1783 | 0.21966 |  |  | 14.9 | 195 | 403 | 459.1467 | -13.9322 | 83.2584 | 327.0733 | 95.4444
[11 empty] | 1996-05-29 | 16:00 | 1101.6 | 17.5 | 105 | 66 | 2 | 0 | 16.2 | 3 |  | 19.2 | 19.2 | 0.84375 | 0 | 17.9501 | 18.1636 | 2.9304 | 80.5696 | 0.22544 |  |  | 9.8 |  | 89 | 419 | 516.68 | -23.3126 | 88.9888 | 302.84 | 96.764 | 105 | 82 | 2.8 | 11.8 | 7.4 | 19.2 | 19.2 | 0.44096 | 0.61458 | 19.6122 | 19.8454 | 1.4585 | 89.2415 | 0.22238 |  |  | 7.85 | 89 | 197 | 218.4014 | -10.8636 | 91.1798 | 153.7007 | 94.8927 | 82 | 66 | 2 | 4.4 | 3 | 7.4 | 7.4 | 0.34481 | 0.59459 | 14.626 | 14.8 | 3.1495 | 68.8505 | 0.21496 |  |  | 15.3 | 197 | 419 | 463.4933 | -10.6189 | 82.809 | 330.2467 | 95.3671
[11 empty] | 1996-05-30 | 8:00 | 1116.9 | 17.2 | 104 | 66 | 2.1 | 0 | 16.2 | 3 |  | 19.2 | 19.2 | 0.84375 | 0 | 17.9501 | 18.3254 | 2.9 | 80 | 0.22907 | [11 empty] | 104 | 82 | 3 | 11.8 | 7.4 | 19.2 | 19.2 | 0.44096 | 0.61458 | 19.6122 | 20.0222 | 1.4 | 88.6 | 0.22598 | [10 empty] | 82 | 66 | 2.1 | 4.4 | 3 | 7.4 | 7.4 | 0.34481 | 0.59459 | 14.626 | 14.9318 | 3.1 | 68.8 | 0.21703
[11 empty] | 1996-05-30 | 16:00 | 1124.6 | 17.5 | 104 | 70 | 2.5 | 0 | 16.2 | 3 |  | 19.2 | 19.2 | 0.84375 | 0 | 17.9501 | 18.1636 | 2.9 | 81.6 | 0.22259 | [11 empty] | 104 | 79 | 3 | 11.8 | 7.4 | 19.2 | 19.2 | 0.44096 | 0.61458 | 19.6122 | 19.8454 | 1.4 | 87.1 | 0.22785 | [10 empty] | 79 | 70 | 2.5 | 4.4 | 3 | 7.4 | 7.4 | 0.34481 | 0.59459 | 14.626 | 14.8 | 3.1 | 68.9 | 0.2148
[11 empty] | 1996-05-31 | 10:30 | 1136.4 | 17.6 | 104 | 65 | 2.2 | 0 | 16.2 | 3 |  | 19.2 | 19.2 | 0.84375 | 0 | 17.9501 | 18.11 | 2.9249 | 79.3752 | 0.22816 |  |  | 9.95 |  | 89 | 413.5 | 515.87 | -24.757 | 88.8202 | 302.435 | 96.71 | 104 | 79 | 2.9 | 11.7 | 7.5 | 19.2 | 19.2 | 0.44262 | 0.60938 | 19.446 | 19.6192 | 1.4382 | 87.1618 | 0.22509 |  |  | 8.2 | 89 | 198.5 | 215.048 | -8.3365 | 90.7865 | 152.024 | 94.6061 | 79 | 65 | 2.2 | 4.5 | 3 | 7.5 | 7.5 | 0.34813 | 0.6 | 14.9584 | 15.0917 | 3.2034 | 66.5966 | 0.22661 |  |  | 15.45 | 198.5 | 413.5 | 473.075 | -14.4075 | 82.6404 | 335.7875 | 95.3989
[11 empty] | 1996-05-31 | 16:00 | 1141.3 | 17.9 | 102 | 64 | 2.1 | 0 | 16.2 | 3 |  | 19.2 | 19.2 | 0.84375 | 0 | 17.9501 | 17.9501 | 2.886 | 78.014 | 0.23009 |  |  | 11 |  | 89 | 422 | 510.2 | -20.9005 | 87.6404 | 299.6 | 96.3284 | 102 | 79 | 2.9 | 11.7 | 7.5 | 19.2 | 19.2 | 0.44262 | 0.60938 | 19.446 | 19.446 | 1.4196 | 86.1804 | 0.22564 |  |  | 9.25 | 89 | 190 | 213.41 | -12.3211 | 89.6067 | 151.205 | 93.8825 | 79 | 64 | 2.1 | 4.5 | 3 | 7.5 | 7.5 | 0.34813 | 0.6 | 14.9584 | 14.9584 | 3.0371 | 66.3629 | 0.2254 |  |  | 16.45 | 190 | 422 | 450.325 | -6.7121 | 81.5169 | 320.1625 | 94.862
[11 empty] | 1996-06-01 | 13:30 | 1163.1 | 17.5 | 102 | 64 | 2.1 | 0 | 16.2 | 3 |  | 19.2 | 19.2 | 0.84375 | 0 | 17.9501 | 18.1636 | 2.8657 | 78.0344 | 0.23276 |  |  | 10.55 |  | 88 | 419.5 | 506.23 | -20.6746 | 88.0114 | 297.115 | 96.4492 | 102 | 78 | 2.9 | 11.8 | 7.4 | 19.2 | 19.2 | 0.44096 | 0.61458 | 19.6122 | 19.8454 | 1.4298 | 85.6702 | 0.23165 |  |  | 8.45 | 88 | 197.5 | 214.85 | -8.7848 | 90.3977 | 151.425 | 94.4197 | 78 | 64 | 2.1 | 4.4 | 3 | 7.4 | 7.4 | 0.34481 | 0.59459 | 14.626 | 14.8 | 3 | 65.9 | 0.22458
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
Note on CW29: sallge: Only target SDS conditions are available.
Note on DQ29: sallge: Only target SDS conditions are available.
Note on EK29: sallge: Only target SDS conditions are available.