## BW30. 1st Quarter
FIELD-SET 1: 1st QUARTER RBSMT RESULTS (FILE: rbsmt-2.xls)
Field 1-1: PWS And Treatment Plant Data |  | Field 1-2: Manufacturer Reported Membrane Characteristics1 |  | Field 1-3: RBSMT Design Parameters | [8 empty] | Field 1-4: Foulants And Fouling Indices1 |  | Field 1-5: Pretreatment Used Prior To Membranes1 |  |  | Field 1-6: Feed Water Quality After Pretreatment | [5 empty] | Field 1-7: Membrane Setting Data | [20 empty] | Field 1-8: Membrane Performance Data During Operation With The Test Water | [16 empty] | Field 1-8: Membrane Performance Data During Operation With The Test Water (continued) | [19 empty] | Field 1-8: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 1-9: Permeate And Concentrate Water Quality For Run 1 | [11 empty] | Field 1-10: Permeate And Concentrate Water Quality For Run 2 | [8 empty] | Field 1-11: Permeate And Concentrate Water Quality For Run 3 | [8 empty] | Field 1-12: Permeate And Concentrate Water Quality For Run 4 | [8 empty] | Field 1-13: Blending Calculations For Stage 1 D-DBP MCLs |  |  |  |  | Field 1-14: Blending Calculations For Proposed Stage 2 D-DBP MCLs |  |  |  |  | Field 1-15: Membrane Cost Parameters
|  | General Information |  | Input Design Parameters | [8 empty] | Parameters Evaluated Prior to Pretreatment | [80 empty] | Operating Parameters During Sample Collection | [11 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Feed and Permeate Water Quality Parameters |  |  |  |  | Feed and Permeate Water Quality Parameters |  |  |  |  | General Cost Parameters
PWS Name | Water District No. 1 of Johnson County, Kansas | Membrane manufacturer | Dow-Filmtec | [5 empty] | Active membrane area in bench-scale cell, Acell (ft2) | 0.167 |  |  | Alkalinity (mg/L as CaCO3) | 151 | Process | Description | Scale | Parameter | Units | CF-1 | CF-2 | Average | RPD |  |  |  | Average TDS rejection (decimal fraction) | 0.98 | [5 empty] | TDS concentration of setting solution (mg/L) | 2000 | [12 empty] | Average bulk TDS rejection (decimal fraction) | 0.97109 | [45 empty] | Recovery during sample collection (decimal) | 0.69 | [10 empty] | Recovery during sample collection (decimal) | 0.87 | [7 empty] | Recovery during sample collection (decimal) | 0.5 | [7 empty] | Recovery during sample collection (decimal) | 0.31 | [8 empty] | RUN ID # |  |  |  |  | RUN ID # |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | KS200910 | Membrane trade name | BW30-XLE | [5 empty] | Active width of membrane in the bench-scale cell, wcell (ft) | 0.333 |  |  | Calcium Hardness (mg/L as CaCO3) | 176 | Presedimentation | 3 Basins | Full-scale | Sampling date | MM/DD/YY | 1998-05-06 | 1998-05-13 | --- | --- | [71 empty] | Feed flow rate during sample collection (mL/min) | 8.5 | [10 empty] | Feed flow rate during sample collection (mL/min) | 6.07 | [7 empty] | Feed flow rate during sample collection (mL/min) | 11.4 | [7 empty] | Feed flow rate during sample collection (mL/min) | 19.4 | [6 empty] | Parameter | 1 | 2 | 3 | 4 | Parameter | 1 | 2 | 3 | 4 | Capital Recovery Interest Rate (%) | 5
Water Industry Data Base Number (optional) | NA | Molecular weight cutoff (Daltons) | 100 | [5 empty] | Average yearly temperature of feed water, TavgoC (oC) | 14 |  |  | LSI | 0.61 | Softening | Lime, 200 mg/L as Ca(OH)2 | Bench-scale | Sampling time | hh:mm | 11:30 | 7:25 | --- | --- | Date | Time | Setting time | Influent | PI | PC | QI | Qp | QW | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) | Date | Time | Operation time | Influent | PI | PC | QI | Qp | QW | Cleaning Event | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1) | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Influent flow rate during sample collection (mL/min) | 370 | [10 empty] | Influent flow rate during sample collection (mL/min) | 370 | [7 empty] | Influent flow rate during sample collection (mL/min) | 370 | [7 empty] | Influent flow rate during sample collection (mL/min) | 370 | [6 empty] | SDS-THM4F, ug/L | 99.995 | 99.995 | 99.995 | 99.995 | SDS-THM4F, ug/L | 99.995 | 99.995 | 99.995 | 99.995 | Capital Recovery Period (years) | 20
|  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide | [5 empty] | Approximate feed water TDS, TDSF (mg/L) | 322 |  |  | Dissolved iron (mg/L) |  | Coagulation | Alum: Al2(SO4)3.14H2O, 15 mg/L | Bench-scale | Operation time | hh.hh | 0 | 163 | --- | --- | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | Indicate with "X" | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) | [39 empty] | SDS-THM4p, ug/L | 2.0275 | 5.33 | 0 | 1.46 | SDS-THM4p, ug/L | 2.0275 | 5.33 | 0 | 1.46 | Overhead & Profit Factor (% of construction costs) | 15
Official ICR Contact Person |  | Membrane construction (e.g., thin-film composite) | Thin Film | [5 empty] | Manufacturer reported TDS rejection, RejTDS (decimal fraction) | 0.98 |  |  | Total iron (mg/L) |  | Sedimentation | Gravity settling in test drums | Bench-scale | pH | --- | 8.57 | 8.67 | 8.62 | 1.1601 | 1998-05-04 | 12:30 | 0 | [6 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-06 | 12:00 | 0 | 24 | 60 | 61 | 360 | 7.2 | 3 |  | 10.2 | 0.24473 | 0.70588 | 34.2941 | 16.4008 | 12.2037 | 1025.0571 | 29.0596 | 1005.1371 | 9.8604 | 50.6396 | 0.24099 | [27 empty] | Permeate and Concentrate Water Quality | [11 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | SDS-HAA5F, ug/L | 25.06 | 25.06 | 25.06 | 25.06 | SDS-HAA5F, ug/L | 25.06 | 25.06 | 25.06 | 25.06 | Special Sitework Factor (% of construction costs) | 0
Mailing Address |  | Membrane hydrophobicity | Hydrophobic | [5 empty] | Temperature normalized MTCW (gfd/psi) | 0.16688 |  |  | Dissolved aluminum (mg/L) |  | Recarbonation | CO2 gas added to pH 9.4 | Bench-scale | Temperature | oC | 21.5 | 23 | 22.25 | 6.7416 | 1998-05-04 | 13:00 | 0.5 | 22.2 | 75 | 75 | 360 | 6.9 | 42.8 | 49.7 | 0.24473 | 0.13883 | 6.2435 | 15.7174 | 12.3344 | 2315.1056 | 45.4321 | 2271.6035 | 22.4792 | 52.5208 | 0.23485 | 1998-05-06 | 15:00 | 3 | 25.6 | 60 | 61 | 360 | 7.1 | 3.2 |  | 10.3 | 0.24473 | 0.68932 | 33.9515 | 16.173 | 11.4783 | 975.0878 | 27.6506 | 956.4022 | 9.3809 | 51.1191 | 0.22454 | 7.97 | 8.55 | 8.42 | 40.9 | 322 | 882 | 945.6906 | -7.2212 | 87.2981 | 936.7684 | 95.6339 | 0.006 | 0.053 | 0.167 | 0.15567 | 6.7833 | 88.5714 | 0.1542 | 96.1088 | [8 empty] | Parameter | Units | Cp-1 | Cp-1 (dup) | Average | RPD | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | SDS-HAA5p, ug/L | 0 | 0 | 0 | 0 | SDS-HAA5p, ug/L | 0 | 0 | 0 | 0 | Construction Contingencies (% of construction costs) | 15
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Slightly Negative | [9 empty] | Total aluminum (mg/L) |  | Cartridge filtration | 1 um size exclusion | Bench-scale | Alkalinity | mg/L as CaCO3 | 55.5 | 54 | 54.75 | 2.7397 | 1998-05-04 | 16:00 | 3.5 | 25.2 | 75 | 75 | 360 | 7.1 | 39.6 | 46.7 | 0.24473 | 0.15203 | 6.7088 | 16.173 | 11.6149 | 2350.3209 | 46.0975 | 2304.8765 | 22.815 | 52.185 | 0.22257 | 1998-05-06 | 17:00 | 5 | 24.7 | 60 | 61 | 360 | 7.2 | 2.7 |  | 9.9 | 0.24473 | 0.72727 | 35.3636 | 16.4008 | 11.9538 | 1097.6841 | 31.1185 | 1076.3527 | 10.559 | 49.941 | 0.23936 | 7.73 |  |  | 40.8 |  |  | 1071.8667 |  | 87.3292 | 1061.556 | 96.1566 | 0.003 |  |  | 0.1845 |  | 94.2857 | 0.18268 | 98.3578 | [8 empty] | Sampling date | MM/DD/YY | 1998-05-09 | 1998-05-09 | --- | --- | 1998-05-09 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-05-10 | 1998-05-10 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-05-11 | 1998-05-11 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-05-12 | 1998-05-12 | --- | --- | --- | --- | --- | SDS-TOXF, ug Cl- /L | 180 | 180 | 180 | 180 | SDS-TOXF, ug Cl- /L | 180 | 180 | 180 | 180 | Engineering Fee Factor (% of construction costs) | 15
Phone Number |  |  |  | Experimental Design1,2 | [8 empty] | Fluoride (mg/L) |  | Antiscalant | 4 mg/L Hypersperse 400UL | Bench-scale | Total dissolved solids | mg/L | 322 | 322 | 322 | 0 | 1998-05-04 | 18:00 | 5.5 | 25.1 | 75 | 75 | 360 | 7.5 | 39.8 | 47.3 | 0.24473 | 0.15856 | 6.611 | 17.0842 | 12.3055 | 2368.1416 | 46.3954 | 2319.7719 | 22.9756 | 52.0244 | 0.23653 | 1998-05-07 | 7:00 | 19 | 23.2 | 60 | 61 | 360 | 6.5 | 3.1 |  | 9.6 | 0.24473 | 0.67708 | 36.5 | 14.8063 | 11.2809 | 941.112 | 26.7312 | 924.6023 | 9.0613 | 51.4387 | 0.21931 | 7.69 |  |  | 32.1 |  |  | 929.8548 |  | 90.0311 | 921.7501 | 96.5175 | 0.004 |  |  | 0.15419 |  | 92.381 | 0.15284 | 97.3828 | [8 empty] | Sampling time | hh:mm | 17:00 | 17:00 | --- | --- | 17:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 16:00 | 16:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 16:00 | 16:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 16:30 | 16:30 | --- | --- | --- | --- | --- | SDS-TOXp, ug Cl- /L | #DIV/0! | BMRL | BMRL | BMRL | SDS-TOXp, ug Cl- /L | #DIV/0! | BMRL | BMRL | BMRL | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920
FAX Number |  | Design Parameters |  | ID# | Recovery | FW-design | Dp | PI | QI-cell | Qp | QF | QW | Phosphate (mg/L) |  |  |  |  | Total hardness | mg/L as CaCO3 | 118.4 | 116.1 | 117.25 | 1.9616 | 1998-05-05 | 7:00 | 18.5 | 23.7 | 75 | 75 | 360 | 6.9 | 39 | 45.9 | 0.24473 | 0.15033 | 6.8431 | 15.7174 | 11.7994 | 2345.7019 | 46.0325 | 2301.6249 | 22.7763 | 52.2237 | 0.22594 | 1998-05-07 | 9:00 | 21 | 23.3 | 61 | 62 | 360 | 6.4 | 2.9 |  | 9.3 | 0.24473 | 0.68817 | 37.7097 | 14.5785 | 11.0746 | 971.6939 | 27.6074 | 954.9102 | 9.3569 | 52.1431 | 0.21239 | [27 empty] | Operation time | hh.hh | 77 | 77 | --- | --- | 77 | --- | --- | --- | --- | --- | Operation time | hh.hh | 100 | 100 | --- | --- | --- | --- | --- | Operation time | hh.hh | 124 | 124 | --- | --- | --- | --- | --- | Cumulative time | hr | 148.5 | 148.5 | --- | --- | --- | --- | --- | SDS-CDF, mg/L | 3.22 | 3.22 | 3.22 | 3.22 | SDS-CDF, mg/L | 3.22 | 3.22 | 3.22 | 3.22 | 1998 Producers Price Index (PPI base year 1967 = 100) | 370
E-Mail Address (optional) |  | Design flux, FW (gfd) | 30(15 ave) |  | (decimal) | (gfd) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | Sulfate (mg/L) |  |  |  |  | Calcium hardness | mg/L as CaCO3 | 99.1 | 95.6 | 97.35 | 3.5953 | 1998-05-05 | 11:00 | 22.5 | 24 | 75 | 75 | 360 | 6.7 | 38.9 | 45.6 | 0.24473 | 0.14693 | 6.8947 | 15.2619 | 11.3563 | 2336.571 | 45.8788 | 2293.9387 | 22.6938 | 52.3062 | 0.21711 | 1998-05-07 | 11:00 | 23 | 23.1 | 61 | 62 | 360 | 6.5 | 2.9 |  | 9.4 | 0.24473 | 0.69149 | 37.2979 | 14.8063 | 11.3143 | 981.2538 | 27.8714 | 964.0399 | 9.4478 | 52.0522 | 0.21736 | 7.2 | 8.22 | 8.14 | 33.1 | 316 | 867 | 969.5345 | -11.8264 | 89.7205 | 961.0806 | 96.556 | 0.004 | 0.052 | 0.166 | 0.16121 | 2.8874 | 92.381 | 0.15979 | 97.4967 | [8 empty] | pH | --- | 7.04 | 7.01 | 7.025 | 0.42705 | 8.44 | --- | --- | --- | --- | --- | pH | --- | 6.99 | 8.35 | --- | --- | --- | --- | --- | pH | --- | 6.59 | 8.01 | --- | --- | --- | --- | --- | pH | --- | 6.53 | 8.32 | --- | --- | --- | --- | --- | SDS-CDp, mg/L | 0.2 | 0.59 | 0.03 | 0.12 | SDS-CDp, mg/L | 0.2 | 0.59 | 0.03 | 0.12 | Labor Rate + Fringe ($/work-hour) | 17
|  | Net driving pressure at the design flux, NDP (psi) | 130 | 1 | 0.7 | 15 | 10.5831 | 100.4684 | 335.6684 | 6.5843 | 9.4062 | 2.8219 | Calcium (mg/L) | 71 |  |  |  | Turbidity | ntu | 0.17 | 0.15 | 0.16 | 12.5 | 1998-05-05 | 15:00 | 26.5 | 24.4 | 75 | 76 | 360 | 6.8 | 39.1 | 45.9 | 0.24473 | 0.14815 | 6.8431 | 15.4897 | 11.3903 | 2339.8382 | 45.9302 | 2296.5089 | 22.7224 | 52.7776 | 0.21582 | 1998-05-07 | 13:00 | 25 | 24.4 | 61 | 62 | 360 | 6.6 | 2.9 |  | 9.5 | 0.24473 | 0.69474 | 36.8947 | 15.0341 | 11.0553 | 990.7968 | 28.1347 | 973.148 | 9.5384 | 51.9616 | 0.21276 | [27 empty] | Temperature | oC | 19 | 19 | 19 | 0 | 19 | --- | --- | --- | --- | --- | Temperature | oC | 21 | 21 | --- | --- | --- | --- | --- | Temperature | oC | 23 | 22 | --- | --- | --- | --- | --- | Temperature | oC | 21 | 21 | --- | --- | --- | --- | --- | TOCF, mg/L | 3.15 | 3.15 | 3.15 | 3.15 | TOCF, mg/L | 3.15 | 3.15 | 3.15 | 3.15 | Labor Overhead Factor (% of labor) | 42
Technical ICR Contact Person |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.231 | 2 | 0.9 | 15 | 31.6204 | 121.5057 | 335.6684 | 6.5843 | 7.3159 | 0.73159 | Barium (mg/L) |  |  |  |  | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! | 1998-05-05 | 17:00 | 28.5 | 25.4 | 76 | 76 | 360 | 6.9 | 40 | 46.9 | 0.24473 | 0.14712 | 6.6759 | 15.7174 | 11.2212 | 2337.0886 | 45.8635 | 2293.1734 | 22.6927 | 53.3073 | 0.2105 | 1998-05-07 | 15:00 | 27 | 24.8 | 61 | 62 | 360 | 6.6 | 3 |  | 9.6 | 0.24473 | 0.6875 | 36.5 | 15.0341 | 10.9253 | 969.8144 | 27.5389 | 952.5394 | 9.3364 | 52.1636 | 0.20944 | [27 empty] | Alkalinity | mg/L as CaCO3 | 5 | 6 | 5.5 | 18.1818 | 161.5 | 164.371 | -1.7777 | 89.9543 | 163.1118 | 96.6281 | Alkalinity | mg/L as CaCO3 | 7.5 | 353 | 370.9615 | -5.0883 | 86.3014 | 368.3677 | 97.964 | Alkalinity | mg/L as CaCO3 | 5 | 108.5 | 104.5 | 3.6866 | 90.8676 | 103.7336 | 95.18 | Alkalinity | mg/L as CaCO3 | 2 | 58.5 | 78.4493 | -34.1013 | 96.347 | 77.828 | 97.4302 | TOCp, mg/L | #DIV/0! | BMRL | BMRL | BMRL | TOCp, mg/L | #DIV/0! | BMRL | BMRL | BMRL | Electric Rate ($/kW-h) | 0.06
Mailing Address |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | 3 | 0.5 | 15 | 6.3756 | 96.2609 | 335.6684 | 6.5843 | 13.1686 | 6.5843 | Strontium (mg/L) |  |  |  |  | Total organic carbon | mg/L | 3.2 | 3.1 | 3.15 | 3.1746 | 1998-05-06 | 7:30 | 43 | 24.2 | 76 | 76 | 360 | 6.9 | 39.2 | 46.1 | 0.24473 | 0.14967 | 6.8091 | 15.7174 | 11.6263 | 2343.9442 | 45.998 | 2299.9003 | 22.7592 | 53.2408 | 0.21837 | 1998-05-07 | 17:00 | 29 | 24.5 | 61 | 62 | 360 | 6.7 | 3 |  | 9.7 | 0.24473 | 0.69072 | 36.1134 | 15.2619 | 11.1897 | 979.0605 | 27.7938 | 961.3564 | 9.4241 | 52.0759 | 0.21487 | 6.74 |  |  | 31.6 |  |  | 970.56 |  | 90.1863 | 961.8225 | 96.7146 | 0.004 |  |  | 0.16082 |  | 92.381 | 0.15936 | 97.4899 | [8 empty] | Total dissolved solids | mg/L | 27.3 | 27.6 | 27.45 | 1.0929 | 863 | 977.6113 | -13.2806 | 91.4752 | 970.0806 | 97.1703 | Total dissolved solids | mg/L | 52.4 | 1556 | 2126.2462 | -36.6482 | 83.7267 | 2111.4465 | 97.5183 | Total dissolved solids | mg/L | 17.3 | 601 | 626.7 | -4.2762 | 94.6273 | 622.006 | 97.2187 | Total dissolved solids | mg/L | 11.8 | 450 | 461.3652 | -2.5256 | 96.3354 | 457.7116 | 97.422 | UV254 F, cm-1 | 0.0525 | 0.0525 | 0.0525 | 0.0525 | UV254 F, cm-1 | 0.0525 | 0.0525 | 0.0525 | 0.0525 | Fuel Oil Rate ($/gal) | NA
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 400 | 4 | 0.3 | 15 | 4.5724 | 94.4577 | 335.6684 | 6.5843 | 21.9477 | 15.3634 | Reactive silica (mg/L as SiO2) |  |  |  |  | UV254 | cm-1 | 0.052 | 0.053 | 0.0525 | 1.9048 | 1998-05-06 | 11:00 | 46.5 | 24 | 76 | 76 | 360 | 6.8 | 40 | 46.8 | 0.24473 | 0.1453 | 6.6923 | 15.4897 | 11.5258 | 2332.2173 | 45.7806 | 2289.0291 | 22.6484 | 53.3516 | 0.21603 | 1998-05-08 | 7:00 | 43 | 23 | 63 | 64 | 360 | 6.2 | 3 |  | 9.2 | 0.24473 | 0.67391 | 38.1304 | 14.1229 | 10.824 | 932.6724 | 26.5133 | 917.0664 | 8.9836 | 54.5164 | 0.19855 | 7.82 |  |  | 28.2 |  |  | 929.1867 |  | 91.2422 | 921.4282 | 96.9395 | 0.001 |  |  | 0.15893 |  | 98.0952 | 0.15757 | 99.3654 | [8 empty] | Total hardness | mg/L as CaCO3 | 1.8 | 6 | 3.9 | 107.6923 | 379.2 | 369.5452 | 2.5461 | 96.6738 | 366.6472 | 98.9363 | Total hardness | mg/L as CaCO3 | 8.7 | 850.5 | 843.7 | 0.79953 | 92.58 | 837.7411 | 98.9615 | Total hardness | mg/L as CaCO3 | 0.8 | 248.1 | 233.7 | 5.8041 | 99.3177 | 231.906 | 99.655 | Total hardness | mg/L as CaCO3 | 0.7 | 167.9 | 169.613 | -1.0203 | 99.403 | 168.2403 | 99.5839 | UV254 p, cm-1 | 0.002 | 0.003 | 0.002 | 0.004 | UV254 p, cm-1 | 0.002 | 0.003 | 0.002 | 0.004 | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Purchase price for an equivalent 8" x 40 " element ($) | 700 | 1: For experimental matrix see Table 4-2 in Part 3 of the ICR Treatment Studies Manual. | [8 empty] | Turbidity (ntu) | 5.8 |  |  |  | SUVA | L/(mg*m) | 1.625 | 1.7097 | 1.6673 | 5.0786 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-08 | 9:00 | 45 | 22.2 | 64 | 64 | 360 | 6.3 | 2.7 |  | 9 | 0.24473 | 0.7 | 39 | 14.3507 | 11.2618 | 1006.5846 | 28.6066 | 989.47 | 9.6942 | 54.3058 | 0.20738 | [27 empty] | Calcium hardness | mg/L as CaCO3 | 1.8 | 6 | 3.9 | 107.6923 | 322.4 | 305.3516 | 5.288 | 95.9938 | 302.9624 | 98.7127 | Calcium hardness | mg/L as CaCO3 | 8.2 | 721.6 | 693.9692 | 3.8291 | 91.5768 | 689.0753 | 98.81 | Calcium hardness | mg/L as CaCO3 | 0.8 | 207.3 | 193.9 | 6.4641 | 99.1782 | 192.4126 | 99.5842 | Calcium hardness | mg/L as CaCO3 | 0.6 | 140.3 | 140.8174 | -0.36877 | 99.3837 | 139.6778 | 99.5704 | BromideF, ug/L | 113.5 | 113.5 | 113.5 | 113.5 | BromideF, ug/L | 113.5 | 113.5 | 113.5 | 113.5 | Current Process Water Rate ($/1000 gal) | 0.375
FAX Number |  | Maximum flow rate to the 8" x 40" element, QI, max (gpm) | 70 | 2: Flow rates and pressures may need to be adjusted in order to obtain the desired operating conditions. | [8 empty] | SDI |  |  |  |  | Bromide | mg/L | 130 | 97 | 113.5 | 29.0749 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-08 | 11:00 | 47 | 23 | 64 | 64 | 360 | 6.2 | 2.7 |  | 8.9 | 0.24473 | 0.69663 | 39.4494 | 14.1229 | 10.824 | 996.3671 | 28.324 | 979.6952 | 9.5971 | 54.4029 | 0.19896 | 7.06 | 8.04 | 8 | 29.4 | 321 | 885 | 993.8963 | -12.3047 | 90.8696 | 985.5909 | 97.017 | 0 | 0.051 | 0.163 |  | #VALUE! | [11 empty] | Turbidity | ntu | 0.1 | 0.1 | 0.1 | 0 | 0.21 | 0.29355 | -39.7849 | 37.5 | 0.29201 | 65.7551 | Turbidity | ntu | 0.11 | 0.29 | 0.49462 | -70.557 | 31.25 | 0.49187 | 77.6364 | Turbidity | ntu | 0.1 | 0.18 | 0.22 | -22.2222 | 37.5 | 0.21908 | 54.3537 | Turbidity | ntu | 0.12 | 0.15 | 0.17797 | -18.6473 | 25 | 0.1775 | 32.3943 | Bromidep, ug/L | #DIV/0! | 33 | BMRL | BMRL | Bromidep, ug/L | #DIV/0! | 33 | BMRL | BMRL | Modifications to Existing Plant (% of construction costs) | 46
E-Mail Address (optional) |  | Minimum flow rate to the 8" x 40" element, QI, min (gpm) | 18.8 | [9 empty] | MFI |  |  |  |  | SDS-Cl2 dose | mg/L | 4.8 | 4 | 4.4 | 18.1818 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-08 | 13:00 | 49 | 23.7 | 62 | 63 | 370 | 6.2 | 2.7 |  | 8.9 | 0.25153 | 0.69663 | 40.573 | 14.1229 | 10.6024 | 996.339 | 28.3362 | 980.1184 | 9.5989 | 52.9011 | 0.20042 | [27 empty] | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! | BMRL | #DIV/0! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | BMRL | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | BMRL | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | BMRL | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | AlkF, mg/L CaCO3 | 54.75 | 54.75 | 54.75 | 54.75 | AlkF, mg/L CaCO3 | 54.75 | 54.75 | 54.75 | 54.75
|  | Total width of all membrane envelopes in the 8" x 40" element, w (ft) | 70.6 | [9 empty] | MPFI |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | SDS-Free Cl2 residual | mg/L | 1.36 | 1 | 1.18 | 30.5085 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-08 | 15:00 | 51 | 24.2 | 62 | 63 | 370 | 6.3 | 2.6 |  | 8.9 | 0.25153 | 0.70787 | 40.573 | 14.3507 | 10.6153 | 1031.1873 | 29.3195 | 1014.1285 | 9.9334 | 52.5666 | 0.20194 | [27 empty] | Total organic carbon | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | 9.7 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L | BMRL | 21 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 6.2 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 4.4 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkp, mg/L CaCO3 | 5.5 | 7.5 | 5 | 2 | Alkp, mg/L CaCO3 | 5.5 | 7.5 | 5 | 2
Plant Name | Facility 1 | Feed spacer thickness in the 8" x 40" element, T (ft) | 0.0026 | [9 empty] | Bromide (mg/L) | 95 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | SDS-Cl2 demand | mg/L | 3.44 | 3 | 3.22 | 13.6646 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-08 | 17:00 | 53 | 24.7 | 62 | 62 | 370 | 6.4 | 2.7 |  | 9.1 | 0.25153 | 0.7033 | 39.6593 | 14.5785 | 10.6256 | 1016.7523 | 28.9014 | 999.6652 | 9.7931 | 52.2069 | 0.20353 | 6.69 |  |  | 31.7 |  |  | 1010.1185 |  | 90.1553 | 1001.6565 | 96.8352 | 0 | [15 empty] | UV254 | cm-1 | 0.002 | 0.002 | 0.002 | 0 | 0.166 | 0.1649 | 0.66071 | 96.1905 | 0.16361 | 98.7776 | UV254 | cm-1 | 0.003 | 0.359 | 0.38377 | -6.8995 | 94.2857 | 0.38105 | 99.2127 | UV254 | cm-1 | 0.002 | 0.107 | 0.103 | 3.7383 | 96.1905 | 0.10222 | 98.0435 | UV254 | cm-1 | 0.004 | 0.077 | 0.07429 | 3.5197 | 92.381 | 0.073719 | 94.574 | T-HdF, mg/L CaCO3 | 117.25 | 117.25 | 117.25 | 117.25 | T-HdF, mg/L CaCO3 | 117.25 | 117.25 | 117.25 | 117.25
Treatment Plant Category | CS/SOFT | [11 empty] | TOC (mg/L) | 4.8 | is to list the pretreatment processes used in this particular RBSMT run. |  |  | SDS-Chlorination temp. | oC | 13 | 13 | 13 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-09 | 7:00 | 67 | 22.2 | 62 | 63 | 370 | 6 | 2.5 |  | 8.5 | 0.25153 | 0.70588 | 42.5294 | 13.6673 | 10.7255 | 1024.8122 | 29.1616 | 1008.6665 | 9.8758 | 52.6242 | 0.20381 | 6.67 |  |  | 27.8 |  |  | 1028.08 |  | 91.3665 | 1019.9696 | 97.2744 | 0.001 |  |  | 0.1761 |  | 98.0952 | 0.17468 | 99.4275 | [8 empty] | SUVA | L/(mg*m) | NR | NR | #DIV/0! | #VALUE! | 1.7113 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 1.7095 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 1.7258 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 1.75 | --- | --- | --- | --- | --- | T-Hdp, mg/L CaCO3 | 3.9 | 8.7 | 0.8 | 0.7 | T-Hdp, mg/L CaCO3 | 3.9 | 8.7 | 0.8 | 0.7
Process Train Name | Coagulation/Sedimentation/Softening | Additional Information | [10 empty] | pH | 7.99 |  |  |  | SDS-Chlorination pH | --- | 9.5 | 9.48 | 9.49 | 0.21075 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-09 | 9:00 | 69 | 22 | 62 | 63 | 370 | 5.9 | 2.7 |  | 8.6 | 0.25153 | 0.68605 | 42.0233 | 13.4396 | 10.6093 | 965.5736 | 27.4833 | 950.6149 | 9.3061 | 53.1939 | 0.19945 | [27 empty] | Bromide | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | Bromide | mg/L | 33 | --- | 652.2308 | --- | 70.9251 | 647.8117 | 94.9059 | Bromide | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Bromide | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Ca-HdF, mg/L CaCO3 | 97.35 | 97.35 | 97.35 | 97.35 | Ca-HdF, mg/L CaCO3 | 97.35 | 97.35 | 97.35 | 97.35
ICR Treatment Plant Identification Number | 381 | Design cross-flow velocity (fps) | [10 empty] | Total Hardness (mg/L as CaCO3) | 239 |  |  |  | SDS-Incubation time | hours | 42 | 42 | 42 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-09 | 11:00 | 71 | 22.2 | 63 | 63 | 370 | 5.8 | 2.6 |  | 8.4 | 0.25153 | 0.69048 | 43.0476 | 13.2118 | 10.368 | 978.1817 | 27.8496 | 963.2846 | 9.4288 | 53.5712 | 0.19354 | 6.63 | 7.83 | 8.03 | 27.7 | 321 | 879 | 978.5154 | -11.3214 | 91.3975 | 971.063 | 97.1475 | 0.001 | 0.051 | 0.162 | 0.16738 | -3.3238 | 98.0952 | 0.16608 | 99.3979 | [8 empty] | SDS-Cl2 dose | mg/L | 1.17 | 1.6 | 1.385 | 31.0469 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1.6 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1.6 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1.17 | --- | --- | --- | --- | --- | --- | Ca-Hdp, mg/L CaCO3 | 3.9 | 8.2 | 0.8 | 0.6 | Ca-Hdp, mg/L CaCO3 | 3.9 | 8.2 | 0.8 | 0.6
PWSID Number of Plant (if assigned) | KS200910 | Required influent flow to permeate flow rate ratio, QI:Qp | 6.7 | [9 empty] | UV254 | 0.117 |  |  |  | SDS-TOX | mg Cl- /L | 210 | 150 | 180 | 33.3333 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-09 | 13:00 | 73 | 23.9 | 63 | 63 | 370 | 5.8 | 2.7 |  | 8.5 | 0.25153 | 0.68235 | 42.5294 | 13.2118 | 9.8599 | 955.2794 | 27.1975 | 940.7311 | 9.2081 | 53.7919 | 0.1833 | [27 empty] | SDS-Free Cl2 residual | mg/L | 0.85 | 1.52 | 1.185 | 56.5401 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.01 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.57 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.05 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 0.1 | Maximum element recovery (%) | 15 | [9 empty] | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | SDS-CHCl3 | mg/L | 59.4 | 41.8 | 50.6 | 34.7826 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-09 | 15:00 | 75 | 23.4 | 63 | 63 | 370 | 5.8 | 2.5 |  | 8.3 | 0.25153 | 0.6988 | 43.5783 | 13.2118 | 10.0067 | 1002.8027 | 28.5505 | 987.5307 | 9.6662 | 53.3338 | 0.18762 | [27 empty] | SDS-Cl2 demand | mg/L | 0.32 | 0.08 | 0.2 | 120 | --- | 9.9419 | --- | 93.7888 | 9.8647 | 97.9726 | SDS-Cl2 demand | mg/L | 0.59 | --- | 20.8208 | --- | 81.677 | 20.6764 | 97.1465 | SDS-Cl2 demand | mg/L | 0.03 | --- | 6.41 | --- | 99.0683 | 6.3609 | 99.5284 | SDS-Cl2 demand | mg/L | 0.12 | --- | 4.6128 | --- | 96.2733 | 4.5762 | 97.3778 | Blended Water Quality if THM4 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if THM4 Controls the Blend Ratio
Historical Average Water Temperature (oC) | 14 | Variability of design flux (%) | 15 | [9 empty] | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | SDS-BDCM | mg/L | 31.4 | 25.6 | 28.5 | 20.3509 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-09 | 17:00 | 77 | 23.4 | 63 | 63 | 370 | 5.9 | 2.6 |  | 8.5 | 0.25153 | 0.69412 | 42.5294 | 13.4396 | 10.1792 | 988.8247 | 28.1451 | 973.5057 | 9.5302 | 53.4698 | 0.19037 | 6.45 |  |  | 28.7 |  |  | 987.5654 |  | 91.087 | 979.9204 | 97.0712 | 0.001 |  |  | 0.16937 |  | 98.0952 | 0.16802 | 99.4048 | [8 empty] | SDS-Chlorination temp. | oC | 13 | 13 | 13 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 13 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 13 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 13 | --- | --- | --- | --- | --- | --- | Qp/QT (THM4), % | 28.5758 | 29.5727 | 27.9964 | 28.4112 | Qp/QT (THM4), % | 65.3227 | 67.6015 | 63.9982 | 64.9465
State Approved Plant Capacity (MGD) | 55 | Rejection of reference solute and conditions of test | 2000 ppm | [14 empty] | SDS-DBCM | mg/L | 18.1 | 16.6 | 17.35 | 8.6455 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-10 | 11:30 | 95.5 | 22.3 | 63 | 63 | 370 | 5.3 | 2.5 |  | 7.8 | 0.25153 | 0.67949 | 46.4359 | 12.0728 | 9.4463 | 947.3817 | 27.0086 | 934.198 | 9.1378 | 53.8622 | 0.17538 | [27 empty] | SDS-Chlorination pH | --- | 9.49 | 9.58 | 9.535 | 0.94389 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 9.53 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 9.48 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 9.48 | --- | --- | --- | --- | --- | --- | SDS-THM4b, ug/L | 72 | 72 | 72 | 72 | SDS-THM4b, ug/L | 36 | 36 | 36 | 36
|  | (e.g., solute type and concentration) | NaCl | [14 empty] | SDS-CHBr3 | mg/L | 3.6 | 3.49 | 3.545 | 3.103 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-10 | 12:00 | 96 | 22.9 | 70 | 71 | 370 | 5.7 | 0.8 |  | 6.5 | 0.25153 | 0.87692 | 55.9231 | 12.984 | 9.9806 | 2174.9374 | 61.9386 | 2142.3858 | 20.9672 | 49.5328 | 0.20149 | [27 empty] | SDS-Incubation time | hours | 42 | 42 | 42 | 0 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 42 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 42 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 42 | --- | --- | --- | --- | --- | --- | SDS-HAA5b, ug/L | 17.8989 | 17.6491 | 18.0441 | 17.9401 | SDS-HAA5b, ug/L | 8.6901 | 8.1191 | 9.0221 | 8.7844
|  | Variability of rejection of reference solute (%) | 3 | [14 empty] | SDS-THM4 | mg/L | 112.5 | 87.49 | 99.995 | 25.0113 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-10 | 13:00 | 97 | 22.4 | 72 | 72 | 370 | 5.6 | 0.77 |  | 6.37 | 0.25153 | 0.87912 | 57.0848 | 12.7562 | 9.9515 | 2206.6629 | 62.8589 | 2174.2161 | 21.2758 | 50.7242 | 0.19619 |  |  |  | 42.7 |  |  | 2353.2727 |  | 86.7391 | 2335.7873 | 98.1719 | 0.003 |  |  | 0.4125 |  | 94.2857 | 0.4094 | 99.2672 | [8 empty] | SDS-TOX | mg Cl- /L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOXb, ug Cl- /L | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | SDS-TOXb, ug Cl- /L | #DIV/0! | #VALUE! | #VALUE! | #VALUE!
|  | Standard testing recovery (%) | 15 | [14 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-10 | 14:00 | 98 | 22 | 72 | 72 | 370 | 5.3 | 0.73 |  | 6.03 | 0.25153 | 0.87894 | 60.3599 | 12.0728 | 9.5304 | 2203.6867 | 62.8243 | 2173.0203 | 21.2553 | 50.7447 | 0.18781 |  |  |  | 45.7 |  |  | 2328.0137 |  | 85.8075 | 2311.6674 | 98.0231 | 0.002 |  |  | 0.41914 |  | 96.1905 | 0.41616 | 99.5194 | [8 empty] | SDS-CHCl3 | mg/L | 1.03 | 3.025 | 2.0275 | 98.397 | --- | 158.713 | --- | 95.9931 | 157.4711 | 98.7125 | SDS-CHCl3 | mg/L | 1.69 | --- | 377.9208 | --- | 96.6601 | 375.2359 | 99.5496 | SDS-CHCl3 | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHCl3 | mg/L | 1.46 | --- | 72.6774 | --- | 97.1146 | 72.0986 | 97.975 | SDS-CDb, mg/L | 2.357 | 2.4422 | 2.3269 | 2.3393 | SDS-CDb, mg/L | 1.2473 | 1.4421 | 1.1785 | 1.2067
|  | Standard testing pH | 7 | [14 empty] | SDS-DCAA* | mg/L | 19.3 | 15.96 | 17.63 | 18.945 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-10 | 15:00 | 99 | 22 | 75 | 75 | 370 | 5.3 | 0.8 |  | 6.1 | 0.25153 | 0.86885 | 59.6557 | 12.0728 | 9.5304 | 2065.1959 | 58.8761 | 2036.4568 | 19.9195 | 55.0805 | 0.17303 |  |  |  | 51.8 |  | 1459 | 2112.075 | -44.7618 | 83.913 | 2097.319 | 97.5302 | 0.004 | 0.054* | 0.306 | 0.37381 | -22.1609 | 92.381 | 0.37116 | 98.9223 | [8 empty] | SDS-BDCM | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-BDCM | mg/L | 1.73 | --- | 207.6531 | --- | 93.9298 | 206.1835 | 99.1609 | SDS-BDCM | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | TOCb, mg/L | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | TOCb, mg/L | #DIV/0! | #VALUE! | #VALUE! | #VALUE!
|  | Acceptable range of operating pressures | < 600 PSI | [14 empty] | SDS-TCAA* | mg/L | 3 | 3.5 | 3.25 | 15.3846 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-10 | 16:00 | 100 | 22.2 | 75 | 75 | 370 | 5.3 | 0.77 |  | 6.07 | 0.25153 | 0.87315 | 59.9555 | 12.0728 | 9.4742 | 2121.9716 | 60.4947 | 2092.4424 | 20.4671 | 54.5329 | 0.17373 |  |  |  | 51.6 |  |  | 2183.1948 |  | 83.9752 | 2167.928 | 97.6198 | 0.006 |  |  | 0.37256 |  | 88.5714 | 0.36994 | 98.3781 | [8 empty] | SDS-DBCM | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DBCM | mg/L | 1.91 | --- | 120.6792 | --- | 88.9914 | 119.8317 | 98.4061 | SDS-DBCM | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 b, cm-1 | 0.038069 | 0.037862 | 0.038362 | 0.038721 | UV254 b, cm-1 | 0.019512 | 0.019037 | 0.020181 | 0.021001
|  | Acceptable range of operating pH values | pH 2-11 | [14 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-11 | 8:00 | 116 | 22.7 | 75 | 75 | 370 | 5 | 4.9 |  | 9.9 | 0.25153 | 0.50505 | 36.3737 | 11.3895 | 8.8068 | 632.1667 | 18.0367 | 623.8676 | 6.0998 | 68.9002 | 0.12782 | [27 empty] | SDS-CHBr3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Bromideb, ug/L | #DIV/0! | 89.694 | #VALUE! | #VALUE! | Bromideb, ug/L | #DIV/0! | 59.0808 | #VALUE! | #VALUE!
|  | Typical pressure drop across a single element (psi) | 6 | [14 empty] | SDS-DBAA* | mg/L | 3.87 | 4.49 | 4.18 | 14.8325 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-11 | 10:00 | 118 | 23.5 | 75 | 75 | 370 | 5.4 | 5.1 |  | 10.5 | 0.25153 | 0.51429 | 34.2381 | 12.3006 | 9.2891 | 643.5212 | 18.3411 | 634.397 | 6.2062 | 68.7938 | 0.13503 | 6.72 |  |  | 15.3 |  |  | 646.7412 |  | 95.2484 | 642.1334 | 97.6173 | 0.001 |  |  | 0.10703 |  | 98.0952 | 0.10626 | 99.0589 | [8 empty] | SDS-THM4 | mg/L | 1.03 | 3.025 | 2.0275 | 98.397 | --- | 318.0517 | --- | 97.9724 | 315.547 | 99.3575 | SDS-THM4 | mg/L | 5.33 | --- | 733.5223 | --- | 94.6697 | 728.3257 | 99.2682 | SDS-THM4 | mg/L | 0 | --- | 199.99 | --- | 100 | 198.4495 | 100 | SDS-THM4 | mg/L | 1.46 | --- | 144.2643 | --- | 98.5399 | 143.1038 | 98.9798 | Alkb, mg/L CaCO3 | 40.6764 | 40.7769 | 40.8218 | 39.7631 | Alkb, mg/L CaCO3 | 22.5786 | 22.8083 | 22.9109 | 20.4907
|  | Maximum permissible SDI | 5 | [14 empty] | SDS-BCAA* | mg/L | 8.92 | 8.43 | 8.675 | 5.6484 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-11 | 12:00 | 120 | 23.5 | 75 | 75 | 370 | 5.5 | 5.5 |  | 11 | 0.25153 | 0.5 | 32.6364 | 12.5284 | 9.4611 | 626.1585 | 17.8415 | 617.116 | 6.038 | 68.962 | 0.13719 | 6.97 |  |  | 15.9 |  |  | 628.1 |  | 95.0621 | 623.5499 | 97.4501 | 0.001 |  |  | 0.104 |  | 98.0952 | 0.10323 | 99.0313 | [8 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | T-Hdb, mg/L CaCO3 | 84.8593 | 85.1488 | 84.6482 | 84.1367 | T-Hdb, mg/L CaCO3 | 43.2067 | 43.8685 | 42.7241 | 41.5549
|  | Maximum permissible turbidity (ntu) | 1 | [14 empty] | SDS-TBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-11 | 14:00 | 122 | 23.9 | 75 | 75 | 370 | 5.6 | 5.4 |  | 11 | 0.25153 | 0.50909 | 32.6364 | 12.7562 | 9.5199 | 637.1052 | 18.1485 | 627.7372 | 6.1427 | 68.8573 | 0.13826 | 6.9 | 8.12 | 8.16 | 16.2 | 324 | 616 | 639.1259 | -3.7542 | 94.9689 | 634.4119 | 97.4465 | 0.001 | 0.053 | 0.106 | 0.10591 | 0.087352 | 98.0952 | 0.10511 | 99.0486 | [8 empty] | SDS-DCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Ca-Hdb, mg/L CaCO3 | 70.6459 | 70.9859 | 70.3195 | 69.8621 | Ca-Hdb, mg/L CaCO3 | 36.306 | 37.0832 | 35.5597 | 34.5143
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | 1000 ppm/hours | [14 empty] | SDS-CDBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-11 | 15:00 | 123 | 24.1 | 75 | 75 | 370 | 5.7 | 5.6 |  | 11.3 | 0.25153 | 0.50442 | 31.7434 | 12.984 | 9.6328 | 631.4463 | 17.9825 | 621.9957 | 6.0874 | 68.9126 | 0.13978 | [27 empty] | SDS-TCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | 1: All of the information requested in this field may not be available, but values for all Design | [15 empty] | SDS-DCBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-11 | 16:00 | 124 | 24 | 75 | 75 | 370 | 5.7 | 5.7 |  | 11.4 | 0.25153 | 0.5 | 31.4561 | 12.984 | 9.6613 | 626.1678 | 17.8322 | 616.7961 | 6.0365 | 68.9635 | 0.14009 | [27 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  | Parameters must be entered in cells E14:E23, since these parameters are used in calculations. | [15 empty] | SDS-HAA5 | mg/L | 26.17 | 23.95 | 25.06 | 8.8587 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-12 | 8:00 | 140 | 23.1 | 75 | 75 | 370 | 5.6 | 13.1 |  | 18.7 | 0.25153 | 0.29947 | 18.7861 | 12.7562 | 9.7477 | 454.119 | 12.936 | 447.4416 | 4.3784 | 70.6216 | 0.13803 | [27 empty] | SDS-DBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Blended Water Quality if HAA5 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if HAA5 Controls the Blend Ratio
[18 empty] | SDS-HAA6 | mg/L | 35.09 | 32.38 | 33.735 | 8.0332 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-12 | 10:00 | 142 | 23.2 | 75 | 75 | 370 | 5.6 | 13 |  | 18.6 | 0.25153 | 0.30108 | 18.8925 | 12.7562 | 9.7189 | 455.1229 | 12.9646 | 448.4308 | 4.3881 | 70.6119 | 0.13764 | 8.08 |  |  | 12 |  |  | 455.5385 |  | 96.2733 | 452.182 | 97.3462 | 0.001 |  |  | 0.074685 |  | 98.0952 | 0.074127 | 98.651 | [8 empty] | SDS-BCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-BCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Qp/QT (HAA5), % | -115.4828 | -115.4828 | -115.4828 | -115.4828 | Qp/QT (HAA5), % | -7.7414 | -7.7414 | -7.7414 | -7.7414
[18 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-12 | 12:00 | 144 | 23.5 | 75 | 75 | 370 | 5.8 | 12.4 |  | 18.2 | 0.25153 | 0.31868 | 19.3297 | 13.2118 | 9.9772 | 466.4018 | 13.2788 | 459.2988 | 4.4957 | 70.5043 | 0.14151 | 8.15 |  |  | 12.1 |  |  | 466.9532 |  | 96.2422 | 463.3882 | 97.3888 | 0.004 |  |  | 0.075185 |  | 92.381 | 0.074628 | 94.64 | [8 empty] | SDS-TBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-THM4b, ug/L | NA | NA | NA | NA | SDS-THM4b, ug/L | NA | NA | NA | NA
[18 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-12 | 14:00 | 146 | 24.8 | 74 | 74 | 370 | 5.9 | 12.8 |  | 18.7 | 0.25153 | 0.31551 | 18.7861 | 13.4396 | 9.7666 | 464.33 | 13.2163 | 457.1366 | 4.4752 | 69.5248 | 0.14048 | 7.87 | 8.59 | 8.57 | 11.4 | 319 | 443 | 465.1672 | -5.0039 | 96.4596 | 461.5493 | 97.5301 | 0.003 | 0.051 | 0.072 | 0.075316 | -4.6061 | 94.2857 | 0.07474 | 95.9861 | [8 empty] | SDS-CDBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-HAA5b, ug/L | NA | NA | NA | NA | SDS-HAA5b, ug/L | NA | NA | NA | NA
[18 empty] | should be reported if measured. | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-12 | 15:00 | 147 | 26.4 | 74 | 74 | 370 | 6.1 | 13.3 |  | 19.4 | 0.25153 | 0.31443 | 18.0722 | 13.8951 | 9.6312 | 463.6349 | 13.1895 | 456.2086 | 4.4673 | 69.5327 | 0.13851 | [27 empty] | SDS-DCBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TOXb, ug Cl- /L | NA | NA | NA | NA | SDS-TOXb, ug Cl- /L | NA | NA | NA | NA
[45 empty] | 1998-05-12 | 16:30 | 148.5 | 26.1 | 74 | 74 | 370 | 6.1 | 13.3 |  | 19.4 | 0.25153 | 0.31443 | 18.0722 | 13.8951 | 9.717 | 463.6349 | 13.1895 | 456.2086 | 4.4673 | 69.5327 | 0.13975 | [27 empty] | SDS-HAA5 | mg/L | 0 | 0 | 0 | #DIV/0! | --- | 80.8387 | --- | 100 | 80.198 | 100 | SDS-HAA5 | mg/L | 0 | --- | 192.7692 | --- | 100 | 191.3936 | 100 | SDS-HAA5 | mg/L | 0 | --- | 50.12 | --- | 100 | 49.7339 | 100 | SDS-HAA5 | mg/L | 0 | --- | 36.3188 | --- | 100 | 36.0237 | 100 | SDS-CDb, mg/L | NA | NA | NA | NA | SDS-CDb, mg/L | NA | NA | NA | NA
[45 empty] | 1998-05-13 | 13:00 | 169 | 26.1 | 62 | 62 | 370 | 7.4 | 17.8 | x | 25.2 | 0.25153 | 0.29365 | 13.6825 | 16.8564 | 11.7878 | 450.5551 | 12.7729 | 441.7994 | 4.334 | 57.666 | 0.20442 | [27 empty] | SDS-HAA6 | mg/L | 0 | 0 | 0 | #DIV/0! | --- | 108.8226 | --- | 100 | 107.9601 | 100 | SDS-HAA6 | mg/L | 0 | --- | 259.5 | --- | 100 | 257.6481 | 100 | SDS-HAA6 | mg/L | 0 | --- | 67.47 | --- | 100 | 66.9503 | 100 | SDS-HAA6 | mg/L | 0 | --- | 48.8913 | --- | 100 | 48.494 | 100 | TOCb, mg/L | NA | NA | NA | NA | TOCb, mg/L | NA | NA | NA | NA
[45 empty] | 1998-05-13 | 14:30 | 170.5 | 26.2 | 62 | 62 | 370 | 7.5 | 17.8 |  | 25.3 | 0.25153 | 0.29644 | 13.6245 | 17.0842 | 11.9119 | 452.2732 | 12.8182 | 443.3654 | 4.35 | 57.65 | 0.20662 | [27 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | UV254 b, cm-1 | NA | NA | NA | NA | UV254 b, cm-1 | NA | NA | NA | NA
[45 empty] | 1998-05-13 | 17:00 | 173 | 27.1 | 62 | 62 | 380 | 7.6 | 18 |  | 25.6 | 0.25833 | 0.29688 | 13.8438 | 17.312 | 11.7538 | 452.5388 | 12.8291 | 443.7446 | 4.3531 | 57.6469 | 0.20389 | [27 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | Bromideb, ug/L | NA | NA | NA | NA | Bromideb, ug/L | NA | NA | NA | NA
[45 empty] | 1998-05-15 | 10:30 | 175.5 | 24.9 | 62 | 62 | 380 | 7.1 | 17.6 |  | 24.7 | 0.25833 | 0.28745 | 14.3846 | 16.173 | 11.7183 | 446.7815 | 12.6824 | 438.6707 | 4.3004 | 57.6996 | 0.20309 | [66 empty] | Alkb, mg/L CaCO3 | NA | NA | NA | NA | Alkb, mg/L CaCO3 | NA | NA | NA | NA
[45 empty] | 1998-05-15 | 12:00 | 177 | 25.9 | 62 | 62 | 380 | 7.3 | 17.5 |  | 24.8 | 0.25833 | 0.29435 | 14.3226 | 16.6286 | 11.6975 | 450.9827 | 12.795 | 442.5648 | 4.3398 | 57.6602 | 0.20287 | 6.43 | 7.79 | 7.91 | 16 | 326 | 391 | 449.6457 | -14.9989 | 95.0311 | 445.4804 | 96.4084 | 0.002 | 0.054 | 0.074 | 0.073566 | 0.58687 | 96.1905 | 0.072878 | 97.2557 | [47 empty] | T-Hdb, mg/L CaCO3 | NA | NA | NA | NA | T-Hdb, mg/L CaCO3 | NA | NA | NA | NA
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Ca-Hdb, mg/L CaCO3 | NA | NA | NA | NA | Ca-Hdb, mg/L CaCO3 | NA | NA | NA | NA
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Notes: |  |  |  |  | Notes:
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to |  |  |  |  | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | determine the percentage of total flow that must be treated by the membrane process to meet the |  |  |  |  | determine the percentage of total flow that must be treated by the membrane process to meet the
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Stage 1 DBP MCLs. |  |  |  |  | Stage 2 DBP MCLs.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | A 10% factor of safety has been applied all the MCLs. i.e., 72 / 54 mg/L for THM4 and HAA5. |  |  |  |  | A 10% factor of safety has been applied all the MCLs. i.e., 36 / 27 mg/L for THM4 and HAA5.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for |  |  |  |  | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | both parameters and the maximum (Qp/QT) ratio controls the design. |  |  |  |  | both parameters and the maximum (Qp/QT) ratio controls the design.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. |  |  |  |  | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. |  |  |  |  | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. |  |  |  |  | The subscript "b" refers to the blended water quality for a given blend ratio.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL. |  |  |  |  | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. |  |  |  |  | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Note on X24: Alison Gusses: High precision incubator was used for SDS testing
Note on CY29: Alison Gusses: High precision incubator was used for SDS testing
Note on DL29: Alison Gusses: High precision incubator was used for SDS testing
Note on DV29: Alison Gusses: High precision incubator was used for SDS testing
Note on EF29: Alison Gusses: High precision incubator was used for SDS testing

## BW30. 2nd Quarter
FIELD-SET 2: 2nd QUARTER RBSMT RESULTS (FILE: rbsmt-2.xls)
Field 2-1: PWS And Treatment Plant Data |  | Field 2-2: Manufacturer Reported Membrane Characteristics1 |  | Field 2-3: RBSMT Design Parameters | [8 empty] | Field 2-4: Foulants And Fouling Indices1 |  | Field 2-5: Pretreatment Used Prior To Membranes1 |  |  | Field 2-6: Feed Water Quality After Pretreatment | [5 empty] | Field 2-7: Membrane Setting Data | [20 empty] | Field 2-8: Membrane Performance Data During Operation With The Test Water | [16 empty] | Field 2-8: Membrane Performance Data During Operation With The Test Water (continued) | [19 empty] | Field 2-8: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 2-9: Permeate And Concentrate Water Quality For Run 1 | [11 empty] | Field 2-10: Permeate And Concentrate Water Quality For Run 2 | [8 empty] | Field 2-11: Permeate And Concentrate Water Quality For Run 3 | [8 empty] | Field 2-12: Permeate And Concentrate Water Quality For Run 4 | [8 empty] | Field 2-13: Blending Calculations For Stage 1 D-DBP MCLs |  |  |  |  | Field 2-14: Blending Calculations For Proposed Stage 2 D-DBP MCLs |  |  |  |  | Field 2-15: Membrane Cost Parameters
|  | General Information |  | Input Design Parameters | [8 empty] | Parameters Evaluated Prior to Pretreatment | [80 empty] | Operating Parameters During Sample Collection | [11 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Feed and Permeate Water Quality Parameters |  |  |  |  | Feed and Permeate Water Quality Parameters |  |  |  |  | General Cost Parameters
PWS Name | Water District No. 1 of Johnson County, Kansas | Membrane manufacturer | Dow-Filmtec | [5 empty] | Active membrane area in bench-scale cell, Acell (ft2) | 0.167 |  |  | Alkalinity (mg/L as CaCO3) | 130 | Process | Description | Scale | Parameter | Units | CF-1 | CF-2 | Average | RPD |  |  |  | Average TDS rejection (decimal fraction) | 0.98 | [5 empty] | TDS concentration of setting solution (mg/L) | 0.8 | [12 empty] | Average bulk TDS rejection (decimal fraction) | 0.96468 | [45 empty] | Recovery during sample collection (decimal) | 0.69 | [10 empty] | Recovery during sample collection (decimal) | 0.89 | [7 empty] | Recovery during sample collection (decimal) | 0.5 | [7 empty] | Recovery during sample collection (decimal) | 0.3 | [8 empty] | RUN ID # |  |  |  |  | RUN ID # |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | KS200910 | Membrane trade name | BW30-XLE | [5 empty] | Active width of membrane in the bench-scale cell, wcell (ft) | 0.333 |  |  | Calcium Hardness (mg/L as CaCO3) | 123 | Presedimentation | 3 Basins | Full-scale | Sampling date | MM/DD/YY | 1998-07-22 | 1998-07-29 | --- | --- | [71 empty] | Feed flow rate during sample collection (mL/min) | 10.1 | [10 empty] | Feed flow rate during sample collection (mL/min) | 5.37 | [7 empty] | Feed flow rate during sample collection (mL/min) | 9.6 | [7 empty] | Feed flow rate during sample collection (mL/min) | 16 | [6 empty] | Parameter | 1 | 2 | 3 | 4 | Parameter | 1 | 2 | 3 | 4 | Capital Recovery Interest Rate (%) | 5
Water Industry Data Base Number (optional) | NA | Molecular weight cutoff (Daltons) | 100 | [5 empty] | Average yearly temperature of feed water, TavgoC (oC) | 14 |  |  | LSI | 0.54 | Softening | Lime, 180 mg/L as Ca(OH)2 | Bench-scale | Sampling time | hh:mm | 12:00 | 7:00 | --- | --- | Date | Time | Setting time | Influent | PI | PC | QI | Qp | QW | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) | Date | Time | Operation time | Influent | PI | PC | QI | Qp | QW | Cleaning Event | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1) | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Influent flow rate during sample collection (mL/min) | 350 | [10 empty] | Influent flow rate during sample collection (mL/min) | 350 | [7 empty] | Influent flow rate during sample collection (mL/min) | 350 | [7 empty] | Influent flow rate during sample collection (mL/min) | 350 | [6 empty] | SDS-THM4F, ug/L | 103.025 | 103.025 | 103.025 | 103.025 | SDS-THM4F, ug/L | 103.025 | 103.025 | 103.025 | 103.025 | Capital Recovery Period (years) | 20
|  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide | [5 empty] | Approximate feed water TDS, TDSF (mg/L) | 322 |  |  | Dissolved iron (mg/L) |  | Coagulation | Alum: Al2(SO4)3.H2O, 15 mg/L | Bench-scale | Operation time | hh.hh | 0 | 173 | --- | --- | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | Indicate with "X" | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) | [39 empty] | SDS-THM4p, ug/L | 4.7625 | 7.97 | 0 | 2.476 | SDS-THM4p, ug/L | 4.7625 | 7.97 | 0 | 2.476 | Overhead & Profit Factor (% of construction costs) | 15
Official ICR Contact Person |  | Membrane construction (e.g., thin-film composite) | Thin Film | [5 empty] | Manufacturer reported TDS rejection, RejTDS (decimal fraction) | 0.98 |  |  | Total iron (mg/L) |  | Sedimentation | Gravity settling in test drums | Bench-scale | pH | --- | 9.28 | 8.97 | 9.125 | 3.3973 | 1998-07-20 | 12:00 | 0 | 24.7 | 52 | 52 | 350 | 9.1 | 3.4 | 12.5 | 0.23793 | 0.728 | 27 | 20.7288 | 15.1083 | 2.7954 | 0.054482 | 2.7241 | 0.027052 | 51.9729 | 0.2907 | 1998-07-22 | 12:00 | 0 | 25.5 | 55 | 56 | 350 | 8.4 | 4.4 |  | 12.8 | 0.23793 | 0.65625 | 26.3438 | 19.1343 | 13.6202 | 600.7227 | 20.7262 | 586.8028 | 5.7304 | 49.7696 | 0.27367 |  | 9.28 |  |  | 242 | [7 empty] | 0.046 | [14 empty] | Permeate and Concentrate Water Quality | [11 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | SDS-HAA5F, ug/L | 26.69 | 26.69 | 26.69 | 26.69 | SDS-HAA5F, ug/L | 26.69 | 26.69 | 26.69 | 26.69 | Special Sitework Factor (% of construction costs) | 0
Mailing Address |  | Membrane hydrophobicity | Hydrophobic | [5 empty] | Temperature normalized MTCW (gfd/psi) | 0.16688 |  |  | Dissolved aluminum (mg/L) |  | Recarbonation | CO2 gas added to pH 9.4 | Bench-scale | Temperature | oC | 26.8 | 23 | 24.9 | 15.261 | 1998-07-20 | 14:00 | 2 | 25.4 | 51 | 52 | 350 | 9.1 | 3.7 | 12.8 | 0.23793 | 0.71094 | 26.3438 | 20.7288 | 14.7989 | 2.641 | 0.051473 | 2.5736 | 0.025558 | 51.4744 | 0.2875 | 1998-07-22 | 13:00 | 1 | 25.5 | 55 | 55 | 350 | 7.8 | 3.3 |  | 11.1 | 0.23793 | 0.7027 | 30.5315 | 17.7675 | 12.6473 | 684.4264 | 23.6542 | 669.7007 | 6.5341 | 48.4659 | 0.26095 | [27 empty] | Parameter | Units | Cp-1 | Cp-1 (dup) | Average | RPD | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | SDS-HAA5p, ug/L | 0 | 0 | 0 | 0 | SDS-HAA5p, ug/L | 0 | 0 | 0 | 0 | Construction Contingencies (% of construction costs) | 15
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Slightly Negative | [9 empty] | Total aluminum (mg/L) |  | Cartridge filtration | 1 um size exclusion | Bench-scale | Alkalinity | mg/L as CaCO3 | 58.5 | 40 | 49.25 | 37.5635 | 1998-07-20 | 16:00 | 4 | 25.7 | 50 | 52 | 350 | 9.2 | 4.7 | 13.9 | 0.23793 | 0.66187 | 24.1799 | 20.9566 | 14.8295 | 2.279 | 0.044406 | 2.2203 | 0.022053 | 50.9779 | 0.2909 | 1998-07-22 | 15:00 | 3 | 26 | 55 | 55 | 350 | 7.8 | 3.3 |  | 11.1 | 0.23793 | 0.7027 | 30.5315 | 17.7675 | 12.4618 | 684.4264 | 23.6542 | 669.7007 | 6.5341 | 48.4659 | 0.25713 | 9.26 |  | 9.23 | 31.6 |  | 687 | 665.6455 | 3.1084 | 85.6429 | 658.5804 | 95.2018 | 0.008 |  | 0.154 | 0.13582 | 11.8064 | 82.6087 | 0.13439 | 94.0473 | [8 empty] | Sampling date | MM/DD/YY | 1998-07-25 | 1998-07-25 | --- | --- | 1998-07-25 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-07-26 | 1998-07-26 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-07-27 | 1998-07-27 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-07-28 | 1998-07-28 | --- | --- | --- | --- | --- | SDS-TOXF, ug Cl- /L | 180 | 180 | 180 | 180 | SDS-TOXF, ug Cl- /L | 180 | 180 | 180 | 180 | Engineering Fee Factor (% of construction costs) | 15
Phone Number |  |  |  | Experimental Design1,2 | [8 empty] | Fluoride (mg/L) |  | Antiscalant | 4 mg/L Hypersperse 400UL | Bench-scale | Total dissolved solids | mg/L | 242 | 198.2 | 220.1 | 19.9 | 1998-07-20 | 17:00 | 5 | 25.5 | 50 | 51 | 360 | 9.4 | 3.9 | 13.3 | 0.24473 | 0.70677 | 26.0677 | 21.4122 | 15.2417 | 2.6058 | 0.050782 | 2.5391 | 0.025217 | 50.4748 | 0.30197 | 1998-07-22 | 17:00 | 5 | 26.4 | 55 | 55 | 350 | 7.9 | 3.4 |  | 11.3 | 0.23793 | 0.69912 | 29.9735 | 17.9953 | 12.4732 | 677.1475 | 23.396 | 662.3914 | 6.4637 | 48.5363 | 0.25699 | [27 empty] | Sampling time | hh:mm | 13:00 | 13:00 | --- | --- | 13:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 12:00 | 12:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 12:00 | 12:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 12:00 | 12:00 | --- | --- | --- | --- | --- | SDS-TOXp, ug Cl- /L | #DIV/0! | BMRL | BMRL | BMRL | SDS-TOXp, ug Cl- /L | #DIV/0! | BMRL | BMRL | BMRL | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920
FAX Number |  | Design Parameters |  | ID# | Recovery | FW-design | Dp | PI | QI-cell | Qp | QF | QW | Phosphate (mg/L) |  |  |  |  | Total hardness | mg/L as CaCO3 | 103 | 92.9 | 97.95 | 10.3114 | 1998-07-21 | 9:00 | 21 | 24.7 | 50 | 51 | 350 | 9 | 3.8 | 12.8 | 0.23793 | 0.70312 | 26.3438 | 20.501 | 14.9423 | 2.5758 | 0.050217 | 2.5109 | 0.024931 | 50.4751 | 0.29603 | 1998-07-23 | 7:00 | 19 | 23.4 | 54 | 55 | 350 | 7 | 3.2 |  | 10.2 | 0.23793 | 0.68627 | 33.3137 | 15.9452 | 12.0771 | 652.1538 | 22.5897 | 639.5625 | 6.2327 | 48.2673 | 0.25021 | 8.92 |  |  | 26.5 |  |  | 643.6 |  | 87.96 | 637.429 | 95.8427 | 0 | [15 empty] | Operation time | hh.hh | 73 | 73 | --- | --- | 73 | --- | --- | --- | --- | --- | Operation time | hh.hh | 96 | 96 | --- | --- | --- | --- | --- | Operation time | hh.hh | 120 | 120 | --- | --- | --- | --- | --- | Cumulative time | hr | 144 | 144 | --- | --- | --- | --- | --- | SDS-CDF, mg/L | 0.725 | 0.725 | 0.725 | 0.725 | SDS-CDF, mg/L | 0.725 | 0.725 | 0.725 | 0.725 | 1998 Producers Price Index (PPI base year 1967 = 100) | 370
E-Mail Address (optional) |  | Design flux, FW (gfd) | 30(15 ave) |  | (decimal) | (gfd) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | Sulfate (mg/L) |  |  |  |  | Calcium hardness | mg/L as CaCO3 | 85.9 | 77.4 | 81.65 | 10.4103 | 1998-07-21 | 11:00 | 23 | 25.6 | 52 | 53 | 350 | 9 | 3.8 | 12.8 | 0.23793 | 0.70312 | 26.3438 | 20.501 | 14.55 | 2.5758 | 0.050217 | 2.5109 | 0.024931 | 52.4751 | 0.27727 | 1998-07-23 | 9:00 | 21 | 23.5 | 54 | 54 | 350 | 6.8 | 3.2 |  | 10 | 0.23793 | 0.68 | 34 | 15.4897 | 11.6974 | 640.631 | 22.2031 | 628.6158 | 6.1242 | 47.8758 | 0.24433 | [27 empty] | pH | --- | 7.56 | 7.43 | 7.495 | 1.7345 | 8.6 | --- | --- | --- | --- | --- | pH | --- | 7.13 | 8.27 | --- | --- | --- | --- | --- | pH | --- | 7.61 | 8.23 | --- | --- | --- | --- | --- | pH | --- | 8.2 | 8.88 | --- | --- | --- | --- | --- | SDS-CDp, mg/L | 0.172 | 0.367 | 0.198 | 0.281 | SDS-CDp, mg/L | 0.172 | 0.367 | 0.198 | 0.281 | Labor Rate + Fringe ($/work-hour) | 17
|  | Net driving pressure at the design flux, NDP (psi) | 130 | 1 | 0.7 | 15 | 10.5831 | 100.4684 | 335.6684 | 6.5843 | 9.4062 | 2.8219 | Calcium (mg/L) | 49 |  |  |  | Turbidity | ntu | 0.12 | 0.14 | 0.13 | 15.3846 | 1998-07-21 | 12:00 | 24 | 26.1 | 51 | 52 | 350 | 9 | 4 | 13 | 0.23793 | 0.69231 | 25.9231 | 20.501 | 14.3366 | 2.4907 | 0.048559 | 2.4279 | 0.024108 | 51.4759 | 0.27851 | 1998-07-23 | 11:00 | 23 | 23.5 | 54 | 54 | 350 | 6.7 | 2.9 |  | 9.6 | 0.23793 | 0.69792 | 35.4583 | 15.2619 | 11.5253 | 674.5769 | 23.3861 | 662.1112 | 6.4496 | 47.5504 | 0.24238 | 8.61 | 9.02 | 8.92 | 29.3 | 254 | 719 | 660.9138 | 8.0787 | 86.6879 | 654.8683 | 95.5258 | 0.001 | 0.044 | 0.146 | 0.14997 | -2.7161 | 97.8261 | 0.14854 | 99.3268 | [8 empty] | Temperature | oC | 22.7 | 22.7 | 22.7 | 0 | 22.7 | --- | --- | --- | --- | --- | Temperature | oC | 24.8 | 24.8 | --- | --- | --- | --- | --- | Temperature | oC | 26.2 | 26.2 | --- | --- | --- | --- | --- | Temperature | oC | 23 | 23 | --- | --- | --- | --- | --- | TOCF, mg/L | 2.6 | 2.6 | 2.6 | 2.6 | TOCF, mg/L | 2.6 | 2.6 | 2.6 | 2.6 | Labor Overhead Factor (% of labor) | 42
Technical ICR Contact Person |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.231 | 2 | 0.9 | 15 | 31.6204 | 121.5057 | 335.6684 | 6.5843 | 7.3159 | 0.73159 | Barium (mg/L) |  |  |  |  | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! | 1998-07-21 | 14:00 | 26 | 26.6 | 51 | 52 | 350 | 9.6 | 3.8 | 13.4 | 0.23793 | 0.71642 | 25.1194 | 21.8678 | 15.068 | 2.6888 | 0.052331 | 2.6165 | 0.026004 | 51.474 | 0.29273 | 1998-07-23 | 13:00 | 25 | 24.3 | 54 | 54 | 350 | 6.8 | 2.9 |  | 9.7 | 0.23793 | 0.70103 | 35.0825 | 15.4897 | 11.424 | 680.8645 | 23.5975 | 668.0948 | 6.5088 | 47.4912 | 0.24055 | [27 empty] | Alkalinity | mg/L as CaCO3 | 2.7 | 3.3 | 3 | 20 | 130.25 | 152.1935 | -16.8473 | 93.9086 | 150.7082 | 98.0094 | Alkalinity | mg/L as CaCO3 | 4.1 | 228.5 | 414.5545 | -81.4243 | 91.6751 | 411.7521 | 99.0043 | Alkalinity | mg/L as CaCO3 | 1.9 | 105 | 96.6 | 8 | 96.1421 | 95.9506 | 98.0198 | Alkalinity | mg/L as CaCO3 | 2.8 | 65.2 | 69.1571 | -6.0692 | 94.3147 | 68.7021 | 95.9244 | TOCp, mg/L | #DIV/0! | BMRL | BMRL | BMRL | TOCp, mg/L | #DIV/0! | BMRL | BMRL | BMRL | Electric Rate ($/kW-h) | 0.06
Mailing Address |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | 3 | 0.5 | 15 | 6.3756 | 96.2609 | 335.6684 | 6.5843 | 13.1686 | 6.5843 | Strontium (mg/L) |  |  |  |  | Total organic carbon | mg/L | 2.6 | 2.6 | 2.6 | 0 | 1998-07-21 | 16:00 | 28 | 26.7 | 52 | 52 | 350 | 9.6 | 4.2 | 13.8 | 0.23793 | 0.69565 | 24.3623 | 21.8678 | 15.0235 | 2.5166 | 0.048979 | 2.4489 | 0.024338 | 51.9757 | 0.28905 | 1998-07-23 | 15:00 | 27 | 23.8 | 56 | 56 | 350 | 7 | 3 |  | 10 | 0.23793 | 0.7 | 34 | 15.9452 | 11.9351 | 678.8035 | 23.5128 | 665.6976 | 6.4874 | 49.5126 | 0.24105 | [27 empty] | Total dissolved solids | mg/L | 22.8 | 22.3 | 22.55 | 2.2173 | 661 | 659.8081 | 0.18032 | 89.7547 | 653.4637 | 96.5492 | Total dissolved solids | mg/L | 47.1 | 1322 | 1619.8273 | -22.5285 | 78.6006 | 1609.0894 | 97.0729 | Total dissolved solids | mg/L | 18.3 | 475 | 421.9 | 11.1789 | 91.6856 | 419.1325 | 95.6338 | Total dissolved solids | mg/L | 15.2 | 339 | 307.9143 | 9.1698 | 93.094 | 305.9071 | 95.0312 | UV254 F, cm-1 | 0.046 | 0.046 | 0.046 | 0.046 | UV254 F, cm-1 | 0.046 | 0.046 | 0.046 | 0.046 | Fuel Oil Rate ($/gal) | NA
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 400 | 4 | 0.3 | 15 | 4.5724 | 94.4577 | 335.6684 | 6.5843 | 21.9477 | 15.3634 | Reactive silica (mg/L as SiO2) |  |  |  |  | UV254 | cm-1 | 0.046 | 0.046 | 0.046 | 0 | 1998-07-21 | 17:00 | 29 | 26.8 | 52 | 52 | 350 | 10 | 4.4 | 14.4 | 0.23793 | 0.69444 | 23.3056 | 22.7789 | 15.6033 | 2.5074 | 0.048743 | 2.4372 | 0.024235 | 51.9758 | 0.3002 | 1998-07-23 | 17:00 | 29 | 24.5 | 55 | 56 | 350 | 7 | 3.2 |  | 10.2 | 0.23793 | 0.68627 | 33.3137 | 15.9452 | 11.6907 | 652.1538 | 22.5897 | 639.5625 | 6.2327 | 49.2673 | 0.23729 | 8.88 |  |  | 27.2 |  |  | 642.0688 |  | 87.642 | 635.9201 | 95.7227 | 0.001 |  |  | 0.14444 |  | 97.8261 | 0.143 | 99.3007 | [8 empty] | Total hardness | mg/L as CaCO3 | 1.3 | 1.3 | 1.3 | 0 | 275.4 | 313.0742 | -13.6798 | 98.6728 | 309.9703 | 99.5806 | Total hardness | mg/L as CaCO3 | 1.9 | 570.4 | 875.0818 | -53.4155 | 98.0602 | 869.1201 | 99.7814 | Total hardness | mg/L as CaCO3 | 1.1 | 194.5 | 194.8 | -0.15424 | 98.877 | 193.4718 | 99.4314 | Total hardness | mg/L as CaCO3 | 1.1 | 129.2 | 139.4571 | -7.939 | 98.877 | 138.5084 | 99.2058 | UV254 p, cm-1 | 0.001 | 0 | 0.001 | 0.003 | UV254 p, cm-1 | 0.001 | 0 | 0.001 | 0.003 | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Purchase price for an equivalent 8" x 40 " element ($) | 700 | 1: For experimental matrix see Table 4-2 in Part 3 of the ICR Treatment Studies Manual. | [8 empty] | Turbidity (ntu) | 3.9 |  |  |  | SUVA | L/(mg*m) | 1.7692 | 1.7692 | 1.7692 | 0 | 1998-07-22 | 8:00 | 44 | 24.1 | 52 | 52 | 340 | 9 | 4.2 | 13.2 | 0.23113 | 0.68182 | 24.7576 | 20.501 | 15.2097 | 2.4135 | 0.047018 | 2.3509 | 0.023352 | 51.9766 | 0.29262 | 1998-07-24 | 7:00 | 43 | 22.6 | 55 | 56 | 350 | 6.8 | 3.1 |  | 9.9 | 0.23793 | 0.68687 | 34.3535 | 15.4897 | 12.0127 | 653.2381 | 22.64 | 640.9865 | 6.2447 | 49.2553 | 0.24389 | 8.35 |  |  | 24.5 |  |  | 649.1581 |  | 88.8687 | 643.09 | 96.1903 | 0.001 |  |  | 0.14471 |  | 97.8261 | 0.14331 | 99.3022 | [8 empty] | Calcium hardness | mg/L as CaCO3 | 1.1 | 1.1 | 1.1 | 0 | 233.4 | 260.9387 | -11.7989 | 98.6528 | 258.3518 | 99.5742 | Calcium hardness | mg/L as CaCO3 | 1.6 | 476.7 | 729.3273 | -52.995 | 98.0404 | 724.3587 | 99.7791 | Calcium hardness | mg/L as CaCO3 | 0.9 | 171 | 162.4 | 5.0292 | 98.8977 | 161.2926 | 99.442 | Calcium hardness | mg/L as CaCO3 | 0.9 | 108.4 | 116.2571 | -7.2483 | 98.8977 | 115.4661 | 99.2206 | BromideF, ug/L | 110 | 110 | 110 | 110 | BromideF, ug/L | 110 | 110 | 110 | 110 | Current Process Water Rate ($/1000 gal) | 0.375
FAX Number |  | Maximum flow rate to the 8" x 40" element, QI, max (gpm) | 70 | 2: Flow rates and pressures may need to be adjusted in order to obtain the desired operating conditions. | [8 empty] | SDI |  |  |  |  | Bromide | mg/L | 100 | 120 | 110 | 18.1818 | 1998-07-22 | 10:00 | 46 | 24.5 | 52 | 53 | 350 | 9 | 4.2 | 13.2 | 0.23793 | 0.68182 | 25.5152 | 20.501 | 15.0309 | 2.4135 | 0.047052 | 2.3526 | 0.02336 | 52.4766 | 0.28643 | 1998-07-24 | 9:00 | 45 | 23.8 | 55 | 56 | 350 | 6.7 | 3 |  | 9.7 | 0.23793 | 0.69072 | 35.0825 | 15.2619 | 11.4236 | 660.5163 | 22.8987 | 648.3105 | 6.3151 | 49.1849 | 0.23226 | [27 empty] | Turbidity | ntu | 0.12 | 0.14 | 0.13 | 15.3846 | 0.16 | 0.13 | 18.75 | 0 | 0.13 | 0 | Turbidity | ntu | 0.12 | 0.2 | 0.21091 | -5.4545 | 7.6923 | 0.21029 | 42.9355 | Turbidity | ntu | 0.12 | 0.16 | 0.14 | 12.5 | 7.6923 | 0.13986 | 14.2017 | Turbidity | ntu | 0.09 | 0.15 | 0.14714 | 1.9048 | 30.7692 | 0.14675 | 38.6716 | Bromidep, ug/L | #DIV/0! | 47 | BMRL | BMRL | Bromidep, ug/L | #DIV/0! | 47 | BMRL | BMRL | Modifications to Existing Plant (% of construction costs) | 46
E-Mail Address (optional) |  | Minimum flow rate to the 8" x 40" element, QI, min (gpm) | 18.8 | [9 empty] | MFI |  |  |  |  | SDS-Cl2 dose | mg/L | 1.4 | 1.4 | 1.4 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-24 | 11:00 | 47 | 22.7 | 54 | 54 | 350 | 6.5 | 2.8 |  | 9.3 | 0.23793 | 0.69892 | 36.6344 | 14.8063 | 11.4489 | 676.5665 | 23.4683 | 664.4375 | 6.4703 | 47.5297 | 0.24088 | 8.1 | 8.82 | 8.76 | 24.8 | 257 | 712 | 673.475 | 5.4108 | 88.7324 | 667.4516 | 96.2844 | 0.001 | 0.046 | 0.148 | 0.15046 | -1.6651 | 97.8261 | 0.14908 | 99.3292 | [8 empty] | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! | BMRL | #DIV/0! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | BMRL | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | BMRL | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | BMRL | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | AlkF, mg/L CaCO3 | 49.25 | 49.25 | 49.25 | 49.25 | AlkF, mg/L CaCO3 | 49.25 | 49.25 | 49.25 | 49.25
|  | Total width of all membrane envelopes in the 8" x 40" element, w (ft) | 70.6 | [9 empty] | MPFI |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | SDS-Free Cl2 residual | mg/L | 0.63 | 0.72 | 0.675 | 13.3333 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-24 | 13:00 | 49 | 22.8 | 54 | 54 | 350 | 6.6 | 2.8 |  | 9.4 | 0.23793 | 0.70213 | 36.234 | 15.0341 | 11.5907 | 683.0727 | 23.6873 | 670.6386 | 6.5317 | 47.4683 | 0.24418 | [27 empty] | Total organic carbon | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | 6.55 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L | BMRL | 10 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 4.9 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 3.6 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkp, mg/L CaCO3 | 3 | 4.1 | 1.9 | 2.8 | Alkp, mg/L CaCO3 | 3 | 4.1 | 1.9 | 2.8
Plant Name | Facility 1 | Feed spacer thickness in the 8" x 40" element, T (ft) | 0.0026 | [9 empty] | Bromide (mg/L) | 86 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | SDS-Cl2 demand | mg/L | 0.77 | 0.68 | 0.725 | 12.4138 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-24 | 15:00 | 51 | 23.5 | 54 | 54 | 350 | 6.69 | 2.8 |  | 9.49 | 0.23793 | 0.70495 | 35.8809 | 15.2391 | 11.5081 | 688.9163 | 23.8839 | 676.2047 | 6.5868 | 47.4132 | 0.24272 | [27 empty] | UV254 | cm-1 | 0.001 | 0.001 | 0.001 | 0 | 0.1375 | 0.14616 | -6.2991 | 97.8261 | 0.14472 | 99.309 | UV254 | cm-1 | 0 | 0.33 | 0.41818 | -26.7218 | 100 | 0.41533 | 100 | UV254 | cm-1 | 0.001 | 0.092 | 0.091 | 1.087 | 97.8261 | 0.090383 | 98.8936 | UV254 | cm-1 | 0.003 | 0.064 | 0.064429 | -0.66964 | 93.4783 | 0.064007 | 95.313 | T-HdF, mg/L CaCO3 | 97.95 | 97.95 | 97.95 | 97.95 | T-HdF, mg/L CaCO3 | 97.95 | 97.95 | 97.95 | 97.95
Treatment Plant Category | CS/SOFT | [11 empty] | TOC (mg/L) | 3.8 | is to list the pretreatment processes used in this particular RBSMT run. |  |  | SDS-Chlorination temp. | oC | 26 | 26.2 | 26.1 | 0.76628 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-24 | 17:00 | 53 | 23.5 | 56 | 56 | 350 | 6.8 | 2.9 |  | 9.7 | 0.23793 | 0.70103 | 35.0825 | 15.4897 | 11.6974 | 680.8645 | 23.5975 | 668.0948 | 6.5088 | 49.4912 | 0.23635 | 7.46 |  |  | 24 |  |  | 679.9207 |  | 89.0959 | 673.5489 | 96.4368 | 0.001 |  |  | 0.15152 |  | 97.8261 | 0.15006 | 99.3336 | [8 empty] | SUVA | L/(mg*m) | NR | NR | #DIV/0! | #VALUE! | 2.0992 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 3.3 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 1.8776 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 1.7778 | --- | --- | --- | --- | --- | T-Hdp, mg/L CaCO3 | 1.3 | 1.9 | 1.1 | 1.1 | T-Hdp, mg/L CaCO3 | 1.3 | 1.9 | 1.1 | 1.1
Process Train Name | Coagulation/Sedimentation/Softening | Additional Information | [10 empty] | pH | 8.08 |  |  |  | SDS-Chlorination pH | --- | 9.4 | 9.44 | 9.42 | 0.42463 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-25 | 7:00 | 67 | 22.9 | 57 | 57 | 350 | 6.9 | 3 |  | 9.9 | 0.23793 | 0.69697 | 34.3535 | 15.7174 | 12.0818 | 672.7201 | 23.3086 | 659.9174 | 6.4301 | 50.5699 | 0.23891 | 8.25 |  |  | 24.2 |  |  | 670.67 |  | 89.005 | 664.2977 | 96.3571 | 0.001 |  |  | 0.1495 |  | 97.8261 | 0.14804 | 99.3245 | [8 empty] | Bromide | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | Bromide | mg/L | 47 | --- | 619.7273 | --- | 57.2727 | 615.8169 | 92.3679 | Bromide | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Bromide | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Ca-HdF, mg/L CaCO3 | 81.65 | 81.65 | 81.65 | 81.65 | Ca-HdF, mg/L CaCO3 | 81.65 | 81.65 | 81.65 | 81.65
ICR Treatment Plant Identification Number | 381 | Design cross-flow velocity (fps) | [10 empty] | Total Hardness (mg/L as CaCO3) | 168.6 |  |  |  | SDS-Incubation time | hours | 24 | 24 | 24 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-25 | 9:00 | 69 | 22.7 | 57 | 57 | 350 | 7 | 3.1 |  | 10.1 | 0.23793 | 0.69307 | 33.6535 | 15.9452 | 12.3295 | 665.08 | 23.0374 | 652.2391 | 6.3562 | 50.6438 | 0.24346 | [27 empty] | SDS-Cl2 dose | mg/L | 1 | 1 | 1 | 0 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1 | --- | --- | --- | --- | --- | --- | Ca-Hdp, mg/L CaCO3 | 1.1 | 1.6 | 0.9 | 0.9 | Ca-Hdp, mg/L CaCO3 | 1.1 | 1.6 | 0.9 | 0.9
PWSID Number of Plant (if assigned) | KS200910 | Required influent flow to permeate flow rate ratio, QI:Qp | 6.7 | [9 empty] | UV254 | 0.106 |  |  |  | SDS-TOX | mg Cl- /L | 180 | 180 | 180 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-25 | 11:00 | 71 | 22.8 | 57 | 57 | 350 | 7 | 3.1 |  | 10.1 | 0.23793 | 0.69307 | 33.6535 | 15.9452 | 12.2932 | 665.08 | 23.0374 | 652.2391 | 6.3562 | 50.6438 | 0.24274 | 8.15 | 8.72 | 8.85 | 24.1 | 257 | 723 | 662.6806 | 8.3429 | 89.0504 | 656.2948 | 96.3279 | 0.001 | 0.045 | 0.15 | 0.14761 | 1.5914 | 97.8261 | 0.14615 | 99.3158 | [8 empty] | SDS-Free Cl2 residual | mg/L | 0.747 | 0.909 | 0.828 | 19.5652 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.633 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.802 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.719 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 0.1 | Maximum element recovery (%) | 15 | [9 empty] | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | SDS-CHCl3 | mg/L | 65.55 | 55.28 | 60.415 | 16.9991 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-25 | 13:00 | 73 | 22.9 | 57 | 57 | 350 | 7 | 3.1 |  | 10.1 | 0.23793 | 0.69307 | 33.6535 | 15.9452 | 12.2569 | 665.08 | 23.0374 | 652.2391 | 6.3562 | 50.6438 | 0.24202 | [27 empty] | SDS-Cl2 demand | mg/L | 0.253 | 0.091 | 0.172 | 94.186 | --- | 1.9559 | --- | 76.2759 | 1.9381 | 91.1254 | SDS-Cl2 demand | mg/L | 0.367 | --- | 3.6215 | --- | 49.3793 | 3.5993 | 89.8036 | SDS-Cl2 demand | mg/L | 0.198 | --- | 1.252 | --- | 72.6897 | 1.2448 | 84.0935 | SDS-Cl2 demand | mg/L | 0.281 | --- | 0.91529 | --- | 61.2414 | 0.91094 | 69.1526 | Blended Water Quality if THM4 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if THM4 Controls the Blend Ratio
Historical Average Water Temperature (oC) | 14 | Variability of design flux (%) | 15 | [9 empty] | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | SDS-BDCM | mg/L | 24.75 | 27.53 | 26.14 | 10.635 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-25 | 15:00 | 75 | 22.4 | 57 | 57 | 350 | 7 | 3.1 |  | 10.1 | 0.23793 | 0.69307 | 33.6535 | 15.9452 | 12.4394 | 665.08 | 23.0374 | 652.2391 | 6.3562 | 50.6438 | 0.24562 | [27 empty] | SDS-Chlorination temp. | oC | 26.2 | 26.2 | 26.2 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 26.2 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 26.2 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 26.2 | --- | --- | --- | --- | --- | --- | Qp/QT (THM4), % | 31.5736 | 32.639 | 30.114 | 30.8556 | Qp/QT (THM4), % | 68.2102 | 70.5118 | 65.057 | 66.659
State Approved Plant Capacity (MGD) | 55 | Rejection of reference solute and conditions of test | 2000 ppm | [14 empty] | SDS-DBCM | mg/L | 12.46 | 15.18 | 13.82 | 19.6816 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-25 | 17:00 | 77 | 22.6 | 56 | 56 | 350 | 7 | 3.1 |  | 10.1 | 0.23793 | 0.69307 | 33.6535 | 15.9452 | 12.366 | 665.08 | 23.0374 | 652.2391 | 6.3562 | 49.6438 | 0.2491 | 8.2 |  |  | 24.9 |  |  | 660.8742 |  | 88.687 | 654.5145 | 96.1957 | 0.001 |  |  | 0.14761 |  | 97.8261 | 0.14615 | 99.3158 | [8 empty] | SDS-Chlorination pH | --- | 9.39 | 9.43 | 9.41 | 0.42508 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 9.45 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 9.43 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 9.42 | --- | --- | --- | --- | --- | --- | SDS-THM4b, ug/L | 72 | 72 | 72 | 72 | SDS-THM4b, ug/L | 36 | 36 | 36 | 36
|  | (e.g., solute type and concentration) | NaCl | [14 empty] | SDS-CHBr3 | mg/L | 2.34 | 2.96 | 2.65 | 23.3962 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-26 | 8:00 | 92 | 22 | 65 | 66 | 340 | 5.5 | 0.67 |  | 6.17 | 0.23113 | 0.89141 | 54.1053 | 12.5284 | 9.89 | 1576.8347 | 54.825 | 1552.2139 | 15.097 | 50.403 | 0.19622 | [27 empty] | SDS-Incubation time | hours | 24 | 24 | 24 | 0 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-HAA5b, ug/L | 18.263 | 17.9787 | 18.6526 | 18.4546 | SDS-HAA5b, ug/L | 8.4847 | 7.8704 | 9.3263 | 8.8987
|  | Variability of rejection of reference solute (%) | 3 | [14 empty] | SDS-THM4 | mg/L | 105.1 | 100.95 | 103.025 | 4.0281 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-26 | 9:00 | 93 | 22.3 | 66 | 66 | 350 | 5.2 | 0.67 |  | 5.87 | 0.23793 | 0.88586 | 58.6252 | 11.845 | 9.268 | 1518.1396 | 52.8526 | 1496.3696 | 14.544 | 51.456 | 0.18012 | 7.09 |  |  | 33.6 |  |  | 1667.5627 |  | 84.7342 | 1655.4247 | 97.9703 | 0.003 |  |  | 0.37973 |  | 93.4783 | 0.37693 | 99.2041 | [8 empty] | SDS-TOX | mg Cl- /L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOXb, ug Cl- /L | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | SDS-TOXb, ug Cl- /L | #DIV/0! | #VALUE! | #VALUE! | #VALUE!
|  | Standard testing recovery (%) | 15 | [14 empty] | SDS-MCAA* | mg/L | BMRL | 3.37 | 3.37 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-26 | 10:00 | 94 | 22.2 | 65 | 66 | 350 | 5.1 | 0.67 |  | 5.77 | 0.23793 | 0.88388 | 59.6586 | 11.6172 | 9.1167 | 1498.3187 | 52.1772 | 1477.2463 | 14.3561 | 51.1439 | 0.17826 | 7 |  |  | 38.5 |  |  | 1602.4284 |  | 82.508 | 1591.034 | 97.5802 | 0.004 |  |  | 0.3657 |  | 91.3043 | 0.36307 | 98.8983 | [8 empty] | SDS-CHCl3 | mg/L | 1.04 | 2.154 | 1.597 | 69.7558 | --- | 191.3325 | --- | 97.3566 | 189.4435 | 99.157 | SDS-CHCl3 | mg/L | 1.874 | --- | 534.0649 | --- | 96.8981 | 530.4313 | 99.6467 | SDS-CHCl3 | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHCl3 | mg/L | 2.476 | --- | 85.246 | --- | 95.9017 | 84.6784 | 97.076 | SDS-CDb, mg/L | 0.5504 | 0.60815 | 0.5663 | 0.588 | SDS-CDb, mg/L | 0.3478 | 0.47257 | 0.38215 | 0.42903
|  | Standard testing pH | 7 | [14 empty] | SDS-DCAA* | mg/L | 18.73 | 17.96 | 18.345 | 4.1973 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-26 | 11:00 | 95 | 22.3 | 66 | 67 | 350 | 4.9 | 0.57 |  | 5.47 | 0.23793 | 0.8958 | 62.9854 | 11.1617 | 8.7333 | 1625.3474 | 56.6325 | 1603.3853 | 15.5773 | 50.9227 | 0.1715 | 7.02 |  |  | 43 |  |  | 1742.5386 |  | 80.4634 | 1730.6418 | 97.5154 | 0.003 |  |  | 0.41565 |  | 93.4783 | 0.41276 | 99.2732 | [8 empty] | SDS-BDCM | mg/L | 1.094 | 2.15 | 1.622 | 65.1048 | --- | 80.7123 | --- | 93.795 | 79.9249 | 97.9706 | SDS-BDCM | mg/L | 1.573 | --- | 224.9094 | --- | 93.9824 | 223.3845 | 99.2958 | SDS-BDCM | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | TOCb, mg/L | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | TOCb, mg/L | #DIV/0! | #VALUE! | #VALUE! | #VALUE!
|  | Acceptable range of operating pressures | < 600 PSI | [14 empty] | SDS-TCAA* | mg/L | 2.92 | 4 | 3.46 | 31.2139 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-26 | 12:00 | 96 | 22.1 | 66 | 67 | 350 | 4.8 | 0.57 |  | 5.37 | 0.23793 | 0.89385 | 64.1769 | 10.9339 | 8.6058 | 1603.073 | 55.872 | 1581.8542 | 15.3659 | 51.1341 | 0.1683 | 7.03 | 9 | 8.25 | 43.2 | 260 | 1197 | 1709.7842 | -42.8391 | 80.3726 | 1698.3562 | 97.4564 | 0.003 | 0.046 | 0.287 | 0.40811 | -42.197 | 93.4783 | 0.40533 | 99.2599 | [8 empty] | SDS-DBCM | mg/L | 1.205 | 1.882 | 1.5435 | 43.8614 | --- | 41.1451 | --- | 88.8314 | 40.7509 | 96.2123 | SDS-DBCM | mg/L | 2.506 | --- | 105.3605 | --- | 81.8669 | 104.6583 | 97.6055 | SDS-DBCM | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 b, cm-1 | 0.031792 | 0.030986 | 0.032449 | 0.032732 | UV254 b, cm-1 | 0.015305 | 0.013565 | 0.016724 | 0.017337
|  | Acceptable range of operating pH values | pH 2-11 | [14 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-26 | 15:00 | 99 | 22.1 | 69 | 69 | 350 | 4.8 | 0.57 |  | 5.37 | 0.23793 | 0.89385 | 64.1769 | 10.9339 | 8.6058 | 1603.073 | 55.872 | 1581.8542 | 15.3659 | 53.6341 | 0.16045 | [27 empty] | SDS-CHBr3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 2.017 | --- | 7.7715 | --- | 23.8868 | 7.7323 | 73.9145 | SDS-CHBr3 | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Bromideb, ug/L | #DIV/0! | 89.4374 | #VALUE! | #VALUE! | Bromideb, ug/L | #DIV/0! | 65.5776 | #VALUE! | #VALUE!
|  | Typical pressure drop across a single element (psi) | 6 | [14 empty] | SDS-DBAA* | mg/L | 2.66 | 3.74 | 3.2 | 33.75 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-27 | 8:00 | 116 | 24.2 | 68 | 68 | 350 | 4.8 | 4.8 |  | 9.6 | 0.23793 | 0.5 | 35.4583 | 10.9339 | 8.0879 | 425.3744 | 14.8256 | 419.744 | 4.0773 | 63.9227 | 0.12653 | [27 empty] | SDS-THM4 | mg/L | 3.339 | 6.186 | 4.7625 | 59.7795 | --- | 321.7383 | --- | 95.3773 | 318.5826 | 98.5051 | SDS-THM4 | mg/L | 7.97 | --- | 872.1064 | --- | 92.264 | 866.2064 | 99.0799 | SDS-THM4 | mg/L | 0 | --- | 206.05 | --- | 100 | 204.6371 | 100 | SDS-THM4 | mg/L | 2.476 | --- | 146.1174 | --- | 97.5967 | 145.1325 | 98.294 | Alkb, mg/L CaCO3 | 34.6472 | 34.5135 | 34.991 | 34.9176 | Alkb, mg/L CaCO3 | 17.7028 | 17.4139 | 18.4455 | 18.2869
|  | Maximum permissible SDI | 5 | [14 empty] | SDS-BCAA* | mg/L | 7.09 | 8.42 | 7.755 | 17.1502 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-27 | 10:00 | 118 | 24.9 | 67 | 68 | 350 | 4.9 | 4.9 |  | 9.8 | 0.23793 | 0.5 | 34.7143 | 11.1617 | 8.0873 | 425.3784 | 14.8216 | 419.6306 | 4.0768 | 63.4232 | 0.12751 | 6.99 |  |  | 13.4 |  |  | 426.8 |  | 93.9119 | 423.9062 | 96.8389 | 0 | [15 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | T-Hdb, mg/L CaCO3 | 67.4341 | 66.6002 | 68.7845 | 68.0663 | T-Hdb, mg/L CaCO3 | 32.0249 | 30.2234 | 34.9423 | 33.3907
|  | Maximum permissible turbidity (ntu) | 1 | [14 empty] | SDS-TBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-27 | 11:00 | 119 | 25.5 | 65 | 65 | 350 | 4.9 | 4.9 |  | 9.8 | 0.23793 | 0.5 | 34.7143 | 11.1617 | 7.9451 | 425.3784 | 14.8216 | 419.6306 | 4.0768 | 60.9232 | 0.13041 | 7.08 |  |  | 13.8 |  |  | 426.4 |  | 93.7301 | 423.5118 | 96.7415 | 0 | [15 empty] | SDS-DCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Ca-Hdb, mg/L CaCO3 | 56.2175 | 55.5225 | 57.3329 | 56.7341 | Ca-Hdb, mg/L CaCO3 | 26.7067 | 25.2053 | 29.1165 | 27.8228
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | 1000 ppm/hours | [14 empty] | SDS-CDBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-27 | 12:00 | 120 | 25.7 | 66 | 67 | 350 | 4.8 | 4.8 |  | 9.6 | 0.23793 | 0.5 | 35.4583 | 10.9339 | 7.7371 | 425.3744 | 14.8256 | 419.744 | 4.0773 | 62.4227 | 0.12395 | 7.09 | 8.39 | 8.28 | 13.05 | 258 | 493 | 427.15 | 13.357 | 94.0709 | 424.3105 | 96.9244 | 0.001 | 0.044 | 0.09 | 0.091 | -1.1111 | 97.8261 | 0.090383 | 98.8936 | [8 empty] | SDS-TCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | 1: All of the information requested in this field may not be available, but values for all Design | [15 empty] | SDS-DCBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-27 | 15:00 | 123 | 26.3 | 66 | 67 | 350 | 4.9 | 4.8 |  | 9.7 | 0.23793 | 0.50515 | 35.0825 | 11.1617 | 7.7595 | 429.5082 | 14.9655 | 423.7046 | 4.1164 | 62.3836 | 0.12438 | [27 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  | Parameters must be entered in cells E14:E23, since these parameters are used in calculations. | [15 empty] | SDS-HAA5 | mg/L | 24.31 | 29.07 | 26.69 | 17.8344 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-27 | 17:00 | 125 | 26 | 67 | 67 | 350 | 4.9 | 4.8 |  | 9.7 | 0.23793 | 0.50515 | 35.0825 | 11.1617 | 7.8286 | 429.5082 | 14.9655 | 423.7046 | 4.1164 | 62.8836 | 0.12449 | [27 empty] | SDS-DBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Blended Water Quality if HAA5 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if HAA5 Controls the Blend Ratio
[18 empty] | SDS-HAA6 | mg/L | 31.4 | 37.49 | 34.445 | 17.6804 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-28 | 8:00 | 140 | 24.3 | 67 | 67 | 350 | 4.8 | 12.5 |  | 17.3 | 0.23793 | 0.27746 | 19.2312 | 10.9339 | 8.064 | 300.5954 | 10.4767 | 296.6166 | 2.8813 | 64.1187 | 0.12577 | [27 empty] | SDS-BCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-BCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Qp/QT (HAA5), % | -102.323 | -102.323 | -102.323 | -102.323 | Qp/QT (HAA5), % | -1.1615 | -1.1615 | -1.1615 | -1.1615
[18 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-28 | 10:00 | 142 | 24.3 | 66 | 66 | 350 | 4.4 | 11 |  | 15.4 | 0.23793 | 0.28571 | 21.7273 | 10.0227 | 7.392 | 303.8985 | 10.6036 | 300.2114 | 2.9145 | 63.0855 | 0.11717 | 8.12 |  |  | 12.4 |  |  | 303.18 |  | 94.3662 | 301.3522 | 95.8852 | 0.007 |  |  | 0.0616 |  | 84.7826 | 0.061257 | 88.5727 | [8 empty] | SDS-TBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-THM4b, ug/L | NA | NA | NA | NA | SDS-THM4b, ug/L | NA | NA | NA | NA
[18 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-28 | 11:00 | 143 | 23.8 | 66 | 66 | 350 | 4.6 | 11 |  | 15.6 | 0.23793 | 0.29487 | 21.4359 | 10.4783 | 7.8431 | 307.6553 | 10.7287 | 303.7528 | 2.9498 | 63.0502 | 0.12439 | 7.99 |  |  | 11.6 |  |  | 307.2909 |  | 94.7297 | 305.3478 | 96.2011 | 0.003 |  |  | 0.063982 |  | 93.4783 | 0.063581 | 95.2816 | [8 empty] | SDS-CDBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-HAA5b, ug/L | NA | NA | NA | NA | SDS-HAA5b, ug/L | NA | NA | NA | NA
[18 empty] | should be reported if measured. | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-28 | 12:00 | 144 | 24 | 66 | 66 | 350 | 4.8 | 11.2 |  | 16 | 0.23793 | 0.3 | 20.875 | 10.9339 | 8.1358 | 309.8011 | 10.7975 | 305.7004 | 2.9695 | 63.0305 | 0.12908 | 8.03 | 8.98 | 8.92 | 11.8 | 194.1 | 341 | 309.3714 | 9.2752 | 94.6388 | 307.3309 | 96.1605 | 0.002 | 0.044 | 0.063 | 0.064857 | -2.9478 | 95.6522 | 0.064426 | 96.8957 | [8 empty] | SDS-DCBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TOXb, ug Cl- /L | NA | NA | NA | NA | SDS-TOXb, ug Cl- /L | NA | NA | NA | NA
[45 empty] | 1998-07-28 | 15:00 | 147 | 26.4 | 66 | 66 | 350 | 4.5 | 11.2 |  | 15.7 | 0.23793 | 0.28662 | 21.293 | 10.2505 | 7.105 | 304.2687 | 10.6136 | 300.4931 | 2.9177 | 63.0823 | 0.11263 | [27 empty] | SDS-HAA5 | mg/L | 0 | 0 | 0 | #DIV/0! | --- | 86.0968 | --- | 100 | 85.2396 | 100 | SDS-HAA5 | mg/L | 0 | --- | 242.6364 | --- | 100 | 240.9797 | 100 | SDS-HAA5 | mg/L | 0 | --- | 53.38 | --- | 100 | 53.014 | 100 | SDS-HAA5 | mg/L | 0 | --- | 38.1286 | --- | 100 | 37.8671 | 100 | SDS-CDb, mg/L | NA | NA | NA | NA | SDS-CDb, mg/L | NA | NA | NA | NA
[45 empty] | 1998-07-28 | 17:00 | 149 | 26.3 | 66 | 66 | 350 | 4.8 | 11.5 |  | 16.3 | 0.23793 | 0.29448 | 20.4724 | 10.9339 | 7.6011 | 307.4946 | 10.7171 | 303.4245 | 2.9474 | 63.0526 | 0.12055 | [27 empty] | SDS-HAA6 | mg/L | 0 | 0 | 0 | #DIV/0! | --- | 111.1129 | --- | 100 | 110.0067 | 100 | SDS-HAA6 | mg/L | 0 | --- | 313.1364 | --- | 100 | 310.9984 | 100 | SDS-HAA6 | mg/L | 0 | --- | 68.89 | --- | 100 | 68.4176 | 100 | SDS-HAA6 | mg/L | 0 | --- | 49.2071 | --- | 100 | 48.8697 | 100 | TOCb, mg/L | NA | NA | NA | NA | TOCb, mg/L | NA | NA | NA | NA
[45 empty] | 1998-07-29 | 14:00 | 170 | 24 | 65 | 66 | 350 | 7.2 | 11 | X | 18.2 | 0.23793 | 0.3956 | 18.2308 | 16.4008 | 12.2037 | 356.0964 | 12.3277 | 349.0246 | 3.4023 | 62.0977 | 0.19653 | [27 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | UV254 b, cm-1 | NA | NA | NA | NA | UV254 b, cm-1 | NA | NA | NA | NA
[45 empty] | 1998-07-29 | 16:00 | 172 | 23.7 | 65 | 65 | 350 | 7.4 | 16.4 |  | 23.8 | 0.23793 | 0.31092 | 13.7059 | 16.8564 | 12.6545 | 314.5034 | 10.8817 | 308.084 | 3.0041 | 61.9959 | 0.20412 | [27 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | Bromideb, ug/L | NA | NA | NA | NA | Bromideb, ug/L | NA | NA | NA | NA
[45 empty] | 1998-07-29 | 17:00 | 173 | 24.2 | 66 | 66 | 350 | 7.8 | 16.8 |  | 24.6 | 0.23793 | 0.31707 | 13.2276 | 17.7675 | 13.1428 | 317.1995 | 10.9626 | 310.3748 | 3.0282 | 62.9718 | 0.20871 | [66 empty] | Alkb, mg/L CaCO3 | NA | NA | NA | NA | Alkb, mg/L CaCO3 | NA | NA | NA | NA
[45 empty] | 1998-07-30 | 7:00 | 187 | 23.1 | 65 | 66 | 350 | 7.2 | 16.4 |  | 23.6 | 0.23793 | 0.30508 | 13.8305 | 16.4008 | 12.5328 | 311.9875 | 10.8007 | 305.7916 | 2.9809 | 62.5191 | 0.20046 | [66 empty] | T-Hdb, mg/L CaCO3 | NA | NA | NA | NA | T-Hdb, mg/L CaCO3 | NA | NA | NA | NA
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Ca-Hdb, mg/L CaCO3 | NA | NA | NA | NA | Ca-Hdb, mg/L CaCO3 | NA | NA | NA | NA
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Notes: |  |  |  |  | Notes:
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to |  |  |  |  | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | determine the percentage of total flow that must be treated by the membrane process to meet the |  |  |  |  | determine the percentage of total flow that must be treated by the membrane process to meet the
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Stage 1 DBP MCLs. |  |  |  |  | Stage 2 DBP MCLs.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | A 10% factor of safety has been applied all the MCLs. i.e., 72 / 54 mg/L for THM4 and HAA5. |  |  |  |  | A 10% factor of safety has been applied all the MCLs. i.e., 36 / 27 mg/L for THM4 and HAA5.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for |  |  |  |  | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | both parameters and the maximum (Qp/QT) ratio controls the design. |  |  |  |  | both parameters and the maximum (Qp/QT) ratio controls the design.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. |  |  |  |  | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. |  |  |  |  | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. |  |  |  |  | The subscript "b" refers to the blended water quality for a given blend ratio.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL. |  |  |  |  | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. |  |  |  |  | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Note on X24: Alison Gusses: High precision incubator was used for SDS testing
Note on CY29: Alison Gusses: High precision incubator was used for SDS testing
Note on DL29: Alison Gusses: High precision incubator was used for SDS testing
Note on DQ10: C. Rice: Consultant verified all water quality parameters for the 90% recovery run. The membrane appears to have been stable before the composite sample was taken. All of the measurements are low biased relative to the calculated mass balance. The consultant stated that there is no direct cause known for the high MB closure errors; perhaps an error in recording flow-rate measurements and/or membrane fouling occurred.
Note on DV29: Alison Gusses: High precision incubator was used for SDS testing
Note on EF29: Alison Gusses: High precision incubator was used for SDS testing

## BW30. 3rd Quarter
FIELD-SET 3: 3rd QUARTER RBSMT RESULTS (FILE: rbsmt-2.xls)
Field 3-1: PWS And Treatment Plant Data |  | Field 3-2: Manufacturer Reported Membrane Characteristics1 |  | Field 3-3: RBSMT Design Parameters | [8 empty] | Field 3-4: Foulants And Fouling Indices1 |  | Field 3-5: Pretreatment Used Prior To Membranes1 |  |  | Field 3-6: Feed Water Quality After Pretreatment | [5 empty] | Field 3-7: Membrane Setting Data | [20 empty] | Field 3-8: Membrane Performance Data During Operation With The Test Water | [16 empty] | Field 3-8: Membrane Performance Data During Operation With The Test Water (continued) | [19 empty] | Field 3-8: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 3-9: Permeate And Concentrate Water Quality For Run 1 | [11 empty] | Field 3-10: Permeate And Concentrate Water Quality For Run 2 | [8 empty] | Field 3-11: Permeate And Concentrate Water Quality For Run 3 | [8 empty] | Field 3-12: Permeate And Concentrate Water Quality For Run 4 | [8 empty] | Field 3-13: Blending Calculations For Stage 1 D-DBP MCLs |  |  |  |  | Field 3-14: Blending Calculations For Proposed Stage 2 D-DBP MCLs |  |  |  |  | Field 3-15: Membrane Cost Parameters
|  | General Information |  | Input Design Parameters | [8 empty] | Parameters Evaluated Prior to Pretreatment | [80 empty] | Operating Parameters During Sample Collection | [11 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Feed and Permeate Water Quality Parameters |  |  |  |  | Feed and Permeate Water Quality Parameters |  |  |  |  | General Cost Parameters
PWS Name | Water District No. 1 of Johnson County, Kansas | Membrane manufacturer | Dow-Filmtec | [5 empty] | Active membrane area in bench-scale cell, Acell (ft2) | 0.167 |  |  | Alkalinity (mg/L as CaCO3) | 151 | Process | Description | Scale | Parameter | Units | CF-1 | CF-2 | Average | RPD |  |  |  | Average TDS rejection (decimal fraction) | 0.98 | [5 empty] | TDS concentration of setting solution (mg/L) | 0.8 | [12 empty] | Average bulk TDS rejection (decimal fraction) | 0.96079 | [45 empty] | Recovery during sample collection (decimal) | 0.71 | [10 empty] | Recovery during sample collection (decimal) | 0.89 | [7 empty] | Recovery during sample collection (decimal) | 0.51 | [7 empty] | Recovery during sample collection (decimal) | 0.29 | [8 empty] | RUN ID # |  |  |  |  | RUN ID # |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | KS200910 | Membrane trade name | BW30-XLE | [5 empty] | Active width of membrane in the bench-scale cell, wcell (ft) | 0.333 |  |  | Calcium Hardness (mg/L as CaCO3) | 134 | Presedimentation | 3 Basins | Full-scale | Sampling date | MM/DD/YY | 1998-10-21 | 1998-10-28 | --- | --- | [71 empty] | Feed flow rate during sample collection (mL/min) | 9.3 | [10 empty] | Feed flow rate during sample collection (mL/min) | 6.53 | [7 empty] | Feed flow rate during sample collection (mL/min) | 12.4 | [7 empty] | Feed flow rate during sample collection (mL/min) | 21.8 | [6 empty] | Parameter | 1 | 2 | 3 | 4 | Parameter | 1 | 2 | 3 | 4 | Capital Recovery Interest Rate (%) | 5
Water Industry Data Base Number (optional) | NA | Molecular weight cutoff (Daltons) | 100 | [5 empty] | Average yearly temperature of feed water, TavgoC (oC) | 14 |  |  | LSI | 0.58 | Softening | Lime, 190 mg/L as Ca(OH)2 | Bench-scale | Sampling time | hh:mm | 12:00 | 12:00 | --- | --- | Date | Time | Setting time | Influent | PI | PC | QI | Qp | QW | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) | Date | Time | Operation time | Influent | PI | PC | QI | Qp | QW | Cleaning Event | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1) | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Influent flow rate during sample collection (mL/min) | 350 | [10 empty] | Influent flow rate during sample collection (mL/min) | 350 | [7 empty] | Influent flow rate during sample collection (mL/min) | 350 | [7 empty] | Influent flow rate during sample collection (mL/min) | 350 | [6 empty] | SDS-THM4F, ug/L | 80.86 | 80.86 | 80.86 | 80.86 | SDS-THM4F, ug/L | 80.86 | 80.86 | 80.86 | 80.86 | Capital Recovery Period (years) | 20
|  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide | [5 empty] | Approximate feed water TDS, TDSF (mg/L) | 322 |  |  | Dissolved iron (mg/L) |  | Coagulation | Alum: Al2(SO4)3.14 H2O, 15 mg/L | Bench-scale | Operation time | hh.hh | 2 | 150 | --- | --- | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | Indicate with "X" | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) | [39 empty] | SDS-THM4p, ug/L | 4.8 | 6.13 | 1.24 | 1.58 | SDS-THM4p, ug/L | 4.8 | 6.13 | 1.24 | 1.58 | Overhead & Profit Factor (% of construction costs) | 15
Official ICR Contact Person |  | Membrane construction (e.g., thin-film composite) | Thin Film | [5 empty] | Manufacturer reported TDS rejection, RejTDS (decimal fraction) | 0.98 |  |  | Total iron (mg/L) |  | Sedimentation | Gravity settling in test drums | Bench-scale | pH | --- | 9.61 | 8.02 | 8.815 | 18.0374 | 1998-10-19 | 10:00 | 0 | 21.7 | 51 | 51 | 350 | 8.3 | 3.2 | 11.5 | 0.23793 | 0.72174 | 29.4348 | 18.9065 | 15.0579 | 2.7364 | 0.053455 | 2.6727 | 0.026511 | 50.9735 | 0.29541 | 1998-10-21 | 10:00 | 0 | [7 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [27 empty] | Permeate and Concentrate Water Quality | [11 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | SDS-HAA5F, ug/L | 26.635 | 26.635 | 26.635 | 26.635 | SDS-HAA5F, ug/L | 26.635 | 26.635 | 26.635 | 26.635 | Special Sitework Factor (% of construction costs) | 0
Mailing Address |  | Membrane hydrophobicity | Hydrophobic | [5 empty] | Temperature normalized MTCW (gfd/psi) | 0.16688 |  |  | Dissolved aluminum (mg/L) |  | Recarbonation | CO2 gas added to pH 9.4 | Bench-scale | Temperature | oC | 21.7 | 25.5 | 23.6 | 16.1017 | 1998-10-19 | 12:00 | 2 | 21.9 | 52 | 52 | 350 | 8.6 | 3.6 | 12.2 | 0.23793 | 0.70492 | 27.6885 | 19.5899 | 15.5102 | 2.5903 | 0.050559 | 2.5279 | 0.025086 | 51.9749 | 0.29842 | 1998-10-21 | 12:00 | 2 | 21.3 | 54 | 55 | 350 | 7 | 3.7 |  | 10.7 | 0.23793 | 0.65421 | 31.7103 | 15.9452 | 12.8505 | 513.0052 | 19.7272 | 503.1397 | 4.8835 | 49.6165 | 0.259 | 9.34 | 9.61 | 9.44 | 26.7 | 178.6 | 489 | 499.8135 | -2.2114 | 85.9695 | 495.0824 | 94.607 | 0.004 | 0.043 | 0.12 | 0.10955 | 8.705 | 90.1235 | 0.1085 | 96.3133 | [8 empty] | Parameter | Units | Cp-1 | Cp-1 (dup) | Average | RPD | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | SDS-HAA5p, ug/L | 0 | 1.09 | 0 | 0 | SDS-HAA5p, ug/L | 0 | 1.09 | 0 | 0 | Construction Contingencies (% of construction costs) | 15
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Slightly Negative | [9 empty] | Total aluminum (mg/L) |  | Cartridge filtration | 1 um size exclusion | Bench-scale | Alkalinity | mg/L as CaCO3 | 61.5 | 47.8 | 54.65 | 25.0686 | 1998-10-19 | 14:00 | 4 | 22.4 | 52 | 52 | 350 | 8.8 | 3.6 | 12.4 | 0.23793 | 0.70968 | 27.2258 | 20.0454 | 15.6381 | 2.6301 | 0.051306 | 2.5653 | 0.025464 | 51.9745 | 0.30088 | 1998-10-21 | 14:00 | 4 | 21 | 54 | 54 | 350 | 6.9 | 3.1 |  | 10 | 0.23793 | 0.69 | 34 | 15.7174 | 12.7797 | 565.4588 | 21.7504 | 554.74 | 5.3835 | 48.6165 | 0.26287 | [27 empty] | Sampling date | MM/DD/YY | 1998-10-24 | 1998-10-24 | --- | --- | 1998-10-24 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-10-25 | 1998-10-25 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-10-26 | 1998-10-26 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-12-27 | 1998-12-27 | --- | --- | --- | --- | --- | SDS-TOXF, ug Cl- /L | 165 | 165 | 165 | 165 | SDS-TOXF, ug Cl- /L | 165 | 165 | 165 | 165 | Engineering Fee Factor (% of construction costs) | 15
Phone Number |  |  |  | Experimental Design1,2 | [8 empty] | Fluoride (mg/L) |  | Antiscalant | 4 mg/L Hypersperse 400UL | Bench-scale | Total dissolved solids | mg/L | 178.6 | 202 | 190.3 | 12.2964 | 1998-10-19 | 16:30 | 6.5 | 22 | 53 | 54 | 350 | 8.8 | 3.6 | 12.4 | 0.23793 | 0.70968 | 27.2258 | 20.0454 | 15.8241 | 2.6301 | 0.051306 | 2.5653 | 0.025464 | 53.4745 | 0.29592 | 1998-10-21 | 17:00 | 7 | 21.6 | 55 | 55 | 350 | 6.8 | 2.9 |  | 9.7 | 0.23793 | 0.70103 | 35.0825 | 15.4897 | 12.3731 | 583.8466 | 22.464 | 572.9397 | 5.5593 | 49.4407 | 0.25026 | [27 empty] | Sampling time | hh:mm | 12:00 | 12:00 | --- | --- | 12:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 12:30 | 12:30 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 12:30 | 12:30 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 12:30 | 12:30 | --- | --- | --- | --- | --- | SDS-TOXp, ug Cl- /L | 36.5 | BMRL | BMRL | BMRL | SDS-TOXp, ug Cl- /L | 36.5 | BMRL | BMRL | BMRL | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920
FAX Number |  | Design Parameters |  | ID# | Recovery | FW-design | Dp | PI | QI-cell | Qp | QF | QW | Phosphate (mg/L) |  |  |  |  | Total hardness | mg/L as CaCO3 | 90.5 | 84.8 | 87.65 | 6.5031 | 1998-10-20 | 8:00 | 22 | 21.2 | 53 | 54 | 350 | 8.7 | 3.6 | 12.3 | 0.23793 | 0.70732 | 27.4553 | 19.8176 | 16.0186 | 2.6102 | 0.050933 | 2.5466 | 0.025275 | 53.4747 | 0.29955 | 1998-10-22 | 7:00 | 21 | 21.1 | 55 | 55 | 350 | 6.6 | 3 |  | 9.6 | 0.23793 | 0.6875 | 35.4583 | 15.0341 | 12.188 | 561.4117 | 21.6129 | 551.2326 | 5.3471 | 49.6529 | 0.24546 | 9.06 |  |  | 23.7 |  |  | 556.82 |  | 87.546 | 551.7934 | 95.7049 | 0.002 |  |  | 0.1252 |  | 95.0617 | 0.12404 | 98.3876 | [8 empty] | Operation time | hh.hh | 74 | 74 | --- | --- | 74 | --- | --- | --- | --- | --- | Operation time | hh.hh | 98.5 | 98.5 | --- | --- | --- | --- | --- | Operation time | hh.hh | 122.5 | 122.5 | --- | --- | --- | --- | --- | Cumulative time | hr | 146.5 | 146.5 | --- | --- | --- | --- | --- | SDS-CDF, mg/L | 2.715 | 2.715 | 2.715 | 2.715 | SDS-CDF, mg/L | 2.715 | 2.715 | 2.715 | 2.715 | 1998 Producers Price Index (PPI base year 1967 = 100) | 370
E-Mail Address (optional) |  | Design flux, FW (gfd) | 30(15 ave) |  | (decimal) | (gfd) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | Sulfate (mg/L) |  |  |  |  | Calcium hardness | mg/L as CaCO3 | 76.9 | 71.4 | 74.15 | 7.4174 | 1998-10-20 | 12:00 | 26 | 21.7 | 53 | 54 | 350 | 8.8 | 3.6 | 12.4 | 0.23793 | 0.70968 | 27.2258 | 20.0454 | 15.965 | 2.6301 | 0.051306 | 2.5653 | 0.025464 | 53.4745 | 0.29855 | 1998-10-22 | 9:00 | 23 | 21.4 | 55 | 55 | 350 | 6.6 | 2.7 |  | 9.3 | 0.23793 | 0.70968 | 36.6344 | 15.0341 | 12.0804 | 599.0997 | 23.0638 | 588.2373 | 5.706 | 49.294 | 0.24507 | [27 empty] | pH | --- | 8 | 7.97 | 7.985 | 0.3757 | 8.62 | --- | --- | --- | --- | --- | pH | --- | 8.43 | 8.86 | --- | --- | --- | --- | --- | pH | --- | 7.03 | 8.46 | --- | --- | --- | --- | --- | pH | --- | 7.74 | 8.93 | --- | --- | --- | --- | --- | SDS-CDp, mg/L | 0.334 | 0.54 | 0.296 | 0.32 | SDS-CDp, mg/L | 0.334 | 0.54 | 0.296 | 0.32 | Labor Rate + Fringe ($/work-hour) | 17
|  | Net driving pressure at the design flux, NDP (psi) | 130 | 1 | 0.7 | 15 | 10.5831 | 100.4684 | 335.6684 | 6.5843 | 9.4062 | 2.8219 | Calcium (mg/L) | 54 |  |  |  | Turbidity | ntu | 0.08 | 0.12 | 0.1 | 40 | 1998-10-20 | 14:00 | 28 | 22 | 53 | 54 | 350 | 8.7 | 3.8 | 12.5 | 0.23793 | 0.696 | 27 | 19.8176 | 15.6442 | 2.519 | 0.049153 | 2.4577 | 0.024392 | 53.4756 | 0.29255 | 1998-10-22 | 11:00 | 25 | 21.4 | 56 | 56 | 350 | 6.6 | 2.7 |  | 9.3 | 0.23793 | 0.70968 | 36.6344 | 15.0341 | 12.0804 | 599.0997 | 23.0638 | 588.2373 | 5.706 | 50.294 | 0.2402 | 9.01 | 9.31 | 9.19 | 24.9 | 178 | 571 | 594.6111 | -4.135 | 86.9154 | 589.2395 | 95.7742 | 0.002 | 0.042 | 0.133 | 0.13461 | -1.2114 | 95.0617 | 0.13336 | 98.5003 | [8 empty] | Temperature | oC | 22.7 | 22.7 | 22.7 | 0 | 22.7 | --- | --- | --- | --- | --- | Temperature | oC | 22.5 | 22.5 | --- | --- | --- | --- | --- | Temperature | oC | 23.7 | 23.7 | --- | --- | --- | --- | --- | Temperature | oC | 25.5 | 25.5 | --- | --- | --- | --- | --- | TOCF, mg/L | 2.45 | 2.45 | 2.45 | 2.45 | TOCF, mg/L | 2.45 | 2.45 | 2.45 | 2.45 | Labor Overhead Factor (% of labor) | 42
Technical ICR Contact Person |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.231 | 2 | 0.9 | 15 | 31.6204 | 121.5057 | 335.6684 | 6.5843 | 7.3159 | 0.73159 | Barium (mg/L) |  |  |  |  | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! | 1998-10-20 | 17:00 | 31 | 21.9 | 53 | 53 | 350 | 8.7 | 3.8 | 12.5 | 0.23793 | 0.696 | 27 | 19.8176 | 15.6905 | 2.519 | 0.049153 | 2.4577 | 0.024392 | 52.9756 | 0.29618 | 1998-10-22 | 13:00 | 27 | 21.7 | 56 | 56 | 350 | 6.5 | 2.8 |  | 9.3 | 0.23793 | 0.69892 | 36.6344 | 14.8063 | 11.7923 | 580.2014 | 22.3425 | 569.8412 | 5.5268 | 50.4732 | 0.23364 | [27 empty] | Alkalinity | mg/L as CaCO3 | 5.1 | 4.7 | 4.9 | 8.1633 | 194.5 | 176.4517 | 9.2793 | 91.0339 | 174.8335 | 97.1973 | Alkalinity | mg/L as CaCO3 | 7.2 | 268.5 | 438.5636 | -63.3384 | 86.8253 | 434.9823 | 98.3448 | Alkalinity | mg/L as CaCO3 | 3 | 111.5 | 108.4082 | 2.7729 | 94.5105 | 107.4559 | 97.2082 | Alkalinity | mg/L as CaCO3 | 2.2 | 61.1 | 76.0732 | -24.5061 | 95.9744 | 75.4061 | 97.0825 | TOCp, mg/L | #DIV/0! | BMRL | BMRL | BMRL | TOCp, mg/L | #DIV/0! | BMRL | BMRL | BMRL | Electric Rate ($/kW-h) | 0.06
Mailing Address |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | 3 | 0.5 | 15 | 6.3756 | 96.2609 | 335.6684 | 6.5843 | 13.1686 | 6.5843 | Strontium (mg/L) |  |  |  |  | Total organic carbon | mg/L | 2.5 | 2.4 | 2.45 | 4.0816 | 1998-10-21 | 8:00 | 46 | 21.1 | 53 | 53 | 350 | 8.6 | 3.7 | 12.3 | 0.23793 | 0.69919 | 27.4553 | 19.5899 | 15.8813 | 2.544 | 0.049655 | 2.4828 | 0.024637 | 52.9754 | 0.29979 | 1998-10-22 | 15:00 | 29 | 22.5 | 56 | 56 | 350 | 6.8 | 2.8 |  | 9.6 | 0.23793 | 0.70833 | 35.4583 | 15.4897 | 12.0483 | 596.7007 | 22.9585 | 585.5537 | 5.6817 | 50.3183 | 0.23944 | [27 empty] | Total dissolved solids | mg/L | 23.5 | 24.8 | 24.15 | 5.383 | 592 | 597.081 | -0.85828 | 87.3095 | 591.6767 | 95.9184 | Total dissolved solids | mg/L | 38.4 | 1001 | 1419.3091 | -41.7891 | 79.8213 | 1407.8442 | 97.2724 | Total dissolved solids | mg/L | 13.6 | 388 | 374.2122 | 3.5535 | 92.8534 | 370.9544 | 96.3338 | Total dissolved solids | mg/L | 10.6 | 266 | 263.6986 | 0.86519 | 94.4298 | 261.4127 | 95.9451 | UV254 F, cm-1 | 0.0405 | 0.0405 | 0.0405 | 0.0405 | UV254 F, cm-1 | 0.0405 | 0.0405 | 0.0405 | 0.0405 | Fuel Oil Rate ($/gal) | NA
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 400 | 4 | 0.3 | 15 | 4.5724 | 94.4577 | 335.6684 | 6.5843 | 21.9477 | 15.3634 | Reactive silica (mg/L as SiO2) |  |  |  |  | UV254 | cm-1 | 0.043 | 0.038 | 0.0405 | 12.3457 | 1998-10-21 | 10:00 | 48 | 21.8 | 53 | 53 | 350 | 8.5 | 3.7 | 12.2 | 0.23793 | 0.69672 | 27.6885 | 19.3621 | 15.3752 | 2.5246 | 0.04929 | 2.4645 | 0.024453 | 52.9755 | 0.29023 | 1998-10-22 | 17:00 | 31 | 22.1 | 56 | 56 | 350 | 6.8 | 2.8 |  | 9.6 | 0.23793 | 0.70833 | 35.4583 | 15.4897 | 12.1916 | 596.7007 | 22.9585 | 585.5537 | 5.6817 | 50.3183 | 0.24229 | 8.76 |  |  | 25.7 |  |  | 590.0429 |  | 86.495 | 584.5607 | 95.6035 | 0.002 |  |  | 0.134 |  | 95.0617 | 0.13272 | 98.493 | [8 empty] | Total hardness | mg/L as CaCO3 | 2.8 | 2.8 | 2.8 | 0 | 285.5 | 295.3862 | -3.4628 | 96.8055 | 292.6263 | 99.0431 | Total hardness | mg/L as CaCO3 | 6.9 | 533.6 | 740.9909 | -38.8664 | 92.1278 | 734.8962 | 99.0611 | Total hardness | mg/L as CaCO3 | 1.4 | 171 | 177.4204 | -3.7546 | 98.4027 | 175.8302 | 99.2038 | Total hardness | mg/L as CaCO3 | 1.2 | 111.2 | 122.9606 | -10.576 | 98.6309 | 121.8609 | 99.0153 | UV254 p, cm-1 | 0.004 | 0.002 | 0.001 | 0.001 | UV254 p, cm-1 | 0.004 | 0.002 | 0.001 | 0.001 | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Purchase price for an equivalent 8" x 40 " element ($) | 700 | 1: For experimental matrix see Table 4-2 in Part 3 of the ICR Treatment Studies Manual. | [8 empty] | Turbidity (ntu) | 1.5 |  |  |  | SUVA | L/(mg*m) | 1.72 | 1.5833 | 1.6517 | 8.2745 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-23 | 7:00 | 45 | 21.1 | 56 | 56 | 350 | 6.4 | 2.7 |  | 9.1 | 0.23793 | 0.7033 | 37.4615 | 14.5785 | 11.8187 | 587.7202 | 22.6383 | 577.3873 | 5.5992 | 50.4008 | 0.23449 | 9.24 |  |  | 23 |  |  | 586.863 |  | 87.9138 | 581.7076 | 96.0461 | 0.001 |  |  | 0.13413 |  | 97.5309 | 0.13291 | 99.2476 | [8 empty] | Calcium hardness | mg/L as CaCO3 | 2.3 | 2.3 | 2.3 | 0 | 247.5 | 250.0586 | -1.0338 | 96.8982 | 247.7215 | 99.0715 | Calcium hardness | mg/L as CaCO3 | 6.2 | 433.7 | 623.9273 | -43.8615 | 91.6386 | 618.7986 | 98.9981 | Calcium hardness | mg/L as CaCO3 | 1.1 | 143.1 | 150.1816 | -4.9487 | 98.5165 | 148.8348 | 99.2609 | Calcium hardness | mg/L as CaCO3 | 1 | 92.6 | 104.0282 | -12.3414 | 98.6514 | 103.0977 | 99.03 | BromideF, ug/L | 77.5 | 77.5 | 77.5 | 77.5 | BromideF, ug/L | 77.5 | 77.5 | 77.5 | 77.5 | Current Process Water Rate ($/1000 gal) | 0.375
FAX Number |  | Maximum flow rate to the 8" x 40" element, QI, max (gpm) | 70 | 2: Flow rates and pressures may need to be adjusted in order to obtain the desired operating conditions. | [8 empty] | SDI |  |  |  |  | Bromide | mg/L | 75 | 80 | 77.5 | 6.4516 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-23 | 9:00 | 47 | 21.6 | 56 | 56 | 350 | 6.4 | 2.7 |  | 9.1 | 0.23793 | 0.7033 | 37.4615 | 14.5785 | 11.6453 | 587.7202 | 22.6383 | 577.3873 | 5.5992 | 50.4008 | 0.23105 | [27 empty] | Turbidity | ntu | 0.07 | 0.09 | 0.08 | 25 | 0.15 | 0.14897 | 0.68966 | 20 | 0.14831 | 46.0607 | Turbidity | ntu | 0.06 | 0.25 | 0.42364 | -69.4545 | 40 | 0.42062 | 85.7353 | Turbidity | ntu | 0.06 | 0.16 | 0.14163 | 11.4796 | 40 | 0.1409 | 57.4151 | Turbidity | ntu | 0.07 | 0.11 | 0.11225 | -2.0487 | 30 | 0.11187 | 37.4284 | Bromidep, ug/L | #DIV/0! | 32 | BMRL | BMRL | Bromidep, ug/L | #DIV/0! | 32 | BMRL | BMRL | Modifications to Existing Plant (% of construction costs) | 46
E-Mail Address (optional) |  | Minimum flow rate to the 8" x 40" element, QI, min (gpm) | 18.8 | [9 empty] | MFI |  |  |  |  | SDS-Cl2 dose | mg/L | 3.64 | 3.64 | 3.64 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-23 | 11:00 | 49 | 21.8 | 56 | 56 | 350 | 6.4 | 2.7 |  | 9.1 | 0.23793 | 0.7033 | 37.4615 | 14.5785 | 11.5766 | 587.7202 | 22.6383 | 577.3873 | 5.5992 | 50.4008 | 0.22969 | 9.26 | 9.55 | 9.42 | 23 | 212 | 561 | 586.863 | -4.6102 | 87.9138 | 581.7076 | 96.0461 | 0.001 | 0.04 | 0.132 | 0.13413 | -1.6134 | 97.5309 | 0.13291 | 99.2476 | [8 empty] | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! | BMRL | #DIV/0! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | BMRL | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | BMRL | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | BMRL | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | AlkF, mg/L CaCO3 | 54.65 | 54.65 | 54.65 | 54.65 | AlkF, mg/L CaCO3 | 54.65 | 54.65 | 54.65 | 54.65
|  | Total width of all membrane envelopes in the 8" x 40" element, w (ft) | 70.6 | [9 empty] | MPFI |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | SDS-Free Cl2 residual | mg/L | 1.02 | 0.83 | 0.925 | 20.5405 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-23 | 13:00 | 51 | 22.1 | 56 | 56 | 350 | 6.4 | 2.8 |  | 9.2 | 0.23793 | 0.69565 | 37.0435 | 14.5785 | 11.4744 | 574.6752 | 22.1359 | 564.5716 | 5.4749 | 50.5251 | 0.2271 | [27 empty] | Total organic carbon | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | 6.8 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L | BMRL | 11 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 4.7 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 3.4 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkp, mg/L CaCO3 | 4.9 | 7.2 | 3 | 2.2 | Alkp, mg/L CaCO3 | 4.9 | 7.2 | 3 | 2.2
Plant Name | Facility 1 | Feed spacer thickness in the 8" x 40" element, T (ft) | 0.0026 | [9 empty] | Bromide (mg/L) | 79 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | SDS-Cl2 demand | mg/L | 2.62 | 2.81 | 2.715 | 6.9982 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-23 | 15:00 | 53 | 22.4 | 56 | 56 | 350 | 6.5 | 2.8 |  | 9.3 | 0.23793 | 0.69892 | 36.6344 | 14.8063 | 11.5508 | 580.2014 | 22.3425 | 569.8412 | 5.5268 | 50.4732 | 0.22885 | [27 empty] | UV254 | cm-1 | 0.005 | 0.003 | 0.004 | 50 | 0.134 | 0.12986 | 3.088 | 90.1235 | 0.12867 | 96.8914 | UV254 | cm-1 | 0.002 | 0.306 | 0.352 | -15.0327 | 95.0617 | 0.34909 | 99.4271 | UV254 | cm-1 | 0.001 | 0.087 | 0.081612 | 6.1928 | 97.5309 | 0.080884 | 98.7637 | UV254 | cm-1 | 0.001 | 0.057 | 0.056634 | 0.64245 | 97.5309 | 0.056131 | 98.2185 | T-HdF, mg/L CaCO3 | 87.65 | 87.65 | 87.65 | 87.65 | T-HdF, mg/L CaCO3 | 87.65 | 87.65 | 87.65 | 87.65
Treatment Plant Category | CS/SOFT | [11 empty] | TOC (mg/L) | 3.6 | is to list the pretreatment processes used in this particular RBSMT run. |  |  | SDS-Chlorination temp. | oC | 20 | 19.8 | 19.9 | 1.005 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-23 | 17:00 | 55 | 22.5 | 56 | 56 | 350 | 6.6 | 2.8 |  | 9.4 | 0.23793 | 0.70213 | 36.234 | 15.0341 | 11.6939 | 585.7143 | 22.5485 | 575.0946 | 5.5786 | 50.4214 | 0.23192 | 9.24 |  |  | 23 |  |  | 584.65 |  | 87.9138 | 579.3544 | 96.0301 | 0.001 |  |  | 0.13361 |  | 97.5309 | 0.13236 | 99.2445 | [8 empty] | SUVA | L/(mg*m) | NR | NR | #DIV/0! | #VALUE! | 1.9706 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 2.7818 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 1.8511 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 1.6765 | --- | --- | --- | --- | --- | T-Hdp, mg/L CaCO3 | 2.8 | 6.9 | 1.4 | 1.2 | T-Hdp, mg/L CaCO3 | 2.8 | 6.9 | 1.4 | 1.2
Process Train Name | Coagulation/Sedimentation/Softening | Additional Information | [10 empty] | pH | 8.03 |  |  |  | SDS-Chlorination temp. | --- | 9.5 | 9.5 | 9.5 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-24 | 7:00 | 69 | 21.3 | 56 | 56 | 350 | 6.4 | 2.8 |  | 9.2 | 0.23793 | 0.69565 | 37.0435 | 14.5785 | 11.749 | 574.6752 | 22.1359 | 564.5716 | 5.4749 | 50.5251 | 0.23254 | 8.51 |  |  | 23 |  |  | 572.7 |  | 87.9138 | 567.6742 | 95.9484 | 0.003 |  |  | 0.12621 |  | 92.5926 | 0.12509 | 97.6017 | [8 empty] | Bromide | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | Bromide | mg/L | 32 | --- | 445.6364 | --- | 58.7097 | 442.2022 | 92.7635 | Bromide | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Bromide | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Ca-HdF, mg/L CaCO3 | 74.15 | 74.15 | 74.15 | 74.15 | Ca-HdF, mg/L CaCO3 | 74.15 | 74.15 | 74.15 | 74.15
ICR Treatment Plant Identification Number | 381 | Design cross-flow velocity (fps) | [10 empty] | Total Hardness (mg/L as CaCO3) | 182 |  |  |  | SDS-Incubation time | hours | 31 | 31 | 31 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-24 | 9:00 | 71 | 21.3 | 56 | 56 | 350 | 6.4 | 2.8 |  | 9.2 | 0.23793 | 0.69565 | 37.0435 | 14.5785 | 11.749 | 574.6752 | 22.1359 | 564.5716 | 5.4749 | 50.5251 | 0.23254 | [27 empty] | SDS-Cl2 dose | mg/L | 1 | 1 | 1 | 0 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1.5 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1 | --- | --- | --- | --- | --- | --- | Ca-Hdp, mg/L CaCO3 | 2.3 | 6.2 | 1.1 | 1 | Ca-Hdp, mg/L CaCO3 | 2.3 | 6.2 | 1.1 | 1
PWSID Number of Plant (if assigned) | KS200910 | Required influent flow to permeate flow rate ratio, QI:Qp | 6.7 | [9 empty] | UV254 | 0.0987 |  |  |  | SDS-TOX | mg Cl- /L | 170 | 160 | 165 | 6.0606 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-24 | 11:00 | 73 | 21.7 | 56 | 56 | 350 | 6.6 | 2.7 |  | 9.3 | 0.23793 | 0.70968 | 36.6344 | 15.0341 | 11.9738 | 599.0997 | 23.0638 | 588.2373 | 5.706 | 50.294 | 0.23808 | 8.6 | 8.98 | 8.86 | 23.2 | 182 | 594 | 598.7667 | -0.80247 | 87.8087 | 593.3399 | 96.0899 | 0.003 | 0.042 | 0.137 | 0.13217 | 3.528 | 92.5926 | 0.13095 | 97.709 | [8 empty] | SDS-Free Cl2 residual | mg/L | 0.672 | 0.66 | 0.666 | 1.8018 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.96 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.704 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.68 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 0.1 | Maximum element recovery (%) | 15 | [9 empty] | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | SDS-CHCl3 | mg/L | 47.34 | 45.51 | 46.425 | 3.9418 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-24 | 13:00 | 75 | 22 | 56 | 56 | 350 | 6.6 | 2.7 |  | 9.3 | 0.23793 | 0.70968 | 36.6344 | 15.0341 | 11.868 | 599.0997 | 23.0638 | 588.2373 | 5.706 | 50.294 | 0.23597 | [27 empty] | SDS-Cl2 demand | mg/L | 0.328 | 0.34 | 0.334 | 3.5928 | --- | 8.5443 | --- | 87.698 | 8.4669 | 96.0552 | SDS-Cl2 demand | mg/L | 0.54 | --- | 20.3127 | --- | 80.1105 | 20.1486 | 97.3199 | SDS-Cl2 demand | mg/L | 0.296 | --- | 5.2327 | --- | 89.0976 | 5.1881 | 94.2947 | SDS-Cl2 demand | mg/L | 0.32 | --- | 3.6932 | --- | 88.2136 | 3.6628 | 91.2635 | Blended Water Quality if THM4 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if THM4 Controls the Blend Ratio
Historical Average Water Temperature (oC) | 14 | Variability of design flux (%) | 15 | [9 empty] | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | SDS-BDCM | mg/L | 22 | 21.84 | 21.92 | 0.72993 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-24 | 15:00 | 77 | 22.2 | 56 | 56 | 350 | 6.6 | 2.7 |  | 9.3 | 0.23793 | 0.70968 | 36.6344 | 15.0341 | 11.7981 | 599.0997 | 23.0638 | 588.2373 | 5.706 | 50.294 | 0.23458 | [27 empty] | SDS-Chlorination temp. | oC | 19.8 | 19.8 | 19.8 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 19.8 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 19.8 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 19.8 | --- | --- | --- | --- | --- | --- | Qp/QT (THM4), % | 11.6487 | 11.856 | 11.1279 | 11.1756 | Qp/QT (THM4), % | 58.9798 | 60.0294 | 56.3426 | 56.5843
State Approved Plant Capacity (MGD) | 55 | Rejection of reference solute and conditions of test | 2000 ppm | [14 empty] | SDS-DBCM | mg/L | 10.49 | 10.84 | 10.665 | 3.2818 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-24 | 17:00 | 79 | 22.2 | 56 | 56 | 350 | 6.6 | 2.7 |  | 9.3 | 0.23793 | 0.70968 | 36.6344 | 15.0341 | 11.7981 | 599.0997 | 23.0638 | 588.2373 | 5.706 | 50.294 | 0.23458 | 8.43 |  |  | 22.9 |  |  | 599.5 |  | 87.9664 | 594.0635 | 96.1452 | 0.004 |  |  | 0.12972 |  | 90.1235 | 0.12854 | 96.8881 | [8 empty] | SDS-Chlorination pH | --- | 9.52 | 9.51 | 9.515 | 0.1051 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 9.51 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 9.53 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 9.52 | --- | --- | --- | --- | --- | --- | SDS-THM4b, ug/L | 72 | 72 | 72 | 72 | SDS-THM4b, ug/L | 36 | 36 | 36 | 36
|  | (e.g., solute type and concentration) | NaCl | [14 empty] | SDS-CHBr3 | mg/L | 1.75 | 1.95 | 1.85 | 10.8108 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-25 | 8:00 | 94 | 21.9 | 56 | 57 | 350 | 6 | 0.77 |  | 6.77 | 0.23793 | 0.88626 | 50.6987 | 13.6673 | 10.8211 | 1286.5656 | 49.6126 | 1265.3607 | 12.2635 | 44.2365 | 0.24462 | [27 empty] | SDS-Incubation time | hours | 31 | 31 | 31 | 0 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 31 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 31 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 31 | --- | --- | --- | --- | --- | --- | SDS-HAA5b, ug/L | 23.5324 | 23.6064 | 23.6711 | 23.6584 | SDS-HAA5b, ug/L | 10.9257 | 11.3005 | 11.6281 | 11.5638
|  | Variability of rejection of reference solute (%) | 3 | [14 empty] | SDS-THM4 | mg/L | 81.58 | 80.14 | 80.86 | 1.7809 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-25 | 9:00 | 95 | 21.8 | 57 | 58 | 350 | 6.5 | 0.8 |  | 7.3 | 0.23793 | 0.89041 | 46.9452 | 14.8063 | 11.7575 | 1322.6565 | 50.933 | 1299.0388 | 12.5991 | 44.9009 | 0.26186 | 9.03 |  |  | 49.2 |  |  | 1336.7375 |  | 74.1461 | 1324.7818 | 96.2862 | 0.007 |  |  | 0.31269 |  | 82.716 | 0.30985 | 97.7408 | [8 empty] | SDS-TOX | mg Cl- /L | BMRL | 36.5 | 36.5 | #VALUE! | --- | 479.6034 | --- | 77.8788 | 475.4237 | 92.3226 | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOXb, ug Cl- /L | 150.0314 | #VALUE! | #VALUE! | #VALUE! | SDS-TOXb, ug Cl- /L | 89.211 | #VALUE! | #VALUE! | #VALUE!
|  | Standard testing recovery (%) | 15 | [14 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-25 | 10:00 | 96 | 21.4 | 57 | 58 | 350 | 6 | 0.8 |  | 6.8 | 0.23793 | 0.88235 | 50.4706 | 13.6673 | 10.9822 | 1254.678 | 48.3829 | 1233.9986 | 11.9596 | 45.5404 | 0.24115 | 9.03 |  |  | 46.4 |  |  | 1269.55 |  | 75.6174 | 1259.0659 | 96.3147 | 0.006 |  |  | 0.29925 |  | 85.1852 | 0.29674 | 97.978 | [8 empty] | SDS-CHCl3 | mg/L | 2.79 | 1.76 | 2.275 | 45.2747 | --- | 154.5164 | --- | 95.0996 | 153.0803 | 98.5139 | SDS-CHCl3 | mg/L | 1.74 | --- | 407.9673 | --- | 96.252 | 404.5946 | 99.5699 | SDS-CHCl3 | mg/L | 1.24 | --- | 93.4543 | --- | 97.329 | 92.6212 | 98.6612 | SDS-CHCl3 | mg/L | 1.58 | --- | 64.742 | --- | 96.5967 | 64.1715 | 97.5378 | SDS-CDb, mg/L | 2.4376 | 2.4571 | 2.4458 | 2.4473 | SDS-CDb, mg/L | 1.3107 | 1.4094 | 1.3521 | 1.3598
|  | Standard testing pH | 7 | [14 empty] | SDS-DCAA* | mg/L | 19.36 | 20.3 | 19.83 | 4.7403 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-25 | 11:00 | 97 | 21.5 | 57 | 58 | 350 | 5.8 | 0.73 |  | 6.53 | 0.23793 | 0.88821 | 52.5988 | 13.2118 | 10.5848 | 1302.8714 | 50.2695 | 1282.114 | 12.4222 | 45.0778 | 0.23481 | 9.08 |  |  | 41 |  |  | 1376.5192 |  | 78.4551 | 1365.4534 | 96.9973 | 0.005 |  |  | 0.32255 |  | 87.6543 | 0.31992 | 98.4371 | [8 empty] | SDS-BDCM | mg/L | 1.23 | 1.13 | 1.18 | 8.4746 | --- | 72.6972 | --- | 94.6168 | 72.0226 | 98.3616 | SDS-BDCM | mg/L | 1.39 | --- | 188.0264 | --- | 93.6588 | 186.4768 | 99.2546 | SDS-BDCM | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | TOCb, mg/L | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | TOCb, mg/L | #DIV/0! | #VALUE! | #VALUE! | #VALUE!
|  | Acceptable range of operating pressures | < 600 PSI | [14 empty] | SDS-TCAA* | mg/L | 3.25 | 3.36 | 3.305 | 3.3283 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-25 | 12:00 | 98 | 21 | 57 | 58 | 350 | 5.8 | 0.73 |  | 6.53 | 0.23793 | 0.88821 | 52.5988 | 13.2118 | 10.7424 | 1302.8714 | 50.2695 | 1282.114 | 12.4222 | 45.0778 | 0.23831 | 9.05 | 9.44 | 9.27 | 40.8 | 174.6 | 978 | 1378.1082 | -40.9109 | 78.5602 | 1367.0277 | 97.0154 | 0.005 | 0.041 | 0.282 | 0.32255 | -14.3811 | 87.6543 | 0.31992 | 98.4371 | [8 empty] | SDS-DBCM | mg/L | 1.39 | 1.3 | 1.345 | 6.6914 | --- | 33.4829 | --- | 87.3887 | 33.1798 | 95.9463 | SDS-DBCM | mg/L | 1.92 | --- | 81.42 | --- | 81.9972 | 80.76 | 97.6226 | SDS-DBCM | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 b, cm-1 | 0.036248 | 0.035935 | 0.036104 | 0.036086 | UV254 b, cm-1 | 0.018972 | 0.017389 | 0.018245 | 0.018149
|  | Acceptable range of operating pH values | pH 2-11 | [14 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-25 | 14:00 | 100 | 22.4 | 57 | 58 | 350 | 5.9 | 0.77 |  | 6.67 | 0.23793 | 0.88456 | 51.4738 | 13.4396 | 10.4846 | 1272.3807 | 49.0793 | 1251.7593 | 12.1299 | 45.3701 | 0.23109 | [27 empty] | SDS-CHBr3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 1.08 | --- | 8.08 | --- | 41.6216 | 8.0219 | 86.5368 | SDS-CHBr3 | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Bromideb, ug/L | #DIV/0! | 72.1055 | #VALUE! | #VALUE! | Bromideb, ug/L | #DIV/0! | 50.1866 | #VALUE! | #VALUE!
|  | Typical pressure drop across a single element (psi) | 6 | [14 empty] | SDS-DBAA* | mg/L | 3.4 | 3.6 | 3.5 | 5.7143 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-26 | 8:00 | 118 | 22.2 | 56 | 57 | 350 | 5.5 | 5.6 |  | 11.1 | 0.23793 | 0.4955 | 30.5315 | 12.5284 | 9.8317 | 363.4186 | 14.0337 | 357.9283 | 3.4664 | 53.0336 | 0.18539 | [27 empty] | SDS-THM4 | mg/L | 5.41 | 4.19 | 4.8 | 25.4167 | --- | 267.0759 | --- | 94.0638 | 264.6019 | 98.186 | SDS-THM4 | mg/L | 6.13 | --- | 685.4936 | --- | 92.419 | 679.8533 | 99.0983 | SDS-THM4 | mg/L | 1.24 | --- | 163.7298 | --- | 98.4665 | 162.2618 | 99.2358 | SDS-THM4 | mg/L | 1.58 | --- | 113.242 | --- | 98.046 | 112.2335 | 98.5922 | Alkb, mg/L CaCO3 | 48.8548 | 49.0243 | 48.9025 | 48.7884 | Alkb, mg/L CaCO3 | 25.3076 | 26.166 | 25.549 | 24.9716
|  | Maximum permissible SDI | 5 | [14 empty] | SDS-BCAA* | mg/L | 8.92 | 10.4 | 9.66 | 15.3209 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-26 | 9:00 | 119 | 21.9 | 56 | 57 | 350 | 6 | 5.9 |  | 11.9 | 0.23793 | 0.5042 | 28.4118 | 13.6673 | 10.8211 | 369.3415 | 14.2426 | 363.2541 | 3.5206 | 52.9794 | 0.20425 | [27 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | T-Hdb, mg/L CaCO3 | 77.7661 | 78.0763 | 78.0522 | 77.9887 | T-Hdb, mg/L CaCO3 | 37.6057 | 39.1762 | 39.0545 | 38.7329
|  | Maximum permissible turbidity (ntu) | 1 | [14 empty] | SDS-TBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-26 | 10:00 | 120 | 22.2 | 56 | 57 | 350 | 6.2 | 5.9 |  | 12.1 | 0.23793 | 0.5124 | 27.9256 | 14.1229 | 11.0831 | 375.0853 | 14.456 | 368.697 | 3.5744 | 52.9256 | 0.20941 | 8.91 |  |  | 13.4 |  |  | 376.1949 |  | 92.9585 | 372.9816 | 96.4073 | 0.002 |  |  | 0.080958 |  | 95.0617 | 0.080258 | 97.508 | [8 empty] | SDS-DCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Ca-Hdb, mg/L CaCO3 | 65.7804 | 66.0938 | 66.0211 | 65.9751 | Ca-Hdb, mg/L CaCO3 | 31.773 | 33.36 | 32.9917 | 32.7586
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | 1000 ppm/hours | [14 empty] | SDS-CDBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-26 | 11:00 | 121 | 22.1 | 56 | 57 | 350 | 6.2 | 6.1 |  | 12.3 | 0.23793 | 0.50407 | 27.4553 | 14.1229 | 11.1159 | 369.2551 | 14.2313 | 362.9661 | 3.5188 | 52.9812 | 0.20981 | 8.91 |  |  | 13.8 |  |  | 369.6934 |  | 92.7483 | 366.5412 | 96.2351 | 0.003 |  |  | 0.078615 |  | 92.5926 | 0.077945 | 96.1511 | [8 empty] | SDS-TCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | 1: All of the information requested in this field may not be available, but values for all Design | [15 empty] | SDS-DCBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-26 | 12:00 | 122 | 22.3 | 56 | 57 | 350 | 6.3 | 6.1 |  | 12.4 | 0.23793 | 0.50806 | 27.2258 | 14.3507 | 11.2286 | 372.035 | 14.3344 | 365.5964 | 3.5448 | 52.9552 | 0.21204 | 8.91 | 9.14 | 9.05 | 13.9 | 174.5 | 366 | 372.4836 | -1.7715 | 92.6957 | 369.2564 | 96.2357 | 0.004 | 0.044 | 0.088 | 0.078197 | 11.1401 | 90.1235 | 0.077529 | 94.8406 | [8 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  | Parameters must be entered in cells E14:E23, since these parameters are used in calculations. | [15 empty] | SDS-HAA5 | mg/L | 26.01 | 27.26 | 26.635 | 4.6931 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-26 | 15:30 | 125.5 | 23 | 56 | 57 | 350 | 6.6 | 6.8 |  | 13.4 | 0.23793 | 0.49254 | 25.1194 | 15.0341 | 11.5224 | 361.4956 | 13.9166 | 354.9413 | 3.443 | 53.057 | 0.21717 | [27 empty] | SDS-DBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DBAA* | mg/L | 1.09 | --- | 22.9991 | --- | 68.8571 | 22.8172 | 95.2229 | SDS-DBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Blended Water Quality if HAA5 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if HAA5 Controls the Blend Ratio
[18 empty] | SDS-HAA6 | mg/L | 34.93 | 37.66 | 36.295 | 7.5217 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-27 | 8:00 | 142 | 23.1 | 54 | 55 | 350 | 6.3 | 15.2 |  | 21.5 | 0.23793 | 0.29302 | 15.2791 | 14.3507 | 10.9662 | 264.9433 | 10.2082 | 260.3581 | 2.5244 | 51.9756 | 0.21099 | [27 empty] | SDS-BCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-BCAA* | mg/L | 1.05 | --- | 79.3227 | --- | 89.1304 | 78.6729 | 98.6654 | SDS-BCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Qp/QT (HAA5), % | -102.7408 | -107.1247 | -102.7408 | -102.7408 | Qp/QT (HAA5), % | -1.3704 | -1.4289 | -1.3704 | -1.3704
[18 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-27 | 9:00 | 143 | 22.8 | 55 | 56 | 350 | 6.5 | 15.2 |  | 21.7 | 0.23793 | 0.29954 | 15.129 | 14.8063 | 11.4151 | 267.277 | 10.2923 | 262.5044 | 2.546 | 52.954 | 0.21557 | [27 empty] | SDS-TBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-THM4b, ug/L | NA | NA | NA | NA | SDS-THM4b, ug/L | NA | NA | NA | NA
[18 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-27 | 10:00 | 144 | 22.2 | 55 | 55 | 350 | 6.4 | 15.2 |  | 21.6 | 0.23793 | 0.2963 | 15.2037 | 14.5785 | 11.4406 | 266.1104 | 10.2503 | 261.4318 | 2.5352 | 52.4648 | 0.21806 | 8.54 |  |  | 10.7 |  |  | 265.9211 |  | 94.3773 | 263.5876 | 95.9406 | 0.001 |  |  | 0.057132 |  | 97.5309 | 0.056618 | 98.2338 | [8 empty] | SDS-CDBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-HAA5b, ug/L | NA | NA | NA | NA | SDS-HAA5b, ug/L | NA | NA | NA | NA
[18 empty] | should be reported if measured. | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-27 | 11:00 | 145 | 22.9 | 55 | 55 | 350 | 6.4 | 15.2 |  | 21.6 | 0.23793 | 0.2963 | 15.2037 | 14.5785 | 11.2063 | 266.1104 | 10.2503 | 261.4318 | 2.5352 | 52.4648 | 0.2136 | 8.54 |  |  | 10.9 |  |  | 265.8368 |  | 94.2722 | 263.506 | 95.8635 | 0.001 |  |  | 0.057132 |  | 97.5309 | 0.056618 | 98.2338 | [8 empty] | SDS-DCBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TOXb, ug Cl- /L | NA | NA | NA | NA | SDS-TOXb, ug Cl- /L | NA | NA | NA | NA
[45 empty] | 1998-10-27 | 12:00 | 146 | 22.9 | 55 | 55 | 350 | 6.4 | 15.4 |  | 21.8 | 0.23793 | 0.29358 | 15.055 | 14.5785 | 11.2063 | 265.1414 | 10.213 | 260.4798 | 2.526 | 52.474 | 0.21356 | 8.59 | 9.22 | 9.11 | 10.9 | 172.7 | 266 | 264.8558 | 0.43013 | 94.2722 | 262.534 | 95.8482 | 0.001 | 0.041 | 0.056 | 0.056916 | -1.635 | 97.5309 | 0.056404 | 98.2271 | [8 empty] | SDS-HAA5 | mg/L | 0 | 0 | 0 | #DIV/0! | --- | 91.8448 | --- | 100 | 90.9785 | 100 | SDS-HAA5 | mg/L | 1.09 | --- | 233.3173 | --- | 95.9076 | 231.3892 | 99.5289 | SDS-HAA5 | mg/L | 0 | --- | 54.3571 | --- | 100 | 53.8661 | 100 | SDS-HAA5 | mg/L | 0 | --- | 37.5141 | --- | 100 | 37.1753 | 100 | SDS-CDb, mg/L | NA | NA | NA | NA | SDS-CDb, mg/L | NA | NA | NA | NA
[45 empty] | 1998-10-27 | 16:00 | 150 | 24.1 | 55 | 55 | 350 | 6.6 | 15.5 |  | 22.1 | 0.23793 | 0.29864 | 14.8371 | 15.0341 | 11.1537 | 266.9549 | 10.2771 | 262.1147 | 2.5426 | 52.4574 | 0.21262 | [27 empty] | SDS-HAA6 | mg/L | 0 | 0 | 0 | #DIV/0! | --- | 125.1552 | --- | 100 | 123.9746 | 100 | SDS-HAA6 | mg/L | 2.14 | --- | 312.64 | --- | 94.1039 | 310.0621 | 99.3098 | SDS-HAA6 | mg/L | 0 | --- | 74.0714 | --- | 100 | 73.4022 | 100 | SDS-HAA6 | mg/L | 0 | --- | 51.1197 | --- | 100 | 50.658 | 100 | TOCb, mg/L | NA | NA | NA | NA | TOCb, mg/L | NA | NA | NA | NA
[45 empty] | 1998-10-29 | 8:00 | 170 | 21.9 | 53 | 54 | 350 | 6.8 | 15.2 | X | 22 | 0.23793 | 0.30909 | 14.9091 | 15.4897 | 12.2639 | 270.7734 | 10.4182 | 265.7151 | 2.5783 | 50.9217 | 0.24084 | [27 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | UV254 b, cm-1 | NA | NA | NA | NA | UV254 b, cm-1 | NA | NA | NA | NA
[45 empty] | 1998-10-29 | 10:00 | 172 | 22.1 | 53 | 54 | 350 | 6.9 | 15.1 |  | 22 | 0.23793 | 0.31364 | 14.9091 | 15.7174 | 12.3709 | 272.4692 | 10.4805 | 267.3042 | 2.5941 | 50.9059 | 0.24301 | 8.61 | 8.75 | 8.64 | 9.4 | 168.9 | 254 | 272.9629 | -7.4657 | 95.0604 | 270.3649 | 96.5232 | 0 | 0.039 | 0.057 |  | #VALUE! | [11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | Bromideb, ug/L | NA | NA | NA | NA | Bromideb, ug/L | NA | NA | NA | NA
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Alkb, mg/L CaCO3 | NA | NA | NA | NA | Alkb, mg/L CaCO3 | NA | NA | NA | NA
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | T-Hdb, mg/L CaCO3 | NA | NA | NA | NA | T-Hdb, mg/L CaCO3 | NA | NA | NA | NA
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Ca-Hdb, mg/L CaCO3 | NA | NA | NA | NA | Ca-Hdb, mg/L CaCO3 | NA | NA | NA | NA
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Notes: |  |  |  |  | Notes:
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to |  |  |  |  | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | determine the percentage of total flow that must be treated by the membrane process to meet the |  |  |  |  | determine the percentage of total flow that must be treated by the membrane process to meet the
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Stage 1 DBP MCLs. |  |  |  |  | Stage 2 DBP MCLs.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | A 10% factor of safety has been applied all the MCLs. i.e., 72 / 54 mg/L for THM4 and HAA5. |  |  |  |  | A 10% factor of safety has been applied all the MCLs. i.e., 36 / 27 mg/L for THM4 and HAA5.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for |  |  |  |  | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | both parameters and the maximum (Qp/QT) ratio controls the design. |  |  |  |  | both parameters and the maximum (Qp/QT) ratio controls the design.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. |  |  |  |  | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. |  |  |  |  | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. |  |  |  |  | The subscript "b" refers to the blended water quality for a given blend ratio.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL. |  |  |  |  | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. |  |  |  |  | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Note on X25: Alison Gusses: High precision incubator was used for SDS testing
Note on CY29: Alison Gusses: High precision incubator was used for SDS testing
Note on DL29: Alison Gusses: High precision incubator was used for SDS testing
Note on DQ10: C. Rice: Consultant verified all water quality parameters for the 90% recovery run. The membrane appears to have been stable before the composite sample was taken. All of the measurements are low biased relative to the calculated mass balance. The consultant stated that there is no direct cause known for the high MB closure errors; perhaps an error in recording flow-rate measurements and/or membrane fouling occurred.
Note on DV29: Alison Gusses: High precision incubator was used for SDS testing
Note on EF29: Alison Gusses: High precision incubator was used for SDS testing

## BW30. 4th Quarter
FIELD-SET 4: 4th QUARTER RBSMT RESULTS (FILE: rbsmt-2.xls)
Field 4-1: PWS And Treatment Plant Data |  | Field 4-2: Manufacturer Reported Membrane Characteristics1 |  | Field 4-3: RBSMT Design Parameters | [8 empty] | Field 4-4: Foulants And Fouling Indices1 |  | Field 4-5: Pretreatment Used Prior To Membranes1 |  |  | Field 4-6: Feed Water Quality After Pretreatment | [5 empty] | Field 4-7: Membrane Setting Data | [20 empty] | Field 4-8: Membrane Performance Data During Operation With The Test Water | [16 empty] | Field 4-8: Membrane Performance Data During Operation With The Test Water (continued) | [19 empty] | Field 4-8: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 4-9: Permeate And Concentrate Water Quality For Run 1 | [11 empty] | Field 4-10: Permeate And Concentrate Water Quality For Run 2 | [8 empty] | Field 4-11: Permeate And Concentrate Water Quality For Run 3 | [8 empty] | Field 4-12: Permeate And Concentrate Water Quality For Run 4 | [8 empty] | Field 4-13: Blending Calculations For Stage 1 D-DBP MCLs |  |  |  |  | Field 4-14: Blending Calculations For Proposed Stage 2 D-DBP MCLs |  |  |  |  | Field 4-15: Membrane Cost Parameters
|  | General Information |  | Input Design Parameters | [8 empty] | Parameters Evaluated Prior to Pretreatment | [80 empty] | Operating Parameters During Sample Collection | [11 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Feed and Permeate Water Quality Parameters |  |  |  |  | Feed and Permeate Water Quality Parameters |  |  |  |  | General Cost Parameters
PWS Name | Water District No. 1 of Johnson County, Kansas | Membrane manufacturer | Dow-Filmtec | [5 empty] | Active membrane area in bench-scale cell, Acell (ft2) | 0.167 |  |  | Alkalinity (mg/L as CaCO3) | 275 | Process | Description | Scale | Parameter | Units | CF-1 | CF-2 | Average | RPD |  |  |  | Average TDS rejection (decimal fraction) | 0.98 | [5 empty] | TDS concentration of setting solution (mg/L) | 0.8 | [12 empty] | Average bulk TDS rejection (decimal fraction) | 0.94199 | [45 empty] | Recovery during sample collection (decimal) | 0.71 | [10 empty] | Recovery during sample collection (decimal) | 0.87 | [7 empty] | Recovery during sample collection (decimal) | 0.5 | [7 empty] | Recovery during sample collection (decimal) | 0.29 | [8 empty] | RUN ID # |  |  |  |  | RUN ID # |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | KS200910 | Membrane trade name | BW30-XLE | [5 empty] | Active width of membrane in the bench-scale cell, wcell (ft) | 0.333 |  |  | Calcium Hardness (mg/L as CaCO3) | 258 | Presedimentation | 3 Basins | Full-scale | Sampling date | MM/DD/YY | 1999-01-28 | 1999-02-04 | --- | --- | [71 empty] | Feed flow rate during sample collection (mL/min) | 7.2 | [10 empty] | Feed flow rate during sample collection (mL/min) | 4.7 | [7 empty] | Feed flow rate during sample collection (mL/min) | 11.9 | [7 empty] | Feed flow rate during sample collection (mL/min) | 20 | [6 empty] | Parameter | 1 | 2 | 3 | 4 | Parameter | 1 | 2 | 3 | 4 | Capital Recovery Interest Rate (%) | 5
Water Industry Data Base Number (optional) | NA | Molecular weight cutoff (Daltons) | 100 | [5 empty] | Average yearly temperature of feed water, TavgoC (oC) | 14 |  |  | LSI | 1.03 | Softening | Lime, 270 mg/L as Ca(OH)2 | Bench-scale | Sampling time | hh:mm | 14:00 | 7:00 | --- | --- | Date | Time | Setting time | Influent | PI | PC | QI | Qp | QW | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) | Date | Time | Operation time | Influent | PI | PC | QI | Qp | QW | Cleaning Event | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1) | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Influent flow rate during sample collection (mL/min) | 350 | [10 empty] | Influent flow rate during sample collection (mL/min) | 350 | [7 empty] | Influent flow rate during sample collection (mL/min) | 350 | [7 empty] | Influent flow rate during sample collection (mL/min) | 350 | [6 empty] | SDS-THM4F, ug/L | 59.951 | 59.951 | 59.951 | 59.951 | SDS-THM4F, ug/L | 59.951 | 59.951 | 59.951 | 59.951 | Capital Recovery Period (years) | 20
|  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide | [5 empty] | Approximate feed water TDS, TDSF (mg/L) | 553 |  |  | Dissolved iron (mg/L) |  | Coagulation | Alum: Al2(SO4)3.14H2O, 15 mg/L | Bench-scale | Operation time | hh.hh | 3 | 164 | --- | --- | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | Indicate with "X" | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) | [39 empty] | SDS-THM4p, ug/L | 0 | 4.533 | 0 | 0 | SDS-THM4p, ug/L | 0 | 4.533 | 0 | 0 | Overhead & Profit Factor (% of construction costs) | 15
Official ICR Contact Person |  | Membrane construction (e.g., thin-film composite) | Thin Film | [5 empty] | Manufacturer reported TDS rejection, RejTDS (decimal fraction) | 0.98 |  |  | Total iron (mg/L) |  | Sedimentation | Gravity settling in test drums | Bench-scale | pH | --- | 9.36 | 9.36 | 9.36 | 0 | 1999-01-26 | 8:00 | 0 | [6 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-28 | 11:00 | 0 | [7 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [27 empty] | Permeate and Concentrate Water Quality | [11 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | SDS-HAA5F, ug/L | 23.429 | 23.429 | 23.429 | 23.429 | SDS-HAA5F, ug/L | 23.429 | 23.429 | 23.429 | 23.429 | Special Sitework Factor (% of construction costs) | 0
Mailing Address |  | Membrane hydrophobicity | Hydrophobic | [5 empty] | Temperature normalized MTCW (gfd/psi) | 0.16688 |  |  | Dissolved aluminum (mg/L) |  | Recarbonation | CO2 gas added to pH 9.4 | Bench-scale | Temperature | oC | 22.8 | 23 | 22.9 | 0.87336 | 1999-01-26 | 10:00 | 2 | 21.2 | 50 | 50 | 350 | 7.4 | 2.9 | 10.3 | 0.23793 | 0.71845 | 32.9806 | 16.8564 | 13.625 | 2.7061 | 0.053001 | 2.65 | 0.026251 | 49.9737 | 0.27264 | 1999-01-28 | 12:00 | 1 | 22.2 | 50 | 50 | 350 | 6.4 | 2.9 |  | 9.3 | 0.23793 | 0.68817 | 36.6344 | 14.5785 | 11.4406 | 1583.7844 | 90.2852 | 1556.4747 | 14.7984 | 35.2016 | 0.325 | [27 empty] | Parameter | Units | Cp-1 | Cp-1 (dup) | Average | RPD | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | SDS-HAA5p, ug/L | 1.3854 | 2.8141 | 1.2124 | 1.4208 | SDS-HAA5p, ug/L | 1.3854 | 2.8141 | 1.2124 | 1.4208 | Construction Contingencies (% of construction costs) | 15
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Slightly Negative | [9 empty] | Total aluminum (mg/L) |  | Cartridge filtration | 1 um size exclusion | Bench-scale | Alkalinity | mg/L as CaCO3 | 42 | 46.1 | 44.05 | 9.3076 | 1999-01-26 | 12:00 | 4 | 21.2 | 50 | 50 | 350 | 7.8 | 3.5 | 11.3 | 0.23793 | 0.69027 | 29.9735 | 17.7675 | 14.3615 | 2.475 | 0.048418 | 2.4209 | 0.023995 | 49.976 | 0.28737 | 1999-01-28 | 14:00 | 3 | 23 | 50 | 50 | 350 | 5.9 | 3 |  | 8.9 | 0.23793 | 0.66292 | 38.3258 | 13.4396 | 10.3003 | 1482.9791 | 84.6547 | 1459.4073 | 13.8654 | 36.1346 | 0.28505 | 9.23 | 9.36 | 9.19 | 118 | 556 | 1310 | 1417.4 | -8.1985 | 78.777 | 1406.4479 | 91.6101 | 0.001 | 0.03 | 0.088 | 0.087033 | 1.0985 | 96.6667 | 0.086308 | 98.8414 | [8 empty] | Sampling date | MM/DD/YY | 1999-02-01 | 1999-02-01 | --- | --- | 1999-02-01 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-02-02 | 1999-02-02 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-02-03 | 1999-02-03 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-02-04 | 1999-02-04 | --- | --- | --- | --- | --- | SDS-TOXF, ug Cl- /L | 95 | 95 | 95 | 95 | SDS-TOXF, ug Cl- /L | 95 | 95 | 95 | 95 | Engineering Fee Factor (% of construction costs) | 15
Phone Number |  |  |  | Experimental Design1,2 | [8 empty] | Fluoride (mg/L) |  | Antiscalant | 4 mg/L Hypersperse 400UL | Bench-scale | Total dissolved solids | mg/L | 556 | 556 | 556 | 0 | 1999-01-26 | 14:00 | 6 | 22.1 | 51 | 52 | 350 | 8.2 | 3.6 | 11.8 | 0.23793 | 0.69492 | 28.661 | 18.6787 | 14.7016 | 2.5105 | 0.049056 | 2.4528 | 0.024326 | 51.4757 | 0.2856 | 1999-01-28 | 16:00 | 5 | 22.7 | 50 | 50 | 350 | 5.7 | 2.3 |  | 8 | 0.23793 | 0.7125 | 42.75 | 12.984 | 10.0398 | 1694.1159 | 96.7603 | 1668.1018 | 15.8435 | 34.1565 | 0.29393 | [27 empty] | Sampling time | hh:mm | 8:00 | 8:00 | --- | --- | 8:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 8:00 | 8:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 8:00 | 8:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 7:00 | 7:00 | --- | --- | --- | --- | --- | SDS-TOXp, ug Cl- /L | #DIV/0! | BMRL | BMRL | BMRL | SDS-TOXp, ug Cl- /L | #DIV/0! | BMRL | BMRL | BMRL | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920
FAX Number |  | Design Parameters |  | ID# | Recovery | FW-design | Dp | PI | QI-cell | Qp | QF | QW | Phosphate (mg/L) |  |  |  |  | Total hardness | mg/L as CaCO3 | 151.3 | 162.3 | 156.8 | 7.0153 | 1999-01-26 | 16:00 | 8 | 21.6 | 50 | 50 | 350 | 8.2 | 3.5 | 11.7 | 0.23793 | 0.70085 | 28.9145 | 18.6787 | 14.9205 | 2.5572 | 0.049969 | 2.4985 | 0.024779 | 49.9752 | 0.29856 | 1999-01-28 | 17:00 | 6 | 22.9 | 50 | 50 | 350 | 5.7 | 2.5 |  | 8.2 | 0.23793 | 0.69512 | 41.6829 | 12.984 | 9.9806 | 1613.5572 | 92.1591 | 1588.7801 | 15.0901 | 34.9099 | 0.2859 | [27 empty] | Operation time | hh.hh | 93 | 93 | --- | --- | 93 | --- | --- | --- | --- | --- | Operation time | hh.hh | 117 | 117 | --- | --- | --- | --- | --- | Operation time | hh.hh | 141 | 141 | --- | --- | --- | --- | --- | Cumulative time | hr | 164 | 164 | --- | --- | --- | --- | --- | SDS-CDF, mg/L | 3.5155 | 3.5155 | 3.5155 | 3.5155 | SDS-CDF, mg/L | 3.5155 | 3.5155 | 3.5155 | 3.5155 | 1998 Producers Price Index (PPI base year 1967 = 100) | 370
E-Mail Address (optional) |  | Design flux, FW (gfd) | 30(15 ave) |  | (decimal) | (gfd) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | Sulfate (mg/L) |  |  |  |  | Calcium hardness | mg/L as CaCO3 | 97.4 | 109.4 | 103.4 | 11.6054 | 1999-01-27 | 8:00 | 24 | 21.7 | 50 | 50 | 350 | 8.6 | 3.6 | 12.2 | 0.23793 | 0.70492 | 27.6885 | 19.5899 | 15.6022 | 2.5903 | 0.050559 | 2.5279 | 0.025086 | 49.9749 | 0.3122 | 1999-01-29 | 7:00 | 20 | 22 | 51 | 52 | 350 | 5.5 | 2.4 |  | 7.9 | 0.23793 | 0.6962 | 43.3038 | 12.5284 | 9.89 | 1618.2398 | 92.4772 | 1594.2635 | 15.1377 | 36.3623 | 0.27199 | 8.98 |  |  | 101.9 |  |  | 1596.6458 |  | 81.6727 | 1584.9014 | 93.5706 | 0.002 |  |  | 0.094167 |  | 93.3333 | 0.093442 | 97.8596 | [8 empty] | pH | --- | 7.01 | 6.97 | 6.99 | 0.57225 | 8.31 | --- | --- | --- | --- | --- | pH | --- | 8.5 | 8.98 | --- | --- | --- | --- | --- | pH | --- | 7.78 | 8.67 | --- | --- | --- | --- | --- | pH | --- | 8.52 | 9.33 | --- | --- | --- | --- | --- | SDS-CDp, mg/L | 1.0895 | 1.856 | 1.187 | 1.417 | SDS-CDp, mg/L | 1.0895 | 1.856 | 1.187 | 1.417 | Labor Rate + Fringe ($/work-hour) | 17
|  | Net driving pressure at the design flux, NDP (psi) | 130 | 1 | 0.7 | 12 | 18.1753 | 90.0835 | 335.6684 | 5.2675 | 7.5249 | 2.2575 | Calcium (mg/L) | 103 |  |  |  | Turbidity | ntu | 0.08 | 0.1 | 0.09 | 22.2222 | 1999-01-27 | 10:00 | 26 | 21.6 | 50 | 50 | 350 | 8.5 | 3.5 | 12 | 0.23793 | 0.70833 | 28.1667 | 19.3621 | 15.4664 | 2.6187 | 0.051127 | 2.5563 | 0.025364 | 49.9746 | 0.30948 | 1999-01-29 | 9:00 | 22 | 21.4 | 52 | 52 | 350 | 5.5 | 2.4 |  | 7.9 | 0.23793 | 0.6962 | 43.3038 | 12.5284 | 10.067 | 1618.2398 | 92.4772 | 1594.2635 | 15.1377 | 36.8623 | 0.2731 | [27 empty] | Temperature | oC | 22.9 | 23 | 22.95 | 0.43573 | 23.2 | --- | --- | --- | --- | --- | Temperature | oC | 23.1 | 22.7 | --- | --- | --- | --- | --- | Temperature | oC | 22.9 | 22 | --- | --- | --- | --- | --- | Temperature | oC | 22.4 | 22.3 | --- | --- | --- | --- | --- | TOCF, mg/L | 2.275 | 2.275 | 2.275 | 2.275 | TOCF, mg/L | 2.275 | 2.275 | 2.275 | 2.275 | Labor Overhead Factor (% of labor) | 42
Technical ICR Contact Person |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.231 | 2 | 0.9 | 12 | 54.3046 | 126.2129 | 335.6684 | 5.2675 | 5.8527 | 0.58527 | Barium (mg/L) |  |  |  |  | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! | 1999-01-27 | 14:00 | 30 | 22 | 50 | 50 | 350 | 8.5 | 3.5 | 12 | 0.23793 | 0.70833 | 28.1667 | 19.3621 | 15.2846 | 2.6187 | 0.051127 | 2.5563 | 0.025364 | 49.9746 | 0.30585 | 1999-01-29 | 11:00 | 24 | 21.5 | 52 | 52 | 350 | 5.6 | 2.4 |  | 8 | 0.23793 | 0.7 | 42.75 | 12.7562 | 10.2198 | 1635.3336 | 93.4285 | 1610.6631 | 15.2957 | 36.7043 | 0.27844 | 8.72 | 8.84 | 8.76 | 102.2 | 556 | 1402 | 1614.8667 | -15.1831 | 81.6187 | 1602.7653 | 93.6235 | 0.002 | 0.033 | 0.103 | 0.095333 | 7.4434 | 93.3333 | 0.094587 | 97.8855 | [8 empty] | Alkalinity | mg/L as CaCO3 | 6 | 5.6 | 5.8 | 6.8966 | 136.5 | 137.6966 | -0.87659 | 86.8331 | 136.7333 | 95.7582 | Alkalinity | mg/L as CaCO3 | 10.3 | 266.8 | 269.9154 | -1.1677 | 76.6175 | 268.3989 | 96.1624 | Alkalinity | mg/L as CaCO3 | 5 | 86.3 | 83.1 | 3.708 | 88.6493 | 82.4361 | 93.9347 | Alkalinity | mg/L as CaCO3 | 6 | 62.1 | 59.5915 | 4.0394 | 86.3791 | 59.1475 | 89.8559 | TOCp, mg/L | #DIV/0! | BMRL | BMRL | BMRL | TOCp, mg/L | #DIV/0! | BMRL | BMRL | BMRL | Electric Rate ($/kW-h) | 0.06
Mailing Address |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | 3 | 0.5 | 12 | 10.9494 | 82.8577 | 335.6684 | 5.2675 | 10.5349 | 5.2675 | Strontium (mg/L) |  |  |  |  | Total organic carbon | mg/L | 2.4 | 2.15 | 2.275 | 10.989 | 1999-01-27 | 16:00 | 32 | 22.4 | 50 | 50 | 350 | 8.5 | 3.6 | 12.1 | 0.23793 | 0.70248 | 27.9256 | 19.3621 | 15.1049 | 2.5704 | 0.050184 | 2.5092 | 0.024896 | 49.9751 | 0.30225 | 1999-01-29 | 13:00 | 26 | 22.2 | 51 | 51 | 350 | 5.4 | 2.3 |  | 7.7 | 0.23793 | 0.7013 | 44.4545 | 12.3006 | 9.653 | 1641.1384 | 93.8114 | 1617.2653 | 15.3539 | 35.6461 | 0.2708 | [27 empty] | Total dissolved solids | mg/L | 91.8 | 92.5 | 92.15 | 0.75963 | 1420 | 1691.6328 | -19.1291 | 83.4263 | 1679.952 | 94.5147 | Total dissolved solids | mg/L | 174 | 2488 | 3112.4615 | -25.0989 | 68.705 | 3095.2967 | 94.3786 | Total dissolved solids | mg/L | 54.2 | 1008 | 1057.8 | -4.9405 | 90.2518 | 1049.2694 | 94.8345 | Total dissolved solids | mg/L | 39 | 713 | 767.169 | -7.5973 | 92.9856 | 761.1356 | 94.8761 | UV254 F, cm-1 | 0.03 | 0.03 | 0.03 | 0.03 | UV254 F, cm-1 | 0.03 | 0.03 | 0.03 | 0.03 | Fuel Oil Rate ($/gal) | NA
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 400 | 4 | 0.3 | 12 | 7.8526 | 79.7609 | 335.6684 | 5.2675 | 17.5582 | 12.2907 | Reactive silica (mg/L as SiO2) |  |  |  |  | UV254 | cm-1 | 0.03 | 0.03 | 0.03 | 0 | 1999-01-27 | 17:00 | 33 | 21.8 | 50 | 50 | 350 | 8.7 | 3.6 | 12.3 | 0.23793 | 0.70732 | 27.4553 | 19.8176 | 15.737 | 2.6102 | 0.050933 | 2.5466 | 0.025275 | 49.9747 | 0.3149 | 1999-01-29 | 15:00 | 28 | 22.8 | 51 | 51 | 350 | 5.4 | 2.4 |  | 7.8 | 0.23793 | 0.69231 | 43.8718 | 12.3006 | 9.4833 | 1601.0768 | 91.5214 | 1577.7865 | 14.9791 | 36.0209 | 0.26327 | [27 empty] | Total hardness | mg/L as CaCO3 | 4.7 | 4.6 | 4.65 | 2.1505 | 499.5 | 529.3052 | -5.967 | 97.0344 | 525.4737 | 99.1151 | Total hardness | mg/L as CaCO3 | 10.1 | 1159.8 | 1138.5615 | 1.8312 | 93.5587 | 1131.9697 | 99.1077 | Total hardness | mg/L as CaCO3 | 2.2 | 313.7 | 311.4 | 0.73318 | 98.5969 | 308.7718 | 99.2875 | Total hardness | mg/L as CaCO3 | 1.6 | 234 | 220.1915 | 5.901 | 98.9796 | 218.3804 | 99.2673 | UV254 p, cm-1 | 0.0025 | 0.005 | 0.003 | 0.002 | UV254 p, cm-1 | 0.0025 | 0.005 | 0.003 | 0.002 | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Purchase price for an equivalent 8" x 40 " element ($) | 700 | 1: For experimental matrix see Table 4-2 in Part 3 of the ICR Treatment Studies Manual. | [8 empty] | Turbidity (ntu) | 1.3 |  |  |  | SUVA | L/(mg*m) | 1.25 | 1.3953 | 1.3227 | 10.989 | 1999-01-28 | 8:00 | 48 | 22.8 | 50 | 50 | 350 | 8.6 | 3.6 | 12.2 | 0.23793 | 0.70492 | 27.6885 | 19.5899 | 15.103 | 2.5903 | 0.050559 | 2.5279 | 0.025086 | 49.9749 | 0.30221 | 1999-01-29 | 17:00 | 30 | 22.8 | 51 | 52 | 350 | 5.7 | 2.4 |  | 8.1 | 0.23793 | 0.7037 | 42.2099 | 12.984 | 10.0101 | 1652.3587 | 94.3753 | 1626.9858 | 15.453 | 36.047 | 0.2777 | 8.36 |  |  | 101.6 |  |  | 1635.2 |  | 81.7266 | 1622.7121 | 93.7389 | 0.002 |  |  | 0.0965 |  | 93.3333 | 0.09573 | 97.9108 | [8 empty] | Calcium hardness | mg/L as CaCO3 | 2.9 | 2.8 | 2.85 | 3.5088 | 324.6 | 349.5741 | -7.6938 | 97.2437 | 347.0421 | 99.1788 | Calcium hardness | mg/L as CaCO3 | 6.6 | 792.5 | 751.2154 | 5.2094 | 93.617 | 746.8658 | 99.1163 | Calcium hardness | mg/L as CaCO3 | 1.5 | 207.3 | 205.3 | 0.96479 | 98.5493 | 203.5677 | 99.2631 | Calcium hardness | mg/L as CaCO3 | 1.1 | 160.3 | 145.1845 | 9.4295 | 98.9362 | 143.9907 | 99.2361 | BromideF, ug/L | 150 | 150 | 150 | 150 | BromideF, ug/L | 150 | 150 | 150 | 150 | Current Process Water Rate ($/1000 gal) | 0.375
FAX Number |  | Maximum flow rate to the 8" x 40" element, QI, max (gpm) | 70 | 2: Flow rates and pressures may need to be adjusted in order to obtain the desired operating conditions. | [8 empty] | SDI |  |  |  |  | Bromide | mg/L | 150 | 150 | 150 | 0 | 1999-01-28 | 10:00 | 50 | 22.5 | 50 | 50 | 350 | 8.6 | 3.5 | 12.1 | 0.23793 | 0.71074 | 27.9256 | 19.5899 | 15.2375 | 2.6391 | 0.051511 | 2.5756 | 0.025558 | 49.9744 | 0.30491 | 1999-01-30 | 7:00 | 44 | 21.3 | 51 | 52 | 350 | 5.1 | 2.4 |  | 7.5 | 0.23793 | 0.68 | 45.6667 | 11.6172 | 9.3625 | 1549.1679 | 88.6269 | 1527.8857 | 14.499 | 37.001 | 0.25303 | 8.97 |  |  | 97.8 |  |  | 1529.675 |  | 82.4101 | 1519.2428 | 93.5626 | 0.003 |  |  | 0.087375 |  | 90 | 0.08676 | 96.5422 | [8 empty] | Turbidity | ntu | 0.1 | 0.12 | 0.11 | 18.1818 | 0.14 | 0.041034 | 70.6897 | -22.2222 | 0.041538 | -164.8169 | Turbidity | ntu | 0.11 | 0.15 | -0.043846 | 129.2308 | -22.2222 | -0.042947 | 356.1268 | Turbidity | ntu | 0.13 | 0.12 | 0.05 | 58.3333 | -44.4444 | 0.05068 | -156.5114 | Turbidity | ntu | 0.08 | 0.1 | 0.094085 | 5.9155 | 11.1111 | 0.093968 | 14.8645 | Bromidep, ug/L | 47.5 | 86 | 28 | 22 | Bromidep, ug/L | 47.5 | 86 | 28 | 22 | Modifications to Existing Plant (% of construction costs) | 46
E-Mail Address (optional) |  | Minimum flow rate to the 8" x 40" element, QI, min (gpm) | 18.8 | [9 empty] | MFI |  |  |  |  | SDS-Cl2 dose | mg/L | 4.3 | 4.3 | 4.3 | 0 | 1999-01-28 | 11:00 | 51 | 22.4 | 50 | 50 | 350 | 8.7 | 3.6 | 12.3 | 0.23793 | 0.70732 | 27.4553 | 19.8176 | 15.4604 | 2.6102 | 0.050933 | 2.5466 | 0.025275 | 49.9747 | 0.30936 | 1999-01-30 | 9:00 | 46 | 21 | 51 | 52 | 350 | 5.2 | 2.2 |  | 7.4 | 0.23793 | 0.7027 | 46.2973 | 11.845 | 9.6311 | 1647.4686 | 94.2248 | 1624.3918 | 15.4171 | 36.0829 | 0.26692 | [27 empty] | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! | BMRL | #DIV/0! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | BMRL | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | BMRL | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | BMRL | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | AlkF, mg/L CaCO3 | 44.05 | 44.05 | 44.05 | 44.05 | AlkF, mg/L CaCO3 | 44.05 | 44.05 | 44.05 | 44.05
|  | Total width of all membrane envelopes in the 8" x 40" element, w (ft) | 70.6 | [9 empty] | MPFI |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | SDS-Free Cl2 residual | mg/L | 0.869 | 0.7 | 0.7845 | 21.5424 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-30 | 11:00 | 48 | 21 | 51 | 52 | 350 | 5.2 | 2.2 |  | 7.4 | 0.23793 | 0.7027 | 46.2973 | 11.845 | 9.6311 | 1647.4686 | 94.2248 | 1624.3918 | 15.4171 | 36.0829 | 0.26692 | 8.92 | 9.09 | 8.91 | 98 | 556 | 1441 | 1638.5455 | -13.7089 | 82.3741 | 1627.1014 | 93.977 | 0.003 | 0.033 | 0.104 | 0.093818 | 9.7902 | 90 | 0.093144 | 96.7792 | [8 empty] | Total organic carbon | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | 6.2 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L | BMRL | 12 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 4.25 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 2.9 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkp, mg/L CaCO3 | 5.8 | 10.3 | 5 | 6 | Alkp, mg/L CaCO3 | 5.8 | 10.3 | 5 | 6
Plant Name | Facility 1 | Feed spacer thickness in the 8" x 40" element, T (ft) | 0.0026 | [9 empty] | Bromide (mg/L) | 160 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | SDS-Cl2 demand | mg/L | 3.431 | 3.6 | 3.5155 | 4.8073 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-30 | 13:00 | 50 | 21 | 52 | 52 | 350 | 5.3 | 2.3 |  | 7.6 | 0.23793 | 0.69737 | 45.0526 | 12.0728 | 9.8163 | 1623.3304 | 92.8189 | 1600.1541 | 15.1892 | 36.8108 | 0.26667 | [27 empty] | UV254 | cm-1 | 0.003 | 0.002 | 0.0025 | 40 | 0.103 | 0.097328 | 5.5072 | 91.6667 | 0.096635 | 97.4129 | UV254 | cm-1 | 0.005 | 0.214 | 0.19731 | 7.8001 | 83.3333 | 0.19618 | 97.4514 | UV254 | cm-1 | 0.003 | 0.061 | 0.057 | 6.5574 | 90 | 0.056541 | 94.6941 | UV254 | cm-1 | 0.002 | 0.046 | 0.041437 | 9.9204 | 93.3333 | 0.04111 | 95.135 | T-HdF, mg/L CaCO3 | 156.8 | 156.8 | 156.8 | 156.8 | T-HdF, mg/L CaCO3 | 156.8 | 156.8 | 156.8 | 156.8
Treatment Plant Category | CS/SOFT | [11 empty] | TOC (mg/L) | 2.6 | is to list the pretreatment processes used in this particular RBSMT run. |  |  | SDS-Chlorination temp. | oC | 6.3 | 6 | 6.15 | 4.878 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-30 | 15:00 | 52 | 21.2 | 51 | 52 | 350 | 5.3 | 2.3 |  | 7.6 | 0.23793 | 0.69737 | 45.0526 | 12.0728 | 9.7584 | 1623.3304 | 92.8189 | 1600.1541 | 15.1892 | 36.3108 | 0.26875 | [27 empty] | SUVA | L/(mg*m) | NR | NR | #DIV/0! | #VALUE! | 1.6613 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 1.7833 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 1.4353 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 1.5862 | --- | --- | --- | --- | --- | T-Hdp, mg/L CaCO3 | 4.65 | 10.1 | 2.2 | 1.6 | T-Hdp, mg/L CaCO3 | 4.65 | 10.1 | 2.2 | 1.6
Process Train Name | Coagulation/Sedimentation/Softening | Additional Information | [10 empty] | pH | 8.04 |  |  |  | SDS-Chlorination pH | --- | 9.54 | 9.5 | 9.52 | 0.42017 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-30 | 17:00 | 54 | 21 | 52 | 52 | 350 | 5.3 | 2.3 |  | 7.6 | 0.23793 | 0.69737 | 45.0526 | 12.0728 | 9.8163 | 1623.3304 | 92.8189 | 1600.1541 | 15.1892 | 36.8108 | 0.26667 | 8.98 |  |  | 97.5 |  |  | 1612.5435 |  | 82.464 | 1601.0724 | 93.9103 | 0.004 |  |  | 0.089913 |  | 86.6667 | 0.089263 | 95.5188 | [8 empty] | Bromide | mg/L | 48 | 47 | 47.5 | 2.1053 | --- | 400.9483 | --- | 68.3333 | 398.3671 | 88.0763 | Bromide | mg/L | 86 | --- | 578.3077 | --- | 42.6667 | 575.4319 | 85.0547 | Bromide | mg/L | 28 | --- | 272 | --- | 81.3333 | 269.926 | 89.6268 | Bromide | mg/L | 22 | --- | 202.2817 | --- | 85.3333 | 200.7879 | 89.0432 | Ca-HdF, mg/L CaCO3 | 103.4 | 103.4 | 103.4 | 103.4 | Ca-HdF, mg/L CaCO3 | 103.4 | 103.4 | 103.4 | 103.4
ICR Treatment Plant Identification Number | 381 | Design cross-flow velocity (fps) | [10 empty] | Total Hardness (mg/L as CaCO3) | 345 |  |  |  | SDS-Incubation time | hours | 40 | 40 | 40 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-31 | 7:00 | 68 | 20.8 | 52 | 52 | 350 | 5.1 | 2.2 |  | 7.3 | 0.23793 | 0.69863 | 46.9452 | 11.6172 | 9.5019 | 1628.8838 | 93.1874 | 1606.5065 | 15.2451 | 36.7549 | 0.25852 | 8.47 |  |  | 92.3 |  |  | 1630.9409 |  | 83.3993 | 1619.7308 | 94.3015 | 0.002 |  |  | 0.094909 |  | 93.3333 | 0.094232 | 97.8776 | [8 empty] | SDS-Cl2 dose | mg/L | 2 | 2 | 2 | 0 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2.8 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2.8 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2.8 | --- | --- | --- | --- | --- | --- | Ca-Hdp, mg/L CaCO3 | 2.85 | 6.6 | 1.5 | 1.1 | Ca-Hdp, mg/L CaCO3 | 2.85 | 6.6 | 1.5 | 1.1
PWSID Number of Plant (if assigned) | KS200910 | Required influent flow to permeate flow rate ratio, QI:Qp | 6.7 | [9 empty] | UV254 | 0.0756 |  |  |  | SDS-TOX | mg Cl- /L | 95 | 95 | 95 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-31 | 9:00 | 70 | 20.9 | 52 | 52 | 350 | 5.1 | 2.1 |  | 7.2 | 0.23793 | 0.70833 | 47.6111 | 11.6172 | 9.4738 | 1673.7412 | 95.7536 | 1650.7477 | 15.6649 | 36.3351 | 0.26074 | [27 empty] | SDS-Free Cl2 residual | mg/L | 0.897 | 0.924 | 0.9105 | 2.9654 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.944 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.613 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.383 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 0.1 | Maximum element recovery (%) | 15 | [9 empty] | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | SDS-CHCl3 | mg/L | 16.503 | 13.325 | 14.914 | 21.3088 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-31 | 11:00 | 72 | 21 | 52 | 52 | 350 | 5.1 | 2.1 |  | 7.2 | 0.23793 | 0.70833 | 47.6111 | 11.6172 | 9.4459 | 1673.7412 | 95.7536 | 1650.7477 | 15.6649 | 36.3351 | 0.25997 | 8.48 | 8.72 | 8.5 | 93.7 | 561 | 1447 | 1678.7286 | -16.0144 | 83.1475 | 1667.1805 | 94.3797 | 0.002 | 0.031 | 0.104 | 0.098 | 5.7692 | 93.3333 | 0.097301 | 97.9445 | [8 empty] | SDS-Cl2 demand | mg/L | 1.103 | 1.076 | 1.0895 | 2.4782 | --- | 9.455 | --- | 69.0087 | 9.3939 | 88.4021 | SDS-Cl2 demand | mg/L | 1.856 | --- | 14.6214 | --- | 47.2052 | 14.5468 | 87.2412 | SDS-Cl2 demand | mg/L | 1.187 | --- | 5.844 | --- | 66.2352 | 5.8044 | 79.5501 | SDS-Cl2 demand | mg/L | 1.417 | --- | 4.3726 | --- | 59.6928 | 4.3481 | 67.4114 | Blended Water Quality if THM4 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if THM4 Controls the Blend Ratio
Historical Average Water Temperature (oC) | 14 | Variability of design flux (%) | 15 | [9 empty] | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | SDS-BDCM | mg/L | 17.59 | 17.404 | 17.497 | 1.063 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-31 | 13:00 | 74 | 21.5 | 52 | 52 | 350 | 5.1 | 2.1 |  | 7.2 | 0.23793 | 0.70833 | 47.6111 | 11.6172 | 9.3073 | 1673.7412 | 95.7536 | 1650.7477 | 15.6649 | 36.3351 | 0.25615 | [27 empty] | SDS-Chlorination temp. | oC | 6.8 | 6.8 | 6.8 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 6 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 6 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 6 | --- | --- | --- | --- | --- | --- | Qp/QT (THM4), % | -20.0981 | -21.742 | -20.0981 | -20.0981 | Qp/QT (THM4), % | 39.951 | 43.2188 | 39.951 | 39.951
State Approved Plant Capacity (MGD) | 55 | Rejection of reference solute and conditions of test | 2000 ppm | [14 empty] | SDS-DBCM | mg/L | 16.807 | 18.239 | 17.523 | 8.1721 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-31 | 15:00 | 76 | 21.7 | 52 | 52 | 350 | 5.2 | 2.2 |  | 7.4 | 0.23793 | 0.7027 | 46.2973 | 11.845 | 9.4339 | 1647.4686 | 94.2248 | 1624.3918 | 15.4171 | 36.5829 | 0.25788 | [27 empty] | SDS-Chlorination pH | --- | 9.48 | 9.54 | 9.51 | 0.63091 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 9.53 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 9.48 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 9.51 | --- | --- | --- | --- | --- | --- | SDS-THM4b, ug/L | NA | NA | NA | NA | SDS-THM4b, ug/L | 36 | 36 | 36 | 36
|  | (e.g., solute type and concentration) | NaCl | [14 empty] | SDS-CHBr3 | mg/L | 9.422 | 10.612 | 10.017 | 11.8798 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-31 | 17:00 | 78 | 21.2 | 52 | 52 | 350 | 5.4 | 2.4 |  | 7.8 | 0.23793 | 0.69231 | 43.8718 | 12.3006 | 9.9426 | 1601.0768 | 91.5214 | 1577.7865 | 14.9791 | 37.0209 | 0.26857 | 8.5 |  |  | 94.6 |  |  | 1594.15 |  | 82.9856 | 1582.582 | 94.0224 | 0.002 |  |  | 0.093 |  | 93.3333 | 0.092298 | 97.8331 | [8 empty] | SDS-Incubation time | hours | 40 | 40 | 40 | 0 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 40 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 40 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 40 | --- | --- | --- | --- | --- | --- | SDS-HAA5b, ug/L | NA | NA | NA | NA | SDS-HAA5b, ug/L | 14.6223 | 14.5195 | 14.5532 | 14.6365
|  | Variability of rejection of reference solute (%) | 3 | [14 empty] | SDS-THM4 | mg/L | 60.322 | 59.58 | 59.951 | 1.2377 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-02-01 | 8:00 | 93 | 21.2 | 52 | 52 | 350 | 4.9 | 0.6 |  | 5.5 | 0.23793 | 0.89091 | 62.6364 | 11.1617 | 9.022 | 3473.1095 | 198.8029 | 3427.2692 | 32.5139 | 19.4861 | 0.46299 | [27 empty] | SDS-TOX | mg Cl- /L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOXb, ug Cl- /L | NA | NA | NA | NA | SDS-TOXb, ug Cl- /L | #DIV/0! | #VALUE! | #VALUE! | #VALUE!
|  | Standard testing recovery (%) | 15 | [14 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-02-01 | 9:00 | 94 | 21.3 | 52 | 52 | 350 | 4.3 | 0.6 |  | 4.9 | 0.23793 | 0.87755 | 70.4286 | 9.7949 | 7.8939 | 3218.2842 | 184.5185 | 3181.0123 | 30.1513 | 21.8487 | 0.3613 | 8.84 |  |  | 142.9 |  |  | 3516.55 |  | 74.2986 | 3495.8261 | 95.9123 | 0.003 |  |  | 0.2235 |  | 90 | 0.22215 | 98.6495 | [8 empty] | SDS-CHCl3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHCl3 | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHCl3 | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHCl3 | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDb, mg/L | NA | NA | NA | NA | SDS-CDb, mg/L | 2.5463 | 2.7983 | 2.5852 | 2.6771
|  | Standard testing pH | 7 | [14 empty] | SDS-DCAA* | mg/L | 14.4401 | 12.3522 | 13.3962 | 15.5858 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-02-01 | 10:00 | 95 | 21.5 | 53 | 53 | 350 | 4.3 | 0.57 |  | 4.87 | 0.23793 | 0.88296 | 70.8686 | 9.7949 | 7.8473 | 3316.0978 | 190.1266 | 3277.6931 | 31.0677 | 21.9323 | 0.3578 | 8.93 |  |  | 152.8 |  |  | 3597.6842 |  | 72.518 | 3576.5228 | 95.7277 | 0.003 |  |  | 0.23368 |  | 90 | 0.23227 | 98.7084 | [8 empty] | SDS-BDCM | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-BDCM | mg/L | 1.194 | --- | 126.6017 | --- | 93.176 | 125.8691 | 99.0514 | SDS-BDCM | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | TOCb, mg/L | NA | NA | NA | NA | TOCb, mg/L | #DIV/0! | #VALUE! | #VALUE! | #VALUE!
|  | Acceptable range of operating pressures | < 600 PSI | [14 empty] | SDS-TCAA* | mg/L | 2.7037 | 2.6531 | 2.6784 | 1.8892 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-02-01 | 11:00 | 96 | 21.5 | 53 | 53 | 350 | 4.2 | 0.57 |  | 4.77 | 0.23793 | 0.8805 | 72.3753 | 9.5671 | 7.6648 | 3270.7082 | 187.5753 | 3233.7106 | 30.6463 | 22.3537 | 0.34289 | 8.99 |  |  | 160 |  |  | 3473.8947 |  | 71.223 | 3454.0114 | 95.3677 | 0.003 |  |  | 0.22895 |  | 90 | 0.22759 | 98.6818 | [8 empty] | SDS-DBCM | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DBCM | mg/L | 1.81 | --- | 122.6792 | --- | 89.6707 | 121.9732 | 98.5161 | SDS-DBCM | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 b, cm-1 | NA | NA | NA | NA | UV254 b, cm-1 | 0.019013 | 0.019195 | 0.019213 | 0.018814
|  | Acceptable range of operating pH values | pH 2-11 | [14 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-02-01 | 12:00 | 97 | 21.7 | 54 | 53 | 350 | 4.1 | 0.6 |  | 4.7 | 0.23793 | 0.87234 | 73.4681 | 9.3394 | 7.4382 | 3128.8339 | 179.4877 | 3094.2844 | 29.3207 | 24.1793 | 0.30763 | 9.03 | 9.46 | 9.08 | 163.1 | 544 | 1965 | 3240.8167 | -64.9271 | 70.6655 | 3222.79 | 94.9392 | 0.003 | 0.032 | 0.194 | 0.2145 | -10.567 | 90 | 0.21326 | 98.5933 | [8 empty] | SDS-CHBr3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 1.529 | --- | 66.8213 | --- | 84.7359 | 66.4399 | 97.6987 | SDS-CHBr3 | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Bromideb, ug/L | NA | NA | NA | NA | Bromideb, ug/L | 109.0503 | 122.34 | 101.2598 | 98.8628
|  | Typical pressure drop across a single element (psi) | 6 | [14 empty] | SDS-DBAA* | mg/L | 7.0018 | 7.707 | 7.3544 | 9.5888 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-02-01 | 15:00 | 100 | 22.4 | 54 | 54 | 350 | 4.1 | 0.57 |  | 4.67 | 0.23793 | 0.87794 | 73.9465 | 9.3394 | 7.2859 | 3224.6922 | 184.9867 | 3189.0842 | 30.219 | 23.781 | 0.30638 | [27 empty] | SDS-THM4 | mg/L | 0 | 0 | 0 | #DIV/0! | --- | 206.7276 | --- | 100 | 205.2179 | 100 | SDS-THM4 | mg/L | 4.533 | --- | 430.8253 | --- | 92.4388 | 428.3352 | 98.9417 | SDS-THM4 | mg/L | 0 | --- | 119.902 | --- | 100 | 118.8828 | 100 | SDS-THM4 | mg/L | 0 | --- | 84.438 | --- | 100 | 83.7384 | 100 | Alkb, mg/L CaCO3 | NA | NA | NA | NA | Alkb, mg/L CaCO3 | 28.7688 | 29.4637 | 28.4492 | 28.8487
|  | Maximum permissible SDI | 5 | [14 empty] | SDS-BCAA* | mg/L | 8.7824 | 7.4294 | 8.1059 | 16.6915 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-02-02 | 8:00 | 115 | 22.8 | 54 | 54 | 350 | 4.2 | 4.3 |  | 8.5 | 0.23793 | 0.49412 | 40.1765 | 9.5671 | 7.3759 | 1040.7697 | 59.6882 | 1028.9967 | 9.7519 | 44.2481 | 0.16669 | [27 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | T-Hdb, mg/L CaCO3 | NA | NA | NA | NA | T-Hdb, mg/L CaCO3 | 96.0146 | 93.398 | 95.0358 | 94.7961
|  | Maximum permissible turbidity (ntu) | 1 | [14 empty] | SDS-TBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-02-02 | 9:00 | 116 | 22.9 | 53 | 53 | 350 | 5.3 | 5.5 |  | 10.8 | 0.23793 | 0.49074 | 31.4074 | 12.0728 | 9.2802 | 1034.7673 | 59.166 | 1019.9939 | 9.6821 | 43.3179 | 0.21424 | 8.76 |  |  | 60.7 |  |  | 1033.2891 |  | 89.0827 | 1025.9252 | 94.0834 | 0 | [15 empty] | SDS-DCAA* | mg/L | 1.3876 | 1.3831 | 1.3854 | 0.32483 | --- | 42.8019 | --- | 89.6586 | 42.4994 | 96.7403 | SDS-DCAA* | mg/L | 1.773 | --- | 91.1818 | --- | 86.7649 | 90.6596 | 98.0443 | SDS-DCAA* | mg/L | 1.2124 | --- | 25.5799 | --- | 90.9496 | 25.3728 | 95.2217 | SDS-DCAA* | mg/L | 1.4208 | --- | 18.2875 | --- | 89.394 | 18.1477 | 92.1709 | Ca-Hdb, mg/L CaCO3 | NA | NA | NA | NA | Ca-Hdb, mg/L CaCO3 | 63.2293 | 61.5642 | 62.69 | 62.5302
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | 1000 ppm/hours | [14 empty] | SDS-CDBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-02-02 | 10:00 | 117 | 22.9 | 53 | 53 | 350 | 5.6 | 5.4 |  | 11 | 0.23793 | 0.50909 | 30.8182 | 12.7562 | 9.8055 | 1069.243 | 61.0871 | 1053.1125 | 10.0009 | 42.9991 | 0.22804 | 8.84 |  |  | 55.8 |  |  | 1074.7259 |  | 89.964 | 1066.5745 | 94.7683 | 0.001 |  |  | 0.060074 |  | 96.6667 | 0.059601 | 98.3222 | [8 empty] | SDS-TCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TCAA* | mg/L | 1.0411 | --- | 13.6357 | --- | 61.1298 | 13.5621 | 92.3235 | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | 1: All of the information requested in this field may not be available, but values for all Design | [15 empty] | SDS-DCBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-02-02 | 11:00 | 118 | 22.4 | 53 | 53 | 350 | 5.8 | 5.6 |  | 11.4 | 0.23793 | 0.50877 | 29.7018 | 13.2118 | 10.3069 | 1068.6577 | 61.0202 | 1051.9597 | 9.9929 | 43.0071 | 0.23966 | 8.85 |  |  | 56.6 |  |  | 1073.2357 |  | 89.8201 | 1064.8122 | 94.6845 | 0.002 |  |  | 0.059 |  | 93.3333 | 0.058528 | 96.5828 | [8 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  | Parameters must be entered in cells E14:E23, since these parameters are used in calculations. | [15 empty] | SDS-HAA5 | mg/L | 24.1456 | 22.7123 | 23.429 | 6.1176 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-02-02 | 12:00 | 119 | 23.1 | 53 | 53 | 350 | 6 | 5.9 |  | 11.9 | 0.23793 | 0.5042 | 28.4118 | 13.6673 | 10.444 | 1059.9109 | 60.4876 | 1042.7779 | 9.9086 | 43.0914 | 0.24237 | 8.77 | 8.97 | 8.87 | 56.1 | 543 | 968 | 1064.3729 | -9.9559 | 89.9101 | 1055.7305 | 94.6861 | 0.003 | 0.035 | 0.064 | 0.057458 | 10.2225 | 90 | 0.056991 | 94.736 | [8 empty] | SDS-DBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Blended Water Quality if HAA5 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if HAA5 Controls the Blend Ratio
[18 empty] | SDS-HAA6 | mg/L | 32.928 | 30.1417 | 31.5348 | 8.8356 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-02-02 | 16:00 | 123 | 22.9 | 52 | 52 | 350 | 6.2 | 6.2 |  | 12.4 | 0.23793 | 0.5 | 27.2258 | 14.1229 | 10.8561 | 1051.997 | 60.003 | 1034.4245 | 9.8321 | 42.1679 | 0.25745 | [27 empty] | SDS-BCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-BCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Qp/QT (HAA5), % | -138.6845 | -148.2963 | -137.6048 | -138.9079 | Qp/QT (HAA5), % | -16.1999 | -17.3227 | -16.0738 | -16.226
[18 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-02-03 | 8:00 | 139 | 22 | 51 | 51 | 350 | 5.8 | 14.5 |  | 20.3 | 0.23793 | 0.28571 | 16.2414 | 13.2118 | 10.4295 | 761.0184 | 43.454 | 749.1273 | 7.1162 | 43.8838 | 0.23766 | [27 empty] | SDS-TBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-THM4b, ug/L | NA | NA | NA | NA | SDS-THM4b, ug/L | NA | NA | NA | NA
[18 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-02-03 | 9:00 | 140 | 21.9 | 51 | 51 | 350 | 5.8 | 13 |  | 18.8 | 0.23793 | 0.30851 | 17.617 | 13.2118 | 10.4604 | 784.0867 | 44.7712 | 771.8352 | 7.3319 | 43.6681 | 0.23954 | 9.22 |  |  | 47.1 |  |  | 783.0477 |  | 91.5288 | 776.9498 | 93.9378 | 0 | [15 empty] | SDS-CDBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-HAA5b, ug/L | NA | NA | NA | NA | SDS-HAA5b, ug/L | NA | NA | NA | NA
[18 empty] | should be reported if measured. | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-02-03 | 10:00 | 141 | 21.8 | 51 | 51 | 350 | 5.7 | 13.2 |  | 18.9 | 0.23793 | 0.30159 | 17.5185 | 12.984 | 10.3104 | 776.9291 | 44.3747 | 764.9989 | 7.2659 | 43.7341 | 0.23575 | 9.25 |  |  | 47.2 |  |  | 775.7091 |  | 91.5108 | 769.7769 | 93.8684 | 0 | [15 empty] | SDS-DCBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TOXb, ug Cl- /L | NA | NA | NA | NA | SDS-TOXb, ug Cl- /L | NA | NA | NA | NA
[45 empty] | 1999-02-03 | 11:00 | 142 | 21.6 | 51 | 51 | 350 | 6.3 | 14.2 |  | 20.5 | 0.23793 | 0.30732 | 16.0732 | 14.3507 | 11.4633 | 782.8707 | 44.6406 | 769.5826 | 7.3159 | 43.6841 | 0.26241 | 9.22 |  |  | 47.1 |  |  | 781.7796 |  | 91.5288 | 775.1675 | 93.9239 | 0 | [15 empty] | SDS-HAA5 | mg/L | 1.3876 | 1.3831 | 1.3854 | 0.32483 | --- | 77.3978 | --- | 94.087 | 76.8427 | 98.1972 | SDS-HAA5 | mg/L | 2.8141 | --- | 161.3899 | --- | 87.9888 | 160.4636 | 98.2463 | SDS-HAA5 | mg/L | 1.2124 | --- | 45.6455 | --- | 94.8252 | 45.2678 | 97.3217 | SDS-HAA5 | mg/L | 1.4208 | --- | 32.4182 | --- | 93.9357 | 32.1614 | 95.5823 | SDS-CDb, mg/L | NA | NA | NA | NA | SDS-CDb, mg/L | NA | NA | NA | NA
[45 empty] | 1999-02-03 | 12:00 | 143 | 22.1 | 51 | 51 | 350 | 5.8 | 14.2 |  | 20 | 0.23793 | 0.29 | 16.5 | 13.2118 | 10.3987 | 765.251 | 43.6957 | 753.2938 | 7.1558 | 43.8442 | 0.23717 | 9.3 | 9.51 | 9.44 | 47.1 | 553 | 750 | 763.8606 | -1.8481 | 91.5288 | 757.9217 | 93.7856 | 0.003 | 0.032 | 0.045 | 0.041028 | 8.8263 | 90 | 0.040713 | 92.6314 | [8 empty] | SDS-HAA6 | mg/L | 1.3876 | 1.3831 | 1.3854 | 0.32483 | --- | 105.3491 | --- | 95.6069 | 104.5899 | 98.6754 | SDS-HAA6 | mg/L | 2.8141 | --- | 223.7429 | --- | 91.0762 | 222.4524 | 98.735 | SDS-HAA6 | mg/L | 1.2124 | --- | 61.8573 | --- | 96.1554 | 61.3418 | 98.0235 | SDS-HAA6 | mg/L | 1.4208 | --- | 43.835 | --- | 95.4945 | 43.4835 | 96.7326 | TOCb, mg/L | NA | NA | NA | NA | TOCb, mg/L | NA | NA | NA | NA
[45 empty] | 1999-02-03 | 16:00 | 147 | 22.9 | 51 | 51 | 350 | 6.1 | 14.6 |  | 20.7 | 0.23793 | 0.29469 | 15.9082 | 13.8951 | 10.681 | 769.948 | 43.9278 | 757.2945 | 7.1969 | 43.8031 | 0.24384 | [27 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | UV254 b, cm-1 | NA | NA | NA | NA | UV254 b, cm-1 | NA | NA | NA | NA
[45 empty] | 1999-02-04 | 17:00 | 161 | 22.4 | 52 | 52 | 350 | 6 | 14.8 | X | 20.8 | 0.23793 | 0.28846 | 15.8269 | 13.6673 | 10.6623 | 763.7357 | 43.5853 | 751.3903 | 7.1398 | 44.8602 | 0.23768 | 8.95 | 9.35 | 9.37 | 43.9 | 530 | 709 | 763.6081 | -7.7021 | 92.1043 | 757.4392 | 94.2042 | 0 | 0.03 | 0.043 |  | #VALUE! | [11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | Bromideb, ug/L | NA | NA | NA | NA | Bromideb, ug/L | NA | NA | NA | NA
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Alkb, mg/L CaCO3 | NA | NA | NA | NA | Alkb, mg/L CaCO3 | NA | NA | NA | NA
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | T-Hdb, mg/L CaCO3 | NA | NA | NA | NA | T-Hdb, mg/L CaCO3 | NA | NA | NA | NA
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Ca-Hdb, mg/L CaCO3 | NA | NA | NA | NA | Ca-Hdb, mg/L CaCO3 | NA | NA | NA | NA
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Notes: |  |  |  |  | Notes:
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to |  |  |  |  | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | determine the percentage of total flow that must be treated by the membrane process to meet the |  |  |  |  | determine the percentage of total flow that must be treated by the membrane process to meet the
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Stage 1 DBP MCLs. |  |  |  |  | Stage 2 DBP MCLs.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | A 10% factor of safety has been applied all the MCLs. i.e., 72 / 54 mg/L for THM4 and HAA5. |  |  |  |  | A 10% factor of safety has been applied all the MCLs. i.e., 36 / 27 mg/L for THM4 and HAA5.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for |  |  |  |  | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | both parameters and the maximum (Qp/QT) ratio controls the design. |  |  |  |  | both parameters and the maximum (Qp/QT) ratio controls the design.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. |  |  |  |  | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. |  |  |  |  | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. |  |  |  |  | The subscript "b" refers to the blended water quality for a given blend ratio.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL. |  |  |  |  | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. |  |  |  |  | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Note on X24: Alison Gusses: High precision incubator was used for SDS testing
Note on CY29: Alison Gusses: High precision incubator was used for SDS testing
Note on DL29: Alison Gusses: High precision incubator was used for SDS testing
Note on DV29: Alison Gusses: High precision incubator was used for SDS testing
Note on EF29: Alison Gusses: High precision incubator was used for SDS testing

## NF200. 1st Quarter
FIELD-SET 1: 1st QUARTER RBSMT RESULTS (FILE: rbsmt-1.xls)
Field 1-1: PWS And Treatment Plant Data |  | Field 1-2: Manufacturer Reported Membrane Characteristics1 |  | Field 1-3: RBSMT Design Parameters | [8 empty] | Field 1-4: Foulants And Fouling Indices1 |  | Field 1-5: Pretreatment Used Prior To Membranes1 |  |  | Field 1-6: Feed Water Quality After Pretreatment | [5 empty] | Field 1-7: Membrane Setting Data | [20 empty] | Field 1-8: Membrane Performance Data During Operation With The Test Water | [16 empty] | Field 1-8: Membrane Performance Data During Operation With The Test Water (continued) | [19 empty] | Field 1-8: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 1-9: Permeate And Concentrate Water Quality For Run 1 | [11 empty] | Field 1-10: Permeate And Concentrate Water Quality For Run 2 | [8 empty] | Field 1-11: Permeate And Concentrate Water Quality For Run 3 | [8 empty] | Field 1-12: Permeate And Concentrate Water Quality For Run 4 | [8 empty] | Field 1-13: Blending Calculations For Stage 1 D-DBP MCLs |  |  |  |  | Field 1-14: Blending Calculations For Proposed Stage 2 D-DBP MCLs |  |  |  |  | Field 1-15: Membrane Cost Parameters
|  | General Information |  | Input Design Parameters | [8 empty] | Parameters Evaluated Prior to Pretreatment | [80 empty] | Operating Parameters During Sample Collection | [11 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Feed and Permeate Water Quality Parameters |  |  |  |  | Feed and Permeate Water Quality Parameters |  |  |  |  | General Cost Parameters
PWS Name | Water District No. 1 of Johnson County, Kansas | Membrane manufacturer | FilmTec Corporation | [5 empty] | Active membrane area in bench-scale cell, Acell (ft2) | 0.167 |  |  | Alkalinity (mg/L as CaCO3) | 151 | Process | Description | Scale | Parameter | Units | CF-1 | CF-2 | Average | RPD |  |  |  | Average TDS rejection (decimal fraction) | 0.96 | [5 empty] | TDS concentration of setting solution (mg/L) | 840 | [12 empty] | Average bulk TDS rejection (decimal fraction) | 0.76907 | [45 empty] | Recovery during sample collection (decimal) | 0.71 | [10 empty] | Recovery during sample collection (decimal) | 0.89 | [7 empty] | Recovery during sample collection (decimal) | 0.5 | [7 empty] | Recovery during sample collection (decimal) | 0.29 | [8 empty] | RUN ID # |  |  |  |  | RUN ID # |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | KS200910 | Membrane trade name | NF200B-4040 | [5 empty] | Active width of membrane in the bench-scale cell, wcell (ft) | 0.333 |  |  | Calcium Hardness (mg/L as CaCO3) | 176 | Presedimentation | 3 Basins | Full-scale | Sampling date | MM/DD/YY | 1998-05-06 | 1998-05-13 | --- | --- | [71 empty] | Feed flow rate during sample collection (mL/min) | 10.1 | [10 empty] | Feed flow rate during sample collection (mL/min) | 7.63 | [7 empty] | Feed flow rate during sample collection (mL/min) | 14.9 | [7 empty] | Feed flow rate during sample collection (mL/min) | 24.5 | [6 empty] | Parameter | 1 | 2 | 3 | 4 | Parameter | 1 | 2 | 3 | 4 | Capital Recovery Interest Rate (%) | 5
Water Industry Data Base Number (optional) | NA | Molecular weight cutoff (Daltons) | 400 | [5 empty] | Average yearly temperature of feed water, TavgoC (oC) | 14 |  |  | LSI | 0.61 | Softening | Lime, 200 mg/L as Ca(OH)2 | Bench-scale | Sampling time | hh:mm | 11:30 | 7:25 | --- | --- | Date | Time | Setting time | Influent | PI | PC | QI | Qp | QW | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) | Date | Time | Operation time | Influent | PI | PC | QI | Qp | QW | Cleaning Event | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1) | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Influent flow rate during sample collection (mL/min) | 590 | [10 empty] | Influent flow rate during sample collection (mL/min) | 590 | [7 empty] | Influent flow rate during sample collection (mL/min) | 590 | [7 empty] | Influent flow rate during sample collection (mL/min) | 590 | [6 empty] | SDS-THM4F, ug/L | 99.995 | 99.995 | 99.995 | 99.995 | SDS-THM4F, ug/L | 99.995 | 99.995 | 99.995 | 99.995 | Capital Recovery Period (years) | 20
|  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide | [5 empty] | Approximate feed water TDS, TDSF (mg/L) | 322 |  |  | Dissolved iron (mg/L) |  | Coagulation | Alum: Al2(SO4)3.14H2O, 15 mg/L | Bench-scale | Operation time | hh.hh | 0 | 163 | --- | --- | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | Indicate with "X" | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) | [39 empty] | SDS-THM4p, ug/L | 8.16 | 11.83 | 5.66 | 5.58 | SDS-THM4p, ug/L | 8.16 | 11.83 | 5.66 | 5.58 | Overhead & Profit Factor (% of construction costs) | 15
Official ICR Contact Person |  | Membrane construction (e.g., thin-film composite) | Thin-Film composite | [5 empty] | Manufacturer reported TDS rejection, RejTDS (decimal fraction) | 0.7 |  |  | Total iron (mg/L) |  | Sedimentation | Gravity settling in test drums | Bench-scale | pH | --- | 8.57 | 8.67 | 8.62 | 1.1601 | 1998-05-04 | 12:30 | 0 | [6 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-06 | 12:00 | 0 | 24.3 | 60 | 61 | 590 | 7.3 | 3.5 |  | 10.8 | 0.4534 | 0.67593 | 53.6296 | 16.6286 | 12.264 | 672.693 | 153.8595 | 666.2736 | 5.1562 | 55.3438 | 0.2216 | [27 empty] | Permeate and Concentrate Water Quality | [11 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | SDS-HAA5F, ug/L | 25.06 | 25.06 | 25.06 | 25.06 | SDS-HAA5F, ug/L | 25.06 | 25.06 | 25.06 | 25.06 | Special Sitework Factor (% of construction costs) | 0
Mailing Address |  | Membrane hydrophobicity | hydrophilic | [5 empty] | Temperature normalized MTCW (gfd/psi) | 0.16977 |  |  | Dissolved aluminum (mg/L) |  | Recarbonation | CO2 gas added to pH 9.4 | Bench-scale | Temperature | oC | 21.5 | 23 | 22.25 | 6.7416 | 1998-05-04 | 13:00 | 0.5 | 22.4 | 60 | 61 | 605 | 7.1 | 26 | 33.1 | 0.46493 | 0.2145 | 17.2779 | 16.173 | 12.6171 | 1057.9587 | 41.8414 | 1046.034 | 10.1016 | 50.3984 | 0.25035 | 1998-05-06 | 15:00 | 3 | 24.5 | 60 | 61 | 590 | 7.1 | 3.1 |  | 10.2 | 0.4534 | 0.69608 | 56.8431 | 16.173 | 11.8577 | 695.2061 | 159.0508 | 688.7541 | 5.3293 | 55.1707 | 0.21493 | 8.37 | 8.55 | 8.42 | 154.4 | 322 | 637 | 705.8581 | -10.8097 | 52.0497 | 702.54 | 78.0226 | 0.004 | 0.052 | 0.164 | 0.16358 | 0.2557 | 92.381 | 0.16262 | 97.5403 | [8 empty] | Parameter | Units | Cp-1 | Cp-1 (dup) | Average | RPD | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | SDS-HAA5p, ug/L | 0 | 0 | 0 | 0 | SDS-HAA5p, ug/L | 0 | 0 | 0 | 0 | Construction Contingencies (% of construction costs) | 15
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | negative | [9 empty] | Total aluminum (mg/L) |  | Cartridge filtration | 1 um size exclusion | Bench-scale | Alkalinity | mg/L as CaCO3 | 55.5 | 54 | 54.75 | 2.7397 | 1998-05-04 | 16:00 | 3.5 | 23.9 | 60 | 61 | 590 | 7.2 | 39.6 | 46.8 | 0.4534 | 0.15385 | 11.6068 | 16.4008 | 12.2399 | 985.643 | 38.9636 | 974.0903 | 9.409 | 51.091 | 0.23957 | 1998-05-06 | 17:00 | 5 | 23.4 | 60 | 61 | 590 | 7.2 | 3.1 |  | 10.3 | 0.4534 | 0.69903 | 56.2816 | 16.4008 | 12.4221 | 698.6707 | 159.8223 | 692.0949 | 5.3556 | 55.1444 | 0.22527 | 8.14 |  |  | 154.4 |  |  | 711.2645 |  | 52.0497 | 707.8667 | 78.188 | 0.005 |  |  | 0.16282 |  | 90.4762 | 0.16186 | 96.9109 | [8 empty] | Sampling date | MM/DD/YY | 1998-05-09 | 1998-05-09 | --- | --- | 1998-05-09 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-05-10 | 1998-05-10 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-05-11 | 1998-05-11 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-05-12 | 1998-05-12 | --- | --- | --- | --- | --- | SDS-TOXF, ug Cl- /L | 180 | 180 | 180 | 180 | SDS-TOXF, ug Cl- /L | 180 | 180 | 180 | 180 | Engineering Fee Factor (% of construction costs) | 15
Phone Number |  |  |  | Experimental Design1,2 | [8 empty] | Fluoride (mg/L) |  | Antiscalant | 4 mg/L Hypersperse 400UL | Bench-scale | Total dissolved solids | mg/L | 322 | 322 | 322 | 0 | 1998-05-04 | 18:00 | 5.5 | 24 | 60 | 61 | 590 | 7.2 | 39.7 | 46.9 | 0.4534 | 0.15352 | 11.58 | 16.4008 | 12.2037 | 985.2787 | 38.9492 | 973.7303 | 9.4056 | 51.0944 | 0.23885 | 1998-05-07 | 7:00 | 19 | 22 | 60 | 61 | 590 | 7 | 3 |  | 10 | 0.4534 | 0.7 | 58 | 15.9452 | 12.5873 | 699.7433 | 160.11 | 693.3408 | 5.3643 | 55.1357 | 0.2283 | 8.11 |  |  | 150.1 |  |  | 723.1 |  | 53.3851 | 719.7008 | 79.1441 | 0.002 |  |  | 0.17033 |  | 96.1905 | 0.16933 | 98.8189 | [8 empty] | Sampling time | hh:mm | 17:00 | 17:00 | --- | --- | 17:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 16:00 | 16:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 16:00 | 16:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 16:30 | 16:30 | --- | --- | --- | --- | --- | SDS-TOXp, ug Cl- /L | #DIV/0! | BMRL | BMRL | BMRL | SDS-TOXp, ug Cl- /L | #DIV/0! | BMRL | BMRL | BMRL | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920
FAX Number |  | Design Parameters |  | ID# | Recovery | FW-design | Dp | PI | QI-cell | Qp | QF | QW | Phosphate (mg/L) |  |  |  |  | Total hardness | mg/L as CaCO3 | 118.4 | 116.1 | 117.25 | 1.9616 | 1998-05-05 | 7:00 | 18.5 | 22.5 | 60 | 61 | 590 | 7.1 | 40.8 | 47.9 | 0.4534 | 0.14823 | 11.3173 | 16.173 | 12.5798 | 979.4376 | 38.7247 | 968.1172 | 9.3505 | 51.1495 | 0.24594 | 1998-05-07 | 9:00 | 21 | 22 | 62 | 62 | 590 | 7 | 3 |  | 10 | 0.4534 | 0.7 | 58 | 15.9452 | 12.5873 | 699.7433 | 160.11 | 693.3408 | 5.3643 | 56.6357 | 0.22225 | [27 empty] | Operation time | hh.hh | 77 | 77 | --- | --- | 77 | --- | --- | --- | --- | --- | Operation time | hh.hh | 100 | 100 | --- | --- | --- | --- | --- | Operation time | hh.hh | 124 | 124 | --- | --- | --- | --- | --- | Cumulative time | hr | 148.5 | 148.5 | --- | --- | --- | --- | --- | SDS-CDF, mg/L | 3.22 | 3.22 | 3.22 | 3.22 | SDS-CDF, mg/L | 3.22 | 3.22 | 3.22 | 3.22 | 1998 Producers Price Index (PPI base year 1967 = 100) | 370
E-Mail Address (optional) |  | Design flux, FW (gfd) | 16.5 |  | (decimal) | (gfd) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | Sulfate (mg/L) |  |  |  |  | Calcium hardness | mg/L as CaCO3 | 99.1 | 95.6 | 97.35 | 3.5953 | 1998-05-05 | 11:00 | 22.5 | 23.2 | 60 | 61 | 590 | 7.1 | 41.2 | 48.3 | 0.4534 | 0.147 | 11.2153 | 16.173 | 12.3222 | 978.093 | 38.6715 | 966.7881 | 9.3377 | 51.1623 | 0.24085 | 1998-05-07 | 11:00 | 23 | 23 | 62 | 62 | 590 | 7 | 3 |  | 10 | 0.4534 | 0.7 | 58 | 15.9452 | 12.2207 | 699.7433 | 160.11 | 693.3408 | 5.3643 | 56.6357 | 0.21578 | 8 | 8.22 | 8.16 | 153.5 | 316 | 648 | 715.1667 | -10.3652 | 52.3292 | 711.8347 | 78.436 | 0.003 | 0.052 | 0.166 | 0.168 | -1.2048 | 94.2857 | 0.16702 | 98.2038 | [8 empty] | pH | --- | 8.18 | 8.42 | 8.3 | 2.8916 | 8.47 | --- | --- | --- | --- | --- | pH | --- | 8.16 | 8.27 | --- | --- | --- | --- | --- | pH | --- | 8.26 | 7.86 | --- | --- | --- | --- | --- | pH | --- | 7.66 | 8.33 | --- | --- | --- | --- | --- | SDS-CDp, mg/L | 0.435 | 0.78 | 0.63 | 0.51 | SDS-CDp, mg/L | 0.435 | 0.78 | 0.63 | 0.51 | Labor Rate + Fringe ($/work-hour) | 17
|  | Net driving pressure at the design flux, NDP (psi) | 70 | 1 | 0.7 | 15 | 8.4793 | 96.8347 | 606.4586 | 6.5843 | 9.4062 | 2.8219 | Calcium (mg/L) | 71 |  |  |  | Turbidity | ntu | 0.17 | 0.15 | 0.16 | 12.5 | 1998-05-05 | 15:00 | 26.5 | 23.9 | 60 | 61 | 590 | 7.2 | 41.5 | 48.7 | 0.4534 | 0.14784 | 11.115 | 16.4008 | 12.2399 | 979.0204 | 38.7018 | 967.5453 | 9.3458 | 51.1542 | 0.23927 | 1998-05-07 | 13:00 | 25 | 23.4 | 61 | 62 | 590 | 7.2 | 3 |  | 10.2 | 0.4534 | 0.70588 | 56.8431 | 16.4008 | 12.4221 | 706.7764 | 161.6765 | 700.1243 | 5.4177 | 56.0823 | 0.2215 | [27 empty] | Temperature | oC | 19 | 19 | 19 | 0 | 19 | --- | --- | --- | --- | --- | Temperature | oC | 21 | 21 | --- | --- | --- | --- | --- | Temperature | oC | 22 | 22 | --- | --- | --- | --- | --- | Temperature | oC | 21 | 21 | --- | --- | --- | --- | --- | TOCF, mg/L | 3.15 | 3.15 | 3.15 | 3.15 | TOCF, mg/L | 3.15 | 3.15 | 3.15 | 3.15 | Labor Overhead Factor (% of labor) | 42
Technical ICR Contact Person |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.235 | 2 | 0.9 | 15 | 23.506 | 111.8614 | 606.4586 | 6.5843 | 7.3159 | 0.73159 | Barium (mg/L) |  |  |  |  | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! | 1998-05-05 | 17:00 | 28.5 | 24.3 | 60 | 61 | 590 | 7.2 | 41.3 | 48.5 | 0.4534 | 0.14845 | 11.1649 | 16.4008 | 12.096 | 979.689 | 38.7282 | 968.2061 | 9.3522 | 51.1478 | 0.23649 | 1998-05-07 | 15:00 | 27 | 24.2 | 62 | 62 | 590 | 7.2 | 3.1 |  | 10.3 | 0.4534 | 0.69903 | 56.2816 | 16.4008 | 12.1318 | 698.6707 | 159.8223 | 692.0949 | 5.3556 | 56.6444 | 0.21417 | [27 empty] | Alkalinity | mg/L as CaCO3 | 42.5 | 38 | 40.25 | 11.1801 | 90.5 | 90.25 | 0.27624 | 26.484 | 89.9461 | 55.251 | Alkalinity | mg/L as CaCO3 | 50 | 95 | 93.1818 | 1.9139 | 8.6758 | 92.9333 | 46.198 | Alkalinity | mg/L as CaCO3 | 33 | 76 | 76.5 | -0.65789 | 39.726 | 76.2254 | 56.7073 | Alkalinity | mg/L as CaCO3 | 27 | 102.5 | 66.0845 | 35.5273 | 50.6849 | 65.8492 | 58.9972 | TOCp, mg/L | #DIV/0! | BMRL | BMRL | BMRL | TOCp, mg/L | #DIV/0! | BMRL | BMRL | BMRL | Electric Rate ($/kW-h) | 0.06
Mailing Address |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | 3 | 0.5 | 15 | 5.474 | 93.8294 | 606.4586 | 6.5843 | 13.1686 | 6.5843 | Strontium (mg/L) |  |  |  |  | Total organic carbon | mg/L | 3.2 | 3.1 | 3.15 | 3.1746 | 1998-05-06 | 7:30 | 43 | 23 | 60 | 61 | 590 | 7.1 | 41.2 | 48.3 | 0.4534 | 0.147 | 11.2153 | 16.173 | 12.3953 | 978.093 | 38.6715 | 966.7881 | 9.3377 | 51.1623 | 0.24227 | 1998-05-07 | 17:00 | 29 | 23.5 | 62 | 62 | 590 | 7.2 | 3 |  | 10.2 | 0.4534 | 0.70588 | 56.8431 | 16.4008 | 12.3854 | 706.7764 | 161.6765 | 700.1243 | 5.4177 | 56.5823 | 0.21889 | 7.73 |  |  | 155.5 |  |  | 721.6 |  | 51.7081 | 718.1458 | 78.347 | [16 empty] | Total dissolved solids | mg/L | 149.5 | 149.9 | 149.7 | 0.2672 | 654 | 743.8379 | -13.7367 | 53.5093 | 740.2273 | 79.7765 | Total dissolved solids | mg/L | 166.2 | 1149 | 1582.5636 | -37.734 | 48.3851 | 1574.4127 | 89.4437 | Total dissolved solids | mg/L | 141.5 | 472 | 502.5 | -6.4619 | 56.0559 | 500.2208 | 71.7125 | Total dissolved solids | mg/L | 125.1 | 400 | 402.4239 | -0.60599 | 61.1491 | 400.7541 | 68.7839 | UV254 F, cm-1 | 0.0525 | 0.0525 | 0.0525 | 0.0525 | UV254 F, cm-1 | 0.0525 | 0.0525 | 0.0525 | 0.0525 | Fuel Oil Rate ($/gal) | NA
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 400 | 4 | 0.3 | 15 | 4.186 | 92.5414 | 606.4586 | 6.5843 | 21.9477 | 15.3634 | Reactive silica (mg/L as SiO2) |  |  |  |  | UV254 | cm-1 | 0.052 | 0.053 | 0.0525 | 1.9048 | 1998-05-06 | 11:00 | 46.5 | 23.3 | 60 | 61 | 590 | 7 | 41.2 | 48.2 | 0.4534 | 0.14523 | 11.2407 | 15.9452 | 12.1128 | 976.1599 | 38.6015 | 965.0364 | 9.32 | 51.18 | 0.23667 | 1998-05-08 | 7:00 | 43 | 22.1 | 63 | 64 | 580 | 7.1 | 3 |  | 10.1 | 0.44572 | 0.70297 | 56.4257 | 16.173 | 12.7295 | 703.3166 | 160.8803 | 696.6764 | 5.3912 | 58.1088 | 0.21906 | 7.94 |  |  | 148.8 |  |  | 731.9067 |  | 53.7888 | 728.3377 | 79.5699 | 0.002 |  |  | 0.17202 |  | 96.1905 | 0.17098 | 98.8302 | [8 empty] | Total hardness | mg/L as CaCO3 | 39.5 | 38.8 | 39.15 | 1.788 | 326.9 | 308.4603 | 5.6408 | 66.6098 | 306.8237 | 87.2402 | Total hardness | mg/L as CaCO3 | 46.7 | 725.9 | 688.0636 | 5.2123 | 60.1706 | 684.3727 | 93.1762 | Total hardness | mg/L as CaCO3 | 34.3 | 214.7 | 200.2 | 6.7536 | 70.7463 | 199.1526 | 82.777 | Total hardness | mg/L as CaCO3 | 31.4 | 162.2 | 152.3155 | 6.094 | 73.2196 | 151.5874 | 79.2859 | UV254 p, cm-1 | 0.004 | 0.004 | 0.004 | 0.006 | UV254 p, cm-1 | 0.004 | 0.004 | 0.004 | 0.006 | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Purchase price for an equivalent 8" x 40 " element ($) | 700 | 1: For experimental matrix see Table 4-2 in Part 3 of the ICR Treatment Studies Manual. | [8 empty] | Turbidity (ntu) | 5.8 |  |  |  | SUVA | L/(mg*m) | 1.625 | 1.7097 | 1.6673 | 5.0786 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-08 | 9:00 | 45 | 21.5 | 64 | 65 | 580 | 7 | 2.9 |  | 9.9 | 0.44572 | 0.70707 | 57.5859 | 15.9452 | 12.7747 | 708.1746 | 162.0134 | 701.583 | 5.4287 | 59.0713 | 0.21626 | [27 empty] | Calcium hardness | mg/L as CaCO3 | 33.7 | 33 | 33.35 | 2.099 | 274.7 | 254.0397 | 7.5211 | 65.7422 | 252.6985 | 86.8025 | Calcium hardness | mg/L as CaCO3 | 40.2 | 618.8 | 559.7455 | 9.5434 | 58.7057 | 556.7556 | 92.7796 | Calcium hardness | mg/L as CaCO3 | 29.2 | 179.5 | 165.5 | 7.7994 | 70.0051 | 164.6395 | 82.2643 | Calcium hardness | mg/L as CaCO3 | 26.2 | 136.3 | 126.4113 | 7.2551 | 73.0868 | 125.8079 | 79.1746 | BromideF, ug/L | 113.5 | 113.5 | 113.5 | 113.5 | BromideF, ug/L | 113.5 | 113.5 | 113.5 | 113.5 | Current Process Water Rate ($/1000 gal) | 0.375
FAX Number |  | Maximum flow rate to the 8" x 40" element, QI, max (gpm) | 70 | 2: Flow rates and pressures may need to be adjusted in order to obtain the desired operating conditions. | [8 empty] | SDI |  |  |  |  | Bromide | mg/L | 130 | 97 | 113.5 | 29.0749 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-08 | 11:00 | 47 | 22.4 | 63 | 64 | 580 | 7 | 2.9 |  | 9.9 | 0.44572 | 0.70707 | 57.5859 | 15.9452 | 12.4394 | 708.1746 | 162.0134 | 701.583 | 5.4287 | 58.0713 | 0.21421 | 7.81 | 8.04 | 8 | 154 | 321 | 661 | 727.5172 | -10.0631 | 52.1739 | 724.0564 | 78.7309 | 0.002 | 0.051 | 0.168 | 0.1744 | -3.8075 | 96.1905 | 0.17336 | 98.8463 | [8 empty] | Turbidity | ntu | 0.18 | 0.15 | 0.165 | 18.1818 | 0.23 | 0.14776 | 35.7571 | -3.125 | 0.14786 | -11.5895 | Turbidity | ntu | 0.1 | 0.2 | 0.64545 | -222.7273 | 37.5 | 0.64232 | 84.4313 | Turbidity | ntu | 0.1 | 0.19 | 0.22 | -15.7895 | 37.5 | 0.21924 | 54.3884 | Turbidity | ntu | 0.12 | 0.15 | 0.17634 | -17.5587 | 25 | 0.176 | 31.8177 | Bromidep, ug/L | 94 | 95 | 100 | 91 | Bromidep, ug/L | 94 | 95 | 100 | 91 | Modifications to Existing Plant (% of construction costs) | 52
E-Mail Address (optional) |  | Minimum flow rate to the 8" x 40" element, QI, min (gpm) | 34 | [9 empty] | MFI |  |  |  |  | SDS-Cl2 dose | mg/L | 4.8 | 4 | 4.4 | 18.1818 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-08 | 13:00 | 49 | 22.5 | 63 | 64 | 590 | 7.2 | 2.9 |  | 10.1 | 0.4534 | 0.71287 | 57.4158 | 16.4008 | 12.757 | 715.2385 | 163.6123 | 708.5068 | 5.4826 | 58.0174 | 0.21988 | [27 empty] | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! | BMRL | #DIV/0! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | BMRL | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | BMRL | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | BMRL | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | AlkF, mg/L CaCO3 | 54.75 | 54.75 | 54.75 | 54.75 | AlkF, mg/L CaCO3 | 54.75 | 54.75 | 54.75 | 54.75
|  | Total width of all membrane envelopes in the 8" x 40" element, w (ft) | 70.67 | [9 empty] | MPFI |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | SDS-Free Cl2 residual | mg/L | 1.36 | 1 | 1.18 | 30.5085 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-08 | 15:00 | 51 | 22.4 | 63 | 64 | 590 | 7.2 | 2.9 |  | 10.1 | 0.4534 | 0.71287 | 57.4158 | 16.4008 | 12.7948 | 715.2385 | 163.6123 | 708.5068 | 5.4826 | 58.0174 | 0.22053 | [27 empty] | Total organic carbon | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | 9.9 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L | BMRL | 25 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 5.9 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 4.4 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkp, mg/L CaCO3 | 40.25 | 50 | 33 | 27 | Alkp, mg/L CaCO3 | 40.25 | 50 | 33 | 27
Plant Name | Facility 1 | Feed spacer thickness in the 8" x 40" element, T (ft) | 0.0023 | [9 empty] | Bromide (mg/L) | 95 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | SDS-Cl2 demand | mg/L | 3.44 | 3 | 3.22 | 13.6646 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-08 | 17:00 | 53 | 22.5 | 64 | 64 | 590 | 7.2 | 3 |  | 10.2 | 0.4534 | 0.70588 | 56.8431 | 16.4008 | 12.757 | 706.7764 | 161.6765 | 700.1243 | 5.4177 | 58.5823 | 0.21776 | 7.75 |  |  | 149.1 |  |  | 736.96 |  | 53.6957 | 733.3731 | 79.6693 | 0.002 |  |  | 0.1737 |  | 96.1905 | 0.17265 | 98.8416 | [8 empty] | UV254 | cm-1 | 0.004 | 0.004 | 0.004 | 0 | 0.166 | 0.17124 | -3.1575 | 92.381 | 0.17023 | 97.6502 | UV254 | cm-1 | 0.004 | 0.409 | 0.44491 | -8.7797 | 92.381 | 0.44237 | 99.0958 | UV254 | cm-1 | 0.004 | 0.103 | 0.101 | 1.9417 | 92.381 | 0.10039 | 96.0154 | UV254 | cm-1 | 0.006 | 0.074 | 0.071493 | 3.3879 | 88.5714 | 0.071099 | 91.561 | T-HdF, mg/L CaCO3 | 117.25 | 117.25 | 117.25 | 117.25 | T-HdF, mg/L CaCO3 | 117.25 | 117.25 | 117.25 | 117.25
Treatment Plant Category | CS/SOFT | [11 empty] | TOC (mg/L) | 4.8 | is to list the pretreatment processes used in this particular RBSMT run. |  |  | SDS-Chlorination temp. | oC | 13 | 13 | 13 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-09 | 7:00 | 67 | 21.2 | 64 | 64 | 590 | 7 | 2.8 |  | 9.8 | 0.4534 | 0.71429 | 59.2041 | 15.9452 | 12.8885 | 716.9068 | 164.0373 | 710.3474 | 5.4959 | 58.5041 | 0.2203 | 7.6 |  |  | 153 |  |  | 744.5 |  | 52.4845 | 740.9911 | 79.352 | 0.003 |  |  | 0.17625 |  | 94.2857 | 0.17522 | 98.2879 | [8 empty] | SUVA | L/(mg*m) | NR | NR | #DIV/0! | #VALUE! | 1.6768 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 1.636 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 1.7458 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 1.6818 | --- | --- | --- | --- | --- | T-Hdp, mg/L CaCO3 | 39.15 | 46.7 | 34.3 | 31.4 | T-Hdp, mg/L CaCO3 | 39.15 | 46.7 | 34.3 | 31.4
Process Train Name | Coagulation/Sedimentation/Softening | Additional Information | [10 empty] | pH | 7.99 |  |  |  | SDS-Chlorination pH | --- | 9.5 | 9.48 | 9.49 | 0.21075 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-09 | 9:00 | 69 | 21.4 | 63 | 64 | 590 | 7 | 2.9 |  | 9.9 | 0.4534 | 0.70707 | 58.596 | 15.9452 | 12.8125 | 708.1344 | 162.03 | 701.6552 | 5.4286 | 58.0714 | 0.22063 | [27 empty] | Bromide | mg/L | 94 | 94 | 94 | 0 | --- | 161.2414 | --- | 17.1806 | 160.8327 | 41.5542 | Bromide | mg/L | 95 | --- | 263.1818 | --- | 16.2996 | 262.214 | 63.77 | Bromide | mg/L | 100 | --- | 127 | --- | 11.8943 | 126.8295 | 21.154 | Bromide | mg/L | 91 | --- | 122.6901 | --- | 19.8238 | 122.4993 | 25.7139 | Ca-HdF, mg/L CaCO3 | 97.35 | 97.35 | 97.35 | 97.35 | Ca-HdF, mg/L CaCO3 | 97.35 | 97.35 | 97.35 | 97.35
ICR Treatment Plant Identification Number | 381 | Design cross-flow velocity (fps) | 0.43 | [9 empty] | Total Hardness (mg/L as CaCO3) | 239 |  |  |  | SDS-Incubation time | hours | 42 | 42 | 42 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-09 | 11:00 | 71 | 21.8 | 63 | 64 | 590 | 6.9 | 2.8 |  | 9.7 | 0.4534 | 0.71134 | 59.8247 | 15.7174 | 12.4811 | 713.2654 | 163.2256 | 706.8327 | 5.4682 | 58.0318 | 0.21507 | 7.6 | 7.83 | 7.9 | 154.1 | 321 | 662 | 735.7536 | -11.141 | 52.1429 | 732.3524 | 78.9582 | 0.002 | 0.051 | 0.17 | 0.17695 | -4.0861 | 96.1905 | 0.17592 | 98.8631 | [8 empty] | SDS-Cl2 dose | mg/L | 1.6 | 1.6 | 1.6 | 0 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1.6 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1.6 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1.6 | --- | --- | --- | --- | --- | --- | Ca-Hdp, mg/L CaCO3 | 33.35 | 40.2 | 29.2 | 26.2 | Ca-Hdp, mg/L CaCO3 | 33.35 | 40.2 | 29.2 | 26.2
PWSID Number of Plant (if assigned) | KS200910 | Required influent flow to permeate flow rate ratio, QI:Qp | [10 empty] | UV254 | 0.117 |  |  |  | SDS-TOX | mg Cl- /L | 210 | 150 | 180 | 33.3333 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-09 | 13:00 | 73 | 23.1 | 63 | 64 | 590 | 7 | 2.9 |  | 9.9 | 0.4534 | 0.70707 | 58.596 | 15.9452 | 12.1846 | 708.1344 | 162.03 | 701.6552 | 5.4286 | 58.0714 | 0.20982 | [27 empty] | SDS-Free Cl2 residual | mg/L | 1.01 | 1.32 | 1.165 | 26.6094 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.82 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.97 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.09 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 0.1 | Maximum element recovery (%) | 15 | [9 empty] | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | SDS-CHCl3 | mg/L | 59.4 | 41.8 | 50.6 | 34.7826 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-09 | 15:00 | 75 | 23.3 | 63 | 64 | 590 | 7.2 | 2.9 |  | 10.1 | 0.4534 | 0.71287 | 57.4158 | 16.4008 | 12.4589 | 715.2385 | 163.6123 | 708.5068 | 5.4826 | 58.0174 | 0.21474 | [27 empty] | SDS-Cl2 demand | mg/L | 0.59 | 0.28 | 0.435 | 71.2644 | --- | 10.0384 | --- | 86.4907 | 9.9801 | 95.6413 | SDS-Cl2 demand | mg/L | 0.78 | --- | 22.9618 | --- | 75.7764 | 22.8342 | 96.5841 | SDS-Cl2 demand | mg/L | 0.63 | --- | 5.81 | --- | 80.4348 | 5.7773 | 89.0952 | SDS-Cl2 demand | mg/L | 0.51 | --- | 4.3269 | --- | 84.1615 | 4.3039 | 88.1503 | Blended Water Quality if THM4 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if THM4 Controls the Blend Ratio
Historical Average Water Temperature (oC) | 14 | Variability of design flux (%) | [10 empty] | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | SDS-BDCM | mg/L | 31.4 | 25.6 | 28.5 | 20.3509 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-09 | 17:00 | 77 | 22.7 | 63 | 64 | 590 | 7.2 | 2.9 |  | 10.1 | 0.4534 | 0.71287 | 57.4158 | 16.4008 | 12.6818 | 715.2385 | 163.6123 | 708.5068 | 5.4826 | 58.0174 | 0.21859 | 7.56 |  |  | 155.4 |  |  | 735.6276 |  | 51.7391 | 732.0872 | 78.773 | 0.002 |  |  | 0.17788 |  | 96.1905 | 0.17681 | 98.8688 | [8 empty] | SDS-Chlorination temp. | oC | 13 | 13 | 13 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 13 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 13 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 13 | --- | --- | --- | --- | --- | --- | Qp/QT (THM4), % | 30.484 | 31.753 | 29.6762 | 29.651 | Qp/QT (THM4), % | 69.6848 | 72.5855 | 67.838 | 67.7805
State Approved Plant Capacity (MGD) | 55 | Rejection of reference solute and conditions of test | 45 rejection of CaCl2 | [14 empty] | SDS-DBCM | mg/L | 18.1 | 16.6 | 17.35 | 8.6455 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-10 | 9:00 | 93 | 21.3 | 63 | 64 | 590 | 6.8 | 0.87 |  | 7.67 | 0.4534 | 0.88657 | 75.9231 | 15.4897 | 12.4833 | 1017.8883 | 232.9672 | 1008.8418 | 7.804 | 55.696 | 0.22413 | [27 empty] | SDS-Chlorination pH | --- | 9.53 | 9.52 | 9.525 | 0.10499 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 9.47 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 9.52 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 9.48 | --- | --- | --- | --- | --- | --- | SDS-THM4b, ug/L | 72 | 72 | 72 | 72 | SDS-THM4b, ug/L | 36 | 36 | 36 | 36
|  | (e.g., solute type and concentration) | 70psi, 500mg/L CaCl2,25 deg. C,15% recovery | [14 empty] | SDS-CHBr3 | mg/L | 3.6 | 3.49 | 3.545 | 3.103 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-10 | 9:30 | 93.5 | 21.5 | 63 | 64 | 590 | 6.6 | 0.87 |  | 7.47 | 0.4534 | 0.88353 | 77.9826 | 15.0341 | 12.0447 | 1010.2388 | 231.2776 | 1001.525 | 7.746 | 55.754 | 0.21603 | 8.04 |  |  | 159.2 |  |  | 1557.0345 |  | 50.559 | 1549.2161 | 89.7238 | 0.003 |  |  | 0.42802 |  | 94.2857 | 0.42564 | 99.2952 | [8 empty] | SDS-Incubation time | hours | 42 | 42 | 42 | 0 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 42 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 42 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 42 | --- | --- | --- | --- | --- | --- | SDS-HAA5b, ug/L | 17.4207 | 17.1027 | 17.6232 | 17.6295 | SDS-HAA5b, ug/L | 7.597 | 6.8701 | 8.0598 | 8.0742
|  | Variability of rejection of reference solute (%) | 45 rejection of CaCl2 | [14 empty] | SDS-THM4 | mg/L | 112.5 | 87.49 | 99.995 | 25.0113 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-10 | 10:00 | 94 | 21.3 | 63 | 64 | 590 | 6.3 | 0.87 |  | 7.17 | 0.4534 | 0.87866 | 81.2873 | 14.3507 | 11.5654 | 998.2215 | 228.617 | 990.0037 | 7.655 | 55.845 | 0.2071 |  | 8.39 | 8.32 | 162 | 323 | 741 | 1480.6207 | -99.8139 | 49.6894 | 1473.5806 | 89.0064 | 0.003 | 0.053 | 0.2 | 0.41095 | -105.4741 | 94.2857 | 0.40877 | 99.2661 | [8 empty] | SDS-TOX | mg Cl- /L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOXb, ug Cl- /L | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | SDS-TOXb, ug Cl- /L | #DIV/0! | #VALUE! | #VALUE! | #VALUE!
|  | Standard testing recovery (%) | 15 | [14 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-10 | 10:30 | 94.5 | 22 | 63 | 64 | 590 | 6.3 | 0.87 |  | 7.17 | 0.4534 | 0.87866 | 81.2873 | 14.3507 | 11.3286 | 998.2215 | 228.617 | 990.0037 | 7.655 | 55.845 | 0.20286 | 8.06 |  |  | 163.2 |  |  | 1471.931 |  | 49.3168 | 1464.9437 | 88.8596 | 0.002 |  |  | 0.41819 |  | 96.1905 | 0.41597 | 99.5192 | [8 empty] | SDS-CHCl3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHCl3 | mg/L | 1.33 | --- | 449.2391 | --- | 97.3715 | 446.6615 | 99.7022 | SDS-CHCl3 | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHCl3 | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDb, mg/L | 2.371 | 2.4452 | 2.4514 | 2.4165 | SDS-CDb, mg/L | 1.2793 | 1.4489 | 1.463 | 1.3831
|  | Standard testing pH | 8 | [14 empty] | SDS-DCAA* | mg/L | 19.3 | 15.96 | 17.63 | 18.945 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-10 | 12:00 | 96 | 22.9 | 65 | 66 | 590 | 6.7 | 0.83 |  | 7.53 | 0.4534 | 0.88977 | 77.3533 | 15.2619 | 11.7316 | 1025.8108 | 234.8115 | 1016.8282 | 7.8651 | 57.6349 | 0.20355 | [27 empty] | SDS-BDCM | mg/L | 1.49 | 1.64 | 1.565 | 9.5847 | --- | 94.4443 | --- | 94.5088 | 93.8799 | 98.333 | SDS-BDCM | mg/L | 2.1 | --- | 242.1 | --- | 92.6316 | 240.7188 | 99.1276 | SDS-BDCM | mg/L | 1.11 | --- | 55.89 | --- | 96.1053 | 55.5441 | 98.0016 | SDS-BDCM | mg/L | 1.07 | --- | 39.7038 | --- | 96.2456 | 39.4712 | 97.2892 | TOCb, mg/L | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | TOCb, mg/L | #DIV/0! | #VALUE! | #VALUE! | #VALUE!
|  | Acceptable range of operating pressures | 0 to 600 psi | [14 empty] | SDS-TCAA* | mg/L | 3 | 3.5 | 3.25 | 15.3846 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-10 | 16:00 | 100 | 22.1 | 65 | 66 | 590 | 6.8 | 0.83 |  | 7.63 | 0.4534 | 0.89122 | 76.3263 | 15.4897 | 12.1916 | 1029.5529 | 235.6369 | 1020.4027 | 7.8934 | 57.6066 | 0.21164 | [27 empty] | SDS-DBCM | mg/L | 3.07 | 3.4 | 3.235 | 10.2009 | --- | 51.9074 | --- | 81.3545 | 51.6116 | 93.732 | SDS-DBCM | mg/L | 3.9 | --- | 126.1727 | --- | 77.5216 | 125.4691 | 96.8917 | SDS-DBCM | mg/L | 2.11 | --- | 32.59 | --- | 87.8386 | 32.3976 | 93.4872 | SDS-DBCM | mg/L | 2.19 | --- | 23.5421 | --- | 87.3775 | 23.4135 | 90.6464 | UV254 b, cm-1 | 0.037715 | 0.0371 | 0.038107 | 0.038712 | UV254 b, cm-1 | 0.018703 | 0.017296 | 0.019599 | 0.020982
|  | Acceptable range of operating pH values | 3 to 10 | [14 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-11 | 8:00 | 116 | 22.2 | 66 | 67 | 590 | 6.9 | 6.8 |  | 13.7 | 0.4534 | 0.50365 | 42.0657 | 15.7174 | 12.3344 | 526.4819 | 120.4816 | 521.7338 | 4.0363 | 62.4637 | 0.19746 | 7.82 | [26 empty] | SDS-CHBr3 | mg/L | 3.4 | 3.32 | 3.36 | 2.381 | --- | 3.9979 | --- | 5.2186 | 3.9941 | 15.875 | SDS-CHBr3 | mg/L | 4.5 | --- | -4.1818 | --- | -26.9394 | -4.1319 | 208.9099 | SDS-CHBr3 | mg/L | 2.44 | --- | 4.65 | --- | 31.1707 | 4.636 | 47.369 | SDS-CHBr3 | mg/L | 2.32 | --- | 4.0454 | --- | 34.5557 | 4.035 | 42.5026 | Bromideb, ug/L | 107.5556 | 107.6257 | 109.4937 | 106.8285 | Bromideb, ug/L | 99.9115 | 100.0717 | 104.3419 | 98.2494
|  | Typical pressure drop across a single element (psi) | 3 to5 | [14 empty] | SDS-DBAA* | mg/L | 3.87 | 4.49 | 4.18 | 14.8325 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-11 | 10:00 | 118 | 21.9 | 66 | 66 | 590 | 7.2 | 6.9 |  | 14.1 | 0.4534 | 0.51064 | 40.844 | 16.4008 | 12.9853 | 531.203 | 121.5138 | 526.2034 | 4.0719 | 61.9281 | 0.20968 |  |  |  | 138.4 |  |  | 513.5826 |  | 57.0186 | 511.2934 | 72.9314 | 0.003 |  |  | 0.10415 |  | 94.2857 | 0.10353 | 97.1024 | [8 empty] | SDS-THM4 | mg/L | 7.96 | 8.36 | 8.16 | 4.902 | --- | 324.8324 | --- | 91.8396 | 322.908 | 97.473 | SDS-THM4 | mg/L | 11.83 | --- | 813.33 | --- | 88.1694 | 808.7175 | 98.5372 | SDS-THM4 | mg/L | 5.66 | --- | 194.33 | --- | 94.3397 | 193.1388 | 97.0695 | SDS-THM4 | mg/L | 5.58 | --- | 138.5589 | --- | 94.4197 | 137.7582 | 95.9494 | Alkb, mg/L CaCO3 | 50.3298 | 53.2417 | 48.2954 | 46.5218 | Alkb, mg/L CaCO3 | 44.6457 | 51.3022 | 39.9952 | 35.9409
|  | Maximum permissible SDI | 5 | [14 empty] | SDS-BCAA* | mg/L | 8.92 | 8.43 | 8.675 | 5.6484 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-11 | 12:00 | 120 | 23.6 | 65 | 66 | 590 | 7.2 | 7.2 |  | 14.4 | 0.4534 | 0.5 | 39.9722 | 16.4008 | 12.3489 | 524.109 | 119.891 | 519.1762 | 4.0175 | 61.4825 | 0.20085 | 7.97 |  |  | 140.8 |  |  | 503.2 |  | 56.2733 | 500.9887 | 71.8956 | 0.002 |  |  | 0.103 |  | 96.1905 | 0.10238 | 98.0466 | [8 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | T-Hdb, mg/L CaCO3 | 93.442 | 94.8483 | 92.6336 | 91.7946 | T-Hdb, mg/L CaCO3 | 62.8262 | 66.0409 | 60.9784 | 59.0604
|  | Maximum permissible turbidity (ntu) | 1 | [14 empty] | SDS-TBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-11 | 14:00 | 122 | 23.2 | 65 | 66 | 590 | 7.3 | 7.3 |  | 14.6 | 0.4534 | 0.5 | 39.411 | 16.6286 | 12.6693 | 524.1219 | 119.8781 | 519.1203 | 4.0174 | 61.4826 | 0.20606 | 7.91 | 8.12 | 8.12 | 141.9 | 324 | 492 | 502.1 | -2.0528 | 55.9317 | 499.8716 | 71.6127 | 0.002 | 0.053 | 0.103 | 0.103 | 0 | 96.1905 | 0.10238 | 98.0464 | [8 empty] | SDS-DCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Ca-Hdb, mg/L CaCO3 | 77.8402 | 79.2032 | 77.1257 | 76.2533 | Ca-Hdb, mg/L CaCO3 | 52.7518 | 55.8674 | 51.1184 | 49.1241
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | <0.1 ppm | [14 empty] | SDS-CDBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-11 | 15:00 | 123 | 23.7 | 65 | 66 | 590 | 7.4 | 7.4 |  | 14.8 | 0.4534 | 0.5 | 38.8649 | 16.8564 | 12.6545 | 524.1348 | 119.8652 | 519.0643 | 4.0173 | 61.4827 | 0.20582 | [27 empty] | SDS-TCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | 1: All of the information requested in this field may not be available, but values for all Design | [15 empty] | SDS-DCBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-11 | 16:00 | 124 | 23.5 | 65 | 66 | 590 | 7.4 | 7.5 |  | 14.9 | 0.4534 | 0.49664 | 38.5973 | 16.8564 | 12.7295 | 521.9359 | 119.3623 | 516.8867 | 4.0005 | 61.4995 | 0.20699 | [27 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  | Parameters must be entered in cells E14:E23, since these parameters are used in calculations. | [15 empty] | SDS-HAA5 | mg/L | 26.17 | 23.95 | 25.06 | 8.8587 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-12 | 8:00 | 140 | 21.5 | 66 | 66 | 590 | 7.1 | 17 |  | 24.1 | 0.4534 | 0.29461 | 23.4813 | 16.173 | 12.9572 | 416.6695 | 95.3266 | 412.8025 | 3.1941 | 62.8059 | 0.20631 | [27 empty] | SDS-DBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Blended Water Quality if HAA5 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if HAA5 Controls the Blend Ratio
[18 empty] | SDS-HAA6 | mg/L | 35.09 | 32.38 | 33.735 | 8.0332 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-12 | 10:00 | 142 | 22 | 66 | 66 | 590 | 7.2 | 17 |  | 24.2 | 0.4534 | 0.29752 | 23.3802 | 16.4008 | 12.947 | 417.89 | 95.5932 | 413.9568 | 3.2033 | 62.7967 | 0.20617 | 8.2 |  |  | 119.9 |  |  | 407.5953 |  | 62.764 | 405.8399 | 70.4563 | 0.001 |  |  | 0.074312 |  | 98.0952 | 0.073864 | 98.6462 | [8 empty] | SDS-BCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-BCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Qp/QT (HAA5), % | -115.4828 | -115.4828 | -115.4828 | -115.4828 | Qp/QT (HAA5), % | -7.7414 | -7.7414 | -7.7414 | -7.7414
[18 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-12 | 12:00 | 144 | 22.3 | 66 | 66 | 590 | 7.2 | 17 |  | 24.2 | 0.4534 | 0.29752 | 23.3802 | 16.4008 | 12.8327 | 417.89 | 95.5932 | 413.9568 | 3.2033 | 62.7967 | 0.20435 | 8.31 |  |  | 121.9 |  |  | 406.7482 |  | 62.1429 | 405.0102 | 69.902 | 0.002 |  |  | 0.073888 |  | 96.1905 | 0.07345 | 97.277 | [8 empty] | SDS-TBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-THM4b, ug/L | NA | NA | NA | NA | SDS-THM4b, ug/L | NA | NA | NA | NA
[18 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-12 | 14:00 | 146 | 23.9 | 66 | 66 | 590 | 7 | 17.2 |  | 24.2 | 0.4534 | 0.28926 | 23.3802 | 15.9452 | 11.8999 | 414.4522 | 94.8319 | 410.66 | 3.1772 | 62.8228 | 0.18942 | 8.26 | 8.59 | 8.56 | 122.1 | 319 | 383 | 403.3547 | -5.3145 | 62.0807 | 401.6862 | 69.6031 | 0.002 | 0.051 | 0.074 | 0.073052 | 1.2806 | 96.1905 | 0.072631 | 97.2463 | [8 empty] | SDS-CDBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-HAA5b, ug/L | NA | NA | NA | NA | SDS-HAA5b, ug/L | NA | NA | NA | NA
[18 empty] | should be reported if measured. | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-12 | 15:00 | 147 | 25.3 | 65 | 66 | 590 | 7.3 | 17.2 |  | 24.5 | 0.4534 | 0.29796 | 23.0816 | 16.6286 | 11.9068 | 418.0784 | 95.6236 | 414.0887 | 3.2046 | 62.2954 | 0.19113 | [27 empty] | SDS-DCBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TOXb, ug Cl- /L | NA | NA | NA | NA | SDS-TOXb, ug Cl- /L | NA | NA | NA | NA
[45 empty] | 1998-05-12 | 16:30 | 148.5 | 24.7 | 65 | 66 | 590 | 7.2 | 17.3 |  | 24.5 | 0.4534 | 0.29388 | 23.0816 | 16.4008 | 11.9538 | 416.3717 | 95.2459 | 412.4528 | 3.1917 | 62.3083 | 0.19185 | [27 empty] | SDS-HAA5 | mg/L | 0 | 0 | 0 | #DIV/0! | --- | 86.4138 | --- | 100 | 85.8886 | 100 | SDS-HAA5 | mg/L | 0 | --- | 227.8182 | --- | 100 | 226.5071 | 100 | SDS-HAA5 | mg/L | 0 | --- | 50.12 | --- | 100 | 49.8036 | 100 | SDS-HAA5 | mg/L | 0 | --- | 35.2958 | --- | 100 | 35.0833 | 100 | SDS-CDb, mg/L | NA | NA | NA | NA | SDS-CDb, mg/L | NA | NA | NA | NA
[45 empty] | 1998-05-13 | 13:00 | 169 | 25.2 | 51 | 52 | 590 | 7.5 | 16.7 | x | 24.2 | 0.4534 | 0.30992 | 23.3802 | 17.0842 | 12.2692 | 423.156 | 96.7593 | 419.0069 | 3.2432 | 48.2568 | 0.25425 | [27 empty] | SDS-HAA6 | mg/L | 0 | 0 | 0 | #DIV/0! | --- | 116.3276 | --- | 100 | 115.6206 | 100 | SDS-HAA6 | mg/L | 0 | --- | 306.6818 | --- | 100 | 304.9169 | 100 | SDS-HAA6 | mg/L | 0 | --- | 67.47 | --- | 100 | 67.044 | 100 | SDS-HAA6 | mg/L | 0 | --- | 47.5141 | --- | 100 | 47.228 | 100 | TOCb, mg/L | NA | NA | NA | NA | TOCb, mg/L | NA | NA | NA | NA
[45 empty] | 1998-05-13 | 14:30 | 170.5 | 24.9 | 51 | 52 | 590 | 7.5 | 18 |  | 25.5 | 0.4534 | 0.29412 | 22.1373 | 17.0842 | 12.3785 | 416.4858 | 95.2341 | 412.4021 | 3.1921 | 48.3079 | 0.25624 |  |  |  | 125.1 |  | 400 | 404.0417 | -1.0104 | 61.1491 | 402.2687 | 68.9014 | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | UV254 b, cm-1 | NA | NA | NA | NA | UV254 b, cm-1 | NA | NA | NA | NA
[45 empty] | 1998-05-13 | 17:00 | 173 | 25.6 | 51 | 52 | 590 | 7.7 | 18 |  | 25.7 | 0.4534 | 0.29961 | 21.9572 | 17.5398 | 12.4484 | 418.7908 | 95.7358 | 414.5746 | 3.2095 | 48.2905 | 0.25778 | [27 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | Bromideb, ug/L | NA | NA | NA | NA | Bromideb, ug/L | NA | NA | NA | NA
[45 empty] | 1998-05-15 | 10:30 | 175.5 | 24.1 | 51 | 52 | 590 | 7.2 | 17.5 |  | 24.7 | 0.4534 | 0.2915 | 22.8866 | 16.4008 | 12.1677 | 415.3859 | 95.0204 | 411.4764 | 3.1841 | 48.3159 | 0.25184 | [66 empty] | Alkb, mg/L CaCO3 | NA | NA | NA | NA | Alkb, mg/L CaCO3 | NA | NA | NA | NA
[45 empty] | 1998-05-15 | 12:00 | 177 | 25.4 | 51 | 52 | 590 | 7.4 | 17.5 |  | 24.9 | 0.4534 | 0.29719 | 22.6948 | 16.8564 | 12.0343 | 417.7609 | 95.5384 | 413.7195 | 3.202 | 48.298 | 0.24917 | 7.52 | 7.79 | 7.82 | 149.9 | 326 | 391 | 394.7737 | -0.96514 | 53.4472 | 393.2381 | 61.8806 | 0.006 | 0.055 | 0.075 | 0.072163 | 3.7829 | 88.5714 | 0.071748 | 91.6374 | [47 empty] | T-Hdb, mg/L CaCO3 | NA | NA | NA | NA | T-Hdb, mg/L CaCO3 | NA | NA | NA | NA
[45 empty] | 1998-05-15 | 17:00 | 182 | 26.4 | 51 | 52 | 590 | 7.6 | 17 |  | 24.6 | 0.4534 | 0.30894 | 22.9837 | 17.312 | 11.9995 | 422.7437 | 96.6523 | 418.5432 | 3.2399 | 48.2601 | 0.24864 | [66 empty] | Ca-Hdb, mg/L CaCO3 | NA | NA | NA | NA | Ca-Hdb, mg/L CaCO3 | NA | NA | NA | NA
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Notes: |  |  |  |  | Notes:
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to |  |  |  |  | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | determine the percentage of total flow that must be treated by the membrane process to meet the |  |  |  |  | determine the percentage of total flow that must be treated by the membrane process to meet the
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Stage 1 DBP MCLs. |  |  |  |  | Stage 2 DBP MCLs.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | A 10% factor of safety has been applied all the MCLs. i.e., 72 / 54 mg/L for THM4 and HAA5. |  |  |  |  | A 10% factor of safety has been applied all the MCLs. i.e., 36 / 27 mg/L for THM4 and HAA5.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for |  |  |  |  | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | both parameters and the maximum (Qp/QT) ratio controls the design. |  |  |  |  | both parameters and the maximum (Qp/QT) ratio controls the design.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. |  |  |  |  | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. |  |  |  |  | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. |  |  |  |  | The subscript "b" refers to the blended water quality for a given blend ratio.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL. |  |  |  |  | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. |  |  |  |  | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Note on X20: C. Rice: Consultant verified the feed TOX, chloroform and bromide concentrations. The QC in the analytical runs were acceptable based upon ICR criteria. The free chlorine residual at the end of the SDS test was 1.36 mg/L for Treated Feed 1 and 1.00 mg/L for Treated Feed 2; this may explain why the TOX and chloroform results are higher in Treated Feed 1.
Note on X24: Alison Gusses: High precision incubator was used for SDS testing
Note on X27: C. Rice: Consultant verified the feed TOX, chloroform and bromide concentrations. The QC in the analytical runs were acceptable based upon ICR criteria. The free chlorine residual at the end of the SDS test was 1.36 mg/L for Treated Feed 1 and 1.00 mg/L for Treated Feed 2; this may explain why the TOX and chloroform results are higher in Treated Feed 1.
Note on X28: C. Rice: Consultant verified the feed TOX, chloroform and bromide concentrations. The QC in the analytical runs were acceptable based upon ICR criteria. The free chlorine residual at the end of the SDS test was 1.36 mg/L for Treated Feed 1 and 1.00 mg/L for Treated Feed 2; this may explain why the TOX and chloroform results are higher in Treated Feed 1.
Note on CY29: Alison Gusses: High precision incubator was used for SDS testing
Note on DL29: Alison Gusses: High precision incubator was used for SDS testing
Note on DV29: Alison Gusses: High precision incubator was used for SDS testing
Note on EF29: Alison Gusses: High precision incubator was used for SDS testing

## NF200. 2nd Quarter
FIELD-SET 2: 2nd QUARTER RBSMT RESULTS (FILE: rbsmt-1.xls)
Field 2-1: PWS And Treatment Plant Data |  | Field 2-2: Manufacturer Reported Membrane Characteristics1 |  | Field 2-3: RBSMT Design Parameters | [8 empty] | Field 2-4: Foulants And Fouling Indices1 |  | Field 2-5: Pretreatment Used Prior To Membranes1 |  |  | Field 2-6: Feed Water Quality After Pretreatment | [5 empty] | Field 2-7: Membrane Setting Data | [20 empty] | Field 2-8: Membrane Performance Data During Operation With The Test Water | [16 empty] | Field 2-8: Membrane Performance Data During Operation With The Test Water (continued) | [19 empty] | Field 2-8: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 2-9: Permeate And Concentrate Water Quality For Run 1 | [11 empty] | Field 2-10: Permeate And Concentrate Water Quality For Run 2 | [8 empty] | Field 2-11: Permeate And Concentrate Water Quality For Run 3 | [8 empty] | Field 2-12: Permeate And Concentrate Water Quality For Run 4 | [8 empty] | Field 2-13: Blending Calculations For Stage 1 D-DBP MCLs |  |  |  |  | Field 2-14: Blending Calculations For Proposed Stage 2 D-DBP MCLs |  |  |  |  | Field 2-15: Membrane Cost Parameters
|  | General Information |  | Input Design Parameters | [8 empty] | Parameters Evaluated Prior to Pretreatment | [80 empty] | Operating Parameters During Sample Collection | [11 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Feed and Permeate Water Quality Parameters |  |  |  |  | Feed and Permeate Water Quality Parameters |  |  |  |  | General Cost Parameters
PWS Name | Water District No. 1 of Johnson County, Kansas | Membrane manufacturer | FilmTec Corporation | [5 empty] | Active membrane area in bench-scale cell, Acell (ft2) | 0.167 |  |  | Alkalinity (mg/L as CaCO3) | 130 | Process | Description | Scale | Parameter | Units | CF-1 | CF-2 | Average | RPD |  |  |  | Average TDS rejection (decimal fraction) | 0.96 | [5 empty] | TDS concentration of setting solution (mg/L) | 0.8 | [12 empty] | Average bulk TDS rejection (decimal fraction) | 0.65779 | [45 empty] | Recovery during sample collection (decimal) | 0.7 | [10 empty] | Recovery during sample collection (decimal) | 0.89 | [7 empty] | Recovery during sample collection (decimal) | 0.51 | [7 empty] | Recovery during sample collection (decimal) | 0.3 | [8 empty] | RUN ID # |  |  |  |  | RUN ID # |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | KS200910 | Membrane trade name | NF200B-4040 | [5 empty] | Active width of membrane in the bench-scale cell, wcell (ft) | 0.333 |  |  | Calcium Hardness (mg/L as CaCO3) | 123 | Presedimentation | 3 Basins | Full-scale | Sampling date | MM/DD/YY | 1998-07-22 | 1998-07-29 | --- | --- | [71 empty] | Feed flow rate during sample collection (mL/min) | 10.3 | [10 empty] | Feed flow rate during sample collection (mL/min) | 6.97 | [7 empty] | Feed flow rate during sample collection (mL/min) | 14.4 | [7 empty] | Feed flow rate during sample collection (mL/min) | 23.4 | [6 empty] | Parameter | 1 | 2 | 3 | 4 | Parameter | 1 | 2 | 3 | 4 | Capital Recovery Interest Rate (%) | 5
Water Industry Data Base Number (optional) | NA | Molecular weight cutoff (Daltons) | 400 | [5 empty] | Average yearly temperature of feed water, TavgoC (oC) | 14 |  |  | LSI | 0.54 | Softening | Lime, 180 mg/L as Ca(OH)2 | Bench-scale | Sampling time | hh:mm | 12:00 | 7:00 | --- | --- | Date | Time | Setting time | Influent | PI | PC | QI | Qp | QW | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) | Date | Time | Operation time | Influent | PI | PC | QI | Qp | QW | Cleaning Event | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1) | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Influent flow rate during sample collection (mL/min) | 600 | [10 empty] | Influent flow rate during sample collection (mL/min) | 600 | [7 empty] | Influent flow rate during sample collection (mL/min) | 600 | [7 empty] | Influent flow rate during sample collection (mL/min) | 600 | [6 empty] | SDS-THM4F, ug/L | 103.025 | 103.025 | 103.025 | 103.025 | SDS-THM4F, ug/L | 103.025 | 103.025 | 103.025 | 103.025 | Capital Recovery Period (years) | 20
|  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide | [5 empty] | Approximate feed water TDS, TDSF (mg/L) | 322 |  |  | Dissolved iron (mg/L) |  | Coagulation | Alum: Al2(SO4)3.14H2O, 15 mg/L | Bench-scale | Operation time | hh.hh | 0 | 173 | --- | --- | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | Indicate with "X" | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) | [39 empty] | SDS-THM4p, ug/L | 18.5375 | 31.946 | 12.35 | 11.096 | SDS-THM4p, ug/L | 18.5375 | 31.946 | 12.35 | 11.096 | Overhead & Profit Factor (% of construction costs) | 15
Official ICR Contact Person |  | Membrane construction (e.g., thin-film composite) | Thin-Film composite | [5 empty] | Manufacturer reported TDS rejection, RejTDS (decimal fraction) | 0.7 |  |  | Total iron (mg/L) |  | Sedimentation | Gravity settling in test drums | Bench-scale | pH | --- | 9.28 | 8.97 | 9.125 | 3.3973 | 1998-07-20 | 12:00 | 0 | 24.5 | 51 | 52 | 600 | 7.8 | 3.2 | 11 | 0.46109 | 0.70909 | 53.5455 | 17.7675 | 13.0268 | 2.5085 | 0.099086 | 2.4772 | 0.023937 | 51.4761 | 0.25306 | 1998-07-22 | 12:00 | 0 | 24.4 | 55 | 56 | 600 | 6.8 | 3.7 |  | 10.5 | 0.46109 | 0.64762 | 56.1429 | 15.4897 | 11.3903 | 384.5599 | 130.6145 | 381.6818 | 2.5251 | 52.9749 | 0.21501 |  | 9.28 |  |  | 242 | [7 empty] | 0.046 | [14 empty] | Permeate and Concentrate Water Quality | [11 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | SDS-HAA5F, ug/L | 26.6922 | 26.6922 | 26.6922 | 26.6922 | SDS-HAA5F, ug/L | 26.6922 | 26.6922 | 26.6922 | 26.6922 | Special Sitework Factor (% of construction costs) | 0
Mailing Address |  | Membrane hydrophobicity | hydrophilic | [5 empty] | Temperature normalized MTCW (gfd/psi) | 0.16977 |  |  | Dissolved aluminum (mg/L) |  | Recarbonation | CO2 gas added to pH 9.4 | Bench-scale | Temperature | oC | 26.8 | 23 | 24.9 | 15.261 | 1998-07-20 | 14:00 | 2 | 25 | 50 | 51 | 600 | 8.1 | 2.8 | 10.9 | 0.46109 | 0.74312 | 54.0459 | 18.4509 | 13.3293 | 2.7951 | 0.11035 | 2.7588 | 0.026666 | 50.4733 | 0.26409 | 1998-07-22 | 13:00 | 1 | 25 | 56 | 56 | 600 | 7 | 3 |  | 10 | 0.46109 | 0.7 | 59 | 15.9452 | 11.5192 | 409.3363 | 138.9987 | 406.1824 | 2.6876 | 53.3124 | 0.21607 | [27 empty] | Parameter | Units | Cp-1 | Cp-1 (dup) | Average | RPD | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | SDS-HAA5p, ug/L | 2.1465 | 6.7003 | 1.3919 | 1.3042 | SDS-HAA5p, ug/L | 2.1465 | 6.7003 | 1.3919 | 1.3042 | Construction Contingencies (% of construction costs) | 15
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | negative | [9 empty] | Total aluminum (mg/L) |  | Cartridge filtration | 1 um size exclusion | Bench-scale | Alkalinity | mg/L as CaCO3 | 58.5 | 40 | 49.25 | 37.5635 | 1998-07-20 | 16:00 | 4 | 25 | 50 | 50 | 600 | 8.4 | 3.6 | 12 | 0.46109 | 0.7 | 49 | 19.1343 | 13.823 | 2.4418 | 0.09636 | 2.409 | 0.02329 | 49.9767 | 0.27659 | 1998-07-22 | 15:00 | 3 | 25.1 | 56 | 56 | 600 | 7 | 3 |  | 10 | 0.46109 | 0.7 | 59 | 15.9452 | 11.4852 | 409.3363 | 138.9987 | 406.1824 | 2.6876 | 53.3124 | 0.21543 | 9.3 |  | 9.16 | 141.9 |  | 465 | 402.5667 | 13.4265 | 35.5293 | 401.0461 | 64.6175 | 0.01 |  | 0.141 | 0.12667 | 10.1655 | 77.7778 | 0.12599 | 92.0626 | [8 empty] | Sampling date | MM/DD/YY | 1998-07-25 | 1998-07-25 | --- | --- | 1998-07-25 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-07-26 | 1998-07-26 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-07-27 | 1998-07-27 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-07-28 | 1998-07-28 | --- | --- | --- | --- | --- | SDS-TOXF, ug Cl- /L | 177.5 | 177.5 | 177.5 | 177.5 | SDS-TOXF, ug Cl- /L | 177.5 | 177.5 | 177.5 | 177.5 | Engineering Fee Factor (% of construction costs) | 15
Phone Number |  |  |  | Experimental Design1,2 | [8 empty] | Fluoride (mg/L) |  | Antiscalant | 4 mg/L Hypersperse 400UL | Bench-scale | Total dissolved solids | mg/L | 242 | 198.2 | 220.1 | 19.9 | 1998-07-20 | 17:00 | 5 | 25 | 50 | 50 | 600 | 8.2 | 3.6 | 11.8 | 0.46109 | 0.69492 | 49.8475 | 18.6787 | 13.4939 | 2.4059 | 0.094973 | 2.3743 | 0.022951 | 49.977 | 0.27 | 1998-07-22 | 17:00 | 5 | 25.3 | 55 | 56 | 600 | 7.3 | 3.1 |  | 10.4 | 0.46109 | 0.70192 | 56.6923 | 16.6286 | 11.9068 | 410.3664 | 139.302 | 407.0684 | 2.6942 | 52.8058 | 0.22548 | [27 empty] | Sampling time | hh:mm | 13:00 | 13:00 | --- | --- | 13:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 12:00 | 12:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 12:00 | 12:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 12:00 | 12:00 | --- | --- | --- | --- | --- | SDS-TOXp, ug Cl- /L | 36.25 | 31.5 | BMRL | BMRL | SDS-TOXp, ug Cl- /L | 36.25 | 31.5 | BMRL | BMRL | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920
FAX Number |  | Design Parameters |  | ID# | Recovery | FW-design | Dp | PI | QI-cell | Qp | QF | QW | Phosphate (mg/L) |  |  |  |  | Total hardness | mg/L as CaCO3 | 103 | 92.9 | 97.95 | 10.3114 | 1998-07-21 | 9:00 | 21 | 24 | 50 | 52 | 600 | 7.7 | 3.6 | 11.3 | 0.46109 | 0.68142 | 52.0973 | 17.5398 | 13.0512 | 2.3155 | 0.091476 | 2.2869 | 0.022097 | 50.9779 | 0.25602 | 1998-07-23 | 7:00 | 19 | 22.6 | 55 | 56 | 590 | 7 | 2.9 |  | 9.9 | 0.4534 | 0.70707 | 58.596 | 15.9452 | 12.366 | 412.9469 | 140.2063 | 409.711 | 2.7112 | 52.7888 | 0.23426 | 9.09 |  |  | 149.2 |  |  | 391.2379 |  | 32.2126 | 389.8021 | 61.7242 | 0.006 |  |  | 0.13914 |  | 86.6667 | 0.13835 | 95.6631 | [8 empty] | Operation time | hh.hh | 73 | 73 | --- | --- | 73 | --- | --- | --- | --- | --- | Operation time | hh.hh | 96 | 96 | --- | --- | --- | --- | --- | Operation time | hh.hh | 120 | 120 | --- | --- | --- | --- | --- | Cumulative time | hr | 144 | 144 | --- | --- | --- | --- | --- | SDS-CDF, mg/L | 2.978 | 2.978 | 2.978 | 2.978 | SDS-CDF, mg/L | 2.978 | 2.978 | 2.978 | 2.978 | 1998 Producers Price Index (PPI base year 1967 = 100) | 370
E-Mail Address (optional) |  | Design flux, FW (gfd) | 16.5 |  | (decimal) | (gfd) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | Sulfate (mg/L) |  |  |  |  | Calcium hardness | mg/L as CaCO3 | 85.9 | 77.4 | 81.65 | 10.4103 | 1998-07-21 | 11:00 | 23 | 24.6 | 52 | 52 | 600 | 7.8 | 3.2 | 11 | 0.46109 | 0.70909 | 53.5455 | 17.7675 | 12.9883 | 2.5085 | 0.099086 | 2.4772 | 0.023937 | 51.9761 | 0.24989 | 1998-07-23 | 9:00 | 21 | 22.7 | 55 | 56 | 590 | 6.7 | 2.8 |  | 9.5 | 0.4534 | 0.70526 | 61.1053 | 15.2619 | 11.8011 | 411.9613 | 139.9192 | 408.872 | 2.705 | 52.795 | 0.22353 | [27 empty] | pH | --- | 8.67 | 8.61 | 8.64 | 0.69444 | 8.81 | --- | --- | --- | --- | --- | pH | --- | 8.63 | 8.52 | --- | --- | --- | --- | --- | pH | --- | 8.14 | 8.26 | --- | --- | --- | --- | --- | pH | --- | 8.5 | 8.87 | --- | --- | --- | --- | --- | SDS-CDp, mg/L | 0.5145 | 0.714 | 0.663 | 0.504 | SDS-CDp, mg/L | 0.5145 | 0.714 | 0.663 | 0.504 | Labor Rate + Fringe ($/work-hour) | 17
|  | Net driving pressure at the design flux, NDP (psi) | 70 | 1 | 0.7 | 15 | 8.4793 | 96.8347 | 606.4586 | 6.5843 | 9.4062 | 2.8219 | Calcium (mg/L) | 49 |  |  |  | Turbidity | ntu | 0.12 | 0.14 | 0.13 | 15.3846 | 1998-07-21 | 12:00 | 24 | 25.4 | 51 | 52 | 600 | 8.2 | 3.6 | 11.8 | 0.46109 | 0.69492 | 49.8475 | 18.6787 | 13.3353 | 2.4059 | 0.094973 | 2.3743 | 0.022951 | 51.477 | 0.25905 | 1998-07-23 | 11:00 | 23 | 22.7 | 55 | 56 | 590 | 6.8 | 2.8 |  | 9.6 | 0.4534 | 0.70833 | 60.4583 | 15.4897 | 11.9773 | 413.5517 | 140.4434 | 410.404 | 2.7153 | 52.7847 | 0.22691 | 9.03 | 9.02 | 8.97 | 147.7 | 254 | 493 | 395.9286 | 19.6899 | 32.8941 | 394.4981 | 62.56 | 0.005 | 0.044 | 0.136 | 0.14214 | -4.5168 | 88.8889 | 0.14135 | 96.4627 | [8 empty] | Temperature | oC | 22.7 | 22.7 | 22.7 | 0 | 22.7 | --- | --- | --- | --- | --- | Temperature | oC | 24.8 | 24.8 | --- | --- | --- | --- | --- | Temperature | oC | 26.2 | 26.2 | --- | --- | --- | --- | --- | Temperature | oC | 23 | 23 | --- | --- | --- | --- | --- | TOCF, mg/L | 2.6 | 2.6 | 2.6 | 2.6 | TOCF, mg/L | 2.6 | 2.6 | 2.6 | 2.6 | Labor Overhead Factor (% of labor) | 42
Technical ICR Contact Person |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.235 | 2 | 0.9 | 15 | 23.506 | 111.8614 | 606.4586 | 6.5843 | 7.3159 | 0.73159 | Barium (mg/L) |  |  |  |  | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! | 1998-07-21 | 14:00 | 26 | 25.5 | 51 | 52 | 600 | 8.2 | 3.6 | 11.8 | 0.46109 | 0.69492 | 49.8475 | 18.6787 | 13.2959 | 2.4059 | 0.094973 | 2.3743 | 0.022951 | 51.477 | 0.25829 | 1998-07-23 | 13:00 | 25 | 23.4 | 56 | 56 | 590 | 6.8 | 2.8 |  | 9.6 | 0.4534 | 0.70833 | 60.4583 | 15.4897 | 11.732 | 413.5517 | 140.4434 | 410.404 | 2.7153 | 53.2847 | 0.22018 | [27 empty] | Alkalinity | mg/L as CaCO3 | 36.5 | 35.5 | 36 | 2.7778 | 86 | 80.1667 | 6.7829 | 26.9036 | 79.9013 | 54.9444 | Alkalinity | mg/L as CaCO3 | 44 | 88 | 91.7273 | -4.2355 | 10.6599 | 91.4806 | 51.9023 | Alkalinity | mg/L as CaCO3 | 60.5 | 74.5 | 37.5408 | 49.6096 | -22.8426 | 37.6813 | -60.557 | Alkalinity | mg/L as CaCO3 | 22.5 | 54.4 | 60.7143 | -11.6071 | 54.3147 | 60.4907 | 62.8042 | TOCp, mg/L | #DIV/0! | BMRL | BMRL | BMRL | TOCp, mg/L | #DIV/0! | BMRL | BMRL | BMRL | Electric Rate ($/kW-h) | 0.06
Mailing Address |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | 3 | 0.5 | 15 | 5.474 | 93.8294 | 606.4586 | 6.5843 | 13.1686 | 6.5843 | Strontium (mg/L) |  |  |  |  | Total organic carbon | mg/L | 2.6 | 2.6 | 2.6 | 0 | 1998-07-21 | 16:00 | 28 | 25.8 | 51 | 52 | 600 | 8.2 | 3.5 | 11.7 | 0.46109 | 0.70085 | 50.2821 | 18.6787 | 13.1785 | 2.4479 | 0.09663 | 2.4158 | 0.023352 | 51.4766 | 0.25601 | 1998-07-23 | 15:00 | 27 | 23.4 | 56 | 57 | 600 | 6.8 | 2.9 |  | 9.7 | 0.46109 | 0.70103 | 60.8557 | 15.4897 | 11.732 | 409.8148 | 139.1922 | 406.7477 | 2.6909 | 53.8091 | 0.21803 | [27 empty] | Total dissolved solids | mg/L | 139.6 | 139.9 | 139.75 | 0.21467 | 492 | 407.5833 | 17.1579 | 36.5061 | 405.9741 | 65.5766 | Total dissolved solids | mg/L | 154.4 | 773 | 751.6727 | 2.759 | 29.8501 | 748.5852 | 79.3744 | Total dissolved solids | mg/L | 129.4 | 383 | 314.502 | 17.8846 | 41.2085 | 313.3692 | 58.7069 | Total dissolved solids | mg/L | 108.4 | 299 | 267.9714 | 10.3774 | 50.7497 | 267.0379 | 59.4065 | UV254 F, cm-1 | 0.045 | 0.045 | 0.045 | 0.045 | UV254 F, cm-1 | 0.045 | 0.045 | 0.045 | 0.045 | Fuel Oil Rate ($/gal) | NA
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 400 | 4 | 0.3 | 15 | 4.186 | 92.5414 | 606.4586 | 6.5843 | 21.9477 | 15.3634 | Reactive silica (mg/L as SiO2) |  |  |  |  | UV254 | cm-1 | 0.046 | 0.044 | 0.045 | 4.4444 | 1998-07-21 | 17:00 | 29 | 26.2 | 51 | 52 | 600 | 8.2 | 3.5 | 11.7 | 0.46109 | 0.70085 | 50.2821 | 18.6787 | 13.0236 | 2.4479 | 0.09663 | 2.4158 | 0.023352 | 51.4766 | 0.253 | 1998-07-23 | 17:00 | 29 | 23.7 | 56 | 57 | 600 | 7 | 3 |  | 10 | 0.46109 | 0.7 | 59 | 15.9452 | 11.9704 | 409.3363 | 138.9987 | 406.1824 | 2.6876 | 53.8124 | 0.22245 | 9.37 |  |  | 142.4 |  |  | 401.4 |  | 35.3021 | 399.8892 | 64.3901 | 0.006 |  |  | 0.136 |  | 86.6667 | 0.13524 | 95.5635 | [8 empty] | Total hardness | mg/L as CaCO3 | 37.1 | 37.2 | 37.15 | 0.26918 | 241.8 | 239.8167 | 0.82024 | 62.0725 | 238.599 | 84.4299 | Total hardness | mg/L as CaCO3 | 44.4 | 455.9 | 531.2182 | -16.5208 | 54.6708 | 528.7016 | 91.6021 | Total hardness | mg/L as CaCO3 | 34.1 | 167.6 | 164.4061 | 1.9057 | 65.1863 | 163.6086 | 79.1576 | Total hardness | mg/L as CaCO3 | 25.3 | 120.8 | 129.0857 | -6.859 | 74.1705 | 128.4786 | 80.308 | UV254 p, cm-1 | 0.0045 | 0.008 | 0.003 | 0.005 | UV254 p, cm-1 | 0.0045 | 0.008 | 0.003 | 0.005 | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Purchase price for an equivalent 8" x 40 " element ($) | 700 | 1: For experimental matrix see Table 4-2 in Part 3 of the ICR Treatment Studies Manual. | [8 empty] | Turbidity (ntu) | 3.9 |  |  |  | SUVA | L/(mg*m) | 1.7692 | 1.6923 | 1.7308 | 4.4444 | 1998-07-22 | 8:00 | 44 | 23.4 | 51 | 52 | 600 | 7.6 | 3.5 | 11.1 | 0.46109 | 0.68468 | 53.0541 | 17.312 | 13.1122 | 2.3367 | 0.092329 | 2.3082 | 0.022301 | 51.4777 | 0.25472 | 1998-07-24 | 7:00 | 43 | 21.8 | 56 | 57 | 600 | 6.8 | 3 |  | 9.8 | 0.46109 | 0.69388 | 60.2245 | 15.4897 | 12.3002 | 406.2417 | 137.9786 | 403.2014 | 2.6674 | 53.8326 | 0.22849 | 8.7 |  |  | 140.8 |  |  | 399.8467 |  | 36.0291 | 398.3787 | 64.6567 | 0.005 |  |  | 0.13567 |  | 88.8889 | 0.13493 | 96.2943 | [8 empty] | Calcium hardness | mg/L as CaCO3 | 31.8 | 32 | 31.9 | 0.62696 | 208.6 | 197.7333 | 5.2093 | 60.9308 | 196.737 | 83.7855 | Calcium hardness | mg/L as CaCO3 | 38.1 | 394.3 | 434.0091 | -10.0708 | 53.3374 | 431.9625 | 91.1798 | Calcium hardness | mg/L as CaCO3 | 29.2 | 145.1 | 136.2408 | 6.1056 | 64.2376 | 135.5857 | 78.4638 | Calcium hardness | mg/L as CaCO3 | 21.3 | 102.6 | 107.5143 | -4.7898 | 73.913 | 107.0099 | 80.0953 | BromideF, ug/L | 110 | 110 | 110 | 110 | BromideF, ug/L | 110 | 110 | 110 | 110 | Current Process Water Rate ($/1000 gal) | 0.375
FAX Number |  | Maximum flow rate to the 8" x 40" element, QI, max (gpm) | 70 | 2: Flow rates and pressures may need to be adjusted in order to obtain the desired operating conditions. | [8 empty] | SDI |  |  |  |  | Bromide | mg/L | 100 | 120 | 110 | 18.1818 | 1998-07-22 | 10:00 | 46 | 23.6 | 51 | 52 | 600 | 7.6 | 3.5 | 11.1 | 0.46109 | 0.68468 | 53.0541 | 17.312 | 13.0349 | 2.3367 | 0.092329 | 2.3082 | 0.022301 | 51.4777 | 0.25322 | 1998-07-24 | 9:00 | 45 | 22.3 | 56 | 57 | 600 | 6.8 | 3 |  | 9.8 | 0.46109 | 0.69388 | 60.2245 | 15.4897 | 12.1197 | 406.2417 | 137.9786 | 403.2014 | 2.6674 | 53.8326 | 0.22514 | [27 empty] | Turbidity | ntu | 0.14 | 0.11 | 0.125 | 24 | 0.22 | 0.14167 | 35.6061 | 3.8462 | 0.14157 | 11.7023 | Turbidity | ntu | 0.16 | 0.24 | -0.11273 | 146.9697 | -23.0769 | -0.11132 | 243.7331 | Turbidity | ntu | 0.11 | 0.16 | 0.15082 | 5.7398 | 15.3846 | 0.15057 | 26.9426 | Turbidity | ntu | 0.09 | 0.12 | 0.14714 | -22.619 | 30.7692 | 0.14681 | 38.6957 | Bromidep, ug/L | 108.5 | 120 | 120 | 110 | Bromidep, ug/L | 108.5 | 120 | 120 | 110 | Modifications to Existing Plant (% of construction costs) | 52
E-Mail Address (optional) |  | Minimum flow rate to the 8" x 40" element, QI, min (gpm) | 34 | [9 empty] | MFI |  |  |  |  | SDS-Cl2 dose | mg/L | 3.65 | 3.65 | 3.65 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-24 | 11:00 | 47 | 21.9 | 56 | 57 | 600 | 6.6 | 2.8 |  | 9.4 | 0.46109 | 0.70213 | 62.8298 | 15.0341 | 11.9032 | 410.3276 | 139.3974 | 407.3473 | 2.6944 | 53.8056 | 0.22123 | 8.67 | 8.82 | 8.75 | 142.7 | 257 | 492 | 402.5429 | 18.1823 | 35.1658 | 401.1137 | 64.4241 | 0.005 | 0.046 | 0.14 | 0.13929 | 0.5102 | 88.8889 | 0.13855 | 96.3911 | [8 empty] | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! | BMRL | #DIV/0! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | BMRL | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | BMRL | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | BMRL | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | AlkF, mg/L CaCO3 | 49.25 | 49.25 | 49.25 | 49.25 | AlkF, mg/L CaCO3 | 49.25 | 49.25 | 49.25 | 49.25
|  | Total width of all membrane envelopes in the 8" x 40" element, w (ft) | 70.67 | [9 empty] | MPFI |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | SDS-Free Cl2 residual | mg/L | 0.625 | 0.719 | 0.672 | 13.9881 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-24 | 13:00 | 49 | 22.1 | 56 | 57 | 600 | 6.6 | 2.8 |  | 9.4 | 0.46109 | 0.70213 | 62.8298 | 15.0341 | 11.833 | 410.3276 | 139.3974 | 407.3473 | 2.6944 | 53.8056 | 0.21992 | [27 empty] | Total organic carbon | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | 7.9 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L | BMRL | 18 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 5 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 3.6 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkp, mg/L CaCO3 | 36 | 44 | 60.5 | 22.5 | Alkp, mg/L CaCO3 | 36 | 44 | 60.5 | 22.5
Plant Name | Facility 1 | Feed spacer thickness in the 8" x 40" element, T (ft) | 0.0023 | [9 empty] | Bromide (mg/L) | 86 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | SDS-Cl2 demand | mg/L | 3.025 | 2.931 | 2.978 | 3.1565 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-24 | 15:00 | 51 | 22.6 | 57 | 58 | 600 | 6.7 | 2.8 |  | 9.5 | 0.46109 | 0.70526 | 62.1579 | 15.2619 | 11.8361 | 411.938 | 139.9289 | 408.9005 | 2.7049 | 54.7951 | 0.21601 | [27 empty] | UV254 | cm-1 | 0.004 | 0.005 | 0.0045 | 22.2222 | 0.141 | 0.1395 | 1.0638 | 90 | 0.13869 | 96.7553 | UV254 | cm-1 | 0.008 | 0.311 | 0.34436 | -10.7279 | 82.2222 | 0.34262 | 97.6651 | UV254 | cm-1 | 0.003 | 0.091 | 0.088714 | 2.5118 | 93.3333 | 0.08819 | 96.5982 | UV254 | cm-1 | 0.005 | 0.062 | 0.062143 | -0.23041 | 88.8889 | 0.061809 | 91.9105 | T-HdF, mg/L CaCO3 | 97.95 | 97.95 | 97.95 | 97.95 | T-HdF, mg/L CaCO3 | 97.95 | 97.95 | 97.95 | 97.95
Treatment Plant Category | CS/SOFT | [11 empty] | TOC (mg/L) | 3.8 | is to list the pretreatment processes used in this particular RBSMT run. |  |  | SDS-Chlorination temp. | oC | 26 | 26.2 | 26.1 | 0.76628 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-24 | 17:00 | 53 | 22.9 | 57 | 58 | 600 | 6.8 | 2.9 |  | 9.7 | 0.46109 | 0.70103 | 60.8557 | 15.4897 | 11.9067 | 409.8148 | 139.1922 | 406.7477 | 2.6909 | 54.8091 | 0.21724 | 8.49 |  |  | 145 |  |  | 396.1966 |  | 34.1209 | 394.7731 | 63.27 | 0.005 |  |  | 0.13879 |  | 88.8889 | 0.13803 | 96.3777 | [8 empty] | SUVA | L/(mg*m) | NR | NR | #DIV/0! | #VALUE! | 1.7848 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 1.7278 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 1.82 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 1.7222 | --- | --- | --- | --- | --- | T-Hdp, mg/L CaCO3 | 37.15 | 44.4 | 34.1 | 25.3 | T-Hdp, mg/L CaCO3 | 37.15 | 44.4 | 34.1 | 25.3
Process Train Name | Coagulation/Sedimentation/Softening | Additional Information | [10 empty] | pH | 8.08 |  |  |  | SDS-Chlorination pH | --- | 9.425 | 9.42 | 9.4225 | 0.053064 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-25 | 7:00 | 67 | 21.5 | 58 | 59 | 600 | 7 | 3 |  | 10 | 0.46109 | 0.7 | 59 | 15.9452 | 12.7747 | 409.3363 | 138.9987 | 406.1824 | 2.6876 | 55.8124 | 0.22889 | 8.75 |  |  | 144.4 |  |  | 396.7333 |  | 34.3935 | 395.2614 | 63.4672 | 0.005 |  |  | 0.13833 |  | 88.8889 | 0.13756 | 96.3651 | [8 empty] | Bromide | mg/L | 97 | 120 | 108.5 | 21.1982 | --- | 113.5 | --- | 1.3636 | 113.47 | 4.38 | Bromide | mg/L | 120 | --- | 29.0909 | --- | -9.0909 | 29.5609 | -305.9422 | Bromide | mg/L | 120 | --- | 99.5918 | --- | -9.0909 | 99.7167 | -20.3409 | Bromide | mg/L | 110 | --- | 110 | --- | 0 | 110 | 0 | Ca-HdF, mg/L CaCO3 | 81.65 | 81.65 | 81.65 | 81.65 | Ca-HdF, mg/L CaCO3 | 81.65 | 81.65 | 81.65 | 81.65
ICR Treatment Plant Identification Number | 381 | Design cross-flow velocity (fps) | 0.43 | [9 empty] | Total Hardness (mg/L as CaCO3) | 168.6 |  |  |  | SDS-Incubation time | hours | 24 | 24 | 24 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-25 | 9:00 | 69 | 22.2 | 58 | 59 | 600 | 7.1 | 3 |  | 10.1 | 0.46109 | 0.70297 | 58.4059 | 16.173 | 12.6919 | 410.8555 | 139.4991 | 407.6445 | 2.6975 | 55.8025 | 0.22744 | [27 empty] | SDS-Cl2 dose | mg/L | 1.5 | 1.5 | 1.5 | 0 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1.5 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1.5 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1 | --- | --- | --- | --- | --- | --- | Ca-Hdp, mg/L CaCO3 | 31.9 | 38.1 | 29.2 | 21.3 | Ca-Hdp, mg/L CaCO3 | 31.9 | 38.1 | 29.2 | 21.3
PWSID Number of Plant (if assigned) | KS200910 | Required influent flow to permeate flow rate ratio, QI:Qp | [10 empty] | UV254 | 0.106 |  |  |  | SDS-TOX | mg Cl- /L | 180 | 175 | 177.5 | 2.8169 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-25 | 11:00 | 71 | 22 | 58 | 59 | 600 | 7.1 | 3 |  | 10.1 | 0.46109 | 0.70297 | 58.4059 | 16.173 | 12.7671 | 410.8555 | 139.4991 | 407.6445 | 2.6975 | 55.8025 | 0.22879 | 8.69 | 8.72 | 8.8 | 146.1 | 257 | 521 | 395.2333 | 24.1395 | 33.6211 | 393.7593 | 62.8961 | 0.005 | 0.045 | 0.141 | 0.13967 | 0.94563 | 88.8889 | 0.13887 | 96.3995 | [8 empty] | SDS-Free Cl2 residual | mg/L | 0.94 | 1.031 | 0.9855 | 9.2339 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.786 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.837 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.496 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 0.1 | Maximum element recovery (%) | 15 | [9 empty] | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | SDS-CHCl3 | mg/L | 65.545 | 55.275 | 60.41 | 17.0005 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-25 | 13:00 | 73 | 22 | 58 | 59 | 600 | 7.2 | 3.1 |  | 10.3 | 0.46109 | 0.69903 | 57.2524 | 16.4008 | 12.947 | 408.8889 | 138.8159 | 405.648 | 2.6845 | 55.8155 | 0.23196 | [27 empty] | SDS-Cl2 demand | mg/L | 0.56 | 0.469 | 0.5145 | 17.6871 | --- | 8.7262 | --- | 82.7233 | 8.6768 | 94.0704 | SDS-Cl2 demand | mg/L | 0.714 | --- | 21.2958 | --- | 76.0242 | 21.1894 | 96.6304 | SDS-Cl2 demand | mg/L | 0.663 | --- | 5.3875 | --- | 77.7367 | 5.3586 | 87.6273 | SDS-Cl2 demand | mg/L | 0.504 | --- | 4.0383 | --- | 83.0759 | 4.0176 | 87.4552 | Blended Water Quality if THM4 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if THM4 Controls the Blend Ratio
Historical Average Water Temperature (oC) | 14 | Variability of design flux (%) | [10 empty] | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | SDS-BDCM | mg/L | 24.754 | 27.534 | 26.144 | 10.6334 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-25 | 15:00 | 75 | 21.8 | 58 | 58 | 600 | 7.1 | 3 |  | 10.1 | 0.46109 | 0.70297 | 58.4059 | 16.173 | 12.8428 | 410.8555 | 139.4991 | 407.6445 | 2.6975 | 55.3025 | 0.23223 | [27 empty] | SDS-Chlorination temp. | oC | 26.2 | 26.2 | 26.2 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 26.2 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 26.2 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 26.2 | --- | --- | --- | --- | --- | --- | Qp/QT (THM4), % | 36.7214 | 43.6486 | 34.2156 | 33.7489 | Qp/QT (THM4), % | 79.3313 | 94.2965 | 73.9178 | 72.9095
State Approved Plant Capacity (MGD) | 55 | Rejection of reference solute and conditions of test | 45 rejection of CaCl2 | [14 empty] | SDS-DBCM | mg/L | 12.46 | 15.184 | 13.822 | 19.7077 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-25 | 17:00 | 77 | 22.2 | 58 | 58 | 600 | 7.1 | 3 |  | 10.1 | 0.46109 | 0.70297 | 58.4059 | 16.173 | 12.6919 | 410.8555 | 139.4991 | 407.6445 | 2.6975 | 55.3025 | 0.2295 | 8.7 |  |  | 147.2 |  |  | 392.63 |  | 33.1213 | 391.1779 | 62.3701 | 0.005 |  |  | 0.13967 |  | 88.8889 | 0.13887 | 96.3995 | [8 empty] | SDS-Chlorination pH | --- | 9.39 | 9.44 | 9.415 | 0.53107 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 9.43 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 9.46 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 9.45 | --- | --- | --- | --- | --- | --- | SDS-THM4b, ug/L | 72 | 72 | 72 | 72 | SDS-THM4b, ug/L | 36 | 36 | 36 | 36
|  | (e.g., solute type and concentration) | 70psi, 500mg/L CaCl2,25 deg. C,15% recovery | [14 empty] | SDS-CHBr3 | mg/L | 2.337 | 2.961 | 2.649 | 23.5561 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-26 | 8:00 | 92 | 20.9 | 58 | 59 | 600 | 6.7 | 0.8 |  | 7.5 | 0.46109 | 0.89333 | 79 | 15.2619 | 12.446 | 536.6747 | 182.3 | 532.7175 | 3.524 | 54.976 | 0.22639 | [27 empty] | SDS-Incubation time | hours | 24 | 24 | 24 | 0 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-HAA5b, ug/L | 17.6787 | 17.966 | 18.0355 | 18.124 | SDS-HAA5b, ug/L | 7.2197 | 7.8405 | 7.9908 | 8.1819
|  | Variability of rejection of reference solute (%) | 45 rejection of CaCl2 | [14 empty] | SDS-THM4 | mg/L | 105.096 | 100.954 | 103.025 | 4.0204 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-26 | 9:00 | 93 | 21.6 | 58 | 59 | 600 | 6.6 | 0.8 |  | 7.4 | 0.46109 | 0.89189 | 80.0811 | 15.0341 | 12.0092 | 535.3881 | 181.8833 | 531.4996 | 3.5156 | 54.9844 | 0.21841 | 8.57 |  |  | 149.5 |  |  | 802.55 |  | 32.0763 | 798.9582 | 81.2881 | 0.007 |  |  | 0.3585 |  | 84.4444 | 0.35657 | 98.0368 | [8 empty] | SDS-TOX | mg Cl- /L | 45.5 | 27 | 36.25 | 51.0345 | --- | 507.0833 | --- | 79.5775 | 504.2544 | 92.8112 | SDS-TOX | mg Cl- /L | 31.5 | --- | 1358.7727 | --- | 82.2535 | 1351.9115 | 97.67 | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOXb, ug Cl- /L | 125.631 | 113.773 | #VALUE! | #VALUE! | SDS-TOXb, ug Cl- /L | 65.4446 | 39.8271 | #VALUE! | #VALUE!
|  | Standard testing recovery (%) | 15 | [14 empty] | SDS-MCAA* | mg/L | BMRL | 3.3731 | 3.3731 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-26 | 10:00 | 94 | 21.6 | 58 | 59 | 600 | 6.4 | 0.77 |  | 7.17 | 0.46109 | 0.89261 | 82.682 | 14.5785 | 11.6453 | 535.9166 | 182.1033 | 532.1426 | 3.5193 | 54.9807 | 0.21181 | 8.64 |  |  | 152.2 |  |  | 784.4636 |  | 30.8496 | 781.0916 | 80.5144 | 0.0095 |  |  | 0.34006 |  | 78.8889 | 0.3383 | 97.1919 | [8 empty] | SDS-CHCl3 | mg/L | BMRL | 1.2 | 1.2 | #VALUE! | --- | 198.5667 | --- | 98.0136 | 197.3808 | 99.392 | SDS-CHCl3 | mg/L | 3.506 | --- | 520.8151 | --- | 94.1963 | 518.1409 | 99.3234 | SDS-CHCl3 | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHCl3 | mg/L | 1.526 | --- | 85.646 | --- | 97.4739 | 85.1539 | 98.208 | SDS-CDb, mg/L | 2.0734 | 1.9898 | 2.1859 | 2.1431 | SDS-CDb, mg/L | 1.0237 | 0.84313 | 1.2668 | 1.1742
|  | Standard testing pH | 8 | [14 empty] | SDS-DCAA* | mg/L | 18.7268 | 17.9625 | 18.3447 | 4.1663 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-26 | 11:00 | 95 | 21.7 | 59 | 60 | 600 | 6.5 | 0.78 |  | 7.28 | 0.46109 | 0.89286 | 81.4176 | 14.8063 | 11.7923 | 536.1754 | 182.171 | 532.3403 | 3.5209 | 55.9791 | 0.21066 | 8.58 | 9 |  | 151.7 |  |  | 790.1 |  | 31.0768 | 786.642 | 80.7155 | 0.009 |  |  | 0.345 |  | 80 | 0.34318 | 97.3775 | [8 empty] | SDS-BDCM | mg/L | 3.107 | 3.054 | 3.0805 | 1.7205 | --- | 79.9588 | --- | 88.2172 | 79.4969 | 96.125 | SDS-BDCM | mg/L | 6.13 | --- | 188.0755 | --- | 76.5529 | 187.1349 | 96.7243 | SDS-BDCM | mg/L | 1.92 | --- | 51.3567 | --- | 92.6561 | 51.0542 | 96.2393 | SDS-BDCM | mg/L | 1.35 | --- | 36.77 | --- | 94.8363 | 36.5628 | 96.3077 | TOCb, mg/L | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | TOCb, mg/L | #DIV/0! | #VALUE! | #VALUE! | #VALUE!
|  | Acceptable range of operating pressures | 0 to 600 psi | [14 empty] | SDS-TCAA* | mg/L | 2.9195 | 4.002 | 3.4607 | 31.2793 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-26 | 12:00 | 96 | 21.8 | 59 | 60 | 600 | 6.2 | 0.77 |  | 6.97 | 0.46109 | 0.88953 | 85.0832 | 14.1229 | 11.2149 | 533.1881 | 181.2165 | 529.5511 | 3.5015 | 55.9985 | 0.20027 |  |  | 8.68 | 152.3 | 260 | 732 | 766.0221 | -4.6478 | 30.8042 | 762.8512 | 80.0354 | 0.009 | 0.046 | 0.286 | 0.33487 | -17.0875 | 80 | 0.33319 | 97.2988 | [8 empty] | SDS-DBCM | mg/L | 7.364 | 6.896 | 7.13 | 6.5638 | --- | 29.4367 | --- | 48.4156 | 29.3026 | 75.6677 | SDS-DBCM | mg/L | 11.51 | --- | 32.5282 | --- | 16.727 | 32.4195 | 64.4967 | SDS-DBCM | mg/L | 4.73 | --- | 23.2851 | --- | 65.7792 | 23.1715 | 79.587 | SDS-DBCM | mg/L | 3.29 | --- | 18.3357 | --- | 76.1974 | 18.2477 | 81.9703 | UV254 b, cm-1 | 0.030128 | 0.02885 | 0.030629 | 0.0315 | UV254 b, cm-1 | 0.012871 | 0.01011 | 0.013955 | 0.015836
|  | Acceptable range of operating pH values | 3 to 10 | [14 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-26 | 15:00 | 99 | 21.8 | 59 | 60 | 600 | 6.4 | 0.84 |  | 7.24 | 0.46109 | 0.88398 | 81.8729 | 14.5785 | 11.5766 | 528.5835 | 179.6115 | 524.8612 | 3.4711 | 56.0289 | 0.20662 | [27 empty] | SDS-CHBr3 | mg/L | 7.833 | 7.621 | 7.727 | 2.7436 | --- | -9.1997 | --- | -191.695 | -9.098 | 184.9311 | SDS-CHBr3 | mg/L | 10.8 | --- | -63.3 | --- | -307.701 | -62.9169 | 117.1655 | SDS-CHBr3 | mg/L | 5.7 | --- | -0.52653 | --- | -115.1755 | -0.48842 | 1267.0182 | SDS-CHBr3 | mg/L | 4.93 | --- | 1.6714 | --- | -86.108 | 1.6905 | -191.6312 | Bromideb, ug/L | 109.4492 | 114.3649 | 113.4216 | 110 | Bromideb, ug/L | 108.81 | 119.4296 | 117.3918 | 110
|  | Typical pressure drop across a single element (psi) | 3 to5 | [14 empty] | SDS-DBAA* | mg/L | 2.6609 | 3.7396 | 3.2003 | 33.7067 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-27 | 8:00 | 116 | 23.5 | 59 | 60 | 600 | 7 | 7.1 |  | 14.1 | 0.46109 | 0.49645 | 41.5532 | 15.9452 | 12.0414 | 327.4677 | 111.1985 | 324.9445 | 2.1501 | 57.3499 | 0.20996 | [27 empty] | SDS-THM4 | mg/L | 18.304 | 18.771 | 18.5375 | 2.5192 | --- | 300.1625 | --- | 82.0068 | 298.4704 | 93.7892 | SDS-THM4 | mg/L | 31.946 | --- | 678.1187 | --- | 68.992 | 674.7784 | 95.2657 | SDS-THM4 | mg/L | 12.35 | --- | 197.401 | --- | 88.0126 | 196.2685 | 93.7076 | SDS-THM4 | mg/L | 11.096 | --- | 142.4231 | --- | 89.2298 | 141.6549 | 92.1669 | Alkb, mg/L CaCO3 | 44.3844 | 46.9584 | 53.0993 | 40.2222 | Alkb, mg/L CaCO3 | 38.7386 | 44.2994 | 57.5658 | 29.7467
|  | Maximum permissible SDI | 5 | [14 empty] | SDS-BCAA* | mg/L | 7.0923 | 8.4172 | 7.7547 | 17.085 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-27 | 10:00 | 118 | 24.1 | 59 | 60 | 600 | 7.2 | 7.2 |  | 14.4 | 0.46109 | 0.5 | 40.6667 | 16.4008 | 12.1677 | 328.6312 | 111.5688 | 326.0265 | 2.1576 | 57.3424 | 0.21219 | 8.11 |  |  | 128.3 |  |  | 311.9 |  | 41.7083 | 310.7984 | 58.7192 | 0.005 |  |  | 0.085 |  | 88.8889 | 0.08452 | 94.0842 | [8 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | T-Hdb, mg/L CaCO3 | 75.6234 | 74.5762 | 76.1033 | 73.4314 | T-Hdb, mg/L CaCO3 | 49.7166 | 47.4542 | 50.7535 | 44.9812
|  | Maximum permissible turbidity (ntu) | 1 | [14 empty] | SDS-TBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-27 | 11:00 | 119 | 24.7 | 59 | 60 | 600 | 7.4 | 7.3 |  | 14.7 | 0.46109 | 0.5034 | 39.8163 | 16.8564 | 12.2859 | 329.7561 | 111.9257 | 327.0695 | 2.1649 | 57.3351 | 0.21428 | 8.27 |  |  | 129 |  |  | 312.4479 |  | 41.3903 | 311.3167 | 58.5631 | 0.005 |  |  | 0.085548 |  | 88.8889 | 0.085051 | 94.1212 | [8 empty] | SDS-DCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCAA* | mg/L | 2.16 | --- | 149.2932 | --- | 88.2254 | 148.5326 | 98.5458 | SDS-DCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Ca-Hdb, mg/L CaCO3 | 63.3811 | 62.641 | 63.7039 | 61.2826 | Ca-Hdb, mg/L CaCO3 | 42.1827 | 40.5839 | 42.8801 | 37.6491
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | <0.1 ppm | [14 empty] | SDS-CDBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-27 | 12:00 | 120 | 24.7 | 59 | 60 | 600 | 7.4 | 7 |  | 14.4 | 0.46109 | 0.51389 | 40.6667 | 16.8564 | 12.2859 | 333.2147 | 113.0996 | 330.4999 | 2.1876 | 57.3124 | 0.21437 | 8.33 | 8.39 | 8.34 | 130.5 | 258 | 378 | 314.82 | 16.7143 | 40.7088 | 313.6834 | 58.3975 | 0.004 | 0.044 | 0.086 | 0.088343 | -2.7243 | 91.1111 | 0.087823 | 95.4454 | [8 empty] | SDS-TCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | 1: All of the information requested in this field may not be available, but values for all Design | [15 empty] | SDS-DCBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-27 | 15:00 | 123 | 25.9 | 60 | 60 | 610 | 7.4 | 6.8 |  | 14.2 | 0.46877 | 0.52113 | 41.9577 | 16.8564 | 11.8577 | 335.632 | 113.9355 | 332.9425 | 2.2035 | 57.7965 | 0.20516 | [27 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  | Parameters must be entered in cells E14:E23, since these parameters are used in calculations. | [15 empty] | SDS-HAA5 | mg/L | 24.3072 | 29.0772 | 26.6922 | 17.8704 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-27 | 17:00 | 125 | 25.5 | 59 | 60 | 610 | 7.4 | 7 |  | 14.4 | 0.46877 | 0.51389 | 41.3611 | 16.8564 | 11.9988 | 333.2028 | 113.1109 | 330.5328 | 2.1876 | 57.3124 | 0.20936 | [27 empty] | SDS-DBAA* | mg/L | 2.2541 | 2.0388 | 2.1465 | 10.0305 | --- | 5.6591 | --- | 32.9287 | 5.638 | 61.929 | SDS-DBAA* | mg/L | 4.5403 | --- | -7.642 | --- | -41.8733 | -7.579 | 159.9063 | SDS-DBAA* | mg/L | 1.3919 | --- | 5.0824 | --- | 56.5065 | 5.0598 | 72.4911 | SDS-DBAA* | mg/L | 1.3042 | --- | 4.0128 | --- | 59.2469 | 3.997 | 67.3705 | Blended Water Quality if HAA5 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if HAA5 Controls the Blend Ratio
[18 empty] | SDS-HAA6 | mg/L | 31.3995 | 37.4944 | 34.447 | 17.6936 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-28 | 8:00 | 140 | 22.6 | 59 | 60 | 600 | 7 | 17.5 |  | 24.5 | 0.46109 | 0.28571 | 23.4898 | 15.9452 | 12.366 | 271.291 | 92.1225 | 269.2007 | 1.7812 | 57.7188 | 0.21425 | [27 empty] | SDS-BCAA* | mg/L | 1.4046 | 1.2344 | 1.3195 | 12.8988 | --- | 22.7703 | --- | 82.9846 | 22.6414 | 94.1722 | SDS-BCAA* | mg/L | 2.7624 | --- | 48.1474 | --- | 64.378 | 47.9128 | 94.2345 | SDS-BCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Qp/QT (HAA5), % | -111.2527 | -136.5943 | -107.9347 | -107.5618 | Qp/QT (HAA5), % | -1.254 | -1.5396 | -1.2166 | -1.2124
[18 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-28 | 10:00 | 142 | 23.3 | 60 | 60 | 600 | 7 | 16.6 |  | 23.6 | 0.46109 | 0.29661 | 24.4237 | 15.9452 | 12.1128 | 273.7188 | 92.947 | 271.6098 | 1.7972 | 58.2028 | 0.20811 | 8.64 |  |  | 104 |  |  | 269.0578 |  | 52.7488 | 268.095 | 61.2078 | 0.008 |  |  | 0.060602 |  | 82.2222 | 0.060296 | 86.732 | [8 empty] | SDS-TBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-THM4b, ug/L | NA | NA | NA | NA | SDS-THM4b, ug/L | NA | NA | NA | NA
[18 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-28 | 11:00 | 143 | 23.3 | 60 | 60 | 600 | 7 | 16.8 |  | 23.8 | 0.46109 | 0.29412 | 24.2101 | 15.9452 | 12.1128 | 273.1596 | 92.7571 | 271.0549 | 1.7935 | 58.2065 | 0.2081 | 8.72 |  |  | 104.5 |  |  | 268.2667 |  | 52.5216 | 267.3114 | 60.907 | 0.005 |  |  | 0.061667 |  | 88.8889 | 0.061336 | 91.8482 | [8 empty] | SDS-CDBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-HAA5b, ug/L | NA | NA | NA | NA | SDS-HAA5b, ug/L | NA | NA | NA | NA
[18 empty] | should be reported if measured. | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-28 | 12:00 | 144 | 23.7 | 60 | 60 | 600 | 7 | 16.4 |  | 23.4 | 0.46109 | 0.29915 | 24.641 | 15.9452 | 11.9704 | 274.2899 | 93.1409 | 272.1765 | 1.8009 | 58.1991 | 0.20568 | 8.8 | 8.98 | 8.97 | 105 | 194.1 | 298 | 269.228 | 9.655 | 52.2944 | 268.2701 | 60.8603 | 0.004 | 0.044 | 0.063 | 0.0625 | 0.79365 | 91.1111 | 0.062159 | 93.5649 | [8 empty] | SDS-DCBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TOXb, ug Cl- /L | NA | NA | NA | NA | SDS-TOXb, ug Cl- /L | NA | NA | NA | NA
[45 empty] | 1998-07-28 | 15:00 | 147 | 26 | 59 | 60 | 600 | 7.2 | 16.6 |  | 23.8 | 0.46109 | 0.30252 | 24.2101 | 16.4008 | 11.5032 | 275.0619 | 93.3822 | 272.8818 | 1.8059 | 57.6941 | 0.19938 | [27 empty] | SDS-HAA5 | mg/L | 2.2541 | 2.0388 | 2.1465 | 10.0305 | --- | 83.9656 | --- | 91.9585 | 83.474 | 97.4286 | SDS-HAA5 | mg/L | 6.7003 | --- | 188.4448 | --- | 74.8979 | 187.5053 | 96.4266 | SDS-HAA5 | mg/L | 1.3919 | --- | 53.0252 | --- | 94.7854 | 52.7092 | 97.3593 | SDS-HAA5 | mg/L | 1.3042 | --- | 37.5728 | --- | 95.1139 | 37.3606 | 96.5092 | SDS-CDb, mg/L | NA | NA | NA | NA | SDS-CDb, mg/L | NA | NA | NA | NA
[45 empty] | 1998-07-28 | 17:00 | 149 | 25.6 | 59 | 60 | 600 | 7.2 | 16 |  | 23.2 | 0.46109 | 0.31034 | 24.8621 | 16.4008 | 11.64 | 276.8498 | 93.9892 | 274.6555 | 1.8176 | 57.6824 | 0.2018 | [27 empty] | SDS-HAA6 | mg/L | 3.6587 | 3.2732 | 3.4659 | 11.1225 | --- | 106.736 | --- | 89.9383 | 106.1155 | 96.7338 | SDS-HAA6 | mg/L | 9.4627 | --- | 236.5922 | --- | 72.5296 | 235.4181 | 95.9805 | SDS-HAA6 | mg/L | 1.3919 | --- | 68.8512 | --- | 95.9593 | 68.4383 | 97.9662 | SDS-HAA6 | mg/L | 1.3042 | --- | 48.651 | --- | 96.2139 | 48.374 | 97.3039 | TOCb, mg/L | NA | NA | NA | NA | TOCb, mg/L | NA | NA | NA | NA
[45 empty] | 1998-07-29 | 14:00 | 170 | 23.5 | 58 | 58 | 600 | 11.4 | 21 | X | 32.4 | 0.46109 | 0.35185 | 17.5185 | 25.968 | 19.6103 | 286.9473 | 96.9603 | 283.3375 | 1.8818 | 56.1182 | 0.34945 | [27 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | UV254 b, cm-1 | NA | NA | NA | NA | UV254 b, cm-1 | NA | NA | NA | NA
[45 empty] | 1998-07-29 | 16:00 | 172 | 23.5 | 58 | 58 | 600 | 11 | 22 |  | 33 | 0.46109 | 0.33333 | 17.1818 | 25.0568 | 18.9222 | 282.4143 | 95.4715 | 278.987 | 1.8523 | 56.1477 | 0.33701 | [27 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | Bromideb, ug/L | NA | NA | NA | NA | Bromideb, ug/L | NA | NA | NA | NA
[45 empty] | 1998-07-29 | 17:00 | 173 | 23.3 | 58 | 58 | 600 | 11.2 | 23.2 |  | 34.4 | 0.46109 | 0.32558 | 16.4419 | 25.5124 | 19.3805 | 280.5758 | 94.8287 | 277.1085 | 1.8401 | 56.1599 | 0.3451 | [66 empty] | Alkb, mg/L CaCO3 | NA | NA | NA | NA | Alkb, mg/L CaCO3 | NA | NA | NA | NA
[45 empty] | 1998-07-30 | 7:00 | 187 | 22.5 | 57 | 58 | 600 | 9.5 | 23.2 |  | 32.7 | 0.46109 | 0.29052 | 17.3486 | 21.64 | 16.8322 | 272.4491 | 92.2579 | 269.5961 | 1.7876 | 55.7124 | 0.30213 | [66 empty] | T-Hdb, mg/L CaCO3 | NA | NA | NA | NA | T-Hdb, mg/L CaCO3 | NA | NA | NA | NA
[45 empty] | 1998-07-30 | 9:30 | 189.5 | 22.6 | 59 | 60 | 600 | 10.2 | 22.7 |  | 32.9 | 0.46109 | 0.31003 | 17.2371 | 23.2345 | 18.0191 | 276.9003 | 93.6916 | 273.7857 | 1.8165 | 57.6835 | 0.31238 | [66 empty] | Ca-Hdb, mg/L CaCO3 | NA | NA | NA | NA | Ca-Hdb, mg/L CaCO3 | NA | NA | NA | NA
[45 empty] | 1998-07-30 | 10:30 | 190.5 | 22.5 | 59 | 60 | 590 | 10.2 | 22.6 |  | 32.8 | 0.4534 | 0.31098 | 16.9878 | 23.2345 | 18.0724 | 277.1254 | 93.7496 | 273.9552 | 1.8179 | 57.6821 | 0.31331 | [66 empty] | Notes: |  |  |  |  | Notes:
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to |  |  |  |  | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | determine the percentage of total flow that must be treated by the membrane process to meet the |  |  |  |  | determine the percentage of total flow that must be treated by the membrane process to meet the
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Stage 1 DBP MCLs. |  |  |  |  | Stage 2 DBP MCLs.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | A 10% factor of safety has been applied all the MCLs. i.e., 72 / 54 mg/L for THM4 and HAA5. |  |  |  |  | A 10% factor of safety has been applied all the MCLs. i.e., 36 / 27 mg/L for THM4 and HAA5.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for |  |  |  |  | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | both parameters and the maximum (Qp/QT) ratio controls the design. |  |  |  |  | both parameters and the maximum (Qp/QT) ratio controls the design.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. |  |  |  |  | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. |  |  |  |  | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. |  |  |  |  | The subscript "b" refers to the blended water quality for a given blend ratio.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL. |  |  |  |  | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. |  |  |  |  | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Note on X24: Alison Gusses: High precision incubator was used for SDS testing
Note on CY29: Alison Gusses: High precision incubator was used for SDS testing
Note on DL25: C. Rice: Consultant verified the bromide concentrations for the 50% and 90% recovery runs. The values may be due to bias error since the results are less than 10 percent higher than the feed water.
Note on DL29: Alison Gusses: High precision incubator was used for SDS testing
Note on DV25: C. Rice: Consultant verified the bromide concentrations for the 50% and 90% recovery runs. The values may be due to bias error since the results are less than 10 percent higher than the feed water.
Note on DV29: Alison Gusses: High precision incubator was used for SDS testing
Note on DX16: C. Rice: Consultant verified value; all QC criteria for the run was met. The sample may have become contaminated but the exact error is not known.
Note on EF29: Alison Gusses: High precision incubator was used for SDS testing

## NF200. 3rd Quarter
FIELD-SET 3: 3rd QUARTER RBSMT RESULTS (FILE: rbsmt-1.xls)
Field 3-1: PWS And Treatment Plant Data |  | Field 3-2: Manufacturer Reported Membrane Characteristics1 |  | Field 3-3: RBSMT Design Parameters | [8 empty] | Field 3-4: Foulants And Fouling Indices1 |  | Field 3-5: Pretreatment Used Prior To Membranes1 |  |  | Field 3-6: Feed Water Quality After Pretreatment | [5 empty] | Field 3-7: Membrane Setting Data | [20 empty] | Field 3-8: Membrane Performance Data During Operation With The Test Water | [16 empty] | Field 3-8: Membrane Performance Data During Operation With The Test Water (continued) | [19 empty] | Field 3-8: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 3-9: Permeate And Concentrate Water Quality For Run 1 | [11 empty] | Field 3-10: Permeate And Concentrate Water Quality For Run 2 | [8 empty] | Field 3-11: Permeate And Concentrate Water Quality For Run 3 | [8 empty] | Field 3-12: Permeate And Concentrate Water Quality For Run 4 | [8 empty] | Field 3-13: Blending Calculations For Stage 1 D-DBP MCLs |  |  |  |  | Field 3-14: Blending Calculations For Proposed Stage 2 D-DBP MCLs |  |  |  |  | Field 3-15: Membrane Cost Parameters
|  | General Information |  | Input Design Parameters | [8 empty] | Parameters Evaluated Prior to Pretreatment | [80 empty] | Operating Parameters During Sample Collection | [11 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Feed and Permeate Water Quality Parameters |  |  |  |  | Feed and Permeate Water Quality Parameters |  |  |  |  | General Cost Parameters
PWS Name | Water District No. 1 of Johnson County, Kansas | Membrane manufacturer | FilmTec Corporation | [5 empty] | Active membrane area in bench-scale cell, Acell (ft2) | 0.167 |  |  | Alkalinity (mg/L as CaCO3) | 151 | Process | Description | Scale | Parameter | Units | CF-1 | CF-2 | Average | RPD |  |  |  | Average TDS rejection (decimal fraction) | 0.96 | [5 empty] | TDS concentration of setting solution (mg/L) | 0.8 | [12 empty] | Average bulk TDS rejection (decimal fraction) | 0.72833 | [45 empty] | Recovery during sample collection (decimal) | 0.71 | [10 empty] | Recovery during sample collection (decimal) | 0.89 | [7 empty] | Recovery during sample collection (decimal) | 0.5 | [7 empty] | Recovery during sample collection (decimal) | 0.3 | [8 empty] | RUN ID # |  |  |  |  | RUN ID # |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | KS200910 | Membrane trade name | NF200B-4040 | [5 empty] | Active width of membrane in the bench-scale cell, wcell (ft) | 0.333 |  |  | Calcium Hardness (mg/L as CaCO3) | 134 | Presedimentation | 3 Basins | Full-scale | Sampling date | MM/DD/YY | 1998-10-21 | 1998-10-28 | --- | --- | [71 empty] | Feed flow rate during sample collection (mL/min) | 9.6 | [10 empty] | Feed flow rate during sample collection (mL/min) | 6.97 | [7 empty] | Feed flow rate during sample collection (mL/min) | 13.6 | [7 empty] | Feed flow rate during sample collection (mL/min) | 22.9 | [6 empty] | Parameter | 1 | 2 | 3 | 4 | Parameter | 1 | 2 | 3 | 4 | Capital Recovery Interest Rate (%) | 5
Water Industry Data Base Number (optional) | NA | Molecular weight cutoff (Daltons) | 400 | [5 empty] | Average yearly temperature of feed water, TavgoC (oC) | 14 |  |  | LSI | 0.58 | Softening | Lime, 190 mg/L as Ca(OH)2 | Bench-scale | Sampling time | hh:mm | 12:00 | 12:00 | --- | --- | Date | Time | Setting time | Influent | PI | PC | QI | Qp | QW | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) | Date | Time | Operation time | Influent | PI | PC | QI | Qp | QW | Cleaning Event | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1) | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Influent flow rate during sample collection (mL/min) | 600 | [10 empty] | Influent flow rate during sample collection (mL/min) | 600 | [7 empty] | Influent flow rate during sample collection (mL/min) | 600 | [7 empty] | Influent flow rate during sample collection (mL/min) | 600 | [6 empty] | SDS-THM4F, ug/L | 80.86 | 80.86 | 80.86 | 80.86 | SDS-THM4F, ug/L | 80.86 | 80.86 | 80.86 | 80.86 | Capital Recovery Period (years) | 20
|  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide | [5 empty] | Approximate feed water TDS, TDSF (mg/L) | 322 |  |  | Dissolved iron (mg/L) |  | Coagulation | Alum: Al2(SO4)3.14H2O, 15 mg/L | Bench-scale | Operation time | hh.hh | 2 | 150 | --- | --- | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | Indicate with "X" | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) | [39 empty] | SDS-THM4p, ug/L | 9.195 | 14.52 | 4.67 | 11.72 | SDS-THM4p, ug/L | 9.195 | 14.52 | 4.67 | 11.72 | Overhead & Profit Factor (% of construction costs) | 15
Official ICR Contact Person |  | Membrane construction (e.g., thin-film composite) | Thin-Film composite | [5 empty] | Manufacturer reported TDS rejection, RejTDS (decimal fraction) | 0.7 |  |  | Total iron (mg/L) |  | Sedimentation | Gravity settling in test drums | Bench-scale | pH | --- | 9.61 | 8.02 | 8.815 | 18.0374 | 1998-10-19 | 10:00 | 0 | 20.9 | 52 | 53 | 600 | 7.3 | 3.4 | 10.7 | 0.46109 | 0.68224 | 55.0748 | 16.6286 | 13.5606 | 2.3207 | 0.091742 | 2.2936 | 0.022154 | 52.4778 | 0.25841 | 1998-10-21 | 10:00 | 0 | [7 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [27 empty] | Permeate and Concentrate Water Quality | [11 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | SDS-HAA5F, ug/L | 26.635 | 26.635 | 26.635 | 26.635 | SDS-HAA5F, ug/L | 26.635 | 26.635 | 26.635 | 26.635 | Special Sitework Factor (% of construction costs) | 0
Mailing Address |  | Membrane hydrophobicity | hydrophilic | [5 empty] | Temperature normalized MTCW (gfd/psi) | 0.16977 |  |  | Dissolved aluminum (mg/L) |  | Recarbonation | CO2 gas added to pH 9.4 | Bench-scale | Temperature | oC | 21.7 | 25.5 | 23.6 | 16.1017 | 1998-10-19 | 12:00 | 2 | 21.8 | 52 | 53 | 600 | 7.9 | 3.1 | 11 | 0.46109 | 0.71818 | 53.5455 | 17.9953 | 14.2899 | 2.5791 | 0.10186 | 2.5465 | 0.02461 | 52.4754 | 0.27232 | 1998-10-21 | 12:00 | 2 | 20.4 | 56 | 57 | 600 | 6.7 | 3.6 |  | 10.3 | 0.46109 | 0.65049 | 57.2524 | 15.2619 | 12.6313 | 362.6198 | 97.7103 | 359.6616 | 2.6343 | 53.8657 | 0.2345 | 9.47 | 9.61 | 9.49 | 102.5 | 178.6 | 373 | 353.7056 | 5.1728 | 46.1377 | 352.303 | 70.9057 | 0.007 | 0.043 | 0.11 | 0.10285 | 6.5025 | 82.716 | 0.10231 | 93.1582 | [8 empty] | Parameter | Units | Cp-1 | Cp-1 (dup) | Average | RPD | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | SDS-HAA5p, ug/L | 2.175 | 3.9 | 1.21 | 2.31 | SDS-HAA5p, ug/L | 2.175 | 3.9 | 1.21 | 2.31 | Construction Contingencies (% of construction costs) | 15
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | negative | [9 empty] | Total aluminum (mg/L) |  | Cartridge filtration | 1 um size exclusion | Bench-scale | Alkalinity | mg/L as CaCO3 | 61.5 | 47.8 | 54.65 | 25.0686 | 1998-10-19 | 14:00 | 4 | 21.9 | 52 | 53 | 600 | 8 | 3.5 | 11.5 | 0.46109 | 0.69565 | 51.1739 | 18.2231 | 14.4281 | 2.411 | 0.095203 | 2.3801 | 0.023003 | 52.477 | 0.27494 | 1998-10-21 | 14:00 | 4 | 20.9 | 56 | 57 | 600 | 6.7 | 2.7 |  | 9.4 | 0.46109 | 0.71277 | 62.8298 | 15.2619 | 12.446 | 397.0427 | 106.9858 | 393.8038 | 2.8844 | 53.6156 | 0.23213 | [27 empty] | Sampling date | MM/DD/YY | 1998-10-24 | 1998-10-24 | --- | --- | 1998-10-24 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-10-25 | 1998-10-25 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-10-26 | 1998-10-26 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-12-27 | 1998-12-27 | --- | --- | --- | --- | --- | SDS-TOXF, ug Cl- /L | 165 | 165 | 165 | 165 | SDS-TOXF, ug Cl- /L | 165 | 165 | 165 | 165 | Engineering Fee Factor (% of construction costs) | 15
Phone Number |  |  |  | Experimental Design1,2 | [8 empty] | Fluoride (mg/L) |  | Antiscalant | 4 mg/L Hypersperse 400UL | Bench-scale | Total dissolved solids | mg/L | 178.6 | 202 | 190.3 | 12.2964 | 1998-10-19 | 16:30 | 6.5 | 21.6 | 52 | 53 | 600 | 8.2 | 3.4 | 11.6 | 0.46109 | 0.7069 | 50.7241 | 18.6787 | 14.9205 | 2.4921 | 0.098377 | 2.4594 | 0.023774 | 52.4762 | 0.28433 | 1998-10-21 | 17:00 | 7 | 21.1 | 56 | 57 | 600 | 6.7 | 2.7 |  | 9.4 | 0.46109 | 0.71277 | 62.8298 | 15.2619 | 12.3727 | 397.0427 | 106.9858 | 393.8038 | 2.8844 | 53.6156 | 0.23077 | [27 empty] | Sampling time | hh:mm | 12:00 | 12:00 | --- | --- | 12:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 12:30 | 12:30 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 12:30 | 12:30 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 12:30 | 12:30 | --- | --- | --- | --- | --- | SDS-TOXp, ug Cl- /L | #DIV/0! | BMRL | BMRL | BMRL | SDS-TOXp, ug Cl- /L | #DIV/0! | BMRL | BMRL | BMRL | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920
FAX Number |  | Design Parameters |  | ID# | Recovery | FW-design | Dp | PI | QI-cell | Qp | QF | QW | Phosphate (mg/L) |  |  |  |  | Total hardness | mg/L as CaCO3 | 90.5 | 84.8 | 87.65 | 6.5031 | 1998-10-20 | 8:00 | 22 | 20.5 | 54 | 54 | 600 | 8.3 | 3.6 | 11.9 | 0.46109 | 0.69748 | 49.4202 | 18.9065 | 15.6016 | 2.4239 | 0.095667 | 2.3917 | 0.023121 | 53.9769 | 0.28904 | 1998-10-22 | 7:00 | 21 | 20.6 | 56 | 57 | 600 | 6.7 | 2.7 |  | 9.4 | 0.46109 | 0.71277 | 62.8298 | 15.2619 | 12.5569 | 397.0427 | 106.9858 | 393.8038 | 2.8844 | 53.6156 | 0.2342 | 9.27 |  |  | 106.2 |  |  | 398.9926 |  | 44.1934 | 397.3578 | 73.2735 | 0.005 |  |  | 0.12859 |  | 87.6543 | 0.1279 | 96.0908 | [8 empty] | Operation time | hh.hh | 74 | 74 | --- | --- | 74 | --- | --- | --- | --- | --- | Operation time | hh.hh | 98.5 | 98.5 | --- | --- | --- | --- | --- | Operation time | hh.hh | 122.5 | 122.5 | --- | --- | --- | --- | --- | Cumulative time | hr | 146.5 | 146.5 | --- | --- | --- | --- | --- | SDS-CDF, mg/L | 2.715 | 2.715 | 2.715 | 2.715 | SDS-CDF, mg/L | 2.715 | 2.715 | 2.715 | 2.715 | 1998 Producers Price Index (PPI base year 1967 = 100) | 370
E-Mail Address (optional) |  | Design flux, FW (gfd) | 16.5 |  | (decimal) | (gfd) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | Sulfate (mg/L) |  |  |  |  | Calcium hardness | mg/L as CaCO3 | 76.9 | 71.4 | 74.15 | 7.4174 | 1998-10-20 | 12:00 | 26 | 21.1 | 54 | 55 | 600 | 8.4 | 3.7 | 12.1 | 0.46109 | 0.69421 | 48.5868 | 19.1343 | 15.512 | 2.4011 | 0.094753 | 2.3688 | 0.022902 | 54.4771 | 0.28474 | 10/'22/98 | 9:00 | 23 | 21 | 56 | 57 | 600 | 6.8 | 2.8 |  | 9.6 | 0.46109 | 0.70833 | 61.5 | 15.4897 | 12.5945 | 394.3974 | 106.2599 | 391.1319 | 2.865 | 53.635 | 0.23482 | [27 empty] | pH | --- | 8.56 | 8.56 | 8.56 | 0 | 8.6 | --- | --- | --- | --- | --- | pH | --- | 9.16 | 9 | --- | --- | --- | --- | --- | pH | --- | 7.93 | 8.26 | --- | --- | --- | --- | --- | pH | --- | 8.47 | 8.92 | --- | --- | --- | --- | --- | SDS-CDp, mg/L | 0.455 | 0.69 | 0.63 | 0.54 | SDS-CDp, mg/L | 0.455 | 0.69 | 0.63 | 0.54 | Labor Rate + Fringe ($/work-hour) | 17
|  | Net driving pressure at the design flux, NDP (psi) | 70 | 1 | 0.7 | 15 | 8.4793 | 96.8347 | 606.4586 | 6.5843 | 9.4062 | 2.8219 | Calcium (mg/L) | 54 |  |  |  | Turbidity | ntu | 0.08 | 0.12 | 0.1 | 40 | 1998-10-20 | 14:00 | 28 | 21.3 | 54 | 55 | 600 | 8.5 | 3.7 | 12.2 | 0.46109 | 0.69672 | 48.1803 | 19.3621 | 15.6041 | 2.4186 | 0.095428 | 2.3857 | 0.023067 | 54.4769 | 0.28644 | 1998-10-22 | 11:00 | 25 | 20.5 | 56 | 57 | 600 | 6.7 | 2.7 |  | 9.4 | 0.46109 | 0.71277 | 62.8298 | 15.2619 | 12.5941 | 397.0427 | 106.9858 | 393.8038 | 2.8844 | 53.6156 | 0.2349 | 9.24 | 9.31 | 9.25 | 109.1 | 178 | 407 | 391.7963 | 3.7356 | 42.6695 | 390.2179 | 72.0413 | 0.004 | 0.042 | 0.13 | 0.13107 | -0.82621 | 90.1235 | 0.13036 | 96.9317 | [8 empty] | Temperature | oC | 22.7 | 22.7 | 22.7 | 0 | 22.7 | --- | --- | --- | --- | --- | Temperature | oC | 22.5 | 22.5 | --- | --- | --- | --- | --- | Temperature | oC | 23.7 | 23.7 | --- | --- | --- | --- | --- | Temperature | oC | 25.5 | 25.5 | --- | --- | --- | --- | --- | TOCF, mg/L | 2.45 | 2.45 | 2.45 | 2.45 | TOCF, mg/L | 2.45 | 2.45 | 2.45 | 2.45 | Labor Overhead Factor (% of labor) | 42
Technical ICR Contact Person |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.235 | 2 | 0.9 | 15 | 23.506 | 111.8614 | 606.4586 | 6.5843 | 7.3159 | 0.73159 | Barium (mg/L) |  |  |  |  | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! | 1998-10-20 | 17:00 | 31 | 21.4 | 55 | 55 | 600 | 8.6 | 3.8 | 12.4 | 0.46109 | 0.69355 | 47.3871 | 19.5899 | 15.7411 | 2.3966 | 0.094543 | 2.3636 | 0.022855 | 54.9771 | 0.28632 | 1998-10-22 | 13:00 | 27 | 21.6 | 56 | 57 | 600 | 6.8 | 2.8 |  | 9.6 | 0.46109 | 0.70833 | 61.5 | 15.4897 | 12.3731 | 394.3974 | 106.2599 | 391.1319 | 2.865 | 53.635 | 0.23069 | [27 empty] | Alkalinity | mg/L as CaCO3 | 47 | 44.5 | 45.75 | 5.4645 | 97.5 | 76.4397 | 21.6004 | 16.2855 | 76.2653 | 40.0121 | Alkalinity | mg/L as CaCO3 | 47.5 | 104.5 | 112.5 | -7.6555 | 13.0833 | 112.164 | 57.6513 | Alkalinity | mg/L as CaCO3 | 32.8 | 70.6 | 76.5 | -8.3569 | 39.9817 | 76.2524 | 56.9849 | Alkalinity | mg/L as CaCO3 | 22 | 52.7 | 68.6429 | -30.2521 | 59.7438 | 68.3758 | 67.8249 | TOCp, mg/L | #DIV/0! | BMRL | BMRL | BMRL | TOCp, mg/L | #DIV/0! | BMRL | BMRL | BMRL | Electric Rate ($/kW-h) | 0.06
Mailing Address |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | 3 | 0.5 | 15 | 5.474 | 93.8294 | 606.4586 | 6.5843 | 13.1686 | 6.5843 | Strontium (mg/L) |  |  |  |  | Total organic carbon | mg/L | 2.5 | 2.4 | 2.45 | 4.0816 | 1998-10-21 | 8:00 | 46 | 20.7 | 55 | 56 | 600 | 8.4 | 3.7 | 12.1 | 0.46109 | 0.69421 | 48.5868 | 19.1343 | 15.6965 | 2.4011 | 0.094753 | 2.3688 | 0.022902 | 55.4771 | 0.28294 | 1998-10-22 | 15:00 | 29 | 22.1 | 56 | 57 | 600 | 6.9 | 2.9 |  | 9.8 | 0.46109 | 0.70408 | 60.2245 | 15.7174 | 12.3709 | 391.8936 | 105.5723 | 388.6009 | 2.8467 | 53.6533 | 0.23057 | [27 empty] | Total dissolved solids | mg/L | 114.9 | 113.2 | 114.05 | 1.4906 | 411 | 376.981 | 8.2771 | 40.0683 | 375.4876 | 69.6262 | Total dissolved solids | mg/L | 118.4 | 706 | 772.0364 | -9.3536 | 37.7824 | 768.6574 | 84.5965 | Total dissolved solids | mg/L | 94.5 | 309 | 286.1 | 7.411 | 50.3416 | 285.0143 | 66.8438 | Total dissolved solids | mg/L | 76.6 | 194.3 | 239.0286 | -23.0204 | 59.7478 | 238.0987 | 67.8285 | UV254 F, cm-1 | 0.0405 | 0.0405 | 0.0405 | 0.0405 | UV254 F, cm-1 | 0.0405 | 0.0405 | 0.0405 | 0.0405 | Fuel Oil Rate ($/gal) | NA
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 400 | 4 | 0.3 | 15 | 4.186 | 92.5414 | 606.4586 | 6.5843 | 21.9477 | 15.3634 | Reactive silica (mg/L as SiO2) |  |  |  |  | UV254 | cm-1 | 0.043 | 0.038 | 0.0405 | 12.3457 | 1998-10-21 | 10:00 | 48 | 21 | 55 | 56 | 600 | 8.4 | 3.7 | 12.1 | 0.46109 | 0.69421 | 48.5868 | 19.1343 | 15.5579 | 2.4011 | 0.094753 | 2.3688 | 0.022902 | 55.4771 | 0.28044 | 1998-10-22 | 17:00 | 31 | 21.4 | 56 | 57 | 600 | 6.9 | 2.9 |  | 9.8 | 0.46109 | 0.70408 | 60.2245 | 15.7174 | 12.6295 | 391.8936 | 105.5723 | 388.6009 | 2.8467 | 53.6533 | 0.23539 | 9.11 |  |  | 111.5 |  |  | 377.7897 |  | 41.4083 | 376.2585 | 70.3661 | 0.003 |  |  | 0.12972 |  | 92.5926 | 0.129 | 97.6743 | [8 empty] | Total hardness | mg/L as CaCO3 | 39.5 | 39.3 | 39.4 | 0.50761 | 187.9 | 205.7793 | -9.5153 | 55.0485 | 204.8343 | 80.7649 | Total hardness | mg/L as CaCO3 | 35.7 | 431 | 507.9727 | -17.8591 | 59.2698 | 505.5314 | 92.9381 | Total hardness | mg/L as CaCO3 | 31 | 150 | 144.3 | 3.8 | 64.6321 | 143.658 | 78.421 | Total hardness | mg/L as CaCO3 | 25.8 | 104 | 114.1571 | -9.7665 | 70.5647 | 113.6513 | 77.299 | UV254 p, cm-1 | 0.0045 | 0.006 | 0.003 | 0.003 | UV254 p, cm-1 | 0.0045 | 0.006 | 0.003 | 0.003 | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Purchase price for an equivalent 8" x 40 " element ($) | 700 | 1: For experimental matrix see Table 4-2 in Part 3 of the ICR Treatment Studies Manual. | [8 empty] | Turbidity (ntu) | 1.5 |  |  |  | SUVA | L/(mg*m) | 1.72 | 1.5833 | 1.6517 | 8.2745 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-23 | 7:00 | 45 | 20.6 | 56 | 57 | 600 | 6.6 | 2.7 |  | 9.3 | 0.46109 | 0.70968 | 63.5161 | 15.0341 | 12.3695 | 395.1631 | 106.4924 | 391.9877 | 2.8708 | 53.6292 | 0.23065 | 8.68 |  |  | 107 |  |  | 393.9222 |  | 43.773 | 392.3442 | 72.728 | 0.004 |  |  | 0.12972 |  | 90.1235 | 0.12903 | 96.9 | [8 empty] | Calcium hardness | mg/L as CaCO3 | 32.7 | 32.7 | 32.7 | 0 | 156.8 | 175.631 | -12.0096 | 55.9002 | 174.8192 | 81.295 | Calcium hardness | mg/L as CaCO3 | 29 | 360.6 | 439.4545 | -21.8676 | 60.8901 | 437.3327 | 93.3689 | Calcium hardness | mg/L as CaCO3 | 25.5 | 124.9 | 122.8 | 1.6813 | 65.6102 | 122.2486 | 79.1409 | Calcium hardness | mg/L as CaCO3 | 21.2 | 87.1 | 96.8429 | -11.1858 | 71.4093 | 96.4098 | 78.0105 | BromideF, ug/L | 77.5 | 77.5 | 77.5 | 77.5 | BromideF, ug/L | 77.5 | 77.5 | 77.5 | 77.5 | Current Process Water Rate ($/1000 gal) | 0.375
FAX Number |  | Maximum flow rate to the 8" x 40" element, QI, max (gpm) | 70 | 2: Flow rates and pressures may need to be adjusted in order to obtain the desired operating conditions. | [8 empty] | SDI |  |  |  |  | Bromide | mg/L | 75 | 80 | 77.5 | 6.4516 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-23 | 9:00 | 47 | 21.2 | 56 | 57 | 600 | 6.7 | 2.8 |  | 9.5 | 0.46109 | 0.70526 | 62.1579 | 15.2619 | 12.3362 | 392.5536 | 105.7761 | 389.3512 | 2.8518 | 53.6482 | 0.22995 | [27 empty] | Turbidity | ntu | 0.06 | 0.06 | 0.06 | 0 | 0.15 | 0.19793 | -31.954 | 40 | 0.19715 | 69.5659 | Turbidity | ntu | 0.07 | 0.15 | 0.34273 | -128.4848 | 30 | 0.34132 | 79.4912 | Turbidity | ntu | 0.07 | 0.08 | 0.13 | -62.5 | 30 | 0.12966 | 46.0126 | Turbidity | ntu | 0.09 | 0.11 | 0.10429 | 5.1948 | 10 | 0.1042 | 13.6309 | Bromidep, ug/L | 78 | 76 | 74 | 69 | Bromidep, ug/L | 78 | 76 | 74 | 69 | Modifications to Existing Plant (% of construction costs) | 52
E-Mail Address (optional) |  | Minimum flow rate to the 8" x 40" element, QI, min (gpm) | 34 | [9 empty] | MFI |  |  |  |  | SDS-Cl2 dose | mg/L | 3.64 | 3.64 | 3.64 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-23 | 11:00 | 49 | 20.9 | 56 | 57 | 600 | 6.8 | 2.8 |  | 9.6 | 0.46109 | 0.70833 | 61.5 | 15.4897 | 12.6318 | 394.3974 | 106.2599 | 391.1319 | 2.865 | 53.635 | 0.23551 | 9.44 | 9.55 | 9.47 | 109 | 212 | 423 | 387.7429 | 8.335 | 42.722 | 386.1633 | 71.7736 | 0.004 | 0.04 | 0.127 | 0.12914 | -1.6873 | 90.1235 | 0.12843 | 96.8856 | [8 empty] | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! | BMRL | #DIV/0! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | BMRL | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | BMRL | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | BMRL | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | AlkF, mg/L CaCO3 | 54.65 | 54.65 | 54.65 | 54.65 | AlkF, mg/L CaCO3 | 54.65 | 54.65 | 54.65 | 54.65
|  | Total width of all membrane envelopes in the 8" x 40" element, w (ft) | 70.67 | [9 empty] | MPFI |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | SDS-Free Cl2 residual | mg/L | 1.02 | 0.83 | 0.925 | 20.5405 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-23 | 13:00 | 51 | 22 | 56 | 57 | 600 | 6.8 | 2.8 |  | 9.6 | 0.46109 | 0.70833 | 61.5 | 15.4897 | 12.2277 | 394.3974 | 106.2599 | 391.1319 | 2.865 | 53.635 | 0.22798 | [27 empty] | Total organic carbon | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | 7.4 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L | BMRL | 19 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 4.7 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 3.3 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkp, mg/L CaCO3 | 45.75 | 47.5 | 32.8 | 22 | Alkp, mg/L CaCO3 | 45.75 | 47.5 | 32.8 | 22
Plant Name | Facility 1 | Feed spacer thickness in the 8" x 40" element, T (ft) | 0.0023 | [9 empty] | Bromide (mg/L) | 79 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | SDS-Cl2 demand | mg/L | 2.62 | 2.81 | 2.715 | 6.9982 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-23 | 15:00 | 53 | 21.8 | 56 | 57 | 600 | 6.8 | 2.9 |  | 9.7 | 0.46109 | 0.70103 | 60.8557 | 15.4897 | 12.3002 | 390.0844 | 105.0978 | 386.8545 | 2.8337 | 53.6663 | 0.2292 | [27 empty] | UV254 | cm-1 | 0.004 | 0.005 | 0.0045 | 22.2222 | 0.128 | 0.12864 | -0.49838 | 88.8889 | 0.12793 | 96.4825 | UV254 | cm-1 | 0.006 | 0.322 | 0.31964 | 0.73405 | 85.1852 | 0.31802 | 98.1133 | UV254 | cm-1 | 0.003 | 0.08 | 0.078 | 2.5 | 92.5926 | 0.077575 | 96.1328 | UV254 | cm-1 | 0.003 | 0.055 | 0.056571 | -2.8571 | 92.5926 | 0.056265 | 94.6681 | T-HdF, mg/L CaCO3 | 87.65 | 87.65 | 87.65 | 87.65 | T-HdF, mg/L CaCO3 | 87.65 | 87.65 | 87.65 | 87.65
Treatment Plant Category | CS/SOFT | [11 empty] | TOC (mg/L) | 3.6 | is to list the pretreatment processes used in this particular RBSMT run. |  |  | SDS-Chlorination temp. | oC | 20 | 19.8 | 19.9 | 1.005 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-23 | 17:00 | 55 | 21.9 | 56 | 57 | 600 | 6.8 | 2.9 |  | 9.7 | 0.46109 | 0.70103 | 60.8557 | 15.4897 | 12.2639 | 390.0844 | 105.0978 | 386.8545 | 2.8337 | 53.6663 | 0.22852 | 9.34 |  |  | 113 |  |  | 371.5552 |  | 40.6201 | 370.09 | 69.4669 | 0.003 |  |  | 0.12843 |  | 92.5926 | 0.12772 | 97.6511 | [8 empty] | SUVA | L/(mg*m) | NR | NR | #DIV/0! | #VALUE! | 1.7297 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 1.6947 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 1.7021 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 1.6667 | --- | --- | --- | --- | --- | T-Hdp, mg/L CaCO3 | 39.4 | 35.7 | 31 | 25.8 | T-Hdp, mg/L CaCO3 | 39.4 | 35.7 | 31 | 25.8
Process Train Name | Coagulation/Sedimentation/Softening | Additional Information | [10 empty] | pH | 8.03 |  |  |  | SDS-Chlorination pH | --- | 9.5 | 9.5 | 9.5 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-24 | 7:00 | 69 | 20.7 | 56 | 57 | 600 | 6.8 | 2.8 |  | 9.6 | 0.46109 | 0.70833 | 61.5 | 15.4897 | 12.7067 | 394.3974 | 106.2599 | 391.1319 | 2.865 | 53.635 | 0.23691 | 8.89 |  |  | 110.7 |  |  | 383.6143 |  | 41.8287 | 382.0678 | 71.0261 | 0.005 |  |  | 0.12671 |  | 87.6543 | 0.12602 | 96.0325 | [8 empty] | Bromide | mg/L | 78 | 78 | 78 | 0 | --- | 76.2759 | --- | -0.64516 | 76.2857 | -2.2473 | Bromide | mg/L | 76 | --- | 89.6364 | --- | 1.9355 | 89.5659 | 15.1463 | Bromide | mg/L | 74 | --- | 81 | --- | 4.5161 | 80.9603 | 8.5972 | Bromide | mg/L | 69 | --- | 81.1429 | --- | 10.9677 | 81.0733 | 14.8919 | Ca-HdF, mg/L CaCO3 | 74.15 | 74.15 | 74.15 | 74.15 | Ca-HdF, mg/L CaCO3 | 74.15 | 74.15 | 74.15 | 74.15
ICR Treatment Plant Identification Number | 381 | Design cross-flow velocity (fps) | 0.43 | [9 empty] | Total Hardness (mg/L as CaCO3) | 182 |  |  |  | SDS-Incubation time | hours | 31 | 31 | 31 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-24 | 9:00 | 71 | 21.1 | 56 | 57 | 600 | 6.7 | 2.8 |  | 9.5 | 0.46109 | 0.70526 | 62.1579 | 15.2619 | 12.3727 | 392.5536 | 105.7761 | 389.3512 | 2.8518 | 53.6482 | 0.23063 | [27 empty] | SDS-Cl2 dose | mg/L | 1.5 | 1.5 | 1.5 | 0 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1.5 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1.5 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1.5 | --- | --- | --- | --- | --- | --- | Ca-Hdp, mg/L CaCO3 | 32.7 | 29 | 25.5 | 21.2 | Ca-Hdp, mg/L CaCO3 | 32.7 | 29 | 25.5 | 21.2
PWSID Number of Plant (if assigned) | KS200910 | Required influent flow to permeate flow rate ratio, QI:Qp | [10 empty] | UV254 | 0.0987 |  |  |  | SDS-TOX | mg Cl- /L | 170 | 160 | 165 | 6.0606 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-24 | 11:00 | 73 | 20.9 | 56 | 57 | 600 | 6.8 | 2.8 |  | 9.6 | 0.46109 | 0.70833 | 61.5 | 15.4897 | 12.6318 | 394.3974 | 106.2599 | 391.1319 | 2.865 | 53.635 | 0.23551 | 8.89 | 8.98 | 8.9 | 114.5 | 182 | 420 | 374.3857 | 10.8605 | 39.8318 | 372.913 | 69.2958 | 0.005 | 0.042 | 0.133 | 0.12671 | 4.7261 | 87.6543 | 0.12602 | 96.0325 | [8 empty] | SDS-Free Cl2 residual | mg/L | 1.05 | 1.04 | 1.045 | 0.95694 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.81 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.87 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.96 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 0.1 | Maximum element recovery (%) | 15 | [9 empty] | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | SDS-CHCl3 | mg/L | 47.34 | 45.51 | 46.425 | 3.9418 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-24 | 13:00 | 75 | 21.6 | 56 | 57 | 600 | 6.8 | 2.8 |  | 9.6 | 0.46109 | 0.70833 | 61.5 | 15.4897 | 12.3731 | 394.3974 | 106.2599 | 391.1319 | 2.865 | 53.635 | 0.23069 | [27 empty] | SDS-Cl2 demand | mg/L | 0.45 | 0.46 | 0.455 | 2.1978 | --- | 8.2481 | --- | 83.2413 | 8.2038 | 94.4538 | SDS-Cl2 demand | mg/L | 0.69 | --- | 19.0991 | --- | 74.5856 | 19.0039 | 96.3692 | SDS-Cl2 demand | mg/L | 0.63 | --- | 4.8 | --- | 76.7956 | 4.7764 | 86.8101 | SDS-Cl2 demand | mg/L | 0.54 | --- | 3.6471 | --- | 80.1105 | 3.6294 | 85.1213 | Blended Water Quality if THM4 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if THM4 Controls the Blend Ratio
Historical Average Water Temperature (oC) | 14 | Variability of design flux (%) | [10 empty] | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | SDS-BDCM | mg/L | 22 | 21.84 | 21.92 | 0.72993 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-24 | 15:00 | 77 | 21.7 | 56 | 57 | 600 | 6.8 | 2.8 |  | 9.6 | 0.46109 | 0.70833 | 61.5 | 15.4897 | 12.3366 | 394.3974 | 106.2599 | 391.1319 | 2.865 | 53.635 | 0.23001 | [27 empty] | SDS-Chlorination temp. | oC | 19.8 | 19.8 | 19.8 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 19.8 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 19.8 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 19.8 | --- | --- | --- | --- | --- | --- | Qp/QT (THM4), % | 12.3631 | 13.3554 | 11.6288 | 12.8146 | Qp/QT (THM4), % | 62.5968 | 67.6213 | 58.8791 | 64.8828
State Approved Plant Capacity (MGD) | 55 | Rejection of reference solute and conditions of test | 45 rejection of CaCl2 | [14 empty] | SDS-DBCM | mg/L | 10.49 | 10.84 | 10.665 | 3.2818 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-24 | 17:00 | 79 | 21.6 | 56 | 57 | 600 | 6.8 | 2.8 |  | 9.6 | 0.46109 | 0.70833 | 61.5 | 15.4897 | 12.3731 | 394.3974 | 106.2599 | 391.1319 | 2.865 | 53.635 | 0.23069 | 8.84 |  |  | 113.2 |  |  | 377.5429 |  | 40.515 | 376.0449 | 69.8972 | 0.006 |  |  | 0.12429 |  | 85.1852 | 0.12362 | 95.1462 | [8 empty] | SDS-Chlorination pH | --- | 9.5 | 9.5 | 9.5 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 9.5 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 9.5 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 9.5 | --- | --- | --- | --- | --- | --- | SDS-THM4b, ug/L | 72 | 72 | 72 | 72 | SDS-THM4b, ug/L | 36 | 36 | 36 | 36
|  | (e.g., solute type and concentration) | 70psi, 500mg/L CaCl2,25 deg. C,15% recovery | [14 empty] | SDS-CHBr3 | mg/L | 1.75 | 1.95 | 1.85 | 10.8108 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-25 | 8:00 | 94 | 21.5 | 57 | 57 | 600 | 6.6 | 0.77 |  | 7.37 | 0.46109 | 0.89552 | 80.4111 | 15.0341 | 12.0447 | 550.2995 | 148.3001 | 545.8775 | 3.9979 | 53.0021 | 0.22725 | [27 empty] | SDS-Incubation time | hours | 31 | 31 | 31 | 0 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 31 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 31 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 31 | --- | --- | --- | --- | --- | --- | SDS-HAA5b, ug/L | 23.611 | 23.5986 | 23.6784 | 23.5179 | SDS-HAA5b, ug/L | 11.3238 | 11.2613 | 11.665 | 10.8522
|  | Variability of rejection of reference solute (%) | 45 rejection of CaCl2 | [14 empty] | SDS-THM4 | mg/L | 81.58 | 80.14 | 80.86 | 1.7809 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-25 | 9:00 | 95 | 21.5 | 57 | 57 | 600 | 6.6 | 0.83 |  | 7.43 | 0.46109 | 0.88829 | 79.7537 | 15.0341 | 12.0447 | 542.0193 | 146.0686 | 537.6639 | 3.9377 | 53.0623 | 0.22699 | 9.34 |  |  | 114.6 |  |  | 792.2518 |  | 39.7793 | 788.5247 | 85.4665 | 0.006 |  |  | 0.31484 |  | 85.1852 | 0.31314 | 98.0839 | [8 empty] | SDS-TOX | mg Cl- /L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOXb, ug Cl- /L | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | SDS-TOXb, ug Cl- /L | #DIV/0! | #VALUE! | #VALUE! | #VALUE!
|  | Standard testing recovery (%) | 15 | [14 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-25 | 10:00 | 96 | 21.2 | 57 | 57 | 600 | 6.2 | 0.73 |  | 6.93 | 0.46109 | 0.89466 | 85.5801 | 14.1229 | 11.4155 | 549.1117 | 148.0528 | 544.9674 | 3.9899 | 53.0101 | 0.21535 | 9.4 |  |  | 118.3 |  |  | 801.8068 |  | 37.835 | 798.2754 | 85.1806 | 0.006 |  |  | 0.33351 |  | 85.1852 | 0.33182 | 98.1918 | [8 empty] | SDS-CHCl3 | mg/L | 1.64 | 1.67 | 1.655 | 1.8127 | --- | 156.0343 | --- | 96.4351 | 155.1574 | 98.9333 | SDS-CHCl3 | mg/L | 2.35 | --- | 403.0318 | --- | 94.9381 | 400.9605 | 99.4139 | SDS-CHCl3 | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHCl3 | mg/L | 1.37 | --- | 65.7343 | --- | 97.049 | 65.3658 | 97.9041 | SDS-CDb, mg/L | 2.4356 | 2.4446 | 2.4725 | 2.4363 | SDS-CDb, mg/L | 1.3003 | 1.3457 | 1.4874 | 1.3038
|  | Standard testing pH | 8 | [14 empty] | SDS-DCAA* | mg/L | 19.36 | 20.3 | 19.83 | 4.7403 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-25 | 11:00 | 97 | 21.5 | 57 | 58 | 600 | 6.2 | 0.8 |  | 7 | 0.46109 | 0.88571 | 84.7143 | 14.1229 | 11.3148 | 538.9498 | 145.3129 | 534.8822 | 3.916 | 53.584 | 0.21116 | 9.43 |  |  | 120 |  |  | 735.125 |  | 36.9417 | 731.9469 | 83.6054 | 0.008 |  |  | 0.29237 |  | 80.2469 | 0.29091 | 97.25 | [8 empty] | SDS-BDCM | mg/L | 1.48 | 1.51 | 1.495 | 2.0067 | --- | 71.926 | --- | 93.1797 | 71.526 | 97.9099 | SDS-BDCM | mg/L | 2.56 | --- | 178.56 | --- | 88.3212 | 177.6502 | 98.559 | SDS-BDCM | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | 1.8 | --- | 30.5429 | --- | 91.7883 | 30.3783 | 94.0747 | TOCb, mg/L | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | TOCb, mg/L | #DIV/0! | #VALUE! | #VALUE! | #VALUE!
|  | Acceptable range of operating pressures | 0 to 600 psi | [14 empty] | SDS-TCAA* | mg/L | 3.25 | 3.36 | 3.305 | 3.3283 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-25 | 12:00 | 98 | 21 | 57 | 57 | 600 | 6.2 | 0.77 |  | 6.97 | 0.46109 | 0.88953 | 85.0832 | 14.1229 | 11.4832 | 543.2335 | 146.4679 | 539.1336 | 3.9472 | 53.0528 | 0.21645 | 9.41 | 9.44 | 9.16 | 120.3 | 174.6 | 656 | 753.9364 | -14.9293 | 36.784 | 750.6626 | 83.9742 | 0.007 | 0.041 | 0.271 | 0.31024 | -14.4798 | 82.716 | 0.30867 | 97.7322 | [8 empty] | SDS-DBCM | mg/L | 2.99 | 3.13 | 3.06 | 4.5752 | --- | 29.2841 | --- | 71.308 | 29.1352 | 89.4972 | SDS-DBCM | mg/L | 4.79 | --- | 58.1991 | --- | 55.0867 | 57.923 | 91.7304 | SDS-DBCM | mg/L | 2.24 | --- | 19.09 | --- | 78.9967 | 18.9945 | 88.2071 | SDS-DBCM | mg/L | 4.06 | --- | 13.4957 | --- | 61.9316 | 13.4417 | 69.7955 | UV254 b, cm-1 | 0.036049 | 0.035892 | 0.036139 | 0.035695 | UV254 b, cm-1 | 0.017965 | 0.017171 | 0.01842 | 0.016169
|  | Acceptable range of operating pH values | 3 to 10 | [14 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-25 | 14:00 | 100 | 21.9 | 56 | 57 | 600 | 6.4 | 0.77 |  | 7.17 | 0.46109 | 0.89261 | 82.682 | 14.5785 | 11.5425 | 546.8393 | 147.4039 | 542.5787 | 3.9731 | 52.5269 | 0.21974 | [27 empty] | SDS-CHBr3 | mg/L | 2.81 | 3.16 | 2.985 | 11.7253 | --- | -0.92879 | --- | -61.3514 | -0.90656 | 429.2657 | SDS-CHBr3 | mg/L | 4.82 | --- | -22.18 | --- | -160.5405 | -22.0404 | 121.8689 | SDS-CHBr3 | mg/L | 2.43 | --- | 1.27 | --- | -31.3514 | 1.2766 | -90.3533 | SDS-CHBr3 | mg/L | 4.49 | --- | 0.71857 | --- | -142.7027 | 0.74016 | -506.6233 | Bromideb, ug/L | 77.5618 | 77.2997 | 77.093 | 76.4108 | Bromideb, ug/L | 77.813 | 76.4857 | 75.4392 | 71.985
|  | Typical pressure drop across a single element (psi) | 3 to5 | [14 empty] | SDS-DBAA* | mg/L | 3.4 | 3.6 | 3.5 | 5.7143 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-26 | 8:00 | 118 | 21.1 | 56 | 57 | 600 | 6.4 | 6.6 |  | 13 | 0.46109 | 0.49231 | 45.1538 | 14.5785 | 11.8187 | 297.1595 | 80.1011 | 294.8442 | 2.159 | 54.341 | 0.21749 | [27 empty] | SDS-THM4 | mg/L | 8.92 | 9.47 | 9.195 | 5.9815 | --- | 256.3157 | --- | 88.6285 | 254.912 | 96.3929 | SDS-THM4 | mg/L | 14.52 | --- | 617.6109 | --- | 82.043 | 614.4933 | 97.6371 | SDS-THM4 | mg/L | 4.67 | --- | 157.05 | --- | 94.2246 | 156.1865 | 97.01 | SDS-THM4 | mg/L | 11.72 | --- | 110.4914 | --- | 85.5058 | 109.926 | 89.3383 | Alkb, mg/L CaCO3 | 53.5497 | 53.6951 | 52.1091 | 50.466 | Alkb, mg/L CaCO3 | 49.0789 | 49.8151 | 41.7849 | 33.4658
|  | Maximum permissible SDI | 5 | [14 empty] | SDS-BCAA* | mg/L | 8.92 | 10.4 | 9.66 | 15.3209 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-26 | 9:00 | 119 | 21.1 | 56 | 56 | 600 | 6.7 | 6.8 |  | 13.5 | 0.46109 | 0.4963 | 43.4444 | 15.2619 | 12.3727 | 298.5407 | 80.4437 | 296.1053 | 2.1688 | 53.8312 | 0.22984 | [27 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | T-Hdb, mg/L CaCO3 | 81.6848 | 80.7118 | 81.0623 | 79.7242 | T-Hdb, mg/L CaCO3 | 57.447 | 52.5207 | 54.295 | 47.52
|  | Maximum permissible turbidity (ntu) | 1 | [14 empty] | SDS-TBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-26 | 10:00 | 120 | 21.2 | 56 | 56 | 600 | 6.7 | 6.8 |  | 13.5 | 0.46109 | 0.4963 | 43.4444 | 15.2619 | 12.3362 | 298.5407 | 80.4437 | 296.1053 | 2.1688 | 53.8312 | 0.22916 | 9.06 |  |  | 86.9 |  |  | 292.1794 |  | 54.3353 | 291.0333 | 70.1409 | 0.002 |  |  | 0.078434 |  | 95.0617 | 0.078007 | 97.4361 | [8 empty] | SDS-DCAA* | mg/L | 1.28 | BMRL | 1.28 | #VALUE! | --- | 65.2455 | --- | 93.5451 | 64.8822 | 98.0272 | SDS-DCAA* | mg/L | 1.67 | --- | 166.7609 | --- | 91.5784 | 165.9075 | 98.9934 | SDS-DCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Ca-Hdb, mg/L CaCO3 | 69.0255 | 68.12 | 68.4926 | 67.3647 | Ca-Hdb, mg/L CaCO3 | 48.2036 | 43.619 | 45.5053 | 39.7945
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | <0.1 ppm | [14 empty] | SDS-CDBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-26 | 11:00 | 121 | 21.4 | 56 | 56 | 600 | 6.8 | 6.8 |  | 13.6 | 0.46109 | 0.5 | 43.1176 | 15.4897 | 12.4465 | 299.8212 | 80.7788 | 297.3387 | 2.178 | 53.822 | 0.23125 | 9.08 |  |  | 88.1 |  |  | 292.5 |  | 53.7047 | 291.3417 | 69.7606 | 0.003 |  |  | 0.078 |  | 92.5926 | 0.077575 | 96.1328 | [8 empty] | SDS-TCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | 1: All of the information requested in this field may not be available, but values for all Design | [15 empty] | SDS-DCBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-26 | 12:00 | 122 | 21.5 | 56 | 56 | 600 | 6.8 | 6.8 |  | 13.6 | 0.46109 | 0.5 | 43.1176 | 15.4897 | 12.4097 | 299.8212 | 80.7788 | 297.3387 | 2.178 | 53.822 | 0.23057 | 9.07 | 9.14 | 9.07 | 88.2 | 174.5 | 298 | 292.4 | 1.8792 | 53.6521 | 291.2429 | 69.716 | 0.003 | 0.044 | 0.084 | 0.078 | 7.1429 | 92.5926 | 0.077575 | 96.1328 | [8 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  | Parameters must be entered in cells E14:E23, since these parameters are used in calculations. | [15 empty] | SDS-HAA5 | mg/L | 26.01 | 27.26 | 26.635 | 4.6931 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-26 | 15:30 | 125.5 | 22.9 | 56 | 56 | 600 | 7.2 | 6.9 |  | 14.1 | 0.46109 | 0.51064 | 41.5532 | 16.4008 | 12.6071 | 303.5708 | 81.7488 | 300.909 | 2.2049 | 53.7951 | 0.23435 | [27 empty] | SDS-DBAA* | mg/L | 1.51 | 1.56 | 1.535 | 3.2573 | --- | 8.3109 | --- | 56.1429 | 8.2724 | 81.4443 | SDS-DBAA* | mg/L | 2.23 | --- | 13.7755 | --- | 36.2857 | 13.7158 | 83.7413 | SDS-DBAA* | mg/L | 1.21 | --- | 5.79 | --- | 65.4286 | 5.764 | 79.0078 | SDS-DBAA* | mg/L | 2.31 | --- | 4.01 | --- | 34 | 4.0003 | 42.2539 | Blended Water Quality if HAA5 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if HAA5 Controls the Blend Ratio
[18 empty] | SDS-HAA6 | mg/L | 34.93 | 37.66 | 36.295 | 7.5217 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-27 | 8:00 | 142 | 21.8 | 54 | 54 | 600 | 7.1 | 17.2 |  | 24.3 | 0.46109 | 0.29218 | 23.6914 | 16.173 | 12.8428 | 241.9549 | 65.1642 | 239.8629 | 1.7574 | 52.2426 | 0.24583 | [27 empty] | SDS-BCAA* | mg/L | 1.16 | 1.19 | 1.175 | 2.5532 | --- | 30.4336 | --- | 87.8364 | 30.2674 | 96.1179 | SDS-BCAA* | mg/L | 1.64 | --- | 74.5491 | --- | 83.0228 | 74.1722 | 97.7889 | SDS-BCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | 1.44 | --- | 13.1829 | --- | 85.0932 | 13.1156 | 89.0207 | Qp/QT (HAA5), % | -111.8765 | -120.3651 | -107.6303 | -112.4974 | Qp/QT (HAA5), % | -1.4922 | -1.6055 | -1.4356 | -1.5005
[18 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-27 | 9:00 | 143 | 21.8 | 54 | 55 | 600 | 6.8 | 17.2 |  | 24 | 0.46109 | 0.28333 | 24 | 15.4897 | 12.3002 | 239.9738 | 64.6545 | 237.9868 | 1.7433 | 52.7567 | 0.23315 | [27 empty] | SDS-TBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-THM4b, ug/L | NA | NA | NA | NA | SDS-THM4b, ug/L | NA | NA | NA | NA
[18 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-27 | 10:00 | 144 | 21.6 | 54 | 55 | 600 | 6.6 | 16.4 |  | 23 | 0.46109 | 0.28696 | 25.087 | 15.0341 | 12.0092 | 240.7717 | 64.8855 | 238.8369 | 1.7492 | 52.7508 | 0.22766 | 9.05 |  |  | 71.9 |  |  | 237.9488 |  | 62.2176 | 237.0355 | 69.667 | 0.002 |  |  | 0.055994 |  | 95.0617 | 0.055697 | 96.4091 | [8 empty] | SDS-CDBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-HAA5b, ug/L | NA | NA | NA | NA | SDS-HAA5b, ug/L | NA | NA | NA | NA
[18 empty] | should be reported if measured. | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-27 | 11:00 | 145 | 22.2 | 54 | 55 | 600 | 6.8 | 16 |  | 22.8 | 0.46109 | 0.29825 | 25.3158 | 15.4897 | 12.1556 | 243.3166 | 65.5552 | 241.3019 | 1.7675 | 52.7325 | 0.23051 | 9.09 |  |  | 73.6 |  |  | 239.8975 |  | 61.3242 | 238.9551 | 69.1992 | 0.001 |  |  | 0.057287 |  | 97.5309 | 0.056969 | 98.2446 | [8 empty] | SDS-DCBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TOXb, ug Cl- /L | NA | NA | NA | NA | SDS-TOXb, ug Cl- /L | NA | NA | NA | NA
[45 empty] | 1998-10-27 | 12:00 | 146 | 22.4 | 54 | 55 | 600 | 6.9 | 16 |  | 22.9 | 0.46109 | 0.30131 | 25.2009 | 15.7174 | 12.2617 | 244.0182 | 65.7361 | 241.9679 | 1.7726 | 52.7274 | 0.23255 | 9.05 | 9.22 | 9.16 | 73.9 | 172.7 | 238 | 240.4975 | -1.0494 | 61.1666 | 239.5396 | 69.1491 | 0.002 | 0.041 | 0.057 | 0.057103 | -0.18092 | 95.0617 | 0.056786 | 96.478 | [8 empty] | SDS-HAA5 | mg/L | 2.79 | 1.56 | 2.175 | 56.5517 | --- | 86.5198 | --- | 91.8341 | 86.0407 | 97.4721 | SDS-HAA5 | mg/L | 3.9 | --- | 210.5818 | --- | 85.3576 | 209.5134 | 98.1385 | SDS-HAA5 | mg/L | 1.21 | --- | 52.06 | --- | 95.4571 | 51.7719 | 97.6628 | SDS-HAA5 | mg/L | 2.31 | --- | 37.06 | --- | 91.3272 | 36.8611 | 93.7332 | SDS-CDb, mg/L | NA | NA | NA | NA | SDS-CDb, mg/L | NA | NA | NA | NA
[45 empty] | 1998-10-27 | 16:00 | 150 | 23.2 | 54 | 55 | 600 | 7 | 16 |  | 23 | 0.46109 | 0.30435 | 25.087 | 15.9452 | 12.1487 | 244.7178 | 65.9165 | 242.6318 | 1.7776 | 52.7224 | 0.23043 | [27 empty] | SDS-HAA6 | mg/L | 3.95 | 2.75 | 3.35 | 35.8209 | --- | 116.9534 | --- | 90.7701 | 116.3082 | 97.1197 | SDS-HAA6 | mg/L | 5.54 | --- | 285.1309 | --- | 84.7362 | 283.6856 | 98.0471 | SDS-HAA6 | mg/L | 1.21 | --- | 71.38 | --- | 96.6662 | 70.9824 | 98.2954 | SDS-HAA6 | mg/L | 3.75 | --- | 50.2429 | --- | 89.668 | 49.9767 | 92.4965 | TOCb, mg/L | NA | NA | NA | NA | TOCb, mg/L | NA | NA | NA | NA
[45 empty] | 1998-10-29 | 8:00 | 170 | 21.2 | 53 | 54 | 590 | 8 | 18.6 | X | 26.6 | 0.4534 | 0.30075 | 21.1805 | 18.2231 | 14.7297 | 243.9292 | 65.6121 | 241.5114 | 1.7711 | 51.7289 | 0.28475 | [27 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | UV254 b, cm-1 | NA | NA | NA | NA | UV254 b, cm-1 | NA | NA | NA | NA
[45 empty] | 1998-10-29 | 10:00 | 172 | 21.4 | 52 | 53 | 600 | 8 | 18.8 |  | 26.8 | 0.46109 | 0.29851 | 21.3881 | 18.2231 | 14.6429 | 243.4131 | 65.4842 | 241.0407 | 1.7674 | 50.7326 | 0.28863 | 8.67 | 8.75 | 8.64 | 86.7 | 168.9 | 189.4 | 234.3851 | -23.7514 | 54.4404 | 233.4005 | 62.8536 | 0.003 | 0.038 | 0.055 | 0.056457 | -2.6499 | 92.5926 | 0.056101 | 94.6525 | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | Bromideb, ug/L | NA | NA | NA | NA | Bromideb, ug/L | NA | NA | NA | NA
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Alkb, mg/L CaCO3 | NA | NA | NA | NA | Alkb, mg/L CaCO3 | NA | NA | NA | NA
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | T-Hdb, mg/L CaCO3 | NA | NA | NA | NA | T-Hdb, mg/L CaCO3 | NA | NA | NA | NA
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Ca-Hdb, mg/L CaCO3 | NA | NA | NA | NA | Ca-Hdb, mg/L CaCO3 | NA | NA | NA | NA
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Notes: |  |  |  |  | Notes:
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to |  |  |  |  | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | determine the percentage of total flow that must be treated by the membrane process to meet the |  |  |  |  | determine the percentage of total flow that must be treated by the membrane process to meet the
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Stage 1 DBP MCLs. |  |  |  |  | Stage 2 DBP MCLs.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | A 10% factor of safety has been applied all the MCLs. i.e., 72 / 54 mg/L for THM4 and HAA5. |  |  |  |  | A 10% factor of safety has been applied all the MCLs. i.e., 36 / 27 mg/L for THM4 and HAA5.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for |  |  |  |  | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | both parameters and the maximum (Qp/QT) ratio controls the design. |  |  |  |  | both parameters and the maximum (Qp/QT) ratio controls the design.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. |  |  |  |  | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. |  |  |  |  | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. |  |  |  |  | The subscript "b" refers to the blended water quality for a given blend ratio.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL. |  |  |  |  | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. |  |  |  |  | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Note on X24: Alison Gusses: High precision incubator was used for SDS testing
Note on CY29: Alison Gusses: High precision incubator was used for SDS testing
Note on DL29: Alison Gusses: High precision incubator was used for SDS testing
Note on DV29: Alison Gusses: High precision incubator was used for SDS testing
Note on EF29: Alison Gusses: High precision incubator was used for SDS testing

## NF200. 4th Quarter
FIELD-SET 4: 4th QUARTER RBSMT RESULTS (FILE: rbsmt-1.xls)
Field 4-1: PWS And Treatment Plant Data |  | Field 4-2: Manufacturer Reported Membrane Characteristics1 |  | Field 4-3: RBSMT Design Parameters | [8 empty] | Field 4-4: Foulants And Fouling Indices1 |  | Field 4-5: Pretreatment Used Prior To Membranes1 |  |  | Field 4-6: Feed Water Quality After Pretreatment | [5 empty] | Field 4-7: Membrane Setting Data | [20 empty] | Field 4-8: Membrane Performance Data During Operation With The Test Water | [16 empty] | Field 4-8: Membrane Performance Data During Operation With The Test Water (continued) | [19 empty] | Field 4-8: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 4-9: Permeate And Concentrate Water Quality For Run 1 | [11 empty] | Field 4-10: Permeate And Concentrate Water Quality For Run 2 | [8 empty] | Field 4-11: Permeate And Concentrate Water Quality For Run 3 | [8 empty] | Field 4-12: Permeate And Concentrate Water Quality For Run 4 | [8 empty] | Field 4-13: Blending Calculations For Stage 1 D-DBP MCLs |  |  |  |  | Field 4-14: Blending Calculations For Proposed Stage 2 D-DBP MCLs |  |  |  |  | Field 4-15: Membrane Cost Parameters
|  | General Information |  | Input Design Parameters | [8 empty] | Parameters Evaluated Prior to Pretreatment | [80 empty] | Operating Parameters During Sample Collection | [11 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Feed and Permeate Water Quality Parameters |  |  |  |  | Feed and Permeate Water Quality Parameters |  |  |  |  | General Cost Parameters
PWS Name | Water District No. 1 of Johnson County, Kansas | Membrane manufacturer | FilmTec Corporation | [5 empty] | Active membrane area in bench-scale cell, Acell (ft2) | 0.167 |  |  | Alkalinity (mg/L as CaCO3) | 275 | Process | Description | Scale | Parameter | Units | CF-1 | CF-2 | Average | RPD |  |  |  | Average TDS rejection (decimal fraction) | 0.96 | [5 empty] | TDS concentration of setting solution (mg/L) | 0.8 | [12 empty] | Average bulk TDS rejection (decimal fraction) | 0.64303 | [45 empty] | Recovery during sample collection (decimal) | 0.71 | [10 empty] | Recovery during sample collection (decimal) | 0.88 | [7 empty] | Recovery during sample collection (decimal) | 0.5 | [7 empty] | Recovery during sample collection (decimal) | 0.3 | [8 empty] | RUN ID # |  |  |  |  | RUN ID # |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | KS200910 | Membrane trade name | NF200B-4040 | [5 empty] | Active width of membrane in the bench-scale cell, wcell (ft) | 0.333 |  |  | Calcium Hardness (mg/L as CaCO3) | 258 | Presedimentation | 3 Basins | Full-scale | Sampling date | MM/DD/YY | 1999-01-28 | 1999-02-04 | --- | --- | [71 empty] | Feed flow rate during sample collection (mL/min) | 7.7 | [10 empty] | Feed flow rate during sample collection (mL/min) | 5.67 | [7 empty] | Feed flow rate during sample collection (mL/min) | 11.8 | [7 empty] | Feed flow rate during sample collection (mL/min) | 18.6 | [6 empty] | Parameter | 1 | 2 | 3 | 4 | Parameter | 1 | 2 | 3 | 4 | Capital Recovery Interest Rate (%) | 5
Water Industry Data Base Number (optional) | NA | Molecular weight cutoff (Daltons) | 400 | [5 empty] | Average yearly temperature of feed water, TavgoC (oC) | 14 |  |  | LSI | 1.03 | Softening | Lime, 270 mg/L as Ca(OH)2 | Bench-scale | Sampling time | hh:mm | 14:00 | 7:00 | --- | --- | Date | Time | Setting time | Influent | PI | PC | QI | Qp | QW | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) | Date | Time | Operation time | Influent | PI | PC | QI | Qp | QW | Cleaning Event | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1) | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Influent flow rate during sample collection (mL/min) | 600 | [10 empty] | Influent flow rate during sample collection (mL/min) | 600 | [7 empty] | Influent flow rate during sample collection (mL/min) | 600 | [7 empty] | Influent flow rate during sample collection (mL/min) | 600 | [6 empty] | SDS-THM4F, ug/L | 59.9535 | 59.9535 | 59.9535 | 59.9535 | SDS-THM4F, ug/L | 59.9535 | 59.9535 | 59.9535 | 59.9535 | Capital Recovery Period (years) | 20
|  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide | [5 empty] | Approximate feed water TDS, TDSF (mg/L) | 553 |  |  | Dissolved iron (mg/L) |  | Coagulation | Alum: Al2(SO4)3.14H2O, 15 mg/L | Bench-scale | Operation time | hh.hh | 3 | 164 | --- | --- | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | Indicate with "X" | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) | [39 empty] | SDS-THM4p, ug/L | 7.256 | 11.886 | 3.482 | 4.359 | SDS-THM4p, ug/L | 7.256 | 11.886 | 3.482 | 4.359 | Overhead & Profit Factor (% of construction costs) | 15
Official ICR Contact Person |  | Membrane construction (e.g., thin-film composite) | Thin-Film composite | [5 empty] | Manufacturer reported TDS rejection, RejTDS (decimal fraction) | 0.7 |  |  | Total iron (mg/L) |  | Sedimentation | Gravity settling in test drums | Bench-scale | pH | --- | 9.36 | 9.36 | 9.36 | 0 | 1999-01-26 | 8:00 | 0 | [6 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-28 | 11:00 | 0 | [7 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [27 empty] | Permeate and Concentrate Water Quality | [11 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | SDS-HAA5F, ug/L | 23.429 | 23.429 | 23.429 | 23.429 | SDS-HAA5F, ug/L | 23.429 | 23.429 | 23.429 | 23.429 | Special Sitework Factor (% of construction costs) | 0
Mailing Address |  | Membrane hydrophobicity | hydrophilic | [5 empty] | Temperature normalized MTCW (gfd/psi) | 0.16977 |  |  | Dissolved aluminum (mg/L) |  | Recarbonation | CO2 gas added to pH 9.4 | Bench-scale | Temperature | oC | 22.8 | 23 | 22.9 | 0.87336 | 1999-01-26 | 10:00 | 2 | 20.5 | 50 | 50 | 600 | 6.4 | 2.4 | 8.8 | 0.46109 | 0.72727 | 67.1818 | 14.5785 | 12.0301 | 2.6532 | 0.10504 | 2.626 | 0.025346 | 49.9747 | 0.24072 | 1999-01-28 | 12:00 | 1 | 21.4 | 50 | 50 | 600 | 5.5 | 2.5 |  | 8 | 0.46109 | 0.6875 | 74 | 12.5284 | 10.067 | 999.1578 | 354.5646 | 993.2491 | 6.4164 | 43.5836 | 0.23098 | [27 empty] | Parameter | Units | Cp-1 | Cp-1 (dup) | Average | RPD | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | SDS-HAA5p, ug/L | 6.2518 | 5.9808 | 3.0046 | 4.1866 | SDS-HAA5p, ug/L | 6.2518 | 5.9808 | 3.0046 | 4.1866 | Construction Contingencies (% of construction costs) | 15
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | negative | [9 empty] | Total aluminum (mg/L) |  | Cartridge filtration | 1 um size exclusion | Bench-scale | Alkalinity | mg/L as CaCO3 | 42 | 46.1 | 44.05 | 9.3076 | 1999-01-26 | 12:00 | 4 | 20.5 | 50 | 50 | 600 | 6.9 | 2.9 | 9.8 | 0.46109 | 0.70408 | 60.2245 | 15.7174 | 12.97 | 2.4709 | 0.097744 | 2.4436 | 0.023595 | 49.9764 | 0.25952 | 1999-01-28 | 14:00 | 3 | 22 | 50 | 50 | 600 | 5.5 | 2.4 |  | 7.9 | 0.46109 | 0.6962 | 74.9494 | 12.5284 | 9.89 | 1009.3413 | 358.1783 | 1003.3723 | 6.4818 | 43.5182 | 0.22726 | 9.26 | 9.36 | 9.22 | 356 | 556 | 908 | 1014.3333 | -11.7107 | 35.9712 | 1011.316 | 64.7983 | 0.003 | 0.03 | 0.086 | 0.091875 | -6.8314 | 90 | 0.091468 | 96.7202 | [8 empty] | Sampling date | MM/DD/YY | 1999-02-01 | 1999-02-01 | --- | --- | 1999-02-01 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-02-02 | 1999-02-02 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-02-03 | 1999-02-03 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-02-04 | 1999-02-04 | --- | --- | --- | --- | --- | SDS-TOXF, ug Cl- /L | 95 | 95 | 95 | 95 | SDS-TOXF, ug Cl- /L | 95 | 95 | 95 | 95 | Engineering Fee Factor (% of construction costs) | 15
Phone Number |  |  |  | Experimental Design1,2 | [8 empty] | Fluoride (mg/L) |  | Antiscalant | 4 mg/L Hypersperse 400UL | Bench-scale | Total dissolved solids | mg/L | 556 | 556 | 556 | 0 | 1999-01-26 | 14:00 | 6 | 20.9 | 51 | 51 | 600 | 7.1 | 2.8 | 9.9 | 0.46109 | 0.71717 | 59.6061 | 16.173 | 13.1891 | 2.5708 | 0.10166 | 2.5416 | 0.024545 | 50.9755 | 0.25873 | 1999-01-28 | 16:00 | 5 | 22.3 | 50 | 50 | 600 | 5.6 | 2.5 |  | 8.1 | 0.46109 | 0.69136 | 73.0741 | 12.7562 | 9.981 | 1003.6952 | 356.1361 | 997.6513 | 6.4454 | 43.5546 | 0.22916 | [27 empty] | Sampling time | hh:mm | 8:00 | 8:00 | --- | --- | 8:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 8:00 | 8:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 8:00 | 8:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 7:00 | 7:00 | --- | --- | --- | --- | --- | SDS-TOXp, ug Cl- /L | #DIV/0! | BMRL | 26.3 | BMRL | SDS-TOXp, ug Cl- /L | #DIV/0! | BMRL | 26.3 | BMRL | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920
FAX Number |  | Design Parameters |  | ID# | Recovery | FW-design | Dp | PI | QI-cell | Qp | QF | QW | Phosphate (mg/L) |  |  |  |  | Total hardness | mg/L as CaCO3 | 151.3 | 162.3 | 156.8 | 7.0153 | 1999-01-26 | 16:00 | 8 | 21.2 | 50 | 50 | 600 | 7.4 | 3.1 | 10.5 | 0.46109 | 0.70476 | 56.1429 | 16.8564 | 13.625 | 2.4761 | 0.097869 | 2.4467 | 0.023635 | 49.9764 | 0.27263 | 1999-01-28 | 17:00 | 6 | 22.4 | 50 | 50 | 600 | 5.6 | 2.5 |  | 8.1 | 0.46109 | 0.69136 | 73.0741 | 12.7562 | 9.9515 | 1003.6952 | 356.1361 | 997.6513 | 6.4454 | 43.5546 | 0.22848 | [27 empty] | Operation time | hh.hh | 93 | 93 | --- | --- | 93 | --- | --- | --- | --- | --- | Operation time | hh.hh | 117 | 117 | --- | --- | --- | --- | --- | Operation time | hh.hh | 141 | 141 | --- | --- | --- | --- | --- | Cumulative time | hr | 164 | 164 | --- | --- | --- | --- | --- | SDS-CDF, mg/L | 3.5155 | 3.5155 | 3.5155 | 3.5155 | SDS-CDF, mg/L | 3.5155 | 3.5155 | 3.5155 | 3.5155 | 1998 Producers Price Index (PPI base year 1967 = 100) | 370
E-Mail Address (optional) |  | Design flux, FW (gfd) | 16.5 |  | (decimal) | (gfd) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | Sulfate (mg/L) |  |  |  |  | Calcium hardness | mg/L as CaCO3 | 97.4 | 109.4 | 103.4 | 11.6054 | 1999-01-27 | 8:00 | 24 | 21.1 | 50 | 50 | 600 | 7.1 | 3.1 | 10.2 | 0.46109 | 0.69608 | 57.8235 | 16.173 | 13.1113 | 2.4136 | 0.095449 | 2.3862 | 0.023045 | 49.977 | 0.26235 | 1999-01-29 | 7:00 | 20 | 21.4 | 50 | 50 | 600 | 5.5 | 2.4 |  | 7.9 | 0.46109 | 0.6962 | 74.9494 | 12.5284 | 10.067 | 1009.3413 | 358.1783 | 1003.3723 | 6.4818 | 43.5182 | 0.23133 | 8.97 |  |  | 354 |  |  | 1018.9167 |  | 36.3309 | 1015.8691 | 65.153 | 0.005 |  |  | 0.087292 |  | 83.3333 | 0.086914 | 94.2472 | [8 empty] | pH | --- | 7.87 | 7.9 | 7.885 | 0.38047 | 8.24 | --- | --- | --- | --- | --- | pH | --- | 9.11 | 8.81 | --- | --- | --- | --- | --- | pH | --- | 8.55 | 8.65 | --- | --- | --- | --- | --- | pH | --- | 8.89 | 9.3 | --- | --- | --- | --- | --- | SDS-CDp, mg/L | 1.659 | 2.033 | 1.597 | 1.812 | SDS-CDp, mg/L | 1.659 | 2.033 | 1.597 | 1.812 | Labor Rate + Fringe ($/work-hour) | 17
|  | Net driving pressure at the design flux, NDP (psi) | 70 | 1 | 0.7 | 12 | 14.5623 | 85.2466 | 606.4586 | 5.2675 | 7.5249 | 2.2575 | Calcium (mg/L) | 103 |  |  |  | Turbidity | ntu | 0.08 | 0.1 | 0.09 | 22.2222 | 1999-01-27 | 10:00 | 26 | 21.8 | 50 | 50 | 600 | 7.2 | 3.2 | 10.4 | 0.46109 | 0.69231 | 56.6923 | 16.4008 | 13.0237 | 2.3876 | 0.094403 | 2.3601 | 0.022794 | 49.9772 | 0.26059 | 1999-01-29 | 9:00 | 22 | 20.9 | 50 | 50 | 600 | 5.5 | 2.4 |  | 7.9 | 0.46109 | 0.6962 | 74.9494 | 12.5284 | 10.2169 | 1009.3413 | 358.1783 | 1003.3723 | 6.4818 | 43.5182 | 0.23477 | [27 empty] | Temperature | oC | 22.9 | 23.2 | 23.05 | 1.3015 | 22.8 | --- | --- | --- | --- | --- | Temperature | oC | 23 | 23 | --- | --- | --- | --- | --- | Temperature | oC | 22.1 | 21.9 | --- | --- | --- | --- | --- | Temperature | oC | 22.1 | 22.3 | --- | --- | --- | --- | --- | TOCF, mg/L | 2.275 | 2.275 | 2.275 | 2.275 | TOCF, mg/L | 2.275 | 2.275 | 2.275 | 2.275 | Labor Overhead Factor (% of labor) | 42
Technical ICR Contact Person |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.235 | 2 | 0.9 | 12 | 40.369 | 111.0533 | 606.4586 | 5.2675 | 5.8527 | 0.58527 | Barium (mg/L) |  |  |  |  | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! | 1999-01-27 | 14:00 | 30 | 21.9 | 50 | 50 | 600 | 7.1 | 3.4 | 10.5 | 0.46109 | 0.67619 | 56.1429 | 16.173 | 12.8049 | 2.2821 | 0.090248 | 2.2562 | 0.021789 | 49.9782 | 0.25621 | 1999-01-29 | 11:00 | 24 | 21.2 | 50 | 50 | 600 | 5.5 | 2.4 |  | 7.9 | 0.46109 | 0.6962 | 74.9494 | 12.5284 | 10.1267 | 1009.3413 | 358.1783 | 1003.3723 | 6.4818 | 43.5182 | 0.2327 | 8.77 | 8.84 | 8.78 | 359 | 556 | 948 | 1007.4583 | -6.272 | 35.4317 | 1004.4862 | 64.2603 | 0.004 | 0.033 | 0.097 | 0.089583 | 7.646 | 86.6667 | 0.089191 | 95.5152 | [8 empty] | Alkalinity | mg/L as CaCO3 | 34.5 | 37.8 | 36.15 | 9.1286 | 64.5 | 63.3914 | 1.7188 | 17.9342 | 63.2673 | 42.8615 | Alkalinity | mg/L as CaCO3 | 40.8 | 82.4 | 67.8833 | 17.6173 | 7.378 | 67.7707 | 39.797 | Alkalinity | mg/L as CaCO3 | 31.3 | 60 | 56.8 | 5.3333 | 28.9444 | 56.6746 | 44.7725 | Alkalinity | mg/L as CaCO3 | 36.3 | 55.4 | 47.3714 | 14.492 | 17.5936 | 47.3199 | 23.2882 | TOCp, mg/L | #DIV/0! | BMRL | BMRL | BMRL | TOCp, mg/L | #DIV/0! | BMRL | BMRL | BMRL | Electric Rate ($/kW-h) | 0.06
Mailing Address |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | 3 | 0.5 | 12 | 9.401 | 80.0853 | 606.4586 | 5.2675 | 10.5349 | 5.2675 | Strontium (mg/L) |  |  |  |  | Total organic carbon | mg/L | 2.4 | 2.15 | 2.275 | 10.989 | 1999-01-27 | 16:00 | 32 | 22.1 | 50 | 50 | 600 | 7.1 | 3.4 | 10.5 | 0.46109 | 0.67619 | 56.1429 | 16.173 | 12.7295 | 2.2821 | 0.090248 | 2.2562 | 0.021789 | 49.9782 | 0.2547 | 1999-01-29 | 13:00 | 26 | 21.8 | 50 | 50 | 600 | 5.6 | 2.5 |  | 8.1 | 0.46109 | 0.69136 | 73.0741 | 12.7562 | 10.1296 | 1003.6952 | 356.1361 | 997.6513 | 6.4454 | 43.5546 | 0.23257 | [27 empty] | Total dissolved solids | mg/L | 360 | 362 | 361 | 0.55402 | 973 | 1033.4138 | -6.209 | 35.0719 | 1030.3504 | 64.9634 | Total dissolved solids | mg/L | 389 | 1419 | 1780.6667 | -25.4874 | 30.036 | 1774.8801 | 78.083 | Total dissolved solids | mg/L | 327 | 761 | 785 | -3.1537 | 41.1871 | 782.7482 | 58.2241 | Total dissolved solids | mg/L | 283 | 618 | 673 | -8.8997 | 49.1007 | 671.1865 | 57.8359 | UV254 F, cm-1 | 0.03 | 0.03 | 0.03 | 0.03 | UV254 F, cm-1 | 0.03 | 0.03 | 0.03 | 0.03 | Fuel Oil Rate ($/gal) | NA
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 400 | 4 | 0.3 | 12 | 7.189 | 77.8733 | 606.4586 | 5.2675 | 17.5582 | 12.2907 | Reactive silica (mg/L as SiO2) |  |  |  |  | UV254 | cm-1 | 0.03 | 0.03 | 0.03 | 0 | 1999-01-27 | 17:00 | 33 | 20.9 | 50 | 50 | 600 | 7.1 | 3.4 | 10.5 | 0.46109 | 0.67619 | 56.1429 | 16.173 | 13.1891 | 2.2821 | 0.090248 | 2.2562 | 0.021789 | 49.9782 | 0.2639 | 1999-01-29 | 15:00 | 28 | 22.4 | 50 | 50 | 600 | 5.7 | 2.5 |  | 8.2 | 0.46109 | 0.69512 | 72.1707 | 12.984 | 10.1292 | 1008.1634 | 357.6827 | 1001.9839 | 6.4739 | 43.5261 | 0.23272 | [27 empty] | Total hardness | mg/L as CaCO3 | 64.2 | 67.5 | 65.85 | 5.0114 | 360.1 | 379.4707 | -5.3793 | 58.0038 | 378.0419 | 82.5813 | Total hardness | mg/L as CaCO3 | 74.6 | 784.2 | 759.6 | 3.137 | 52.4235 | 756.7518 | 90.1421 | Total hardness | mg/L as CaCO3 | 60.5 | 259.4 | 253.1 | 2.4287 | 61.4158 | 252.1531 | 76.0066 | Total hardness | mg/L as CaCO3 | 54.3 | 205.8 | 200.7286 | 2.4643 | 65.3699 | 200.0477 | 72.8565 | UV254 p, cm-1 | 0.0045 | 0.007 | 0.004 | 0.003 | UV254 p, cm-1 | 0.0045 | 0.007 | 0.004 | 0.003 | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Purchase price for an equivalent 8" x 40 " element ($) | 700 | 1: For experimental matrix see Table 4-2 in Part 3 of the ICR Treatment Studies Manual. | [8 empty] | Turbidity (ntu) | 1.3 |  |  |  | SUVA | L/(mg*m) | 1.25 | 1.3953 | 1.3227 | 10.989 | 1999-01-28 | 8:00 | 48 | 22 | 50 | 50 | 600 | 7.1 | 3.1 | 10.2 | 0.46109 | 0.69608 | 57.8235 | 16.173 | 12.7671 | 2.4136 | 0.095449 | 2.3862 | 0.023045 | 49.977 | 0.25546 | 1999-01-29 | 17:00 | 30 | 22.5 | 50 | 50 | 600 | 5.9 | 2.5 |  | 8.4 | 0.46109 | 0.70238 | 70.4286 | 13.4396 | 10.4537 | 1016.8992 | 360.7037 | 1010.4466 | 6.5297 | 43.4703 | 0.24048 | 8.56 |  |  | 357 |  |  | 1025.64 |  | 35.7914 | 1022.3525 | 65.0805 | 0.005 |  |  | 0.089 |  | 83.3333 | 0.088587 | 94.3558 | [8 empty] | Calcium hardness | mg/L as CaCO3 | 41.2 | 43.4 | 42.3 | 5.2009 | 233.7 | 252.9897 | -8.254 | 59.0909 | 252.0298 | 83.2163 | Calcium hardness | mg/L as CaCO3 | 47.4 | 535.9 | 514.0667 | 4.0741 | 54.1586 | 512.1263 | 90.7445 | Calcium hardness | mg/L as CaCO3 | 39.7 | 176.8 | 167.1 | 5.4864 | 61.6054 | 166.4736 | 76.1524 | Calcium hardness | mg/L as CaCO3 | 37.5 | 140.1 | 131.6429 | 6.0365 | 63.7331 | 131.2051 | 71.4188 | BromideF, ug/L | 150 | 150 | 150 | 150 | BromideF, ug/L | 150 | 150 | 150 | 150 | Current Process Water Rate ($/1000 gal) | 0.375
FAX Number |  | Maximum flow rate to the 8" x 40" element, QI, max (gpm) | 70 | 2: Flow rates and pressures may need to be adjusted in order to obtain the desired operating conditions. | [8 empty] | SDI |  |  |  |  | Bromide | mg/L | 150 | 150 | 150 | 0 | 1999-01-28 | 10:00 | 50 | 22.2 | 50 | 50 | 600 | 7.2 | 3.2 | 10.4 | 0.46109 | 0.69231 | 56.6923 | 16.4008 | 12.8706 | 2.3876 | 0.094403 | 2.3601 | 0.022794 | 49.9772 | 0.25753 | 1999-01-30 | 7:00 | 44 | 20.2 | 50 | 50 | 600 | 5.2 | 2.5 |  | 7.7 | 0.46109 | 0.67532 | 76.9221 | 11.845 | 9.8616 | 985.1145 | 349.6949 | 979.6076 | 6.3267 | 43.6733 | 0.2258 | 8.96 |  |  | 356 |  |  | 972 |  | 35.9712 | 969.3307 | 63.2736 | 0.004 |  |  | 0.08408 |  | 86.6667 | 0.083733 | 95.2229 | [8 empty] | Turbidity | ntu | 0.1 | 0.08 | 0.09 | 22.2222 | 0.1 | 0.09 | 10 | 0 | 0.09 | 0 | Turbidity | ntu | 0.09 | 0.13 | 0.09 | 30.7692 | 0 | 0.09 | 0 | Turbidity | ntu | 0.08 | 0.13 | 0.1 | 23.0769 | 11.1111 | 0.099902 | 19.9213 | Turbidity | ntu | 0.08 | 0.08 | 0.094286 | -17.8571 | 11.1111 | 0.094219 | 15.0917 | Bromidep, ug/L | 160 | 170 | 160 | 150 | Bromidep, ug/L | 160 | 170 | 160 | 150 | Modifications to Existing Plant (% of construction costs) | 52
E-Mail Address (optional) |  | Minimum flow rate to the 8" x 40" element, QI, min (gpm) | 34 | [9 empty] | MFI |  |  |  |  | SDS-Cl2 dose | mg/L | 4.3 | 4.3 | 4.3 | 0 | 1999-01-28 | 11:00 | 51 | 21.7 | 50 | 51 | 600 | 7.1 | 3.1 | 10.2 | 0.46109 | 0.69608 | 57.8235 | 16.173 | 12.8809 | 2.4136 | 0.095449 | 2.3862 | 0.023045 | 50.477 | 0.25518 | 1999-01-30 | 9:00 | 46 | 20.4 | 51 | 52 | 600 | 5.3 | 2.2 |  | 7.5 | 0.46109 | 0.70667 | 79 | 12.0728 | 9.992 | 1021.7622 | 362.6648 | 1015.9402 | 6.5619 | 44.9381 | 0.22235 | [27 empty] | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! | BMRL | #DIV/0! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | BMRL | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | BMRL | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | BMRL | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | AlkF, mg/L CaCO3 | 44.05 | 44.05 | 44.05 | 44.05 | AlkF, mg/L CaCO3 | 44.05 | 44.05 | 44.05 | 44.05
|  | Total width of all membrane envelopes in the 8" x 40" element, w (ft) | 70.67 | [9 empty] | MPFI |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | SDS-Free Cl2 residual | mg/L | 0.869 | 0.7 | 0.7845 | 21.5424 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-30 | 11:00 | 48 | 21.1 | 51 | 52 | 600 | 5.3 | 2.2 |  | 7.5 | 0.46109 | 0.70667 | 79 | 12.0728 | 9.7873 | 1021.7622 | 362.6648 | 1015.9402 | 6.5619 | 44.9381 | 0.2178 | 9.01 | 9.09 | 8.91 | 358 | 556 | 963 | 1033 | -7.269 | 35.6115 | 1030.0187 | 65.2434 | 0.004 | 0.033 | 0.097 | 0.092636 | 4.4986 | 86.6667 | 0.092245 | 95.6637 | [8 empty] | Total organic carbon | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | 6.75 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L | BMRL | 15 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 4.15 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 2.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkp, mg/L CaCO3 | 36.15 | 40.8 | 31.3 | 36.3 | Alkp, mg/L CaCO3 | 36.15 | 40.8 | 31.3 | 36.3
Plant Name | Facility 1 | Feed spacer thickness in the 8" x 40" element, T (ft) | 0.0023 | [9 empty] | Bromide (mg/L) | 160 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | SDS-Cl2 demand | mg/L | 3.431 | 3.6 | 3.5155 | 4.8073 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-30 | 13:00 | 50 | 21.4 | 51 | 52 | 600 | 5.6 | 2.3 |  | 7.9 | 0.46109 | 0.70886 | 74.9494 | 12.7562 | 10.25 | 1024.5812 | 363.547 | 1018.4116 | 6.5795 | 44.9205 | 0.22818 | [27 empty] | UV254 | cm-1 | 0.004 | 0.005 | 0.0045 | 22.2222 | 0.102 | 0.092431 | 9.3813 | 85 | 0.09203 | 95.1103 | UV254 | cm-1 | 0.007 | 0.205 | 0.19867 | 3.0894 | 76.6667 | 0.19787 | 96.4623 | UV254 | cm-1 | 0.004 | 0.062 | 0.056 | 9.6774 | 86.6667 | 0.055744 | 92.8244 | UV254 | cm-1 | 0.003 | 0.046 | 0.041571 | 9.6273 | 90 | 0.041392 | 92.7522 | T-HdF, mg/L CaCO3 | 156.8 | 156.8 | 156.8 | 156.8 | T-HdF, mg/L CaCO3 | 156.8 | 156.8 | 156.8 | 156.8
Treatment Plant Category | CS/SOFT | [11 empty] | TOC (mg/L) | 2.6 | is to list the pretreatment processes used in this particular RBSMT run. |  |  | SDS-Chlorination temp. | oC | 6.3 | 6 | 6.15 | 4.878 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-30 | 15:00 | 52 | 21.5 | 51 | 52 | 600 | 5.6 | 2.3 |  | 7.9 | 0.46109 | 0.70886 | 74.9494 | 12.7562 | 10.2198 | 1024.5812 | 363.547 | 1018.4116 | 6.5795 | 44.9205 | 0.22751 | [27 empty] | SUVA | L/(mg*m) | NR | NR | #DIV/0! | #VALUE! | 1.5111 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 1.3667 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 1.494 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 1.5593 | --- | --- | --- | --- | --- | T-Hdp, mg/L CaCO3 | 65.85 | 74.6 | 60.5 | 54.3 | T-Hdp, mg/L CaCO3 | 65.85 | 74.6 | 60.5 | 54.3
Process Train Name | Coagulation/Sedimentation/Softening | Additional Information | [10 empty] | pH | 8.04 |  |  |  | SDS-Chlorination pH | --- | 9.54 | 9.5 | 9.52 | 0.42017 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-30 | 17:00 | 54 | 21 | 51 | 52 | 600 | 5.6 | 2.3 |  | 7.9 | 0.46109 | 0.70886 | 74.9494 | 12.7562 | 10.3719 | 1024.5812 | 363.547 | 1018.4116 | 6.5795 | 44.9205 | 0.2309 | 9.01 |  |  | 365 |  |  | 1021.0435 |  | 34.3525 | 1017.9819 | 64.1447 | 0.005 |  |  | 0.09087 |  | 83.3333 | 0.090469 | 94.4732 | [8 empty] | Bromide | mg/L | 160 | 160 | 160 | 0 | --- | 125.5172 | --- | -6.6667 | 125.6743 | -27.3132 | Bromide | mg/L | 170 | --- | 3.3333 | --- | -13.3333 | 4.0263 | -4122.2038 | Bromide | mg/L | 160 | --- | 140 | --- | -6.6667 | 140.0983 | -14.2055 | Bromide | mg/L | 150 | --- | 150 | --- | 0 | 150 | 0 | Ca-HdF, mg/L CaCO3 | 103.4 | 103.4 | 103.4 | 103.4 | Ca-HdF, mg/L CaCO3 | 103.4 | 103.4 | 103.4 | 103.4
ICR Treatment Plant Identification Number | 381 | Design cross-flow velocity (fps) | 0.43 | [9 empty] | Total Hardness (mg/L as CaCO3) | 345 |  |  |  | SDS-Incubation time | hours | 40 | 40 | 40 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-31 | 7:00 | 68 | 20.8 | 52 | 52 | 600 | 5.5 | 2.2 |  | 7.7 | 0.46109 | 0.71429 | 76.9221 | 12.5284 | 10.2471 | 1031.1799 | 365.9281 | 1025.0817 | 6.622 | 45.378 | 0.22582 | 8.98 |  |  | 345 |  |  | 1083.5 |  | 37.9496 | 1080.1152 | 68.059 | 0.003 |  |  | 0.0975 |  | 90 | 0.097067 | 96.9093 | [8 empty] | SDS-Cl2 dose | mg/L | 2.8 | 2.8 | 2.8 | 0 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2.8 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2.8 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2.8 | --- | --- | --- | --- | --- | --- | Ca-Hdp, mg/L CaCO3 | 42.3 | 47.4 | 39.7 | 37.5 | Ca-Hdp, mg/L CaCO3 | 42.3 | 47.4 | 39.7 | 37.5
PWSID Number of Plant (if assigned) | KS200910 | Required influent flow to permeate flow rate ratio, QI:Qp | [10 empty] | UV254 | 0.0756 |  |  |  | SDS-TOX | mg Cl- /L | 95 | 95 | 95 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-31 | 9:00 | 70 | 20.6 | 52 | 52 | 600 | 5.4 | 2.2 |  | 7.6 | 0.46109 | 0.71053 | 77.9474 | 12.3006 | 10.1205 | 1026.5104 | 364.3106 | 1020.5506 | 6.5922 | 45.4078 | 0.22288 | [27 empty] | SDS-Free Cl2 residual | mg/L | 1.123 | 1.159 | 1.141 | 3.1551 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.767 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.203 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.988 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 0.1 | Maximum element recovery (%) | 15 | [9 empty] | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | SDS-CHCl3 | mg/L | 16.503 | 13.33 | 14.9165 | 21.2717 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-31 | 11:00 | 72 | 20.8 | 51 | 52 | 600 | 5.9 | 2.2 |  | 8.1 | 0.46109 | 0.7284 | 73.0741 | 13.4396 | 10.9924 | 1049.109 | 372.1288 | 1042.4521 | 6.7365 | 44.7635 | 0.24557 | 8.86 | 8.72 | 8.52 | 361 | 561 | 965 | 1078.9545 | -11.8088 | 35.0719 | 1075.4246 | 66.4319 | 0.004 | 0.031 | 0.097 | 0.099727 | -2.8116 | 86.6667 | 0.099257 | 95.97 | [8 empty] | SDS-Cl2 demand | mg/L | 1.677 | 1.641 | 1.659 | 2.17 | --- | 8.0607 | --- | 52.809 | 8.0316 | 79.344 | SDS-Cl2 demand | mg/L | 2.033 | --- | 14.3872 | --- | 42.1704 | 14.3358 | 85.8187 | SDS-Cl2 demand | mg/L | 1.597 | --- | 5.434 | --- | 54.5726 | 5.4151 | 70.5086 | SDS-Cl2 demand | mg/L | 1.812 | --- | 4.2456 | --- | 48.4568 | 4.2343 | 57.2062 | Blended Water Quality if THM4 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if THM4 Controls the Blend Ratio
Historical Average Water Temperature (oC) | 14 | Variability of design flux (%) | [10 empty] | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | SDS-BDCM | mg/L | 17.59 | 17.404 | 17.497 | 1.063 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-31 | 13:00 | 74 | 20.9 | 51 | 52 | 600 | 5.6 | 2.3 |  | 7.9 | 0.46109 | 0.70886 | 74.9494 | 12.7562 | 10.4027 | 1024.5812 | 363.547 | 1018.4116 | 6.5795 | 44.9205 | 0.23158 | [27 empty] | SDS-Chlorination temp. | oC | 6 | 6 | 6 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 6 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 6 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 6 | --- | --- | --- | --- | --- | --- | Qp/QT (THM4), % | -22.8597 | -25.0616 | -21.332 | -21.6685 | Qp/QT (THM4), % | 45.4547 | 49.833 | 42.417 | 43.0861
State Approved Plant Capacity (MGD) | 55 | Rejection of reference solute and conditions of test | 45 rejection of CaCl2 | [14 empty] | SDS-DBCM | mg/L | 16.807 | 18.239 | 17.523 | 8.1721 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-31 | 15:00 | 76 | 21.4 | 52 | 52 | 600 | 5.6 | 2.3 |  | 7.9 | 0.46109 | 0.70886 | 74.9494 | 12.7562 | 10.25 | 1024.5812 | 363.547 | 1018.4116 | 6.5795 | 45.4205 | 0.22567 | [27 empty] | SDS-Chlorination pH | --- | 9.5 | 9.47 | 9.485 | 0.31629 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 9.48 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 9.54 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 9.49 | --- | --- | --- | --- | --- | --- | SDS-THM4b, ug/L | NA | NA | NA | NA | SDS-THM4b, ug/L | 36 | 36 | 36 | 36
|  | (e.g., solute type and concentration) | 70psi, 500mg/L CaCl2,25 deg. C,15% recovery | [14 empty] | SDS-CHBr3 | mg/L | 9.422 | 10.612 | 10.017 | 11.8798 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-31 | 17:00 | 78 | 21 | 51 | 52 | 600 | 5.6 | 2.4 |  | 8 | 0.46109 | 0.7 | 74 | 12.7562 | 10.3719 | 1013.9002 | 359.7571 | 1007.7948 | 6.5109 | 44.9891 | 0.23054 | 8.88 |  |  | 360 |  |  | 1013.3333 |  | 35.2518 | 1010.2844 | 64.3665 | 0.005 |  |  | 0.088333 |  | 83.3333 | 0.087944 | 94.3146 | [8 empty] | SDS-Incubation time | hours | 40 | 40 | 40 | 0 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 40 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 40 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 40 | --- | --- | --- | --- | --- | --- | SDS-HAA5b, ug/L | NA | NA | NA | NA | SDS-HAA5b, ug/L | 15.6211 | 14.734 | 14.7656 | 15.1382
|  | Variability of rejection of reference solute (%) | 45 rejection of CaCl2 | [14 empty] | SDS-THM4 | mg/L | 60.322 | 59.585 | 59.9535 | 1.2293 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-02-01 | 8:00 | 93 | 21.4 | 51 | 52 | 600 | 5.2 | 0.67 |  | 5.87 | 0.46109 | 0.88586 | 101.2147 | 11.845 | 9.5179 | 1297.2424 | 460.4938 | 1289.9906 | 8.3312 | 43.1688 | 0.22048 | [27 empty] | SDS-TOX | mg Cl- /L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | 26.3 | --- | 163.7 | --- | 72.3158 | 163.0245 | 83.8675 | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOXb, ug Cl- /L | NA | NA | NA | NA | SDS-TOXb, ug Cl- /L | #DIV/0! | #VALUE! | 65.8595 | #VALUE!
|  | Standard testing recovery (%) | 15 | [14 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-02-01 | 9:00 | 94 | 21.4 | 51 | 52 | 600 | 5.2 | 0.67 |  | 5.87 | 0.46109 | 0.88586 | 101.2147 | 11.845 | 9.5179 | 1297.2424 | 460.4938 | 1289.9906 | 8.3312 | 43.1688 | 0.22048 | 9.19 |  |  | 374 |  |  | 1968.5373 |  | 32.7338 | 1961.6277 | 80.9342 | 0.005 |  |  | 0.22403 |  | 83.3333 | 0.22308 | 97.7587 | [8 empty] | SDS-CHCl3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHCl3 | mg/L | 1.361 | --- | 114.3235 | --- | 90.8759 | 113.8538 | 98.8046 | SDS-CHCl3 | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHCl3 | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDb, mg/L | NA | NA | NA | NA | SDS-CDb, mg/L | 2.6716 | 2.7767 | 2.7017 | 2.7815
|  | Standard testing pH | 8 | [14 empty] | SDS-DCAA* | mg/L | 14.4401 | 12.3522 | 13.3962 | 15.5858 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-02-01 | 10:00 | 95 | 20.8 | 51 | 52 | 600 | 5 | 0.67 |  | 5.67 | 0.46109 | 0.88183 | 104.8201 | 11.3895 | 9.3156 | 1289.2267 | 457.7476 | 1282.2977 | 8.2801 | 43.2199 | 0.21554 | 9.26 |  |  | 383 |  |  | 1847.0448 |  | 31.1151 | 1840.9446 | 79.1955 | 0.006 |  |  | 0.2091 |  | 80 | 0.20826 | 97.119 | [8 empty] | SDS-BDCM | mg/L | 1.74 | 1.613 | 1.6765 | 7.5753 | --- | 56.2299 | --- | 90.4184 | 55.9814 | 97.0053 | SDS-BDCM | mg/L | 2.428 | --- | 128.003 | --- | 86.1233 | 127.4809 | 98.0954 | SDS-BDCM | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | 1.098 | --- | 24.5251 | --- | 93.7246 | 24.4162 | 95.503 | TOCb, mg/L | NA | NA | NA | NA | TOCb, mg/L | #DIV/0! | #VALUE! | #VALUE! | #VALUE!
|  | Acceptable range of operating pressures | 0 to 600 psi | [14 empty] | SDS-TCAA* | mg/L | 2.7037 | 2.6531 | 2.6784 | 1.8892 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-02-01 | 11:00 | 96 | 21 | 52 | 52 | 600 | 5.1 | 0.67 |  | 5.77 | 0.46109 | 0.88388 | 102.9861 | 11.6172 | 9.4459 | 1293.2896 | 459.1404 | 1286.1993 | 8.306 | 43.694 | 0.21618 | 9.29 |  |  | 390 |  |  | 1819.5821 |  | 29.8561 | 1813.5064 | 78.4947 | 0.006 |  |  | 0.21269 |  | 80 | 0.21181 | 97.1672 | [8 empty] | SDS-DBCM | mg/L | 2.563 | 2.794 | 2.6785 | 8.6242 | --- | 53.8664 | --- | 84.7144 | 53.6332 | 95.0059 | SDS-DBCM | mg/L | 3.744 | --- | 118.569 | --- | 78.6338 | 118.0916 | 96.8296 | SDS-DBCM | mg/L | 1.67 | --- | 33.376 | --- | 90.4697 | 33.2201 | 94.9729 | SDS-DBCM | mg/L | 1.568 | --- | 24.3609 | --- | 91.0518 | 24.2549 | 93.5353 | UV254 b, cm-1 | NA | NA | NA | NA | UV254 b, cm-1 | 0.018409 | 0.018538 | 0.018972 | 0.018367
|  | Acceptable range of operating pH values | 3 to 10 | [14 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-02-01 | 12:00 | 97 | 21.1 | 52 | 52 | 600 | 5 | 0.67 |  | 5.67 | 0.46109 | 0.88183 | 104.8201 | 11.3895 | 9.2333 | 1289.2267 | 457.7476 | 1282.2977 | 8.2801 | 43.7199 | 0.21119 | 9.31 | 9.46 | 9.19 | 393 | 544 | 1378 | 1772.4179 | -28.6225 | 29.3165 | 1766.6703 | 77.7548 | 0.006 | 0.032 | 0.189 | 0.2091 | -10.6373 | 80 | 0.20826 | 97.119 | [8 empty] | SDS-CHBr3 | mg/L | 2.736 | 3.066 | 2.901 | 11.3754 | --- | 27.4389 | --- | 71.0392 | 27.3271 | 89.3842 | SDS-CHBr3 | mg/L | 4.353 | --- | 51.553 | --- | 56.5439 | 51.3567 | 91.524 | SDS-CHBr3 | mg/L | 1.812 | --- | 18.222 | --- | 81.9108 | 18.1413 | 90.0118 | SDS-CHBr3 | mg/L | 1.693 | --- | 13.5844 | --- | 83.0987 | 13.5291 | 87.4863 | Bromideb, ug/L | NA | NA | NA | NA | Bromideb, ug/L | 154.5455 | 159.9666 | 154.2417 | 150
|  | Typical pressure drop across a single element (psi) | 3 to5 | [14 empty] | SDS-DBAA* | mg/L | 7.0018 | 7.707 | 7.3544 | 9.5888 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-02-01 | 15:00 | 100 | 22 | 52 | 52 | 600 | 5.1 | 0.7 |  | 5.8 | 0.46109 | 0.87931 | 102.4483 | 11.6172 | 9.1708 | 1284.4794 | 456.0126 | 1277.4375 | 8.2495 | 43.7505 | 0.20961 | [27 empty] | SDS-THM4 | mg/L | 7.039 | 7.473 | 7.256 | 5.9813 | --- | 188.9715 | --- | 87.8973 | 188.1437 | 96.1434 | SDS-THM4 | mg/L | 11.886 | --- | 412.4485 | --- | 80.1746 | 410.783 | 97.1065 | SDS-THM4 | mg/L | 3.482 | --- | 116.425 | --- | 94.1922 | 115.8697 | 96.9949 | SDS-THM4 | mg/L | 4.359 | --- | 83.7797 | --- | 92.7294 | 83.4104 | 94.774 | Alkb, mg/L CaCO3 | NA | NA | NA | NA | Alkb, mg/L CaCO3 | 40.4591 | 42.4304 | 38.6418 | 40.7108
|  | Maximum permissible SDI | 5 | [14 empty] | SDS-BCAA* | mg/L | 8.7824 | 7.4294 | 8.1059 | 16.6915 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-02-02 | 8:00 | 115 | 22.1 | 51 | 52 | 600 | 5.2 | 5.1 |  | 10.3 | 0.46109 | 0.50485 | 57.2524 | 11.845 | 9.323 | 824.4875 | 292.6757 | 819.8785 | 5.2951 | 46.2049 | 0.20177 | [27 empty] | SDS-MCAA* | mg/L | 2.0942 | 2.3709 | 2.2325 | 12.3939 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | 2.1758 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | T-Hdb, mg/L CaCO3 | NA | NA | NA | NA | T-Hdb, mg/L CaCO3 | 115.4589 | 115.8372 | 115.9525 | 112.6368
|  | Maximum permissible turbidity (ntu) | 1 | [14 empty] | SDS-TBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-02-02 | 9:00 | 116 | 22.5 | 51 | 51 | 600 | 5.8 | 5.7 |  | 11.5 | 0.46109 | 0.50435 | 51.1739 | 13.2118 | 10.2765 | 824.2306 | 292.3941 | 819.0895 | 5.2927 | 45.7073 | 0.22483 | 8.87 |  |  | 324 |  |  | 792.0702 |  | 41.7266 | 789.8078 | 58.9774 | 0.002 |  |  | 0.058491 |  | 93.3333 | 0.058218 | 96.5646 | [8 empty] | SDS-DCAA* | mg/L | 2.2249 | 2.0708 | 2.1479 | 7.1746 | --- | 40.9351 | --- | 83.9667 | 40.7584 | 94.7303 | SDS-DCAA* | mg/L | 3.0375 | --- | 89.3596 | --- | 77.3256 | 89.0007 | 96.5871 | SDS-DCAA* | mg/L | 1.9687 | --- | 24.8236 | --- | 85.304 | 24.7112 | 92.0332 | SDS-DCAA* | mg/L | 2.0108 | --- | 18.2756 | --- | 84.9897 | 18.2 | 88.9516 | Ca-Hdb, mg/L CaCO3 | NA | NA | NA | NA | Ca-Hdb, mg/L CaCO3 | 75.6272 | 75.4935 | 76.3804 | 75.0063
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | <0.1 ppm | [14 empty] | SDS-CDBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-02-02 | 10:00 | 117 | 22.1 | 51 | 51 | 600 | 5.9 | 5.6 |  | 11.5 | 0.46109 | 0.51304 | 51.1739 | 13.4396 | 10.578 | 831.1684 | 294.8232 | 825.8943 | 5.3371 | 45.6629 | 0.23165 | 8.92 |  |  | 325 |  |  | 799.375 |  | 41.5468 | 797.0427 | 59.2243 | 0.002 |  |  | 0.0595 |  | 93.3333 | 0.059217 | 96.6226 | [8 empty] | SDS-TCAA* | mg/L | 1.1823 | BMRL | 1.1823 | #VALUE! | --- | 6.3413 | --- | 55.858 | 6.3178 | 81.2861 | SDS-TCAA* | mg/L | 1.1163 | --- | 14.1338 | --- | 58.3221 | 14.0797 | 92.0715 | SDS-TCAA* | mg/L | 1.0359 | --- | 4.3209 | --- | 61.3239 | 4.3047 | 75.9359 | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | 1: All of the information requested in this field may not be available, but values for all Design | [15 empty] | SDS-DCBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-02-02 | 11:00 | 118 | 22.4 | 51 | 51 | 600 | 5.9 | 6 |  | 11.9 | 0.46109 | 0.4958 | 49.4202 | 13.4396 | 10.4846 | 817.5677 | 289.9989 | 812.3799 | 5.2497 | 45.7503 | 0.22917 | 8.91 |  |  | 323 |  |  | 785.1167 |  | 41.9065 | 782.8446 | 58.7402 | 0.002 |  |  | 0.057533 |  | 93.3333 | 0.05726 | 96.5072 | [8 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  | Parameters must be entered in cells E14:E23, since these parameters are used in calculations. | [15 empty] | SDS-HAA5 | mg/L | 24.1456 | 22.7123 | 23.429 | 6.1176 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-02-02 | 12:00 | 119 | 22.5 | 51 | 51 | 600 | 5.9 | 5.9 |  | 11.8 | 0.46109 | 0.5 | 49.8475 | 13.4396 | 10.4537 | 820.8403 | 291.1597 | 815.6317 | 5.2708 | 45.7292 | 0.2286 | 8.87 | 8.97 | 8.87 | 324 | 543 | 739 | 788 | -6.6306 | 41.7266 | 785.7187 | 58.7639 | 0.002 | 0.035 | 0.059 | 0.058 | 1.6949 | 93.3333 | 0.057725 | 96.5353 | [8 empty] | SDS-DBAA* | mg/L | 1.2691 | 1.2914 | 1.2803 | 1.7418 | --- | 22.2256 | --- | 82.5921 | 22.1302 | 94.2149 | SDS-DBAA* | mg/L | 1.827 | --- | 47.8887 | --- | 75.1577 | 47.6971 | 96.1696 | SDS-DBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Blended Water Quality if HAA5 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if HAA5 Controls the Blend Ratio
[18 empty] | SDS-HAA6 | mg/L | 32.928 | 30.1417 | 31.5348 | 8.8356 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-02-02 | 16:00 | 123 | 22.9 | 51 | 51 | 600 | 6 | 5.9 |  | 11.9 | 0.46109 | 0.5042 | 49.4202 | 13.6673 | 10.5059 | 824.1628 | 292.3065 | 818.8443 | 5.292 | 45.708 | 0.22985 | [27 empty] | SDS-BCAA* | mg/L | 1.0661 | 1.0139 | 1.04 | 5.0192 | --- | 25.4052 | --- | 87.1698 | 25.2942 | 95.8884 | SDS-BCAA* | mg/L | 1.4495 | --- | 56.9195 | --- | 82.118 | 56.6889 | 97.4431 | SDS-BCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Qp/QT (HAA5), % | -177.9751 | -175.2108 | -149.6794 | -158.8738 | Qp/QT (HAA5), % | -20.7895 | -20.4666 | -17.4843 | -18.5583
[18 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-02-03 | 8:00 | 139 | 21.4 | 52 | 53 | 600 | 5.4 | 14.2 |  | 19.6 | 0.46109 | 0.27551 | 29.6122 | 12.3006 | 9.884 | 676.1778 | 239.9768 | 672.252 | 4.3424 | 48.1576 | 0.20524 | [27 empty] | SDS-TBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-THM4b, ug/L | NA | NA | NA | NA | SDS-THM4b, ug/L | NA | NA | NA | NA
[18 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-02-03 | 9:00 | 140 | 21.8 | 52 | 53 | 600 | 5 | 12 |  | 17 | 0.46109 | 0.29412 | 34.2941 | 11.3895 | 9.0442 | 686.1567 | 243.624 | 682.4689 | 4.4069 | 48.0931 | 0.18806 | 9.25 |  |  | 288 |  |  | 667.6667 |  | 48.2014 | 666.0847 | 56.7623 | 0.003 |  |  | 0.04125 |  | 90 | 0.041091 | 92.6991 | [8 empty] | SDS-CDBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-HAA5b, ug/L | NA | NA | NA | NA | SDS-HAA5b, ug/L | NA | NA | NA | NA
[18 empty] | should be reported if measured. | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-02-03 | 10:00 | 141 | 21.4 | 52 | 53 | 600 | 5.4 | 12.1 |  | 17.5 | 0.46109 | 0.30857 | 33.2857 | 12.3006 | 9.884 | 694.1833 | 246.367 | 690.153 | 4.458 | 48.042 | 0.20574 | 9.36 |  |  | 293 |  |  | 673.3719 |  | 47.3022 | 671.6602 | 56.3768 | 0.002 |  |  | 0.042496 |  | 93.3333 | 0.042314 | 95.2734 | [8 empty] | SDS-DCBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TOXb, ug Cl- /L | NA | NA | NA | NA | SDS-TOXb, ug Cl- /L | NA | NA | NA | NA
[45 empty] | 1999-02-03 | 11:00 | 142 | 21.4 | 53 | 53 | 600 | 5.5 | 13 |  | 18.5 | 0.46109 | 0.2973 | 31.4324 | 12.5284 | 10.067 | 687.9463 | 244.127 | 683.8779 | 4.4179 | 48.5821 | 0.20722 | 9.32 |  |  | 292 |  |  | 667.6923 |  | 47.482 | 665.9704 | 56.1542 | 0.002 |  |  | 0.041846 |  | 93.3333 | 0.041664 | 95.1996 | [8 empty] | SDS-HAA5 | mg/L | 6.7705 | 5.7331 | 6.2518 | 16.5936 | --- | 65.4834 | --- | 73.3159 | 65.2135 | 90.4133 | SDS-HAA5 | mg/L | 5.9808 | --- | 151.382 | --- | 74.4726 | 150.7775 | 96.0334 | SDS-HAA5 | mg/L | 3.0046 | --- | 43.8533 | --- | 87.1757 | 43.6525 | 93.117 | SDS-HAA5 | mg/L | 4.1866 | --- | 31.6757 | --- | 82.1307 | 31.5478 | 86.7294 | SDS-CDb, mg/L | NA | NA | NA | NA | SDS-CDb, mg/L | NA | NA | NA | NA
[45 empty] | 1999-02-03 | 12:00 | 143 | 21.4 | 52 | 53 | 600 | 5.6 | 13 |  | 18.6 | 0.46109 | 0.30108 | 31.2581 | 12.7562 | 10.25 | 690.0371 | 244.8424 | 685.882 | 4.4312 | 48.0688 | 0.21324 | 9.39 | 9.51 | 9.44 | 292 | 553 | 653 | 669.7231 | -2.561 | 47.482 | 667.9604 | 56.2848 | 0.001 | 0.032 | 0.045 | 0.042492 | 5.5726 | 96.6667 | 0.042299 | 97.6359 | [8 empty] | SDS-HAA6 | mg/L | 7.8366 | 6.747 | 7.2918 | 14.9428 | --- | 90.8885 | --- | 76.877 | 90.5077 | 91.9434 | SDS-HAA6 | mg/L | 7.4303 | --- | 208.3015 | --- | 76.4378 | 207.4663 | 96.4186 | SDS-HAA6 | mg/L | 3.0046 | --- | 60.0651 | --- | 90.4721 | 59.7846 | 94.9743 | SDS-HAA6 | mg/L | 4.1866 | --- | 43.2555 | --- | 86.7239 | 43.0739 | 90.2804 | TOCb, mg/L | NA | NA | NA | NA | TOCb, mg/L | NA | NA | NA | NA
[45 empty] | 1999-02-03 | 16:00 | 147 | 22.4 | 51 | 52 | 600 | 5.9 | 13.4 |  | 19.3 | 0.46109 | 0.3057 | 30.0881 | 13.4396 | 10.4846 | 692.6321 | 245.6831 | 688.2371 | 4.4475 | 47.0525 | 0.22283 | [27 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | UV254 b, cm-1 | NA | NA | NA | NA | UV254 b, cm-1 | NA | NA | NA | NA
[45 empty] | 1999-02-05 | 8:00 | 176 | 20.8 | 51 | 52 | 600 | 7 | 16.6 | X | 23.6 | 0.46109 | 0.29661 | 24.4237 | 15.9452 | 13.0418 | 687.715 | 243.6473 | 682.5342 | 4.4148 | 47.0852 | 0.27698 | [27 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | Bromideb, ug/L | NA | NA | NA | NA | Bromideb, ug/L | NA | NA | NA | NA
[45 empty] | 1999-02-05 | 10:00 | 178 | 20.9 | 51 | 52 | 600 | 7 | 16.6 |  | 23.6 | 0.46109 | 0.29661 | 24.4237 | 15.9452 | 13.0033 | 687.715 | 243.6473 | 682.5342 | 4.4148 | 47.0852 | 0.27617 | 9.09 | 9.23 | 9.17 | 323 | 530 | 612 | 654.253 | -6.9041 | 41.9065 | 652.3207 | 50.4845 | 0.002 | 0.03 | 0.041 | 0.041807 | -1.9689 | 93.3333 | 0.041575 | 95.1894 | [47 empty] | Alkb, mg/L CaCO3 | NA | NA | NA | NA | Alkb, mg/L CaCO3 | NA | NA | NA | NA
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | T-Hdb, mg/L CaCO3 | NA | NA | NA | NA | T-Hdb, mg/L CaCO3 | NA | NA | NA | NA
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Ca-Hdb, mg/L CaCO3 | NA | NA | NA | NA | Ca-Hdb, mg/L CaCO3 | NA | NA | NA | NA
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Notes: |  |  |  |  | Notes:
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to |  |  |  |  | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | determine the percentage of total flow that must be treated by the membrane process to meet the |  |  |  |  | determine the percentage of total flow that must be treated by the membrane process to meet the
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Stage 1 DBP MCLs. |  |  |  |  | Stage 2 DBP MCLs.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | A 10% factor of safety has been applied all the MCLs. i.e., 72 / 54 mg/L for THM4 and HAA5. |  |  |  |  | A 10% factor of safety has been applied all the MCLs. i.e., 36 / 27 mg/L for THM4 and HAA5.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for |  |  |  |  | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | both parameters and the maximum (Qp/QT) ratio controls the design. |  |  |  |  | both parameters and the maximum (Qp/QT) ratio controls the design.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. |  |  |  |  | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. |  |  |  |  | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. |  |  |  |  | The subscript "b" refers to the blended water quality for a given blend ratio.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL. |  |  |  |  | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. |  |  |  |  | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Note on X24: Alison Gusses: High precision incubator was used for SDS testing
Note on CY25: C. Rice: Consultant verified the bromide concentrations for the 70, 50 and 30 percent runs. The values may be due to bias error since the results are less than 10 percent higher than the feed water.
Note on CY29: Alison Gusses: High precision incubator was used for SDS testing
Note on DL29: Alison Gusses: High precision incubator was used for SDS testing
Note on DV25: C. Rice: Consultant verified the bromide concentrations for the 70, 50 and 30 percent runs. The values may be due to bias error since the results are less than 10 percent higher than the feed water.
Note on DV29: Alison Gusses: High precision incubator was used for SDS testing
Note on EF25: C. Rice: Consultant verified the bromide concentrations for the 70, 50 and 30 percent runs. The values may be due to bias error since the results are less than 10 percent higher than the feed water.
Note on EF29: Alison Gusses: High precision incubator was used for SDS testing