## DCSS1. 1st Quarter
FIELD-SET 1: Membrane A, Run 1 (FILE: Delray1.xls)
Field 1-1: PWS And Treatment Plant Data |  | Field 1-2: Manufacturer Reported Membrane Characteristics1 |  | Field 1-3: RBSMT Design Parameters | [8 empty] | Field 1-4: Foulants And Fouling Indices1 |  | Field 1-5: Pretreatment Used Prior To Membranes1 |  |  | Field 1-6: Feed Water Quality After Pretreatment | [5 empty] | Field 1-7: Membrane Setting Data | [20 empty] | Field 1-8: Membrane Performance Data During Operation With The Test Water | [16 empty] | Field 1-8: Membrane Performance Data During Operation With The Test Water (continued) | [19 empty] | Field 1-8: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 1-9: Permeate And Concentrate Water Quality For Run 1 | [11 empty] | Field 1-10: Permeate And Concentrate Water Quality For Run 2 | [8 empty] | Field 1-11: Permeate And Concentrate Water Quality For Run 3 | [8 empty] | Field 1-12: Permeate And Concentrate Water Quality For Run 4 | [8 empty] | Field 1-13: Blending Calculations For Stage 1 D-DBP MCLs |  |  |  |  | Field 1-14: Blending Calculations For Proposed Stage 2 D-DBP MCLs |  |  |  |  | Field 1-15: Membrane Cost Parameters
|  | General Information |  | Input Design Parameters | [8 empty] | Parameters Evaluated Prior to Pretreatment | [80 empty] | Operating Parameters During Sample Collection | [11 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Feed and Permeate Water Quality Parameters |  |  |  |  | Feed and Permeate Water Quality Parameters |  |  |  |  | General Cost Parameters
PWS Name | Delray Beach Water Department | Membrane manufacturer | Film Tec | [5 empty] | Active membrane area in bench-scale cell, Acell (ft2) | 0.16667 |  |  | Alkalinity (mg/L as CaCO3) | 243 | Process | Description | Scale | Parameter | Units | CF-1 | CF-2 | Average | RPD |  |  |  | Average TDS rejection (decimal fraction) | 0.7 | [5 empty] | TDS concentration of setting solution (mg/L) | 50 | [12 empty] | Average bulk TDS rejection (decimal fraction) | 0.80712 | [45 empty] | Recovery during sample collection (decimal) | 0.69 | [10 empty] | Recovery during sample collection (decimal) | 0.91 | [7 empty] | Recovery during sample collection (decimal) | 0.56722 | [7 empty] | Recovery during sample collection (decimal) | 0.30924 | [8 empty] | RUN ID # |  |  |  |  | RUN ID # |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | FL4500351 | Membrane trade name | NF70 | [5 empty] | Active width of membrane in the bench-scale cell, wcell (ft) | 0.33333 |  |  | Calcium Hardness (mg/L as CaCO3) | 295 | Acidification | Hydrochloric acid to pH 6.5 | Bench | Sampling date | MM/DD/YY | 1999-03-23 | 1999-03-26 | --- | --- | [71 empty] | Feed flow rate during sample collection (mL/min) | 15.3 | [10 empty] | Feed flow rate during sample collection (mL/min) | 11.87 | [7 empty] | Feed flow rate during sample collection (mL/min) | 21.6 | [7 empty] | Feed flow rate during sample collection (mL/min) | 37.1 | [6 empty] | Parameter | 1 | 2 | 3 | 4 | Parameter | 1 | 2 | 3 | 4 | Capital Recovery Interest Rate (%) | 5.75
Water Industry Data Base Number (optional) | NA | Molecular weight cutoff (Daltons) | 200 | [5 empty] | Average yearly temperature of feed water, TavgoC (oC) | 22 |  |  | LSI |  | Antiscalant addition | King Lee PreTreat 0100, 3 ppm by volume | Bench | Sampling time | hh:mm | 13:45 | 10:12 | --- | --- | Date | Time | Setting time | Influent | PI | PC | QI | Qp | QW | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) | Date | Time | Operation time | Influent | PI | PC | QI | Qp | QW | Cleaning Event | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1) | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Influent flow rate during sample collection (mL/min) | 530 | [10 empty] | Influent flow rate during sample collection (mL/min) | 530 | [7 empty] | Influent flow rate during sample collection (mL/min) | 530 | [7 empty] | Influent flow rate during sample collection (mL/min) | 530 | [6 empty] | SDS-THM4F, ug/L | 174.4 | 174.4 | 174.4 | 174.4 | SDS-THM4F, ug/L | 174.4 | 174.4 | 174.4 | 174.4 | Capital Recovery Period (years) | 25
|  | Membrane material (e.g., PVD, polyamide, etc.) | polyamide | [5 empty] | Approximate feed water TDS, TDSF (mg/L) | 545 |  |  | Dissolved iron (mg/L) |  | Cartridge filtration | 5 micron nominal | Bench | Operation time | hh.hh | 43.1 | 110 | --- | --- | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | Indicate with "X" | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) | [39 empty] | SDS-THM4p, ug/L | 27.4 | 64.6 | 20.7 | 12.8 | SDS-THM4p, ug/L | 27.4 | 64.6 | 20.7 | 12.8 | Overhead & Profit Factor (% of construction costs) | 15
Official ICR Contact Person |  | Membrane construction (e.g., thin-film composite) | thin-film composite | [5 empty] | Manufacturer reported TDS rejection, RejTDS (decimal fraction) | 0.7 |  |  | Total iron (mg/L) |  |  |  |  | pH | --- | 6.2 | 6.9 | 6.55 | 10.687 | 1999-03-15 | 13:45 | -5.8207e-11 | [18 empty] | 1999-03-21 | 21:05 | 0.4 | 22.6 | 99 |  | 530 | 10.9 | 20 |  | 30.9 | 0.40107 | 0.35275 | 16.1521 | 24.8787 | 24.4413 | 654.6203 | 124.16 | 643.7108 | 5.2501 | [29 empty] | Permeate and Concentrate Water Quality | [11 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | SDS-HAA5F, ug/L | 197.25 | 197.25 | 197.25 | 197.25 | SDS-HAA5F, ug/L | 197.25 | 197.25 | 197.25 | 197.25 | Special Sitework Factor (% of construction costs) | 5
Mailing Address |  | Membrane hydrophobicity | Hydrophobic | [5 empty] | Temperature normalized MTCW (gfd/psi) | 0.32671 |  |  | Dissolved aluminum (mg/L) |  |  |  |  | Temperature | oC | NR | NR | #DIV/0! | #VALUE! | 1999-03-15 | 14:15 | 0.5 | 22.8 | 76 | 76 | 410 | 11 | 4.7 | 15.7 | 0.31026 | 0.70064 | 25.1146 | 25.1069 | 24.5202 | 98.8974 | 29.1075 | 97.025 | 0.68854 | 75.3115 | 0.32558 | 1999-03-22 | 10:10 | 13.5 | 24.1 | 104 |  | 530 | 11 | 4.6 |  | 15.6 | 0.40107 | 0.70513 | 32.9744 | 25.1069 | 23.5958 | 1090.7845 | 206.8537 | 1072.4388 | 8.7476 |  |  | 5.7 |  |  | 235.17 |  |  | 1023.0717 |  | 49.6963 | 1014.8954 | 76.8282 | 0.05 |  |  | 1.0131 |  | 85.0299 | 1.0031 | 95.0156 | [8 empty] | Parameter | Units | Cp-1 | Cp-1 (dup) | Average | RPD | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | SDS-HAA5p, ug/L | 9.85 | 35.6 | 8 | 5.9 | SDS-HAA5p, ug/L | 9.85 | 35.6 | 8 | 5.9 | Construction Contingencies (% of construction costs) | 15
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Slightly negative charge | [9 empty] | Total aluminum (mg/L) |  |  |  |  | Alkalinity | mg/L as CaCO3 | 9.8 | 5 | 7.4 | 64.8649 | 1999-03-15 | 17:40 | 3.9167 | 24.2 | 76 | 76 | 410 | 11 | 4.7 | 15.7 | 0.31026 | 0.70064 | 25.1146 | 25.1069 | 23.5262 | 98.8974 | 29.1075 | 97.025 | 0.68854 | 75.3115 | 0.31239 | 1999-03-22 | 12:41 | 16 | 24.7 | 105 | 105 | 530 | 11.1 | 4.9 |  | 16 | 0.40107 | 0.69375 | 32.125 | 25.3352 | 23.3918 | 1067.8623 | 202.4752 | 1049.7381 | 8.5633 | 96.4367 | 0.24256 | 5.71 |  |  | 221.13 |  |  | 1025.6035 |  | 52.6995 | 1017.1793 | 78.2605 | 0.043 |  |  | 0.9932 |  | 87.1257 | 0.98325 | 95.6268 | [8 empty] | Sampling date | MM/DD/YY | 1999-03-23 | 1999-03-23 | --- | --- | 1999-03-23 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-03-24 | 1999-03-24 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-03-25 | 1999-03-25 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-03-26 | 1999-03-26 | --- | --- | --- | --- | --- | SDS-TOXF, ug Cl- /L | 939.5 | 939.5 | 939.5 | 939.5 | SDS-TOXF, ug Cl- /L | 939.5 | 939.5 | 939.5 | 939.5 | Engineering Fee Factor (% of construction costs) | 10
Phone Number |  |  |  | Experimental Design1,2 | [8 empty] | Fluoride (mg/L) |  |  |  |  | Total dissolved solids | mg/L | 449 | 486 | 467.5 | 7.9144 | 1999-03-16 | 8:27 | 18.7 | 23.6 | 78 | 78 | 410 | 11 | 4.7 | 15.7 | 0.31026 | 0.70064 | 25.1146 | 25.1069 | 23.9471 | 98.8974 | 29.1075 | 97.025 | 0.68854 | 77.3115 | 0.30975 | 1999-03-22 | 15:55 | 19.2 | 24.5 | 105 | 105 | 530 | 10.6 | 4.7 |  | 15.3 | 0.40107 | 0.69281 | 33.6405 | 24.1939 | 22.4705 | 1065.7591 | 202.2342 | 1048.4886 | 8.5489 | 96.4511 | 0.23297 | 5.67 | 5.97 | 6.06 | 201.474 | 468.272 | 991.706 | 1067.4735 | -7.6401 | 56.904 | 1058.8135 | 80.9717 | 0.032 | 0.355 | 1.018 | 1.0151 | 0.28425 | 90.4192 | 1.0053 | 96.8168 | [8 empty] | Sampling time | hh:mm | NR | NR | --- | --- | NR | --- | --- | --- | --- | --- | Sampling time | hh:mm | NR | NR | --- | --- | --- | --- | --- | Sampling time | hh:mm | NR | NR | --- | --- | --- | --- | --- | Sampling time | hh:mm | NR | NR | --- | --- | --- | --- | --- | SDS-TOXp, ug Cl- /L | 82.6 | 217 | 113 | 41.1 | SDS-TOXp, ug Cl- /L | 82.6 | 217 | 113 | 41.1 | 1998 ENR Construction Cost Index (CCI base year 1913) | 5875
FAX Number |  | Design Parameters |  | ID# | Recovery | FW-design | Dp | PI | QI-cell | Qp | QF | QW | Phosphate (mg/L) |  |  |  |  | Total hardness | mg/L as CaCO3 | 225 | 218 | 221.5 | 3.1603 | 1999-03-16 | 14:02 | 24.2833 | 23.8 | 75 | 74 | 410 | 11 | 4.7 | 15.7 | 0.31026 | 0.70064 | 25.1146 | 25.1069 | 23.806 | 98.8974 | 29.1075 | 97.025 | 0.68854 | 73.8115 | 0.32252 | 1999-03-23 | 10:32 | 37.8 | 25 | 124 | 123 | 530 | 10.9 | 1.27 |  | 12.17 | 0.40107 | 0.89565 | 42.5497 | 24.8787 | 22.7675 | 1704.7768 | 323.3402 | 1676.3661 | 13.6723 | 109.8277 | 0.2073 | 5.75 |  |  | 347.995 |  |  | 1493.1728 |  | 25.5626 | 1481.3969 | 76.509 | 0.056 |  |  | 2.72 |  | 83.2335 | 2.6926 | 97.9202 | [8 empty] | Operation time | hh.hh | 28.4 | 28.4 | --- | --- | 28.4 | --- | --- | --- | --- | --- | Operation time | hh.hh | 51.8 | 51.8 | --- | --- | --- | --- | --- | Operation time | hh.hh | 75.9 | 75.9 | --- | --- | --- | --- | --- | Cumulative time | hr | 99.8 | 99.8 | --- | --- | --- | --- | --- | SDS-CDF, mg/L | 11.195 | 11.195 | 11.195 | 11.195 | SDS-CDF, mg/L | 11.195 | 11.195 | 11.195 | 11.195 | 1998 Producers Price Index (PPI base year 1967 = 100) | 369
E-Mail Address (optional) |  | Design flux, FW (gfd) | 25 |  | (decimal) | (gfd) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | Sulfate (mg/L) | 26.5 |  |  |  | Calcium hardness | mg/L as CaCO3 | 214 | 207 | 210.5 | 3.3254 | 1999-03-17 | 9:04 | 43.3167 | 23.4 | 75 | 74 | 410 | 11 | 4.7 | 15.7 | 0.31026 | 0.70064 | 25.1146 | 25.1069 | 24.0891 | 98.8974 | 29.1075 | 97.025 | 0.68854 | 73.8115 | 0.32636 | 1999-03-23 | 14:32 | 41.9 | 26.2 | 131 | 131 | 530 | 10.9 | 1.14 |  | 12.04 | 0.40107 | 0.90532 | 43.0199 | 24.8787 | 21.9741 | 1754.9256 | 332.8518 | 1725.6792 | 14.0745 | 116.9255 | 0.18793 | 5.8 |  |  | 373.544 |  |  | 1365.8512 |  | 20.0975 | 1355.6473 | 72.4453 | 0.065 |  |  | 2.906 |  | 80.5389 | 2.8768 | 97.7405 | [8 empty] | pH | --- | 6.19 | 6.18 | 6.185 | 0.16168 | 6.66 | --- | --- | --- | --- | --- | pH | --- | 6.34 | 7.43 | --- | --- | --- | --- | --- | pH | --- | 6.94 | 6.72 | --- | --- | --- | --- | --- | pH | --- | 6.8 | 6.6 | --- | --- | --- | --- | --- | SDS-CDp, mg/L | 2.34 | 4.8 | 2.4 | 1.75 | SDS-CDp, mg/L | 2.34 | 4.8 | 2.4 | 1.75 | Labor Rate + Fringe ($/work-hour) | 19.89
|  | Net driving pressure at the design flux, NDP (psi) | 70 | 1 | 0.7 | 25 | 14.3517 | 90.8732 | 531.2481 | 10.952 | 15.6457 | 4.6937 | Calcium (mg/L) |  |  |  |  | Turbidity | ntu | 0.39 | 0.17 | 0.28 | 78.5714 | 1999-03-17 | 11:23 | 45.6333 | 23.9 | 83 | 82 | 530 | 10.9 | 4.7 | 15.6 | 0.40107 | 0.69872 | 32.9744 | 24.8787 | 23.5199 | 98.4521 | 29.1078 | 97.026 | 0.68631 | 81.8137 | 0.28748 | 1999-03-23 | 16:00 | 43.3 | 26.3 | 131 | 131 | 530 | 10.8 | 1.07 |  | 11.87 | 0.40107 | 0.90986 | 43.6504 | 24.6504 | 21.7082 | 1779.3246 | 337.5322 | 1749.9447 | 14.271 | 116.729 | 0.18597 | 5.91 | 6.13 | 6.37 | 363.853 | 483.301 | 2290.497 | 1513.6566 | 33.9158 | 22.1705 | 1501.9417 | 75.7745 | 0.064 | 0.348 | 0.621 | 3.0592 | -392.6302 | 80.8383 | 3.0287 | 97.8869 | [8 empty] | Temperature | oC | NR | NR | #DIV/0! | #VALUE! | NR | --- | --- | --- | --- | --- | Temperature | oC | NR | NR | --- | --- | --- | --- | --- | Temperature | oC | NR | NR | --- | --- | --- | --- | --- | Temperature | oC | NR | NR | --- | --- | --- | --- | --- | TOCF, mg/L | 10.74 | 10.74 | 10.74 | 10.74 | TOCF, mg/L | 10.74 | 10.74 | 10.74 | 10.74 | Labor Overhead Factor (% of labor) | 6
Technical ICR Contact Person |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.357 | 2 | 0.9 | 25 | 39.785 | 116.3065 | 531.2481 | 10.952 | 12.1689 | 1.2169 | Barium (mg/L) | 0.018 |  |  |  | Ammonia | mg NH3-N / L | 0.39 | 0.44 | 0.415 | 12.0482 | 1999-03-17 | 16:35 | 50.8333 | 24.5 | 73 | 72 | 530 | 11 | 4.7 | 15.7 | 0.40107 | 0.70064 | 32.758 | 25.1069 | 23.3185 | 98.7203 | 29.1831 | 97.2771 | 0.68816 | 71.8118 | 0.32472 | 1999-03-24 | 8:48 | 60.1 | 25.8 | 141 | 140 | 530 | 10.7 | 10.9 |  | 21.6 | 0.40107 | 0.49537 | 23.537 | 24.4222 | 21.8274 | 780.9701 | 148.1707 | 768.1947 | 6.2641 | 134.2359 | 0.16261 | 5.9 |  |  | 140.866 |  |  | 788.1407 |  | 69.8682 | 781.6069 | 81.9774 | 0.045 |  |  | 0.6177 |  | 86.5269 | 0.61192 | 92.6461 | [8 empty] | Alkalinity | mg/L as CaCO3 | 4.9 | 5.1 | 5 | 4 | 21.1 | 12.7419 | 39.6117 | 32.4324 | 12.6648 | 60.5206 | Alkalinity | mg/L as CaCO3 | 7.2 | NR | 9.4222 | #VALUE! | 2.7027 | 9.3996 | 23.4008 | Alkalinity | mg/L as CaCO3 | 2.1 | 6.1 | 14.3463 | -135.1851 | 71.6216 | 14.2047 | 85.2162 | Alkalinity | mg/L as CaCO3 | 2.8 | 8 | 9.4593 | -18.2416 | 62.1622 | 9.3872 | 70.1723 | TOCp, mg/L | 1.05 | 2.89 | 0.79 | 0.49 | TOCp, mg/L | 1.05 | 2.89 | 0.79 | 0.49 | Electric Rate ($/kW-h) | 0.05
Mailing Address |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | 3 | 0.5 | 25 | 9.265 | 85.7865 | 531.2481 | 10.952 | 21.9039 | 10.952 | Strontium (mg/L) |  |  |  |  | Total organic carbon | mg/L | 11.08 | 10.4 | 10.74 | 6.3315 | 1999-03-17 | 18:44 | 52.9833 | 24.3 | 77 | 76 | 530 | 11 | 4.7 | 15.7 | 0.40107 | 0.70064 | 32.758 | 25.1069 | 23.4567 | 98.7203 | 29.1831 | 97.2771 | 0.68816 | 75.8118 | 0.30941 | 1999-03-24 | 0:00 | 63.9 | 26.3 | 133 | 133 | 530 | 11.3 | 11.1 |  | 22.4 | 0.40107 | 0.50446 | 22.6607 | 25.7916 | 22.7132 | 790.823 | 149.8995 | 777.158 | 6.3409 | 126.6591 | 0.17933 | 5.8 |  |  | 128.734 |  |  | 812.3699 |  | 72.4633 | 805.0821 | 84.0098 | 0.025 |  |  | 0.64857 |  | 92.515 | 0.64192 | 96.1054 | [8 empty] | Total dissolved solids | mg/L | 205 | 198 | 201.5 | 3.4739 | 992 | 1059.5645 | -6.8109 | 56.8984 | 1051.0187 | 80.8281 | Total dissolved solids | mg/L | 364 | 2290 | 1514 | 33.8865 | 22.139 | 1502.2812 | 75.7702 | Total dissolved solids | mg/L | 126 | 844 | 915.077 | -8.4214 | 73.0481 | 905.9565 | 86.092 | Total dissolved solids | mg/L | 100 | 677.5 | 632.0222 | 6.7126 | 78.6096 | 626.2639 | 84.0323 | UV254 F, cm-1 | 0.334 | 0.334 | 0.334 | 0.334 | UV254 F, cm-1 | 0.334 | 0.334 | 0.334 | 0.334 | Fuel Oil Rate ($/gal) | NA
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 400 | 4 | 0.3 | 25 | 7.085 | 83.6065 | 531.2481 | 10.952 | 36.5066 | 25.5546 | Reactive silica (mg/L as SiO2) | 32.8 |  |  |  | UV254 | cm-1 | 0.33 | 0.338 | 0.334 | 2.3952 | 1999-03-17 | 19:06 | 53.35 | 24.4 | 82 | 82 | 530 | 10.7 | 4.3 | 15 | 0.40107 | 0.71333 | 34.3333 | 24.4222 | 22.7497 | 100.4775 | 29.7147 | 99.0489 | 0.70049 | 81.2995 | 0.27983 | 1999-03-24 | 16:18 | 80.2 | 26.5 | 130 | 129 | 530 | 11 | 10.6 |  | 21.6 | 0.40107 | 0.50926 | 23.537 | 25.1069 | 21.9799 | 795.9947 | 150.9505 | 782.607 | 6.3835 | 123.1165 | 0.17853 | 5.88 | 6.32 | 7.37 | 126.038 | 470.645 | 844.606 | 821.8474 | 2.6946 | 73.04 | 814.6267 | 84.5281 | 0.025 | 0.344 | 2.51 | 0.65466 | 73.9179 | 92.515 | 0.64813 | 96.1427 | [8 empty] | Total hardness | mg/L as CaCO3 | 96.5 | 95.5 | 96 | 1.0417 | 516 | 500.8387 | 2.9382 | 56.6591 | 496.8067 | 80.6766 | Total hardness | mg/L as CaCO3 | 168 | 1030 | 762.4444 | 25.9763 | 24.1535 | 756.3869 | 77.7891 | Total hardness | mg/L as CaCO3 | 68.4 | 424 | 422.156 | 0.4349 | 69.1196 | 418.0672 | 83.639 | Total hardness | mg/L as CaCO3 | 44.9 | 309 | 300.5602 | 2.7313 | 79.7291 | 297.7931 | 84.9224 | UV254 p, cm-1 | 0.0295 | 0.082 | 0.025 | 0.016 | UV254 p, cm-1 | 0.0295 | 0.082 | 0.025 | 0.016 | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Purchase price for an equivalent 8" x 40 " element ($) | 600 | 1: For experimental matrix see Table 4-2 in Part 3 of the ICR Treatment Studies Manual. | [8 empty] | Turbidity (ntu) |  |  |  |  | SUVA | L/(mg*m) | 2.9783 | 3.25 | 3.1142 | 8.7234 | 1999-03-18 | 11:20 | 69.5833 | 24.3 | 84 | 83 | 530 | 11.3 | 4.8 | 16.1 | 0.40107 | 0.70186 | 31.9193 | 25.7916 | 24.0965 | 98.9055 | 29.226 | 97.4199 | 0.68937 | 82.8106 | 0.29098 | 1999-03-25 | 8:37 | 96.5167 | 24.9 | 124 | 124 | 530 | 10.7 | 25.3 |  | 36 | 0.40107 | 0.29722 | 13.7222 | 24.4222 | 22.4159 | 615.8052 | 116.8345 | 605.7316 | 4.9393 | 119.0607 | 0.18827 | 6.53 |  |  | 84.165 |  |  | 629.6219 |  | 81.9968 | 624.1159 | 86.5145 | 0.019 |  |  | 0.46722 |  | 94.3114 | 0.4627 | 95.8936 | [8 empty] | Calcium hardness | mg/L as CaCO3 | 91.3 | 90.8 | 91.05 | 0.54915 | 491 | 476.3726 | 2.9791 | 56.7458 | 472.535 | 80.7316 | Calcium hardness | mg/L as CaCO3 | 160 | 981 | 721.1111 | 26.4922 | 23.9905 | 715.3932 | 77.6347 | Calcium hardness | mg/L as CaCO3 | 65.1 | 404 | 401.0642 | 0.72667 | 69.0736 | 397.181 | 83.6095 | Calcium hardness | mg/L as CaCO3 | 42.6 | 294 | 285.6654 | 2.8349 | 79.7625 | 283.0346 | 84.9488 | BromideF, ug/L | 116.5 | 116.5 | 116.5 | 116.5 | BromideF, ug/L | 116.5 | 116.5 | 116.5 | 116.5 | Current Process Water Rate ($/1000 gal) | 0.41
FAX Number |  | Maximum flow rate to the 8" x 40" element, QI, max (gpm) | 75 | 2: Flow rates and pressures may need to be adjusted in order to obtain the desired operating conditions. | [8 empty] | SDI |  |  |  |  | Bromide | mg/L | 128 | 105 | 116.5 | 19.7425 | [21 empty] | 1999-03-25 | 14:01 | 101.9167 | 25.1 | 125 | 124 | 530 | 11 | 25.2 |  | 36.2 | 0.40107 | 0.30387 | 13.6409 | 25.1069 | 22.9086 | 620.2262 | 117.6182 | 609.7947 | 4.9739 | 119.5261 | 0.19166 | 6.58 |  |  | 83.622 |  |  | 635.0658 |  | 82.1129 | 629.3433 | 86.7128 | 0.016 |  |  | 0.47281 |  | 95.2096 | 0.46807 | 96.5817 | [8 empty] | Turbidity | ntu | BMRL | BMRL | #DIV/0! | #VALUE! | 0.37 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu | BMRL | 0.4 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | 0.15 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | 0.19 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Bromidep, ug/L | 60.65 | 99.786 | 47.834 | 26 | Bromidep, ug/L | 60.65 | 99.786 | 47.834 | 26 | Modifications to Existing Plant (% of construction costs) | 10
E-Mail Address (optional) |  | Minimum flow rate to the 8" x 40" element, QI, min (gpm) | 24.7 | [9 empty] | MFI |  |  |  |  | SDS-Cl2 dose | mg/L | 14.85 | 12.5 | 13.675 | 17.1846 | [21 empty] | 1999-03-25 | 16:09 | 104.05 | 25.2 | 125 | 124 | 530 | 11 | 25.3 |  | 36.3 | 0.40107 | 0.30303 | 13.6006 | 25.1069 | 22.841 | 619.6685 | 117.5124 | 609.2464 | 4.9695 | 119.5305 | 0.19109 | [27 empty] | Ammonia | mg NH3-N / L | 0.16 | 0.17 | 0.165 | 6.0606 | 0.56 | 0.97145 | -73.4735 | 60.241 | 0.96342 | 82.8735 | Ammonia | mg NH3-N / L | 0.36 | 1.45 | 0.97111 | 33.0268 | 13.253 | 0.96488 | 62.6898 | Ammonia | mg NH3-N / L | 0.18 | 0.63 | 0.723 | -14.7612 | 56.6265 | 0.71672 | 74.8856 | Ammonia | mg NH3-N / L | 0.18 | 0.51 | 0.5202 | -2.0009 | 56.6265 | 0.51652 | 65.1516 | AlkF, mg/L CaCO3 | 7.4 | 7.4 | 7.4 | 7.4 | AlkF, mg/L CaCO3 | 7.4 | 7.4 | 7.4 | 7.4
|  | Total width of all membrane envelopes in the 8" x 40" element, w (ft) | 58.6667 | [9 empty] | MPFI |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | SDS-Free Cl2 residual | mg/L | 3.42 | 1.54 | 2.48 | 75.8065 | [21 empty] | 1999-03-27 | 8:40 | 144.5667 | 22.7 | 124 | 124 | 530 | 11.4 | 25.7 | X | 37.1 | 0.40107 | 0.30728 | 13.2857 | 26.0199 | 25.487 | 622.5387 | 117.983 | 611.686 | 4.9913 | 119.0087 | 0.21416 | 6.34 | 6.42 | 6.45 | 99.912 | 507.031 | 677.69 | 630.5546 | 6.9553 | 78.6284 | 624.8477 | 84.0102 | 0.018 | 0.331 | 0.478 | 0.47417 | 0.801 | 94.6108 | 0.46927 | 96.1642 | [8 empty] | Total organic carbon | mg/L | 1.05 | 1.05 | 1.05 | 0 | 35 | 32.3081 | 7.6912 | 90.2235 | 31.9968 | 96.7184 | Total organic carbon | mg/L | 2.89 | 107 | 90.1122 | 15.783 | 73.0912 | 89.2234 | 96.7609 | Total organic carbon | mg/L | 0.79 | 24.1 | 23.7807 | 1.325 | 92.6443 | 23.5149 | 96.6404 | Total organic carbon | mg/L | 0.49 | 15.02 | 15.3287 | -2.0553 | 95.4376 | 15.1681 | 96.7695 | Alkp, mg/L CaCO3 | 5 | 7.2 | 2.1 | 2.8 | Alkp, mg/L CaCO3 | 5 | 7.2 | 2.1 | 2.8
Plant Name | Lime Softening Plant | Feed spacer thickness in the 8" x 40" element, T (ft) | 0.0023333 | [9 empty] | pH | 7.2 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | SDS-Cl2 demand | mg/L | 11.43 | 10.96 | 11.195 | 4.1983 | [70 empty] | UV254 | cm-1 | 0.029 | 0.03 | 0.0295 | 3.3898 | 1.11 | 1.0118 | 8.8506 | 91.1677 | 1.002 | 97.0558 | UV254 | cm-1 | 0.082 | 3.2 | 2.882 | 9.9375 | 75.4491 | 2.8535 | 97.1263 | UV254 | cm-1 | 0.025 | 0.757 | 0.73898 | 2.3802 | 92.515 | 0.73073 | 96.5788 | UV254 | cm-1 | 0.016 | 0.478 | 0.47636 | 0.34267 | 95.2096 | 0.47138 | 96.6057 | T-HdF, mg/L CaCO3 | 221.5 | 221.5 | 221.5 | 221.5 | T-HdF, mg/L CaCO3 | 221.5 | 221.5 | 221.5 | 221.5
Treatment Plant Category | SOFT | [11 empty] | Chloride (mg/L) | 59.9 | is to list the pretreatment processes used in this particular RBSMT run. |  |  | SDS-Chlorination temp. | oC | 20 | 20 | 20 | 0 | [70 empty] | SUVA | L/(mg*m) | 2.7619 | 2.8571 | 2.8095 | 3.3898 | 3.1714 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 2.8374 | 2.9907 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 3.1646 | 3.1411 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 3.2653 | 3.1824 | --- | --- | --- | --- | --- | T-Hdp, mg/L CaCO3 | 96 | 168 | 68.4 | 44.9 | T-Hdp, mg/L CaCO3 | 96 | 168 | 68.4 | 44.9
Process Train Name | NA | Additional Information | [10 empty] | Mg (mg/L) | 44 |  |  |  | SDS-Chlorination pH | --- | 7.42 | 7.52 | 7.47 | 1.3387 | [70 empty] | Bromide | mg/L | 59.6 | 61.7 | 60.65 | 3.4625 | --- | 240.8113 | --- | 47.9399 | 239.017 | 74.6252 | Bromide | mg/L | 99.786 | --- | 285.4971 | --- | 14.3468 | 283.6047 | 64.8151 | Bromide | mg/L | 47.834 | --- | 206.4951 | --- | 58.9408 | 204.6612 | 76.6277 | Bromide | mg/L | 26 | --- | 157.015 | --- | 77.6824 | 155.597 | 83.2902 | Ca-HdF, mg/L CaCO3 | 210.5 | 210.5 | 210.5 | 210.5 | Ca-HdF, mg/L CaCO3 | 210.5 | 210.5 | 210.5 | 210.5
ICR Treatment Plant Identification Number | 1086 | Design cross-flow velocity (fps) | Unknown | [9 empty] | Potassium (mg/L) | 25.1 |  |  |  | SDS-Incubation time | hours | 22.9 | 21.6 | 22.25 | 5.8427 | [70 empty] | SDS-Cl2 dose | mg/L | 3.52 | 3.52 | 3.52 | 0 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 5.75 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 3.12 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2.65 | --- | --- | --- | --- | --- | --- | Ca-Hdp, mg/L CaCO3 | 91.05 | 160 | 65.1 | 42.6 | Ca-Hdp, mg/L CaCO3 | 91.05 | 160 | 65.1 | 42.6
PWSID Number of Plant (if assigned) | 45-00351 | Required influent flow to permeate flow rate ratio, QI:Qp | 1.54 | [9 empty] | Strontium (mg/L) | 1.14 |  |  |  | SDS-TOX | mg Cl- /L | 970 | 909 | 939.5 | 6.4928 | [70 empty] | SDS-Free Cl2 residual | mg/L | 1.16 | 1.2 | 1.18 | 3.3898 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.95 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.72 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.9 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 18 | Maximum element recovery (%) | 15 | [14 empty] | SDS-CHCl3 | mg/L | 155 | 138 | 146.5 | 11.6041 | [70 empty] | SDS-Cl2 demand | mg/L | 2.36 | 2.32 | 2.34 | 1.7094 | --- | 30.9045 | --- | 79.0978 | 30.62 | 92.3579 | SDS-Cl2 demand | mg/L | 4.8 | --- | 75.8556 | --- | 57.1237 | 75.1315 | 93.6112 | SDS-Cl2 demand | mg/L | 2.4 | --- | 22.7219 | --- | 78.5619 | 22.487 | 89.3272 | SDS-Cl2 demand | mg/L | 1.75 | --- | 15.4233 | --- | 84.368 | 15.2753 | 88.5436 | Blended Water Quality if THM4 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if THM4 Controls the Blend Ratio
Historical Average Water Temperature (oC) | 20 | Variability of design flux (%) | 10 | [14 empty] | SDS-BDCM | mg/L | 27.6 | 22.8 | 25.2 | 19.0476 | [70 empty] | SDS-Chlorination temp. | oC | 20 | 20 | 20 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 20 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 20 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 20 | --- | --- | --- | --- | --- | --- | Qp/QT (THM4), % | 69.6599 | 93.2605 | 66.6233 | 63.3663 | Qp/QT (THM4), % | 94.1497 | 126.0474 | 90.0455 | 85.6436
State Approved Plant Capacity (MGD) | 22.4 | Rejection of reference solute and conditions of test | 95% | [14 empty] | SDS-DBCM | mg/L | 2.8 | 2.6 | 2.7 | 7.4074 | [70 empty] | SDS-Chlorination pH | --- | 7.48 | 7.59 | 7.535 | 1.4599 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.47 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.44 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.54 | --- | --- | --- | --- | --- | --- | SDS-THM4b, ug/L | 72 | 72 | 72 | 72 | SDS-THM4b, ug/L | 36 | NA | 36 | 36
|  | (e.g., solute type and concentration) | 2000 ppm MgSO4 | [9 empty] | Sodium (mg/L) | 32.8 |  |  |  | SDS-CHBr3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [70 empty] | SDS-Incubation time | hours | 25.2 | 25.2 | 25.2 | 0 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 25.2 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24.95 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24.9 | --- | --- | --- | --- | --- | --- | SDS-HAA5b, ug/L | 66.7074 | 46.4944 | 71.1654 | 75.9985 | SDS-HAA5b, ug/L | 20.8135 | NA | 26.8388 | 33.371
|  | Variability of rejection of reference solute (%) | 3 | [9 empty] | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | SDS-THM4 | mg/L | 185.4 | 163.4 | 174.4 | 12.6147 | [70 empty] | SDS-TOX | mg Cl- /L | 78.5 | 86.7 | 82.6 | 9.9274 | --- | 2846.7935 | --- | 91.2081 | 2819.2637 | 97.0702 | SDS-TOX | mg Cl- /L | 217 | --- | 8244.7778 | --- | 76.9026 | 8162.9725 | 97.3417 | SDS-TOX | mg Cl- /L | 113 | --- | 2022.728 | --- | 87.9723 | 2000.6547 | 94.3518 | SDS-TOX | mg Cl- /L | 41.1 | --- | 1341.6951 | --- | 95.6253 | 1327.6183 | 96.9042 | SDS-TOXb, ug Cl- /L | 342.5846 | 265.6931 | 388.8585 | 370.2168 | SDS-TOXb, ug Cl- /L | 132.7316 | NA | 195.2736 | 170.0782
|  | Standard testing recovery (%) | 15 | [9 empty] | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | SDS-MCAA* | mg/L | 6.9 | 5.7 | 6.3 | 19.0476 | [70 empty] | SDS-CHCl3 | mg/L | 9.5 | 10.1 | 9.8 | 6.1224 | --- | 450.7677 | --- | 93.3106 | 446.376 | 97.8045 | SDS-CHCl3 | mg/L | 35.4 | --- | 1269.8444 | --- | 75.8362 | 1257.2651 | 97.1844 | SDS-CHCl3 | mg/L | 8.2 | --- | 327.7588 | --- | 94.4027 | 324.0653 | 97.4696 | SDS-CHCl3 | mg/L | 5.2 | --- | 209.7571 | --- | 96.4505 | 207.5431 | 97.4945 | SDS-CDb, mg/L | 5.0266 | 5.231 | 5.3355 | 5.21 | SDS-CDb, mg/L | 2.858 | NA | 3.2755 | 3.106
|  | Standard testing pH | 7 | [14 empty] | SDS-DCAA* | mg/L | 70.4 | 55.5 | 62.95 | 23.6696 | [70 empty] | SDS-BDCM | mg/L | 9.7 | 10.2 | 9.95 | 5.0251 | --- | 59.1435 | --- | 60.5159 | 58.6536 | 83.036 | SDS-BDCM | mg/L | 20.5 | --- | 72.7222 | --- | 18.6508 | 72.1901 | 71.6027 | SDS-BDCM | mg/L | 7.7 | --- | 48.1359 | --- | 69.4444 | 47.6685 | 83.8468 | SDS-BDCM | mg/L | 4.7 | --- | 34.3774 | --- | 81.3492 | 34.0562 | 86.1993 | TOCb, mg/L | 3.99 | 3.4191 | 4.111 | 4.245 | TOCb, mg/L | 1.6169 | NA | 1.7805 | 1.9615
|  | Acceptable range of operating pressures | <250 psi | [14 empty] | SDS-TCAA* | mg/L | 138 | 118 | 128 | 15.625 | [70 empty] | SDS-DBCM | mg/L | 6.9 | 7.3 | 7.1 | 5.6338 | --- | -7.0935 | --- | -162.963 | -6.9522 | 202.1261 | SDS-DBCM | mg/L | 8.7 | --- | -57.9667 | --- | -222.2222 | -57.2873 | 115.1866 | SDS-DBCM | mg/L | 4.8 | --- | -0.052303 | --- | -77.7778 | 0.0037813 | -126841.2947 | SDS-DBCM | mg/L | 2.9 | --- | 2.6105 | --- | -7.4074 | 2.6136 | -10.9582 | UV254 b, cm-1 | 0.12189 | 0.098984 | 0.12813 | 0.1325 | UV254 b, cm-1 | 0.047314 | NA | 0.055759 | 0.061653
|  | Acceptable range of operating pH values | 3-9 | [14 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [70 empty] | SDS-CHBr3 | mg/L | BMRL | 1.1 | 1.1 | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | Bromideb, ug/L | 77.595 | 100.9124 | 70.7525 | 59.1535 | Bromideb, ug/L | 63.9174 | NA | 54.6693 | 38.9926
|  | Typical pressure drop across a single element (psi) | 5 | [14 empty] | SDS-DBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [70 empty] | SDS-THM4 | mg/L | 26.1 | 28.7 | 27.4 | 9.4891 | --- | 501.5935 | --- | 84.289 | 496.8708 | 94.4855 | SDS-THM4 | mg/L | 64.6 | --- | 1284.6 | --- | 62.9587 | 1272.1679 | 94.9221 | SDS-THM4 | mg/L | 20.7 | --- | 375.8424 | --- | 88.1307 | 371.7375 | 94.4316 | SDS-THM4 | mg/L | 12.8 | --- | 246.745 | --- | 92.6606 | 244.2129 | 94.7587 | Alkb, mg/L CaCO3 | 5.7282 | 7.2135 | 3.869 | 4.4851 | Alkb, mg/L CaCO3 | 5.1404 | NA | 2.6276 | 3.4604
|  | Maximum permissible SDI | 5 | [14 empty] | SDS-BCAA* | mg/L | 8.6 | 7.6 | 8.1 | 12.3457 | [70 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | 2.2 | --- | 47.7556 | --- | 65.0794 | 47.2913 | 95.348 | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | T-Hdb, mg/L CaCO3 | 134.0769 | 171.6056 | 119.4997 | 109.595 | T-Hdb, mg/L CaCO3 | 103.3422 | NA | 83.6403 | 70.2535
|  | Maximum permissible turbidity (ntu) | 1 | [14 empty] | SDS-TBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [70 empty] | SDS-DCAA* | mg/L | 3.9 | 3.9 | 3.9 | 0 | --- | 194.3839 | --- | 93.8046 | 192.4868 | 97.9739 | SDS-DCAA* | mg/L | 12.8 | --- | 570.0222 | --- | 79.6664 | 564.344 | 97.7319 | SDS-DCAA* | mg/L | 3.7 | --- | 140.6043 | --- | 94.1223 | 139.0219 | 97.3385 | SDS-DCAA* | mg/L | 2.7 | --- | 89.9227 | --- | 95.7109 | 88.9786 | 96.9656 | Ca-Hdb, mg/L CaCO3 | 127.2913 | 163.4035 | 113.6297 | 104.1079 | Ca-Hdb, mg/L CaCO3 | 98.0382 | NA | 79.5738 | 66.7045
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | 1000 ppm-hrs | [14 empty] | SDS-CDBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [70 empty] | SDS-TCAA* | mg/L | 5 | 4.2 | 4.6 | 17.3913 | --- | 402.6645 | --- | 96.4062 | 398.7 | 98.8463 | SDS-TCAA* | mg/L | 19 | --- | 1230.1111 | --- | 85.1562 | 1217.7695 | 98.4398 | SDS-TCAA* | mg/L | 4.3 | --- | 290.1238 | --- | 96.6406 | 286.8201 | 98.5008 | SDS-TCAA* | mg/L | 3.2 | --- | 183.8704 | --- | 97.5 | 181.9149 | 98.2409
|  | 1: All of the information requested in this field may not be available, but values for all Design | [15 empty] | SDS-DCBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [70 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  | Parameters must be entered in cells E14:E23, since these parameters are used in calculations. | [15 empty] | SDS-HAA5 | mg/L | 215.3 | 179.2 | 197.25 | 18.3016 | [70 empty] | SDS-DBAA* | mg/L | 1.3 | 1.4 | 1.35 | 7.4074 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DBAA* | mg/L | 1.6 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | Blended Water Quality if HAA5 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if HAA5 Controls the Blend Ratio
[18 empty] | SDS-HAA6 | mg/L | 223.9 | 186.8 | 205.35 | 18.0667 | [70 empty] | SDS-BCAA* | mg/L | 3 | 3.2 | 3.1 | 6.4516 | --- | 19.229 | --- | 61.7284 | 19.0684 | 83.7427 | SDS-BCAA* | mg/L | 5.9 | --- | 30.3444 | --- | 27.1605 | 30.0953 | 80.3956 | SDS-BCAA* | mg/L | 2.4 | --- | 15.5705 | --- | 70.3704 | 15.4183 | 84.4341 | SDS-BCAA* | mg/L | 1.7 | --- | 10.9651 | --- | 79.0123 | 10.8649 | 84.3532 | Qp/QT (HAA5), % | 76.4408 | 88.6174 | 75.6935 | 74.8628 | Qp/QT (HAA5), % | 90.8485 | 105.3201 | 89.9604 | 88.9731
[18 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [75 empty] | SDS-TBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-THM4b, ug/L | 62.0321 | 77.0981 | 58.059 | 53.4217 | SDS-THM4b, ug/L | 40.8528 | NA | 36.1309 | 30.6195
[18 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, | [75 empty] | SDS-CDBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-HAA5b, ug/L | 54 | 54 | 54 | 54 | SDS-HAA5b, ug/L | 27 | NA | 27 | 27
[18 empty] | should be reported if measured. | [75 empty] | SDS-DCBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TOXb, ug Cl- /L | 284.4791 | 299.2394 | 313.893 | 266.9325 | SDS-TOXb, ug Cl- /L | 161.0196 | NA | 195.9775 | 140.1658
[94 empty] | SDS-HAA5 | mg/L | 10.2 | 9.5 | 9.85 | 7.1066 | --- | 614.3661 | --- | 95.0063 | 608.3455 | 98.3809 | SDS-HAA5 | mg/L | 35.6 | --- | 1831.7111 | --- | 81.9518 | 1813.4082 | 98.0368 | SDS-HAA5 | mg/L | 8 | --- | 445.285 | --- | 95.9442 | 440.2307 | 98.1828 | SDS-HAA5 | mg/L | 5.9 | --- | 282.9134 | --- | 97.0089 | 279.9152 | 97.8922 | SDS-CDb, mg/L | 4.4262 | 5.5279 | 4.5378 | 4.1242 | SDS-CDb, mg/L | 3.1504 | NA | 3.283 | 2.7915
[94 empty] | SDS-HAA6 | mg/L | 13.2 | 12.7 | 12.95 | 3.861 | --- | 633.5952 | --- | 93.6937 | 627.4139 | 97.936 | SDS-HAA6 | mg/L | 41.5 | --- | 1862.0556 | --- | 79.7906 | 1843.5036 | 97.7489 | SDS-HAA6 | mg/L | 10.4 | --- | 460.8555 | --- | 94.9355 | 455.649 | 97.7175 | SDS-HAA6 | mg/L | 7.6 | --- | 293.8786 | --- | 96.299 | 290.7801 | 97.3863 | TOCb, mg/L | 3.3329 | 3.7835 | 3.2085 | 3.0666 | TOCb, mg/L | 1.9368 | NA | 1.7889 | 1.6203
[94 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | UV254 b, cm-1 | 0.10124 | 0.11068 | 0.10011 | 0.095936 | UV254 b, cm-1 | 0.057366 | NA | 0.056022 | 0.051066
[94 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | Bromideb, ug/L | 73.8078 | 101.6885 | 64.5243 | 48.7492 | Bromideb, ug/L | 65.7611 | NA | 54.7278 | 35.9794
[133 empty] | Alkb, mg/L CaCO3 | 5.5654 | 7.2228 | 3.3882 | 3.9563 | Alkb, mg/L CaCO3 | 5.2196 | NA | 2.6321 | 3.3072
[133 empty] | T-Hdb, mg/L CaCO3 | 125.5668 | 174.0897 | 105.6132 | 89.2923 | T-Hdb, mg/L CaCO3 | 107.4852 | NA | 83.7707 | 64.3735
[133 empty] | Ca-Hdb, mg/L CaCO3 | 119.1915 | 165.7482 | 100.4416 | 84.8053 | Ca-Hdb, mg/L CaCO3 | 101.9815 | NA | 79.6976 | 61.1142
[133 empty] | Notes: |  |  |  |  | Notes:
[133 empty] | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to |  |  |  |  | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to
[133 empty] | determine the percentage of total flow that must be treated by the membrane process to meet the |  |  |  |  | determine the percentage of total flow that must be treated by the membrane process to meet the
[133 empty] | Stage 1 DBP MCLs. |  |  |  |  | Stage 2 DBP MCLs.
[133 empty] | A 10% factor of safety has been applied all the MCLs. i.e., 72 / 54 mg/L for THM4 and HAA5. |  |  |  |  | A 10% factor of safety has been applied all the MCLs. i.e., 36 / 27 mg/L for THM4 and HAA5.
[133 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for |  |  |  |  | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for
[133 empty] | both parameters and the maximum (Qp/QT) ratio controls the design. |  |  |  |  | both parameters and the maximum (Qp/QT) ratio controls the design.
[133 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. |  |  |  |  | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[133 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. |  |  |  |  | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[133 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. |  |  |  |  | The subscript "b" refers to the blended water quality for a given blend ratio.
[133 empty] | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL. |  |  |  |  | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL.
[133 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. |  |  |  |  | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
Note on X24: TSC_ADM: Reported SDS temperature is a measured value - the consultant used an incubator for SDS testing.
Note on CY29: TSC_ADM: Reported SDS temperature is a measured value - the consultant used an incubator for SDS testing.
Note on DL29: TSC_ADM: Reported SDS temperature is a measured value - the consultant used an incubator for SDS testing.
Note on DV29: TSC_ADM: Reported SDS temperature is a measured value - the consultant used an incubator for SDS testing.
Note on EF29: TSC_ADM: Reported SDS temperature is a measured value - the consultant used an incubator for SDS testing.
Note on EH20: TSC_ADM: Reviewer changed reported value of 0.02 ntu to BMRL, because MRL was reported as 0.05 ntu in Summary Report
Print All Fields

## DCSS1. 2nd Quarter
FIELD-SET 2: Membrane B, Run 1 (FILE: Delray1.xls)
Field 2-1: PWS And Treatment Plant Data |  | Field 2-2: Manufacturer Reported Membrane Characteristics1 |  | Field 2-3: RBSMT Design Parameters | [8 empty] | Field 2-4: Foulants And Fouling Indices1 |  | Field 2-5: Pretreatment Used Prior To Membranes1 |  |  | Field 2-6: Feed Water Quality After Pretreatment | [5 empty] | Field 2-7: Membrane Setting Data | [20 empty] | Field 2-8: Membrane Performance Data During Operation With The Test Water | [16 empty] | Field 2-8: Membrane Performance Data During Operation With The Test Water (continued) | [19 empty] | Field 2-8: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 2-9: Permeate And Concentrate Water Quality For Run 1 | [11 empty] | Field 2-10: Permeate And Concentrate Water Quality For Run 2 | [8 empty] | Field 2-11: Permeate And Concentrate Water Quality For Run 3 | [8 empty] | Field 2-12: Permeate And Concentrate Water Quality For Run 4 | [8 empty] | Field 2-13: Blending Calculations For Stage 1 D-DBP MCLs |  |  |  |  | Field 2-14: Blending Calculations For Proposed Stage 2 D-DBP MCLs |  |  |  |  | Field 2-15: Membrane Cost Parameters
|  | General Information |  | Input Design Parameters | [8 empty] | Parameters Evaluated Prior to Pretreatment | [80 empty] | Operating Parameters During Sample Collection | [11 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Feed and Permeate Water Quality Parameters |  |  |  |  | Feed and Permeate Water Quality Parameters |  |  |  |  | General Cost Parameters
PWS Name | Delray Beach Water Department | Membrane manufacturer | Film Tec | [5 empty] | Active membrane area in bench-scale cell, Acell (ft2) | 0.16667 |  |  | Alkalinity (mg/L as CaCO3) | 243 | Process | Description | Scale | Parameter | Units | CF-1 | CF-2 | Average | RPD |  |  |  | Average TDS rejection (decimal fraction) | 0.7 | [5 empty] | TDS concentration of setting solution (mg/L) | 50 | [12 empty] | Average bulk TDS rejection (decimal fraction) | 0.68131 | [45 empty] | Recovery during sample collection (decimal) | 0.68 | [10 empty] | Recovery during sample collection (decimal) | 0.9 | [7 empty] | Recovery during sample collection (decimal) | 0.5 | [7 empty] | Recovery during sample collection (decimal) | 0.27 | [8 empty] | RUN ID # |  |  |  |  | RUN ID # |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | FL4500351 | Membrane trade name | NF200B-400 | [5 empty] | Active width of membrane in the bench-scale cell, wcell (ft) | 0.33333 |  |  | Calcium Hardness (mg/L as CaCO3) | 295 | Acidification | Hydrochloric acid to pH 6.5 | Bench | Sampling date | MM/DD/YY | 1999-04-20 | 1999-04-23 | --- | --- | [71 empty] | Feed flow rate during sample collection (mL/min) | 13.2 | [10 empty] | Feed flow rate during sample collection (mL/min) | 10.1 | [7 empty] | Feed flow rate during sample collection (mL/min) | 19 | [7 empty] | Feed flow rate during sample collection (mL/min) | 29.4 | [6 empty] | Parameter | 1 | 2 | 3 | 4 | Parameter | 1 | 2 | 3 | 4 | Capital Recovery Interest Rate (%) | 5.75
Water Industry Data Base Number (optional) | NA | Molecular weight cutoff (Daltons) | 200-400 | [5 empty] | Average yearly temperature of feed water, TavgoC (oC) | 22 |  |  | LSI |  | Antiscalant addition | King Lee PreTreat 0100, 3 ppm by volume | Bench | Sampling time | hh:mm | NR | NR | --- | --- | Date | Time | Setting time | Influent | PI | PC | QI | Qp | QW | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) | Date | Time | Operation time | Influent | PI | PC | QI | Qp | QW | Cleaning Event | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1) | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Influent flow rate during sample collection (mL/min) | 344 | [10 empty] | Influent flow rate during sample collection (mL/min) | 344 | [7 empty] | Influent flow rate during sample collection (mL/min) | 344 | [7 empty] | Influent flow rate during sample collection (mL/min) | 344 | [6 empty] | SDS-THM4F, ug/L | 165.5 | 165.5 | 165.5 | 165.5 | SDS-THM4F, ug/L | 165.5 | 165.5 | 165.5 | 165.5 | Capital Recovery Period (years) | 25
|  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide | [5 empty] | Approximate feed water TDS, TDSF (mg/L) | 545 |  |  | Dissolved iron (mg/L) |  | Cartridge filtration | 5 micron nominal | Bench | Operation time | hh.hh | 82.9 | 154.7 | --- | --- | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | Indicate with "X" | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) | [39 empty] | SDS-THM4p, ug/L | 37.25 | 45.1 | 26.8 | 37.8 | SDS-THM4p, ug/L | 37.25 | 45.1 | 26.8 | 37.8 | Overhead & Profit Factor (% of construction costs) | 15
Official ICR Contact Person |  | Membrane construction (e.g., thin-film composite) | Thin-Film Composite | [5 empty] | Manufacturer reported TDS rejection, RejTDS (decimal fraction) | 0.7 |  |  | Total iron (mg/L) |  |  |  |  | pH | --- | 6.02 | 6.71 | 6.365 | 10.8405 | 1999-04-16 | 13:27 | 0 | [18 empty] | 1999-04-19 | 8:29 | 0 | [46 empty] | Permeate and Concentrate Water Quality | [11 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | SDS-HAA5F, ug/L | 129 | 129 | 129 | 129 | SDS-HAA5F, ug/L | 129 | 129 | 129 | 129 | Special Sitework Factor (% of construction costs) | 5
Mailing Address |  | Membrane hydrophobicity | Hydrophilic | [5 empty] | Temperature normalized MTCW (gfd/psi) | 0.2599 |  |  | Dissolved aluminum (mg/L) |  |  |  |  | Temperature | oC | NR | NR | #DIV/0! | #VALUE! | 1999-04-16 | 15:23 | 1.8 | 24.3 | 88.8 | 88.4 | 380 | 9.2 | 4 | 13.2 | 0.28756 | 0.69697 | 27.7879 | 20.9985 | 19.6184 | 98.3184 | 28.992 | 96.64 | 0.68487 | 87.9151 | 0.22315 | 1999-04-19 | 10:45 | 2.3 | NR | 107.7 | 107.3 | 344 | 9.2 | 4.1 |  | 13.3 | 0.26032 | 0.69173 | 24.8647 | 20.9985 | #VALUE! | 1009.6905 | 315.8635 | 991.1346 | 6.8455 | 100.6545 | #VALUE! | 6.18 |  |  | 342.557 |  |  | 949.7928 |  | 35.3361 | 941.6728 | 63.6225 | 0.039 |  |  | 0.98946 |  | 88.253 | 0.97675 | 96.0072 | [8 empty] | Parameter | Units | Cp-1 | Cp-1 (dup) | Average | RPD | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | SDS-HAA5p, ug/L | 13.75 | 23.9 | 16.2 | 12.5 | SDS-HAA5p, ug/L | 13.75 | 23.9 | 16.2 | 12.5 | Construction Contingencies (% of construction costs) | 15
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Highly Negative | [9 empty] | Total aluminum (mg/L) |  |  |  |  | Alkalinity | mg/L as CaCO3 | 3.5 | 3.1 | 3.3 | 12.1212 | 1999-04-17 | 10:30 | 20.9 | 24.5 | 88.7 | 88.5 | 380 | 9.2 | 4 | 13.2 | 0.28756 | 0.69697 | 27.7879 | 20.9985 | 19.5027 | 98.3184 | 28.992 | 96.64 | 0.68487 | 87.9151 | 0.22184 | 1999-04-19 | 14:20 | 5.8 | 24.2 | 107.6 | 107.3 | 344 | 9.2 | 4.2 |  | 13.4 | 0.26032 | 0.68657 | 24.6716 | 20.9985 | 19.6764 | 1002.9098 | 313.7423 | 984.4785 | 6.7995 | 100.6505 | 0.19549 | 6.17 |  |  | 339.865 |  |  | 945.6886 |  | 35.8443 | 937.5874 | 63.7511 | 0.036 |  |  | 0.98038 |  | 89.1566 | 0.96775 | 96.28 | [8 empty] | Sampling date | MM/DD/YY | 1999-04-20 | 1999-04-20 | --- | --- | 1999-04-20 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-04-21 | 1999-04-21 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-04-22 | 1999-04-22 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-04-23 | 1999-04-23 | --- | --- | --- | --- | --- | SDS-TOXF, ug Cl- /L | 854 | 854 | 854 | 854 | SDS-TOXF, ug Cl- /L | 854 | 854 | 854 | 854 | Engineering Fee Factor (% of construction costs) | 10
Phone Number |  |  |  | Experimental Design1,2 | [8 empty] | Fluoride (mg/L) |  |  |  |  | Total dissolved solids | mg/L | 454 | 605.5 | 529.75 | 28.5984 | 1999-04-17 | 20:10 | 30.5 | 25.2 | 96 | 94.5 | 380 | 9.2 | 4 | 13.2 | 0.28756 | 0.69697 | 27.7879 | 20.9985 | 19.1033 | 98.3184 | 28.992 | 96.64 | 0.68487 | 94.5651 | 0.20201 | 1999-04-19 | 16:11 | 7.7 | 24.3 | 107.3 | 106.9 | 344 | 9.1 | 4.1 |  | 13.2 | 0.26032 | 0.68939 | 25.0606 | 20.7703 | 19.4051 | 1006.5269 | 314.9384 | 988.2319 | 6.8244 | 100.2756 | 0.19352 | 6.21 | 6.2 | 6.14 | 349.96 | 510.195 | 707.71 | 928.7961 | -31.2396 | 33.9387 | 921.14 | 62.0079 | 0.038 | 0.336 | 0.95 | 0.98454 | -3.6354 | 88.5542 | 0.97202 | 96.0906 | [8 empty] | Sampling time | hh:mm | NR | NR | --- | --- | NR | --- | --- | --- | --- | --- | Sampling time | hh:mm | NR | NR | --- | --- | --- | --- | --- | Sampling time | hh:mm | NR | NR | --- | --- | --- | --- | --- | Sampling time | hh:mm | NR | NR | --- | --- | --- | --- | --- | SDS-TOXp, ug Cl- /L | 114.5 | 168 | 149 | 96.6 | SDS-TOXp, ug Cl- /L | 114.5 | 168 | 149 | 96.6 | 1998 ENR Construction Cost Index (CCI base year 1913) | 5875
FAX Number |  | Design Parameters |  | ID# | Recovery | FW-design | Dp | PI | QI-cell | Qp | QF | QW | Phosphate (mg/L) |  |  |  |  | Total hardness | mg/L as CaCO3 | 243 | 269 | 256 | 10.1562 | 1999-04-18 | 10:40 | 45 | 24.8 | 96.9 | 96.4 | 380 | 9.2 | 4 | 13.2 | 0.28756 | 0.69697 | 27.7879 | 20.9985 | 19.3306 | 98.3184 | 28.992 | 96.64 | 0.68487 | 95.9651 | 0.20143 | 1999-04-20 | 9:58 | 25.5 | 24.7 | 108.6 | 108.2 | 344 | 9.2 | 1 |  | 10.2 | 0.26032 | 0.90196 | 32.7255 | 20.9985 | 19.3878 | 1393.3404 | 435.8815 | 1367.734 | 9.4466 | 98.9534 | 0.19593 | 6.2 |  |  | 418.416 |  |  | 1554.0228 |  | 21.0163 | 1538.8374 | 72.8096 | 0.044 |  |  | 2.9816 |  | 86.747 | 2.9423 | 98.5046 | [8 empty] | Operation time | hh.hh | 82.9 | 82.9 | --- | --- | 82.9 | --- | --- | --- | --- | --- | Operation time | hh.hh | 107.2 | 107.2 | --- | --- | --- | --- | --- | Operation time | hh.hh | 131.1 | 131.1 | --- | --- | --- | --- | --- | Cumulative time | hr | 154.7 | 154.7 | --- | --- | --- | --- | --- | SDS-CDF, mg/L | 10.39 | 10.39 | 10.39 | 10.39 | SDS-CDF, mg/L | 10.39 | 10.39 | 10.39 | 10.39 | 1998 Producers Price Index (PPI base year 1967 = 100) | 369
E-Mail Address (optional) |  | Design flux, FW (gfd) | 21.1 |  | (decimal) | (gfd) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | Sulfate (mg/L) | 26.5 |  |  |  | Calcium hardness | mg/L as CaCO3 | 232 | 257 | 244.5 | 10.2249 | 1999-04-18 | 14:10 | 48.6 | 25 | 95.4 | 95 | 380 | 9.2 | 4 | 13.2 | 0.28756 | 0.69697 | 27.7879 | 20.9985 | 19.2166 | 98.3184 | 28.992 | 96.64 | 0.68487 | 94.5151 | 0.20332 | 1999-04-20 | 13:00 | 28.5 | 25.2 | 108.7 | 108.2 | 344 | 9.2 | 1.1 |  | 10.3 | 0.26032 | 0.8932 | 32.3981 | 20.9985 | 19.1033 | 1371.6315 | 429.0902 | 1346.424 | 9.2994 | 99.1506 | 0.19267 | 5.85 |  |  | 430.544 |  |  | 1359.4729 |  | 18.7269 | 1347.0512 | 68.038 | 0.053 |  |  | 2.6655 |  | 84.0361 | 2.6305 | 97.9852 | [8 empty] | pH | --- | 6.62 | 6.59 | 6.605 | 0.4542 | 6.32 | --- | --- | --- | --- | --- | pH | --- | 6.59 | 6.39 | --- | --- | --- | --- | --- | pH | --- | 6.7 | 6.47 | --- | --- | --- | --- | --- | pH | --- | 6.67 | 6.36 | --- | --- | --- | --- | --- | SDS-CDp, mg/L | 4.265 | 4.55 | 3.98 | 3.53 | SDS-CDp, mg/L | 4.265 | 4.55 | 3.98 | 3.53 | Labor Rate + Fringe ($/work-hour) | 19.89
|  | Net driving pressure at the design flux, NDP (psi) | 71 | 1 | 0.7 | 21.1 | 14.3517 | 95.5367 | 344.1283 | 9.2435 | 13.2049 | 3.9615 | Calcium (mg/L) |  |  |  |  | Turbidity | ntu | 0.27 | 0.22 | 0.245 | 20.4082 | 1999-04-19 | 8:23 | 66.8 | 24.8 | 93.8 | 93.4 | 344 | 8.9 | 4.3 | 13.2 | 0.26032 | 0.67424 | 25.0606 | 20.3138 | 18.7002 | 95.3583 | 28.0853 | 93.6178 | 0.66403 | 92.936 | 0.20122 | 1999-04-20 | 16:51 | 32.4 | 25.4 | 108.2 | 107.8 | 344 | 9.1 | 1 |  | 10.1 | 0.26032 | 0.90099 | 33.0594 | 20.7703 | 18.7843 | 1390.689 | 435.1413 | 1365.4114 | 9.4291 | 98.5709 | 0.19057 | 6.36 | 6.46 | 6.89 | 413.868 | 483.301 | 937.365 | 1584.2762 | -69.0138 | 21.8748 | 1568.7955 | 73.6187 | 0.055 | 0.306 | 1.642 | 2.8527 | -73.7333 | 83.4337 | 2.8157 | 98.0467 | [8 empty] | Temperature | oC | NR | NR | #DIV/0! | #VALUE! | NR | --- | --- | --- | --- | --- | Temperature | oC | NR | NR | --- | --- | --- | --- | --- | Temperature | oC | NR | NR | --- | --- | --- | --- | --- | Temperature | oC | NR | NR | --- | --- | --- | --- | --- | TOCF, mg/L | 10.225 | 10.225 | 10.225 | 10.225 | TOCF, mg/L | 10.225 | 10.225 | 10.225 | 10.225 | Labor Overhead Factor (% of labor) | 6
Technical ICR Contact Person |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.284 | 2 | 0.9 | 21.1 | 39.785 | 120.97 | 344.1283 | 9.2435 | 10.2705 | 1.0271 | Barium (mg/L) | 0.018 |  |  |  | Ammonia | mg NH3-N / L | 0.56 | 0.38 | 0.47 | 38.2979 | [21 empty] | 1999-04-21 | 9:40 | 49.2 | 24.7 | 112.8 | 112.6 | 344 | 9.2 | 9.3 |  | 18.5 | 0.26032 | 0.4973 | 17.5946 | 20.9985 | 19.3878 | 804.757 | 251.7538 | 789.9674 | 5.4561 | 107.2439 | 0.18078 | 6.57 |  |  | 306 |  |  | 751.0941 |  | 42.2369 | 745.1422 | 58.934 | 0.076 |  |  | 0.58525 |  | 77.1084 | 0.57844 | 86.8612 | [8 empty] | Alkalinity | mg/L as CaCO3 | 2 | 2 | 2 | 0 | 5.2 | 6.0625 | -16.5865 | 39.3939 | 6.0095 | 66.7194 | Alkalinity | mg/L as CaCO3 | 2.1 | 10.5 | 14.1 | -34.2857 | 36.3636 | 13.9415 | 84.937 | Alkalinity | mg/L as CaCO3 | 1.9 | 7.2 | 4.7 | 34.7222 | 42.4242 | 4.6613 | 59.2392 | Alkalinity | mg/L as CaCO3 | 2 | 4.2 | 3.7808 | 9.9804 | 39.3939 | 3.7603 | 46.8124 | TOCp, mg/L | 1.215 | 1.83 | 1.32 | 1.11 | TOCp, mg/L | 1.215 | 1.83 | 1.32 | 1.11 | Electric Rate ($/kW-h) | 0.05
Mailing Address |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | 3 | 0.5 | 21.1 | 9.265 | 90.45 | 344.1283 | 9.2435 | 18.4869 | 9.2435 | Strontium (mg/L) |  |  |  |  | Total organic carbon | mg/L | 10.6 | 9.85 | 10.225 | 7.335 | [21 empty] | 1999-04-21 | 13:40 | 53.2 | 25.1 | 112 | 111.5 | 344 | 9.6 | 9.6 |  | 19.2 | 0.26032 | 0.5 | 16.9167 | 21.9115 | 19.9929 | 807.1919 | 252.3081 | 791.7068 | 5.4714 | 106.2786 | 0.18812 | 6.53 |  |  | 303.96 |  |  | 755.54 |  | 42.622 | 749.2389 | 59.4308 | 0.044 |  |  | 0.62 |  | 86.747 | 0.61196 | 92.81 | [8 empty] | Total dissolved solids | mg/L | 350 | NR | 350 | #VALUE! | 708 | 911.7188 | -28.7738 | 33.9311 | 904.3903 | 61.2999 | Total dissolved solids | mg/L | 414 | 937 | 1571.5 | -67.7161 | 21.8499 | 1556.2069 | 73.3969 | Total dissolved solids | mg/L | 306 | 592 | 753.5 | -27.2804 | 42.2369 | 747.3209 | 59.0537 | Total dissolved solids | mg/L | 177 | 613.5 | 660.2192 | -7.6152 | 66.588 | 654.6439 | 72.9624 | UV254 F, cm-1 | 0.332 | 0.332 | 0.332 | 0.332 | UV254 F, cm-1 | 0.332 | 0.332 | 0.332 | 0.332 | Fuel Oil Rate ($/gal) | NA
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 400 | 4 | 0.3 | 21.1 | 7.085 | 88.27 | 344.1283 | 9.2435 | 30.8115 | 21.5681 | Reactive silica (mg/L as SiO2) | 32.8 |  |  |  | UV254 | cm-1 | 0.311 | 0.353 | 0.332 | 12.6506 | [21 empty] | 1999-04-21 | 17:02 | 56.5 | 25.2 | 112.3 | 111.5 | 344 | 9.5 | 9.5 |  | 19 | 0.26032 | 0.5 | 17.1053 | 21.6832 | 19.7263 | 807.1524 | 252.3476 | 791.8308 | 5.4714 | 106.4286 | 0.18535 | 6.52 | 6.5 | 6.38 | 306 | 487.256 | 592.128 | 753.5 | -27.2529 | 42.2369 | 747.3209 | 59.0537 | 0.043 | 0.305 | 0.621 | 0.621 | 0 | 87.0482 | 0.61302 | 92.9855 | [8 empty] | Total hardness | mg/L as CaCO3 | 171 | 173 | 172 | 1.1628 | 374 | 434.5 | -16.1765 | 32.8125 | 431.0753 | 60.0998 | Total hardness | mg/L as CaCO3 | 201 | 531 | 751 | -41.4313 | 21.4844 | 743.7333 | 72.9742 | Total hardness | mg/L as CaCO3 | 154 | 319 | 358 | -12.2257 | 39.8438 | 355.1831 | 56.6421 | Total hardness | mg/L as CaCO3 | 160 | 294 | 291.5068 | 0.84801 | 37.5 | 289.9896 | 44.8256 | UV254 p, cm-1 | 0.038 | 0.056 | 0.041 | 0.038 | UV254 p, cm-1 | 0.038 | 0.056 | 0.041 | 0.038 | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Purchase price for an equivalent 8" x 40 " element ($) | 800 | 1: For experimental matrix see Table 4-2 in Part 3 of the ICR Treatment Studies Manual. | [8 empty] | Turbidity (ntu) |  |  |  |  | SUVA | L/(mg*m) | 2.934 | 3.5838 | 3.2589 | 19.9393 | [21 empty] | 1999-04-22 | 8:39 | 72.2 | 24.6 | 110 | 109 | 344 | 9.3 | 12.5 |  | 21.8 | 0.26032 | 0.42661 | 14.7798 | 21.2268 | 19.6565 | 749.4805 | 234.4134 | 735.5557 | 5.081 | 104.419 | 0.18825 | 6.51 |  |  | 181.02 |  |  | 789.2051 |  | 65.8292 | 780.984 | 76.8215 | 0.049 |  |  | 0.54255 |  | 85.241 | 0.53588 | 90.8562 | [8 empty] | Calcium hardness | mg/L as CaCO3 | 165 | 167 | 166 | 1.2048 | 352 | 411.3125 | -16.8501 | 32.1063 | 408.112 | 59.3249 | Calcium hardness | mg/L as CaCO3 | 193 | 494 | 708 | -43.3198 | 21.0634 | 701.1957 | 72.4756 | Calcium hardness | mg/L as CaCO3 | 149 | 302 | 340 | -12.5828 | 39.0593 | 337.3626 | 55.8339 | Calcium hardness | mg/L as CaCO3 | 155 | 279 | 277.6027 | 0.50081 | 36.6053 | 276.1882 | 43.8788 | BromideF, ug/L | 108.5 | 108.5 | 108.5 | 108.5 | BromideF, ug/L | 108.5 | 108.5 | 108.5 | 108.5 | Current Process Water Rate ($/1000 gal) | 0.41
FAX Number |  | Maximum flow rate to the 8" x 40" element, QI, max (gpm) | 70 | 2: Flow rates and pressures may need to be adjusted in order to obtain the desired operating conditions. | [8 empty] | SDI |  |  |  |  | Bromide | mg/L | 107 | 110 | 108.5 | 2.765 | [21 empty] | 1999-04-22 | 9:38 | 72.8 | 24.4 | 108 | 107 | 344 | 9.2 | 19.9 |  | 29.1 | 0.26032 | 0.31615 | 10.8213 | 20.9985 | 19.5605 | 676.7797 | 211.7184 | 664.342 | 4.5884 | 102.9116 | 0.19007 | 6.36 |  |  | 182.744 |  |  | 690.1749 |  | 65.5037 | 683.3895 | 73.2592 | 0.044 |  |  | 0.46515 |  | 86.747 | 0.45951 | 90.4247 | [8 empty] | Turbidity | ntu | BMRL | BMRL | #DIV/0! | #VALUE! | 0.1 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu | BMRL | 0.31 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | 0.09 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | 0.06 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Bromidep, ug/L | 99.5 | 106 | 87 | 85 | Bromidep, ug/L | 99.5 | 106 | 87 | 85 | Modifications to Existing Plant (% of construction costs) | 10
E-Mail Address (optional) |  | Minimum flow rate to the 8" x 40" element, QI, min (gpm) | 16 | [9 empty] | MFI |  |  |  |  | SDS-Cl2 dose | mg/L | 11.8 | 11.3 | 11.55 | 4.329 | [21 empty] | 1999-04-22 | 13:48 | 77 | 25 | 109 | 108.8 | 344 | 9.5 | 20.2 |  | 29.7 | 0.26032 | 0.31987 | 10.5825 | 21.6832 | 19.8432 | 679.0473 | 212.2969 | 666.1574 | 4.6031 | 104.2969 | 0.19026 |  | 6.35 |  |  | 487.256 | [7 empty] | 0.296 | [14 empty] | Ammonia | mg NH3-N / L | 0.48 | 0.48 | 0.48 | 0 | 0.78 | 0.44875 | 42.4679 | -2.1277 | 0.44916 | -6.8667 | Ammonia | mg NH3-N / L | 0.52 | 0.61 | 0.02 | 96.7213 | -10.6383 | 0.026606 | -1854.4387 | Ammonia | mg NH3-N / L | 0.52 | 0.68 | 0.42 | 38.2353 | -10.6383 | 0.42138 | -23.4038 | Ammonia | mg NH3-N / L | 0.53 | 0.66 | 0.44781 | 32.1503 | -12.766 | 0.44876 | -18.1041 | AlkF, mg/L CaCO3 | 3.3 | 3.3 | 3.3 | 3.3 | AlkF, mg/L CaCO3 | 3.3 | 3.3 | 3.3 | 3.3
|  | Total width of all membrane envelopes in the 8" x 40" element, w (ft) | 58.6667 | [9 empty] | MPFI |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | SDS-Free Cl2 residual | mg/L | 1.32 | 1 | 1.16 | 27.5862 | [21 empty] | 1999-04-22 | 17:08 | 80.3 | 25.2 | 108 | 107 | 344 | 9.5 | 19.9 |  | 29.4 | 0.26032 | 0.32313 | 10.7007 | 21.6832 | 19.7263 | 681.0057 | 212.9092 | 668.0786 | 4.6163 | 102.8837 | 0.19173 | 6.68 | 6.2 | 6.41 | 177.141 | 473.809 | 613.41 | 698.0809 | -13.8033 | 66.5614 | 690.8877 | 74.3604 | 0.043 | 0.333 | 0.442 | 0.46996 | -6.3269 | 87.0482 | 0.46407 | 90.7341 | [8 empty] | Total organic carbon | mg/L | 1.25 | 1.18 | 1.215 | 5.7613 | 27.9 | 29.3712 | -5.2733 | 88.1174 | 29.0039 | 95.8109 | Total organic carbon | mg/L | 1.83 | 66.2 | 85.78 | -29.577 | 82.1027 | 84.6708 | 97.8387 | Total organic carbon | mg/L | 1.32 | 19 | 19.13 | -0.68421 | 87.0905 | 18.8841 | 93.01 | Total organic carbon | mg/L | 1.11 | 14.1 | 13.5963 | 3.5723 | 89.1443 | 13.4522 | 91.7486 | Alkp, mg/L CaCO3 | 2 | 2.1 | 1.9 | 2 | Alkp, mg/L CaCO3 | 2 | 2.1 | 1.9 | 2
Plant Name | Lime Softening Plant | Feed spacer thickness in the 8" x 40" element, T (ft) | 0.0023333 | [9 empty] | pH | 7.2 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | SDS-Cl2 demand | mg/L | 10.48 | 10.3 | 10.39 | 1.7324 | [21 empty] | 1999-04-23 | 16:10 | 95.4 | [6 empty] | X | [39 empty] | UV254 | cm-1 | 0.038 | 0.038 | 0.038 | 0 | 0.897 | 0.95675 | -6.6611 | 88.5542 | 0.94476 | 95.9778 | UV254 | cm-1 | 0.056 | 2.115 | 2.816 | -33.1442 | 83.1325 | 2.7795 | 97.9853 | UV254 | cm-1 | 0.041 | 0.59 | 0.623 | -5.5932 | 87.6506 | 0.61496 | 93.3329 | UV254 | cm-1 | 0.038 | 0.461 | 0.44074 | 4.3949 | 88.5542 | 0.43609 | 91.2863 | T-HdF, mg/L CaCO3 | 256 | 256 | 256 | 256 | T-HdF, mg/L CaCO3 | 256 | 256 | 256 | 256
Treatment Plant Category | SOFT | [11 empty] | Chloride (mg/L) | 59.9 | is to list the pretreatment processes used in this particular RBSMT run. |  |  | SDS-Chlorination temp. | oC | 20 | 20 | 20 | 0 | [21 empty] | 1999-04-23 | 17:17 | 96.6 | 24.7 | 69.1 | 69 | 344 | 9.5 | 20.3 |  | 29.8 | 0.26032 | 0.31879 | 10.5436 | 21.6832 | 20.02 | 678.4057 | 212.0963 | 665.5279 | 4.5987 | 64.4513 | 0.31062 | 6.57 |  |  | 191.364 |  |  | 688.108 |  | 63.8765 | 681.2489 | 71.9098 | 0.044 |  |  | 0.46678 |  | 86.747 | 0.46094 | 90.4543 | [8 empty] | SUVA | L/(mg*m) | 3.04 | 3.2203 | 3.1302 | 5.7613 | 3.2151 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 3.0601 | 3.1949 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 3.1061 | 3.1053 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 3.4234 | 3.2695 | --- | --- | --- | --- | --- | T-Hdp, mg/L CaCO3 | 172 | 201 | 154 | 160 | T-Hdp, mg/L CaCO3 | 172 | 201 | 154 | 160
Process Train Name | NA | Additional Information | [10 empty] | Mg (mg/L) | 44 |  |  |  | SDS-Chlorination pH | --- | 7.49 | 7.48 | 7.485 | 0.1336 | [21 empty] | 1999-04-23 | 20:17 | 99.6 | 24.2 | 68.2 | 67.9 | 344 | 9.5 | 19.1 |  | 28.6 | 0.26032 | 0.33217 | 11.028 | 21.6832 | 20.3181 | 686.4884 | 214.6233 | 673.4573 | 4.6535 | 63.3965 | 0.32049 | 6.62 |  |  | 189.64 |  |  | 698.9147 |  | 64.202 | 691.8825 | 72.5907 | 0.036 |  |  | 0.47923 |  | 89.1566 | 0.47311 | 92.3907 | [8 empty] | Bromide | mg/L | 99 | 100 | 99.5 | 1.005 | --- | 127.625 | --- | 8.2949 | 127.2581 | 21.8124 | Bromide | mg/L | 106 | --- | 131 | --- | 2.3041 | 130.6697 | 18.8794 | Bromide | mg/L | 87 | --- | 130 | --- | 19.8157 | 129.4062 | 32.7699 | Bromide | mg/L | 85 | --- | 117.1918 | --- | 21.659 | 116.8204 | 27.2387 | Ca-HdF, mg/L CaCO3 | 244.5 | 244.5 | 244.5 | 244.5 | Ca-HdF, mg/L CaCO3 | 244.5 | 244.5 | 244.5 | 244.5
ICR Treatment Plant Identification Number | 1086 | Design cross-flow velocity (fps) | - | [9 empty] | Potassium (mg/L) | 25.1 |  |  |  | SDS-Incubation time | hours | 24.32 | 24.4 | 24.36 | 0.32841 | [21 empty] | 1999-04-23 | 23:42 | 103 | 24.3 | 67.7 | 67.2 | 344 | 8.3 | 18.9 |  | 27.2 | 0.26032 | 0.30515 | 11.6471 | 18.9443 | 17.6992 | 670.1549 | 210.0328 | 659.0531 | 4.5457 | 62.9043 | 0.28137 | 6.63 | 6.53 | 6.43 | 190.071 | 478.555 | 602.742 | 678.9212 | -12.6388 | 64.1206 | 673.0237 | 71.7586 | 0.032 | 0.337 | 0.479 | 0.46375 | 3.1845 | 90.3614 | 0.45854 | 93.0213 | [8 empty] | SDS-Cl2 dose | mg/L | 5.52 | 5.4 | 5.46 | 2.1978 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 6.48 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 5.76 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 4.75 | --- | --- | --- | --- | --- | --- | Ca-Hdp, mg/L CaCO3 | 166 | 193 | 149 | 155 | Ca-Hdp, mg/L CaCO3 | 166 | 193 | 149 | 155
PWSID Number of Plant (if assigned) | 45-00351 | Required influent flow to permeate flow rate ratio, QI:Qp | - | [9 empty] | Strontium (mg/L) | 1.14 |  |  |  | SDS-TOX | mg Cl- /L | 1080 | 628 | 854 | 52.9274 | [70 empty] | SDS-Free Cl2 residual | mg/L | 1.57 | 0.82 | 1.195 | 62.7615 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.93 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.78 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.22 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 18 | Maximum element recovery (%) | 19 | [14 empty] | SDS-CHCl3 | mg/L | 143 | 131 | 137 | 8.7591 | [70 empty] | SDS-Cl2 demand | mg/L | 3.95 | 4.58 | 4.265 | 14.7714 | --- | 23.4056 | --- | 58.9509 | 23.1559 | 81.5814 | SDS-Cl2 demand | mg/L | 4.55 | --- | 62.95 | --- | 56.2079 | 62.1784 | 92.6823 | SDS-Cl2 demand | mg/L | 3.98 | --- | 16.8 | --- | 61.6939 | 16.623 | 76.0572 | SDS-Cl2 demand | mg/L | 3.53 | --- | 12.9273 | --- | 66.025 | 12.8188 | 72.4624 | Blended Water Quality if THM4 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if THM4 Controls the Blend Ratio
Historical Average Water Temperature (oC) | 20 | Variability of design flux (%) | -10%, +25% | [14 empty] | SDS-BDCM | mg/L | 27.3 | 23.9 | 25.6 | 13.2812 | [70 empty] | SDS-Chlorination temp. | oC | 20 | 20 | 20 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 20 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 20 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 20 | --- | --- | --- | --- | --- | --- | Qp/QT (THM4), % | 72.9045 | 77.6578 | 67.4117 | 73.2185 | Qp/QT (THM4), % | 100.9747 | 107.5581 | 93.367 | 101.4096
State Approved Plant Capacity (MGD) | 22.4 | Rejection of reference solute and conditions of test | >99% of 2,000 ppm MgSO4 | [14 empty] | SDS-DBCM | mg/L | 2.9 | 2.9 | 2.9 | 0 | [70 empty] | SDS-Chlorination pH | --- | 7.46 | 7.4 | 7.43 | 0.80754 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.45 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.41 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.59 | --- | --- | --- | --- | --- | --- | SDS-THM4b, ug/L | 72 | 72 | 72 | 72 | SDS-THM4b, ug/L | NA | NA | 36 | NA
|  | (e.g., solute type and concentration) | <50% 500 ppm CaCl2 | [9 empty] | Sodium (mg/L) | 32.8 |  |  |  | SDS-CHBr3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [70 empty] | SDS-Incubation time | hours | 24.4 | 24.1 | 24.25 | 1.2371 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24.27 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 23.88 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-HAA5b, ug/L | 44.9776 | 47.3816 | 52.9596 | 43.7005 | SDS-HAA5b, ug/L | NA | NA | 23.682 | NA
|  | Variability of rejection of reference solute (%) | - | [9 empty] | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | SDS-THM4 | mg/L | 173.2 | 157.8 | 165.5 | 9.3051 | [70 empty] | SDS-TOX | mg Cl- /L | 121 | 108 | 114.5 | 11.3537 | --- | 2425.4375 | --- | 86.5925 | 2395.2878 | 95.2198 | SDS-TOX | mg Cl- /L | 168 | --- | 7028 | --- | 80.3279 | 6937.3642 | 97.5783 | SDS-TOX | mg Cl- /L | 149 | --- | 1559 | --- | 82.5527 | 1539.5305 | 90.3217 | SDS-TOX | mg Cl- /L | 96.6 | --- | 1134.1342 | --- | 88.6885 | 1122.1634 | 91.3916 | SDS-TOXb, ug Cl- /L | 314.8713 | 321.2674 | 378.7477 | 299.4432 | SDS-TOXb, ug Cl- /L | NA | NA | 195.7628 | NA
|  | Standard testing recovery (%) | 15 | [9 empty] | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | SDS-MCAA* | mg/L | 6.4 | 7.8 | 7.1 | 19.7183 | [70 empty] | SDS-CHCl3 | mg/L | 9.1 | 13 | 11.05 | 35.2941 | --- | 404.6438 | --- | 91.9343 | 399.5087 | 97.2341 | SDS-CHCl3 | mg/L | 17.2 | --- | 1215.2 | --- | 87.4453 | 1199.3718 | 98.5659 | SDS-CHCl3 | mg/L | 8.8 | --- | 265.2 | --- | 93.5766 | 261.6596 | 96.6369 | SDS-CHCl3 | mg/L | 11.2 | --- | 183.5288 | --- | 91.8248 | 181.5405 | 93.8306 | SDS-CDb, mg/L | 5.9246 | 5.8548 | 6.0689 | 5.3672 | SDS-CDb, mg/L | NA | NA | 4.4052 | NA
|  | Standard testing pH | 6.7-7.3 | [14 empty] | SDS-DCAA* | mg/L | NA | 98.8 | 98.8 | #VALUE! | [70 empty] | SDS-BDCM | mg/L | 11.2 | 15.9 | 13.55 | 34.6863 | --- | 51.2062 | --- | 47.0703 | 50.715 | 73.282 | SDS-BDCM | mg/L | 16.2 | --- | 110.2 | --- | 36.7188 | 108.9581 | 85.1319 | SDS-BDCM | mg/L | 10 | --- | 41.2 | --- | 60.9375 | 40.7692 | 75.4717 | SDS-BDCM | mg/L | 14 | --- | 29.8904 | --- | 45.3125 | 29.7071 | 52.8732 | TOCb, mg/L | 3.6563 | 3.7056 | 4.222 | 3.5511 | TOCb, mg/L | NA | NA | 1.9107 | NA
|  | Acceptable range of operating pressures | <105 psi | [14 empty] | SDS-TCAA* | mg/L | NA | 145 | 145 | #VALUE! | [70 empty] | SDS-DBCM | mg/L | 9.7 | 13.1 | 11.4 | 29.8246 | --- | -15.1625 | --- | -293.1034 | -14.816 | 176.9441 | SDS-DBCM | mg/L | 10.7 | --- | -67.3 | --- | -268.9655 | -66.2694 | 116.1462 | SDS-DBCM | mg/L | 8 | --- | -2.2 | --- | -175.8621 | -2.0592 | 488.5085 | SDS-DBCM | mg/L | 11.4 | --- | -0.24384 | --- | -293.1034 | -0.10949 | 10511.7692 | UV254 b, cm-1 | 0.11766 | 0.11766 | 0.13583 | 0.11674 | UV254 b, cm-1 | NA | NA | 0.060302 | NA
|  | Acceptable range of operating pH values | 3-10 | [14 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [70 empty] | SDS-CHBr3 | mg/L | 1.1 | 1.4 | 1.25 | 24 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 1 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 1.2 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | Bromideb, ug/L | 101.9386 | 106.5586 | 94.0065 | 91.2937 | Bromideb, ug/L | NA | NA | 88.4261 | NA
|  | Typical pressure drop across a single element (psi) | 3 | [14 empty] | SDS-DBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [70 empty] | SDS-THM4 | mg/L | 31.1 | 43.4 | 37.25 | 33.0201 | --- | 438.0312 | --- | 77.4924 | 432.8025 | 91.3933 | SDS-THM4 | mg/L | 45.1 | --- | 1249.1 | --- | 72.7492 | 1233.1925 | 96.3428 | SDS-THM4 | mg/L | 26.8 | --- | 304.2 | --- | 83.8066 | 300.3696 | 91.0777 | SDS-THM4 | mg/L | 37.8 | --- | 212.7315 | --- | 77.1601 | 210.7132 | 82.0609 | Alkb, mg/L CaCO3 | 2.3522 | 2.3681 | 2.3562 | 2.3482 | Alkb, mg/L CaCO3 | NA | NA | 1.9929 | NA
|  | Maximum permissible SDI | 5 | [14 empty] | SDS-BCAA* | mg/L | 7.3 | 7.7 | 7.5 | 5.3333 | [70 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | T-Hdb, mg/L CaCO3 | 194.7602 | 213.2882 | 187.2401 | 185.7103 | T-Hdb, mg/L CaCO3 | NA | NA | 160.7657 | NA
|  | Maximum permissible turbidity (ntu) | 1 | [14 empty] | SDS-TBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [70 empty] | SDS-DCAA* | mg/L | 5.8 | 5.2 | 5.5 | 10.9091 | --- | 297.0625 | --- | 94.4332 | 293.2586 | 98.1245 | SDS-DCAA* | mg/L | 9.3 | --- | 904.3 | --- | 90.587 | 892.4751 | 98.958 | SDS-DCAA* | mg/L | 6.3 | --- | 191.3 | --- | 93.6235 | 188.7455 | 96.6622 | SDS-DCAA* | mg/L | 5.4 | --- | 133.3452 | --- | 94.5344 | 131.869 | 95.905 | Ca-Hdb, mg/L CaCO3 | 187.27 | 204.5062 | 180.1218 | 178.9695 | Ca-Hdb, mg/L CaCO3 | NA | NA | 155.3345 | NA
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | 1000 ppm-hr | [14 empty] | SDS-CDBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [70 empty] | SDS-TCAA* | mg/L | 7.2 | 4.6 | 5.9 | 44.0678 | --- | 440.5875 | --- | 95.931 | 434.9163 | 98.6434 | SDS-TCAA* | mg/L | 12.4 | --- | 1338.4 | --- | 91.4483 | 1320.8806 | 99.0612 | SDS-TCAA* | mg/L | 8.1 | --- | 281.9 | --- | 94.4138 | 278.1193 | 97.0876 | SDS-TCAA* | mg/L | 4.4 | --- | 197.0027 | --- | 96.9655 | 194.7805 | 97.741
|  | 1: All of the information requested in this field may not be available, but values for all Design | [15 empty] | SDS-DCBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [70 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  | Parameters must be entered in cells E14:E23, since these parameters are used in calculations. | [15 empty] | SDS-HAA5 | mg/L | 6.4 | 251.6 | 129 | 190.0775 | [70 empty] | SDS-DBAA* | mg/L | 2.1 | 2.6 | 2.35 | 21.2766 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DBAA* | mg/L | 2.2 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DBAA* | mg/L | 1.8 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DBAA* | mg/L | 2.7 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | Blended Water Quality if HAA5 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if HAA5 Controls the Blend Ratio
[18 empty] | SDS-HAA6 | mg/L | 13.7 | 259.3 | 136.5 | 179.9267 | [70 empty] | SDS-BCAA* | mg/L | 4.6 | 4.9 | 4.75 | 6.3158 | --- | 13.3438 | --- | 36.6667 | 13.2316 | 64.1012 | SDS-BCAA* | mg/L | 6.2 | --- | 19.2 | --- | 17.3333 | 19.0282 | 67.4169 | SDS-BCAA* | mg/L | 4.5 | --- | 10.5 | --- | 40 | 10.4172 | 56.802 | SDS-BCAA* | mg/L | 5.1 | --- | 8.3877 | --- | 32 | 8.3497 | 38.9202 | Qp/QT (HAA5), % | 65.0759 | 71.3606 | 66.4894 | 64.3777 | Qp/QT (HAA5), % | 88.5033 | 97.0504 | 90.4255 | 87.5536
[18 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [75 empty] | SDS-TBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-THM4b, ug/L | 82.0401 | 79.5818 | 73.2793 | 83.2897 | SDS-THM4b, ug/L | 51.9946 | 48.6513 | 40.0798 | 53.694
[18 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, | [75 empty] | SDS-CDBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-HAA5b, ug/L | 54 | 54 | 54 | 54 | SDS-HAA5b, ug/L | 27 | 27 | 27 | 27
[18 empty] | should be reported if measured. | [75 empty] | SDS-DCBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TOXb, ug Cl- /L | 372.7636 | 364.4662 | 385.25 | 366.4034 | SDS-TOXb, ug Cl- /L | 199.5184 | 188.2341 | 216.5 | 190.8687
[94 empty] | SDS-HAA5 | mg/L | 15.1 | 12.4 | 13.75 | 19.6364 | --- | 373.9062 | --- | 89.3411 | 369.2075 | 96.2758 | SDS-HAA5 | mg/L | 23.9 | --- | 1074.9 | --- | 81.4729 | 1061.014 | 97.7474 | SDS-HAA5 | mg/L | 16.2 | --- | 241.8 | --- | 87.4419 | 238.6849 | 93.2128 | SDS-HAA5 | mg/L | 12.5 | --- | 172.089 | --- | 90.3101 | 170.2477 | 92.6578 | SDS-CDb, mg/L | 6.4041 | 6.2225 | 6.128 | 5.9737 | SDS-CDb, mg/L | 4.9692 | 4.7223 | 4.5937 | 4.3838
[94 empty] | SDS-HAA6 | mg/L | 19.7 | 17.3 | 18.5 | 12.973 | --- | 387.25 | --- | 86.4469 | 382.4391 | 95.1626 | SDS-HAA6 | mg/L | 30.1 | --- | 1094.1 | --- | 77.9487 | 1080.0422 | 97.2131 | SDS-HAA6 | mg/L | 20.7 | --- | 252.3 | --- | 84.8352 | 249.102 | 91.6902 | SDS-HAA6 | mg/L | 17.6 | --- | 180.4767 | --- | 87.1062 | 178.5975 | 90.1454 | TOCb, mg/L | 4.3617 | 4.2343 | 4.3041 | 4.357 | TOCb, mg/L | 2.2509 | 2.0776 | 2.1726 | 2.2445
[94 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | UV254 b, cm-1 | 0.14068 | 0.13504 | 0.13852 | 0.14273 | UV254 b, cm-1 | 0.0718 | 0.064141 | 0.068862 | 0.074592
[94 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | Bromideb, ug/L | 102.6432 | 106.716 | 94.2048 | 93.3712 | Bromideb, ug/L | 100.5347 | 106.0737 | 89.0585 | 87.9249
[133 empty] | Alkb, mg/L CaCO3 | 2.454 | 2.4437 | 2.3691 | 2.4631 | Alkb, mg/L CaCO3 | 2.1495 | 2.1354 | 2.034 | 2.1618
[133 empty] | T-Hdb, mg/L CaCO3 | 201.3362 | 216.7517 | 188.1809 | 194.1974 | T-Hdb, mg/L CaCO3 | 181.6573 | 202.6223 | 163.766 | 171.9485
[133 empty] | Ca-Hdb, mg/L CaCO3 | 193.4154 | 207.7493 | 181.0027 | 186.882 | Ca-Hdb, mg/L CaCO3 | 175.0249 | 194.519 | 158.1436 | 166.1395
[133 empty] | Notes: |  |  |  |  | Notes:
[133 empty] | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to |  |  |  |  | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to
[133 empty] | determine the percentage of total flow that must be treated by the membrane process to meet the |  |  |  |  | determine the percentage of total flow that must be treated by the membrane process to meet the
[133 empty] | Stage 1 DBP MCLs. |  |  |  |  | Stage 2 DBP MCLs.
[133 empty] | A 10% factor of safety has been applied all the MCLs. i.e., 72 / 54 mg/L for THM4 and HAA5. |  |  |  |  | A 10% factor of safety has been applied all the MCLs. i.e., 36 / 27 mg/L for THM4 and HAA5.
[133 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for |  |  |  |  | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for
[133 empty] | both parameters and the maximum (Qp/QT) ratio controls the design. |  |  |  |  | both parameters and the maximum (Qp/QT) ratio controls the design.
[133 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. |  |  |  |  | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[133 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. |  |  |  |  | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[133 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. |  |  |  |  | The subscript "b" refers to the blended water quality for a given blend ratio.
[133 empty] | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL. |  |  |  |  | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL.
[133 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. |  |  |  |  | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
Note on Z27: C. Hill (11/15/99): Verified by the utility.
Note on AA27: C. Hill (11/15/99): Verified by the utility.
Note on BA24: C. Hill (11/15/99): Utility verified operational data following cleaning. They could not explain the sharp drop in NDP following cleaning, but commented it was observed in both runs with this membrane.
Note on CY29: TSC_ADM: Reported SDS temperature is a measured value - the consultant used an incubator for SDS testing.
Note on DB17: C. Hill (10/19/99): No value reported by consultant. Reviewer inserted NR.
Note on DL29: TSC_ADM: Reported SDS temperature is a measured value - the consultant used an incubator for SDS testing.
Note on DQ10: C. Hill (10/15/99): Utility verified permeate and concentrate values for all water quality parameters during the 90% run, but could not explain the high mass balance closure errors.
Note on DV29: TSC_ADM: Reported SDS temperature is a measured value - the consultant used an incubator for SDS testing.
Note on DV33: C. Hill (11/15/99): Utility verified permeate THM concentrations.
Note on EF29: TSC_ADM: Reported SDS temperature is a measured value - the consultant used an incubator for SDS testing.
Note on EF33: C. Hill (11/15/99): Utility verified permeate THM concentrations.
Print All Fields

## DCSS1. 3rd Quarter
FIELD-SET 3: Membrane C, Run 1 (FILE: Delray1.xls)
Field 3-1: PWS And Treatment Plant Data |  | Field 3-2: Manufacturer Reported Membrane Characteristics1 |  | Field 3-3: RBSMT Design Parameters | [8 empty] | Field 3-4: Foulants And Fouling Indices1 |  | Field 3-5: Pretreatment Used Prior To Membranes1 |  |  | Field 3-6: Feed Water Quality After Pretreatment | [5 empty] | Field 3-7: Membrane Setting Data | [20 empty] | Field 3-8: Membrane Performance Data During Operation With The Test Water | [16 empty] | Field 3-8: Membrane Performance Data During Operation With The Test Water (continued) | [19 empty] | Field 3-8: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 3-9: Permeate And Concentrate Water Quality For Run 1 | [11 empty] | Field 3-10: Permeate And Concentrate Water Quality For Run 2 | [8 empty] | Field 3-11: Permeate And Concentrate Water Quality For Run 3 | [8 empty] | Field 3-12: Permeate And Concentrate Water Quality For Run 4 | [8 empty] | Field 3-13: Blending Calculations For Stage 1 D-DBP MCLs |  |  |  |  | Field 3-14: Blending Calculations For Proposed Stage 2 D-DBP MCLs |  |  |  |  | Field 3-15: Membrane Cost Parameters
|  | General Information |  | Input Design Parameters | [8 empty] | Parameters Evaluated Prior to Pretreatment | [80 empty] | Operating Parameters During Sample Collection | [11 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Feed and Permeate Water Quality Parameters |  |  |  |  | Feed and Permeate Water Quality Parameters |  |  |  |  | General Cost Parameters
PWS Name | Delray Beach Water Department | Membrane manufacturer | Hydranautics | [5 empty] | Active membrane area in bench-scale cell, Acell (ft2) | 0.16667 |  |  | Alkalinity (mg/L as CaCO3) | 243 | Process | Description | Scale | Parameter | Units | CF-1 | CF-2 | Average | RPD |  |  |  | Average TDS rejection (decimal fraction) | 0.7 | [5 empty] | TDS concentration of setting solution (mg/L) | 50 | [12 empty] | Average bulk TDS rejection (decimal fraction) | 0.74063 | [45 empty] | Recovery during sample collection (decimal) | 0.66 | [10 empty] | Recovery during sample collection (decimal) | [8 empty] | Recovery during sample collection (decimal) | 0.49 | [7 empty] | Recovery during sample collection (decimal) | 0.3 | [8 empty] | RUN ID # |  |  |  |  | RUN ID # |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | FL4500351 | Membrane trade name | ESNA1 | [5 empty] | Active width of membrane in the bench-scale cell, wcell (ft) | 0.33333 |  |  | Calcium Hardness (mg/L as CaCO3) | 295 | Acidification | Hydrochloric acid to pH 6.5 | Bench | Sampling date | MM/DD/YY | 1999-04-20 | 1999-04-23 | --- | --- | [71 empty] | Feed flow rate during sample collection (mL/min) | 16.6 | [10 empty] | Feed flow rate during sample collection (mL/min) | [8 empty] | Feed flow rate during sample collection (mL/min) | 23.6 | [7 empty] | Feed flow rate during sample collection (mL/min) | 37.1 | [6 empty] | Parameter | 1 | 2 | 3 | 4 | Parameter | 1 | 2 | 3 | 4 | Capital Recovery Interest Rate (%) | 5.75
Water Industry Data Base Number (optional) | NA | Molecular weight cutoff (Daltons) | 180 | [5 empty] | Average yearly temperature of feed water, TavgoC (oC) | 22 |  |  | LSI |  | Antiscalant addition | King Lee PreTreat 0100, 3 ppm by volume | Bench | Sampling time | hh:mm | NR | NR | --- | --- | Date | Time | Setting time | Influent | PI | PC | QI | Qp | QW | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) | Date | Time | Operation time | Influent | PI | PC | QI | Qp | QW | Cleaning Event | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1) | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Influent flow rate during sample collection (mL/min) | 411 | [10 empty] | Influent flow rate during sample collection (mL/min) | [8 empty] | Influent flow rate during sample collection (mL/min) | 411 | [7 empty] | Influent flow rate during sample collection (mL/min) | 411 | [6 empty] | SDS-THM4F, ug/L | 165.5 | 165.5 | 165.5 | 165.5 | SDS-THM4F, ug/L | 165.5 | 165.5 | 165.5 | 165.5 | Capital Recovery Period (years) | 25
|  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide | [5 empty] | Approximate feed water TDS, TDSF (mg/L) | 545 |  |  | Dissolved iron (mg/L) |  | Cartridge filtration | 5 micron nominal | Bench | Operation time | hh.hh | 82.9 | 154.7 | --- | --- | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | Indicate with "X" | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) | [39 empty] | SDS-THM4p, ug/L | 26.55 | 0 | 17 | 16.4 | SDS-THM4p, ug/L | 26.55 | 0 | 17 | 16.4 | Overhead & Profit Factor (% of construction costs) | 15
Official ICR Contact Person |  | Membrane construction (e.g., thin-film composite) | Thin-Film Composite | [5 empty] | Manufacturer reported TDS rejection, RejTDS (decimal fraction) | 0.7 |  |  | Total iron (mg/L) |  |  |  |  | pH | --- | 6.02 | 6.71 | 6.365 | 10.8405 | 1999-04-16 | 13:27 | 0 | [18 empty] | 1999-04-19 | 19896:00 | 0 | [46 empty] | Permeate and Concentrate Water Quality | [11 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | SDS-HAA5F, ug/L | 251.6 | 251.6 | 251.6 | 251.6 | SDS-HAA5F, ug/L | 251.6 | 251.6 | 251.6 | 251.6 | Special Sitework Factor (% of construction costs) | 5
Mailing Address |  | Membrane hydrophobicity | Hydrophilic | [5 empty] | Temperature normalized MTCW (gfd/psi) | 0.32945 |  |  | Dissolved aluminum (mg/L) |  |  |  |  | Temperature | oC | NR | NR | #DIV/0! | #VALUE! | 1999-04-16 | 17:00 | 3.55 | 24.8 | 91.6 | 90.9 | 411 | 11.8 | 5.4 | 17.2 | 0.31102 | 0.68605 | 22.8953 | 26.9329 | 24.7935 | 96.9753 | 28.5028 | 95.0094 | 0.6749 | 90.5751 | 0.27373 | 1999-04-19 | 11:08 | 2.7 | 23.8 | 140.6 | 140 | 380 | 11.7 | 5.2 |  | 16.9 | 0.28756 | 0.69231 | 21.4852 | 26.7046 | 25.3209 | 1096.5021 | 277.8602 | 1071.2966 | 8.0604 | 132.2396 | 0.19148 | 6.07 |  |  | 299.886 |  |  | 1046.944 |  | 43.391 | 1035.4432 | 71.0379 | 0.038 |  |  | 0.9935 |  | 88.5542 | 0.97879 | 96.1177 | [8 empty] | Parameter | Units | Cp-1 | Cp-1 (dup) | Average | RPD | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | SDS-HAA5p, ug/L | 11.05 | 0 | 7.8 | 7.1 | SDS-HAA5p, ug/L | 11.05 | 0 | 7.8 | 7.1 | Construction Contingencies (% of construction costs) | 15
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Negative | [9 empty] | Total aluminum (mg/L) |  |  |  |  | Alkalinity | mg/L as CaCO3 | 3.5 | 3.1 | 3.3 | 12.1212 | 1999-04-17 | 10:20 | 20.8 | 24.7 | 92.3 | 91.4 | 411 | 11.8 | 5.1 | 16.9 | 0.31102 | 0.69822 | 23.3195 | 26.9329 | 24.8669 | 98.6201 | 28.9862 | 96.6208 | 0.68634 | 91.1637 | 0.27277 | 1999-04-19 | 13:56 | 5.5 | 24.7 | 140.2 | 139.6 | 411 | 11.3 | 5.3 |  | 16.6 | 0.31102 | 0.68072 | 23.759 | 25.7916 | 23.8132 | 1076.2598 | 273.4224 | 1054.1866 | 7.918 | 131.982 | 0.18043 | 6.11 |  |  | 283.336 |  |  | 1055.1232 |  | 46.5151 | 1044.5135 | 72.8739 | 0.034 |  |  | 0.96736 |  | 89.759 | 0.95453 | 96.438 | [8 empty] | Sampling date | MM/DD/YY | 1999-04-20 | 1999-04-20 | --- | --- | 1999-04-20 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY |  |  | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-04-22 | 1999-04-22 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-04-23 | 1999-04-23 | --- | --- | --- | --- | --- | SDS-TOXF, ug Cl- /L | 854 | 854 | 854 | 854 | SDS-TOXF, ug Cl- /L | 854 | 854 | 854 | 854 | Engineering Fee Factor (% of construction costs) | 10
Phone Number |  |  |  | Experimental Design1,2 | [8 empty] | Fluoride (mg/L) |  |  |  |  | Total dissolved solids | mg/L | 454 | 605.5 | 529.75 | 28.5984 | 1999-04-17 | 20:00 | 30.4 | 25.2 | 104.3 | 104.3 | 411 | 11.8 | 5.1 | 16.9 | 0.31102 | 0.69822 | 23.3195 | 26.9329 | 24.5021 | 98.6201 | 28.9862 | 96.6208 | 0.68634 | 103.6137 | 0.23648 | 1999-04-19 | 16:00 | 7.5 | 25.2 | 140.3 | 140 | 411 | 11.3 | 5.3 |  | 16.6 | 0.31102 | 0.68072 | 23.759 | 25.7916 | 23.4639 | 1076.2598 | 273.4224 | 1054.1866 | 7.918 | 132.232 | 0.17744 | 6.18 | 6.05 | 6.05 | 280.026 | 510.195 | 908.831 | 1062.1804 | -16.8733 | 47.14 | 1051.4282 | 73.3671 | 0.031 | 0.336 | 0.999 | 0.97375 | 2.5271 | 90.6627 | 0.96079 | 96.7735 | [8 empty] | Sampling time | hh:mm | NR | NR | --- | --- | NR | --- | --- | --- | --- | --- | Sampling time | hh:mm | NR | NR | --- | --- | --- | --- | --- | Sampling time | hh:mm | NR | NR | --- | --- | --- | --- | --- | Sampling time | hh:mm | NR | NR | --- | --- | --- | --- | --- | SDS-TOXp, ug Cl- /L | 89 | 0 | 62.4 | 47.5 | SDS-TOXp, ug Cl- /L | 89 | 0 | 62.4 | 47.5 | 1998 ENR Construction Cost Index (CCI base year 1913) | 5875
FAX Number |  | Design Parameters |  | ID# | Recovery | FW-design | Dp | PI | QI-cell | Qp | QF | QW | Phosphate (mg/L) |  |  |  |  | Total hardness | mg/L as CaCO3 | 243 | 269 | 256 | 10.1562 | 1999-04-18 | 10:30 | 45 | 25 | 107.5 | 106.9 | 411 | 11.8 | 5.1 | 16.9 | 0.31102 | 0.69822 | 23.3195 | 26.9329 | 24.6474 | 98.6201 | 28.9862 | 96.6208 | 0.68634 | 106.5137 | 0.2314 | 1999-04-20 | 12:50 | 28.4 | 26.8 | 149.8 | 149.5 | 411 | 11.5 | 5.3 |  | 16.8 | 0.31102 | 0.68452 | 23.4643 | 26.2481 | 22.7761 | 1082.6389 | 274.9403 | 1060.0391 | 7.964 | 141.686 | 0.16075 | 5.8 |  |  | 254.208 |  |  | 1127.6242 |  | 52.0136 | 1115.4048 | 77.2094 | 0.024 |  |  | 1.0003 |  | 92.7711 | 0.98664 | 97.5675 | [8 empty] | Operation time | hh.hh | 82.9 | 82.9 | --- | --- | 82.9 | --- | --- | --- | --- | --- | Operation time | hh.hh |  |  | --- | --- | --- | --- | --- | Operation time | hh.hh | 131.1 | 131.1 | --- | --- | --- | --- | --- | Cumulative time | hr | 154.7 | 154.7 | --- | --- | --- | --- | --- | SDS-CDF, mg/L | 10.39 | 10.39 | 10.39 | 10.39 | SDS-CDF, mg/L | 10.39 | 10.39 | 10.39 | 10.39 | 1998 Producers Price Index (PPI base year 1967 = 100) | 369
E-Mail Address (optional) |  | Design flux, FW (gfd) | 27 |  | (decimal) | (gfd) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | Sulfate (mg/L) | 26.5 |  |  |  | Calcium hardness | mg/L as CaCO3 | 232 | 257 | 244.5 | 10.2249 | 1999-04-18 | 13:45 | 48.2 | 25 | 107.5 | 107.2 | 411 | 11.8 | 5.1 | 16.9 | 0.31102 | 0.69822 | 23.3195 | 26.9329 | 24.6474 | 98.6201 | 28.9862 | 96.6208 | 0.68634 | 106.6637 | 0.23108 | 1999-04-20 | 16:46 | 32.3 | 27.1 | 150.4 | 150.3 | 411 | 11.5 | 5.3 |  | 16.8 | 0.31102 | 0.68452 | 23.4643 | 26.2481 | 22.575 | 1082.6389 | 274.9403 | 1060.0391 | 7.964 | 142.386 | 0.15855 | 6.3 | 6.46 | 6.2 | 242.292 | 483.301 | 903.749 | 1153.4796 | -27.6327 | 54.263 | 1140.7319 | 78.76 | 0.024 | 0.306 | 0.97 | 1.0003 | -3.1239 | 92.7711 | 0.98664 | 97.5675 | [8 empty] | pH | --- | 7 | 6.94 | 6.97 | 0.86083 | 6.48 | --- | --- | --- | --- | --- | pH | --- |  |  | --- | --- | --- | --- | --- | pH | --- | 6.51 | 6.36 | --- | --- | --- | --- | --- | pH | --- | 6.74 | 6.31 | --- | --- | --- | --- | --- | SDS-CDp, mg/L | 3.075 | 0 | 2.41 | 2.18 | SDS-CDp, mg/L | 3.075 | 0 | 2.41 | 2.18 | Labor Rate + Fringe ($/work-hour) | 19.89
|  | Net driving pressure at the design flux, NDP (psi) | 68 | 1 | 0.7 | 27 | 14.3517 | 96.3062 | 411.456 | 11.8281 | 16.8973 | 5.0692 | Calcium (mg/L) |  |  |  |  | Turbidity | ntu | 0.27 | 0.22 | 0.245 | 20.4082 | 1999-04-19 | 8:11 | 66.7 | 25 | 107.3 | 106.6 | 411 | 11.3 | 5.4 | 16.7 | 0.31102 | 0.67665 | 23.6108 | 25.7916 | 23.603 | 95.7106 | 28.156 | 93.8533 | 0.66626 | 106.2837 | 0.22208 | 1999-04-21 | 10:20 | 49.6 | 26.5 | 147 | 146.5 | 411 | 11.4 | 11.7 |  | 23.1 | 0.31102 | 0.49351 | 16.7922 | 26.0199 | 22.7792 | 838.4179 | 212.9592 | 821.0694 | 6.1678 | 140.5822 | 0.16203 | 6.33 |  |  | 225.592 |  |  | 826.1091 |  | 57.4154 | 817.7807 | 72.4141 | 0.034 |  |  | 0.62236 |  | 89.759 | 0.6142 | 94.4643 | [8 empty] | Temperature | oC | NR | NR | #DIV/0! | #VALUE! | NR | --- | --- | --- | --- | --- | Temperature | oC | NR | NR | --- | --- | --- | --- | --- | Temperature | oC | NR | NR | --- | --- | --- | --- | --- | Temperature | oC | NR | NR | --- | --- | --- | --- | --- | TOCF, mg/L | 10.225 | 10.225 | 10.225 | 10.225 | TOCF, mg/L | 10.225 | 10.225 | 10.225 | 10.225 | Labor Overhead Factor (% of labor) | 6
Technical ICR Contact Person |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.36 | 2 | 0.9 | 27 | 39.785 | 121.7395 | 411.456 | 11.8281 | 13.1424 | 1.3142 | Barium (mg/L) | 0.018 |  |  |  | Ammonia | mg NH3-N / L | 0.56 | 0.38 | 0.47 | 38.2979 | [21 empty] | 1999-04-21 | 13:33 | 53.1 | 26.8 | 147.6 | 147.1 | 411 | 11.4 | 11.9 |  | 23.3 | 0.31102 | 0.48927 | 16.6395 | 26.0199 | 22.5781 | 834.2455 | 211.8994 | 816.9833 | 6.1371 | 141.2129 | 0.15989 | 6.4 |  |  | 222.132 |  |  | 824.4429 |  | 58.0685 | 816.0897 | 72.7809 | 0.037 |  |  | 0.61461 |  | 88.8554 | 0.60659 | 93.9004 | [8 empty] | Alkalinity | mg/L as CaCO3 | 1.9 | 4.3 | 3.1 | 77.4194 | 6.3 | 3.6882 | 41.4566 | 6.0606 | 3.6804 | 15.7699 | Alkalinity | mg/L as CaCO3 |  |  | 3.3 | #DIV/0! | 100 | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 | 1.6 | 4.5 | 4.9333 | -9.6296 | 51.5152 | 4.8864 | 67.2563 | Alkalinity | mg/L as CaCO3 | 2 | 4.4 | 3.8571 | 12.3377 | 39.3939 | 3.832 | 47.8079 | TOCp, mg/L | 0.85 | 0 | 0.66 | 0.44 | TOCp, mg/L | 0.85 | 0 | 0.66 | 0.44 | Electric Rate ($/kW-h) | 0.05
Mailing Address |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | 3 | 0.5 | 27 | 9.265 | 91.2195 | 411.456 | 11.8281 | 23.6562 | 11.8281 | Strontium (mg/L) |  |  |  |  | Total organic carbon | mg/L | 10.6 | 9.85 | 10.225 | 7.335 | [21 empty] | 1999-04-21 | 16:55 | 56.4 | 26.8 | 148 | 147 | 411 | 11.5 | 12.1 |  | 23.6 | 0.31102 | 0.48729 | 16.4153 | 26.2481 | 22.7761 | 832.3375 | 211.3753 | 814.9626 | 6.1227 | 141.3773 | 0.1611 | 6.44 | 6.5 | 6.23 | 222.132 | 487.256 | 756.01 | 822.1142 | -8.7438 | 58.0685 | 813.7203 | 72.7017 | 0.028 | 0.305 | 0.629 | 0.62093 | 1.2837 | 91.5663 | 0.61263 | 95.4295 | [8 empty] | Total dissolved solids | mg/L | 318 | 242 | 280 | 27.1429 | 909 | 1014.5588 | -11.6126 | 47.1449 | 1004.7683 | 72.1329 | Total dissolved solids | mg/L |  |  | 529.75 | #DIV/0! | 100 | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L | 222 | 756 | 825.4314 | -9.184 | 58.0934 | 816.9422 | 72.8255 | Total dissolved solids | mg/L | 177 | 645 | 680.9286 | -5.5703 | 66.588 | 674.1053 | 73.743 | UV254 F, cm-1 | 0.332 | 0.332 | 0.332 | 0.332 | UV254 F, cm-1 | 0.332 | 0.332 | 0.332 | 0.332 | Fuel Oil Rate ($/gal) | NA
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 400 | 4 | 0.3 | 27 | 7.085 | 89.0395 | 411.456 | 11.8281 | 39.4271 | 27.599 | Reactive silica (mg/L as SiO2) | 32.8 |  |  |  | UV254 | cm-1 | 0.311 | 0.353 | 0.332 | 12.6506 | [21 empty] | 1999-04-22 | 8:39 | 72.2 | 26.3 | 146 | 145 | 411 | 11 | 16.1 |  | 27.1 | 0.31102 | 0.4059 | 14.1661 | 25.1069 | 22.1102 | 759.7454 | 193.1204 | 744.5802 | 5.5904 | 139.9096 | 0.15803 | 6.33 |  |  | 181.608 |  |  | 767.611 |  | 65.7182 | 759.7691 | 76.0969 | 0.02 |  |  | 0.54517 |  | 93.9759 | 0.53814 | 96.2835 | [8 empty] | Total hardness | mg/L as CaCO3 | 137 | 138 | 137.5 | 0.72727 | 447 | 486.0294 | -8.7314 | 46.2891 | 481.384 | 71.4365 | Total hardness | mg/L as CaCO3 |  |  | 256 | #DIV/0! | 100 | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 | 109 | 356 | 397.2353 | -11.5829 | 57.4219 | 393.1804 | 72.2774 | Total hardness | mg/L as CaCO3 | 101 | 319 | 322.4286 | -1.0748 | 60.5469 | 319.4304 | 68.3812 | UV254 p, cm-1 | 0.027 | 0 | 0.023 | 0.019 | UV254 p, cm-1 | 0.027 | 0 | 0.023 | 0.019 | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Purchase price for an equivalent 8" x 40 " element ($) | 875 | 1: For experimental matrix see Table 4-2 in Part 3 of the ICR Treatment Studies Manual. | [8 empty] | Turbidity (ntu) |  |  |  |  | SUVA | L/(mg*m) | 2.934 | 3.5838 | 3.2589 | 19.9393 | [21 empty] | 1999-04-22 | 9:25 | 72.6 | 25.6 | 150 | 148 | 411 | 11.3 | 26.1 |  | 37.4 | 0.31102 | 0.30214 | 9.9893 | 25.7916 | 23.1881 | 683.8846 | 173.74 | 669.8587 | 5.0313 | 143.9687 | 0.16106 | 6.23 |  |  | 180.292 |  |  | 681.0479 |  | 65.9666 | 674.164 | 73.257 | 0.018 |  |  | 0.46795 |  | 94.5783 | 0.46176 | 96.1019 | [8 empty] | Calcium hardness | mg/L as CaCO3 | 130 | 131 | 130.5 | 0.76628 | 426 | 465.7941 | -9.3413 | 46.6258 | 461.3252 | 71.7119 | Calcium hardness | mg/L as CaCO3 |  |  | 244.5 | #DIV/0! | 100 | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 | 103 | 339 | 380.451 | -12.2274 | 57.8732 | 376.5478 | 72.6462 | Calcium hardness | mg/L as CaCO3 | 96.1 | 304 | 308.1 | -1.3487 | 60.6953 | 305.2295 | 68.5155 | BromideF, ug/L | 108.5 | 108.5 | 108.5 | 108.5 | BromideF, ug/L | 108.5 | 108.5 | 108.5 | 108.5 | Current Process Water Rate ($/1000 gal) | 0.41
FAX Number |  | Maximum flow rate to the 8" x 40" element, QI, max (gpm) | 75 | 2: Flow rates and pressures may need to be adjusted in order to obtain the desired operating conditions. | [8 empty] | SDI |  |  |  |  | Bromide | mg/L | 107 | 110 | 108.5 | 2.765 | [21 empty] | 1999-04-22 | 13:37 | 76.8 | 26.4 | 150.1 | 149.8 | 411 | 11.4 | 25.3 |  | 36.7 | 0.31102 | 0.31063 | 10.1989 | 26.0199 | 22.8466 | 689.5336 | 175.1424 | 675.2659 | 5.0726 | 144.8774 | 0.1577 |  | 6.35 |  |  | 487.256 | [7 empty] | 0.296 | [14 empty] | Turbidity | ntu | BMRL | 0.11 | 0.11 | #VALUE! | 0.17 | 0.50706 | -198.2699 | 55.102 | 0.50177 | 78.0775 | Turbidity | ntu |  |  | 0.245 | #DIV/0! | 100 | #DIV/0! | #DIV/0! | Turbidity | ntu | BMRL | 0.07 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | 0.05 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Bromidep, ug/L | 89 | 0 | 60.5 | 55.776 | Bromidep, ug/L | 89 | 0 | 60.5 | 55.776 | Modifications to Existing Plant (% of construction costs) | 10
E-Mail Address (optional) |  | Minimum flow rate to the 8" x 40" element, QI, min (gpm) | 25 | [9 empty] | MFI |  |  |  |  | SDS-Cl2 dose | mg/L | 11.8 | 11.3 | 11.55 | 4.329 | [21 empty] | 1999-04-22 | 396:43 | 80.2 | 26.5 | 150 | 149 | 411 | 11.6 | 25.5 |  | 37.1 | 0.31102 | 0.31267 | 10.0782 | 26.4764 | 23.1788 | 690.9301 | 175.4316 | 676.3808 | 5.0822 | 144.4178 | 0.1605 | 6.57 | 6.2 | 6.3 | 177.002 | 473.809 | 644.924 | 690.2158 | -7.0228 | 66.5876 | 682.9733 | 74.0836 | 0.021 | 0.333 | 0.48 | 0.47347 | 1.3595 | 93.6747 | 0.46709 | 95.5041 | [8 empty] | Ammonia | mg NH3-N / L | 0.34 | 0.34 | 0.34 | 0 | 0.68 | 0.72235 | -6.2284 | 27.6596 | 0.71726 | 52.5972 | Ammonia | mg NH3-N / L |  |  | 0.47 | #DIV/0! | 100 | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | 0.37 | 0.76 | 0.56608 | 25.516 | 21.2766 | 0.56332 | 34.318 | Ammonia | mg NH3-N / L | 0.28 | 0.76 | 0.55143 | 27.4436 | 40.4255 | 0.54775 | 48.8821 | AlkF, mg/L CaCO3 | 3.3 | 3.3 | 3.3 | 3.3 | AlkF, mg/L CaCO3 | 3.3 | 3.3 | 3.3 | 3.3
|  | Total width of all membrane envelopes in the 8" x 40" element, w (ft) | 76.667 | [9 empty] | MPFI |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | SDS-Free Cl2 residual | mg/L | 1.32 | 1 | 1.16 | 27.5862 | [21 empty] | 1999-04-23 | 8:12 | 87.4 | [6 empty] | X | [39 empty] | Total organic carbon | mg/L | 0.86 | 0.84 | 0.85 | 2.3529 | 31.6 | 28.4235 | 10.0521 | 91.687 | 28.056 | 96.9703 | Total organic carbon | mg/L |  |  | 10.225 | #DIV/0! | 100 | #DIV/0! | #DIV/0! | Total organic carbon | mg/L | 0.66 | 19 | 19.4149 | -2.1837 | 93.5452 | 19.1511 | 96.5537 | Total organic carbon | mg/L | 0.44 | 13.9 | 14.4186 | -3.7307 | 95.6968 | 14.2293 | 96.9078 | Alkp, mg/L CaCO3 | 3.1 | 0 | 1.6 | 2 | Alkp, mg/L CaCO3 | 3.1 | 0 | 1.6 | 2
Plant Name | Lime Softening Plant | Feed spacer thickness in the 8" x 40" element, T (ft) | 0.0023333 | [9 empty] | pH | 7.2 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | SDS-Cl2 demand | mg/L | 10.48 | 10.3 | 10.39 | 1.7324 | [21 empty] | 1999-04-23 | 17:03 | 96.4 | 26.2 | 142.5 | 142.3 | 411 | 10 | 25.9 |  | 35.9 | 0.31102 | 0.27855 | 10.4485 | 22.8245 | 20.1597 | 668.5507 | 170.2562 | 656.4268 | 4.9223 | 137.4777 | 0.14664 | 6.49 |  |  | 175.686 |  |  | 666.4542 |  | 66.8361 | 660.4838 | 73.4004 | 0.028 |  |  | 0.44937 |  | 91.5663 | 0.44425 | 93.6972 | [8 empty] | UV254 | cm-1 | 0.027 | 0.027 | 0.027 | 0 | 1.03 | 0.92406 | 10.2856 | 91.8675 | 0.9121 | 97.0398 | UV254 | cm-1 |  |  | 0.332 | #DIV/0! | 100 | #DIV/0! | #DIV/0! | UV254 | cm-1 | 0.023 | 0.63 | 0.62888 | 0.1774 | 93.0723 | 0.62036 | 96.2925 | UV254 | cm-1 | 0.019 | 0.473 | 0.46614 | 1.4497 | 94.2771 | 0.46009 | 95.8704 | T-HdF, mg/L CaCO3 | 256 | 256 | 256 | 256 | T-HdF, mg/L CaCO3 | 256 | 256 | 256 | 256
Treatment Plant Category | SOFT | [11 empty] | Chloride (mg/L) | 59.9 | is to list the pretreatment processes used in this particular RBSMT run. |  |  | SDS-Chlorination temp. | oC | 20 | 20 | 20 | 0 | [21 empty] | 1999-04-23 | 19:58 | 99.3 | 26.5 | 142 | 141.8 | 411 | 10.7 | 26.9 |  | 37.6 | 0.31102 | 0.28457 | 9.9309 | 24.4222 | 21.3805 | 672.4403 | 171.0238 | 659.3864 | 4.9489 | 136.9511 | 0.15612 | 6.59 |  |  | 172.396 |  |  | 671.8945 |  | 67.4571 | 665.3925 | 74.0911 | 0.026 |  |  | 0.45372 |  | 92.1687 | 0.44815 | 94.1984 | [8 empty] | SUVA | L/(mg*m) | 3.1395 | 3.2143 | 3.1769 | 2.3529 | 3.2595 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 3.4848 | 3.3158 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 4.3182 | 3.4029 | --- | --- | --- | --- | --- | T-Hdp, mg/L CaCO3 | 137.5 | 0 | 109 | 101 | T-Hdp, mg/L CaCO3 | 137.5 | 0 | 109 | 101
Process Train Name | NA | Additional Information | [10 empty] | Mg (mg/L) | 44 |  |  |  | SDS-Chlorination pH | --- | 7.49 | 7.48 | 7.485 | 0.1336 | [21 empty] | 1999-04-23 | 23:35 | 102.9 | 26.4 | 141.3 | 141.1 | 411 | 10.9 | 26.5 |  | 37.4 | 0.31102 | 0.29144 | 9.9893 | 24.8787 | 21.8446 | 676.865 | 172.085 | 663.4779 | 4.9809 | 136.2191 | 0.16036 | 6.5 | 6.53 | 6.38 | 169.106 | 478.555 | 636.244 | 678.0904 | -6.5771 | 68.0782 | 671.3411 | 74.8107 | 0.022 | 0.337 | 0.472 | 0.45951 | 2.6463 | 93.3735 | 0.45371 | 95.1511 | [8 empty] | Bromide | mg/L | 78 | 100 | 89 | 24.7191 | --- | 146.3529 | --- | 17.9724 | 145.5885 | 38.8688 | Bromide | mg/L |  | --- | 108.5 | --- | 100 | #DIV/0! | #DIV/0! | Bromide | mg/L | 60.5 | --- | 154.6176 | --- | 44.2396 | 153.2936 | 60.5332 | Bromide | mg/L | 55.776 | --- | 131.096 | --- | 48.5935 | 130.0762 | 57.1205 | Ca-HdF, mg/L CaCO3 | 244.5 | 244.5 | 244.5 | 244.5 | Ca-HdF, mg/L CaCO3 | 244.5 | 244.5 | 244.5 | 244.5
ICR Treatment Plant Identification Number | 1086 | Design cross-flow velocity (fps) | Unknown | [9 empty] | Potassium (mg/L) | 25.1 |  |  |  | SDS-Incubation time | hours | 24.32 | 24.38 | 24.35 | 0.24641 | [70 empty] | SDS-Cl2 dose | mg/L | 3.92 | 3.92 | 3.92 | 0 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L |  | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 3 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 3 | --- | --- | --- | --- | --- | --- | Ca-Hdp, mg/L CaCO3 | 130.5 | 0 | 103 | 96.1 | Ca-Hdp, mg/L CaCO3 | 130.5 | 0 | 103 | 96.1
PWSID Number of Plant (if assigned) | 45-00351 | Required influent flow to permeate flow rate ratio, QI:Qp | 5 | [9 empty] | Strontium (mg/L) | 1.14 |  |  |  | SDS-TOX | mg Cl- /L | 1080 | 628 | 854 | 52.9274 | [70 empty] | SDS-Free Cl2 residual | mg/L | 0.84 | 0.85 | 0.845 | 1.1834 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L |  | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.59 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.82 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 18 | Maximum element recovery (%) | 20 | [14 empty] | SDS-CHCl3 | mg/L | 143 | 131 | 137 | 8.7591 | [70 empty] | SDS-Cl2 demand | mg/L | 3.08 | 3.07 | 3.075 | 0.3252 | --- | 24.5897 | --- | 70.4042 | 24.3029 | 87.3472 | SDS-Cl2 demand | mg/L | 0 | --- | 10.39 | --- | 100 | #DIV/0! | #DIV/0! | SDS-Cl2 demand | mg/L | 2.41 | --- | 18.0571 | --- | 76.8046 | 17.8369 | 86.4887 | SDS-Cl2 demand | mg/L | 2.18 | --- | 13.9086 | --- | 79.0183 | 13.7498 | 84.1452 | Blended Water Quality if THM4 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if THM4 Controls the Blend Ratio
Historical Average Water Temperature (oC) | 20 | Variability of design flux (%) | 15 | [14 empty] | SDS-BDCM | mg/L | 27.3 | 23.9 | 25.6 | 13.2812 | [70 empty] | SDS-Chlorination temp. | oC | 20 | 20 | 20 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC |  | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 20 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 20 | --- | --- | --- | --- | --- | --- | Qp/QT (THM4), % | 67.2904 | 56.4955 | 62.963 | 62.7096 | Qp/QT (THM4), % | 93.199 | 78.2477 | 87.2054 | 86.8545
State Approved Plant Capacity (MGD) | 22.4 | Rejection of reference solute and conditions of test | min 70% avg 80% | [14 empty] | SDS-DBCM | mg/L | 2.9 | 2.9 | 2.9 | 0 | [70 empty] | SDS-Chlorination pH | --- | 7.48 | 7.5 | 7.49 | 0.26702 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- |  | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.4 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.57 | --- | --- | --- | --- | --- | --- | SDS-THM4b, ug/L | 72 | 72 | 72 | 72 | SDS-THM4b, ug/L | 36 | 36 | 36 | 36
|  | (e.g., solute type and concentration) | 500 ppm NaCl | [9 empty] | Sodium (mg/L) | 32.8 |  |  |  | SDS-CHBr3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [70 empty] | SDS-Incubation time | hours | 24.47 | 24.1 | 24.285 | 1.5236 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours |  | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24.08 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 23.88 | --- | --- | --- | --- | --- | --- | SDS-HAA5b, ug/L | 89.733 | 109.4574 | 98.0963 | 98.2751 | SDS-HAA5b, ug/L | 27.4098 | 54.7287 | 38.9933 | 39.2408
|  | Variability of rejection of reference solute (%) | 10 | [9 empty] | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | SDS-THM4 | mg/L | 173.2 | 157.8 | 165.5 | 9.3051 | [70 empty] | SDS-TOX | mg Cl- /L | 95.3 | 82.7 | 89 | 14.1573 | --- | 2339 | --- | 89.5785 | 2309.0109 | 96.1455 | SDS-TOX | mg Cl- /L |  | --- | 854 | --- | 100 | #DIV/0! | #DIV/0! | SDS-TOX | mg Cl- /L | 62.4 | --- | 1614.5569 | --- | 92.6932 | 1592.7209 | 96.0822 | SDS-TOX | mg Cl- /L | 47.5 | --- | 1199.6429 | --- | 94.4379 | 1184.0427 | 95.9883 | SDS-TOXb, ug Cl- /L | 339.2285 | 371.5287 | 355.5852 | 348.2471 | SDS-TOXb, ug Cl- /L | 141.0277 | 185.7644 | 163.6822 | 153.5188
|  | Standard testing recovery (%) | 15 | [9 empty] | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | SDS-MCAA* | mg/L | 6.4 | 7.8 | 7.1 | 19.7183 | [70 empty] | SDS-CHCl3 | mg/L | 7.4 | 9.1 | 8.25 | 20.6061 | --- | 386.9265 | --- | 93.9781 | 381.8793 | 97.8396 | SDS-CHCl3 | mg/L |  | --- | 137 | --- | 100 | #DIV/0! | #DIV/0! | SDS-CHCl3 | mg/L | 4.7 | --- | 264.1118 | --- | 96.5693 | 260.4623 | 98.1955 | SDS-CHCl3 | mg/L | 4.5 | --- | 193.7857 | --- | 96.7153 | 191.2228 | 97.6467 | SDS-CDb, mg/L | 5.4677 | 4.5201 | 5.3656 | 5.2415 | SDS-CDb, mg/L | 3.5725 | 2.2601 | 3.431 | 3.2592
|  | Standard testing pH | 6.5-7 | [14 empty] | SDS-DCAA* | mg/L | NR | 98.8 | 98.8 | #VALUE! | [70 empty] | SDS-BDCM | mg/L | 8.1 | 10.4 | 9.25 | 24.8649 | --- | 57.3382 | --- | 63.8672 | 56.6973 | 83.6853 | SDS-BDCM | mg/L |  | --- | 25.6 | --- | 100 | #DIV/0! | #DIV/0! | SDS-BDCM | mg/L | 6.2 | --- | 44.2392 | --- | 75.7812 | 43.7041 | 85.8137 | SDS-BDCM | mg/L | 6.1 | --- | 33.9571 | --- | 76.1719 | 33.58 | 81.8344 | TOCb, mg/L | 3.9165 | 4.4483 | 4.2026 | 4.0889 | TOCb, mg/L | 1.4876 | 2.2242 | 1.8838 | 1.7263
|  | Acceptable range of operating pressures | <400 psi | [14 empty] | SDS-TCAA* | mg/L | NR | 145 | 145 | #VALUE! | [70 empty] | SDS-DBCM | mg/L | 6.4 | 9.4 | 7.9 | 37.9747 | --- | -6.8059 | --- | -172.4138 | -6.6099 | 219.5181 | SDS-DBCM | mg/L |  | --- | 2.9 | --- | 100 | #DIV/0! | #DIV/0! | SDS-DBCM | mg/L | 6.1 | --- | -0.17451 | --- | -110.3448 | -0.086239 | 7173.349 | SDS-DBCM | mg/L | 5.8 | --- | 1.6571 | --- | -100 | 1.7132 | -238.5403 | UV254 b, cm-1 | 0.12676 | 0.14444 | 0.13744 | 0.13572 | UV254 b, cm-1 | 0.047743 | 0.072218 | 0.062535 | 0.060146
|  | Acceptable range of operating pH values | 3-10 | [14 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [70 empty] | SDS-CHBr3 | mg/L | 1.1 | 1.2 | 1.15 | 8.6957 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L |  | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | Bromideb, ug/L | 95.3784 | 47.2024 | 78.2778 | 75.437 | Bromideb, ug/L | 90.3262 | 23.6012 | 66.6414 | 62.7069
|  | Typical pressure drop across a single element (psi) | 3-5 | [14 empty] | SDS-DBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [70 empty] | SDS-THM4 | mg/L | 23 | 30.1 | 26.55 | 26.742 | --- | 435.2265 | --- | 83.9577 | 429.7794 | 93.8224 | SDS-THM4 | mg/L | 0 | --- | 165.5 | --- | 100 | #DIV/0! | #DIV/0! | SDS-THM4 | mg/L | 17 | --- | 308.1765 | --- | 89.7281 | 304.0802 | 94.4094 | SDS-THM4 | mg/L | 16.4 | --- | 229.4 | --- | 90.0906 | 226.5159 | 92.7599 | Alkb, mg/L CaCO3 | 3.1654 | 1.4356 | 2.2296 | 2.4848 | Alkb, mg/L CaCO3 | 3.1136 | 0.71782 | 1.8175 | 2.1709
|  | Maximum permissible SDI | 5 | [14 empty] | SDS-BCAA* | mg/L | 7.3 | 7.7 | 7.5 | 5.3333 | [70 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L |  | --- | 7.1 | --- | 100 | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | T-Hdb, mg/L CaCO3 | 176.2609 | 111.3716 | 163.4444 | 158.8001 | T-Hdb, mg/L CaCO3 | 145.5592 | 55.6858 | 127.8081 | 121.3756
|  | Maximum permissible turbidity (ntu) | 1 | [14 empty] | SDS-TBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [70 empty] | SDS-DCAA* | mg/L | 4.5 | 4.2 | 4.35 | 6.8966 | --- | 282.1441 | --- | 95.5972 | 278.4415 | 98.4377 | SDS-DCAA* | mg/L |  | --- | 98.8 | --- | 100 | #DIV/0! | #DIV/0! | SDS-DCAA* | mg/L | 3.1 | --- | 190.7471 | --- | 96.8623 | 188.1072 | 98.352 | SDS-DCAA* | mg/L | 2.8 | --- | 139.9429 | --- | 97.166 | 138.0859 | 97.9723 | Ca-Hdb, mg/L CaCO3 | 167.789 | 106.3686 | 155.4074 | 151.439 | Ca-Hdb, mg/L CaCO3 | 138.2531 | 53.1843 | 121.1044 | 115.608
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | <0.1 mg/L | [14 empty] | SDS-CDBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [70 empty] | SDS-TCAA* | mg/L | 5.5 | 4.5 | 5 | 20 | --- | 416.7647 | --- | 96.5517 | 411.2765 | 98.7843 | SDS-TCAA* | mg/L |  | --- | 145 | --- | 100 | #DIV/0! | #DIV/0! | SDS-TCAA* | mg/L | 3.3 | --- | 281.1431 | --- | 97.7241 | 277.2344 | 98.8097 | SDS-TCAA* | mg/L | 2.9 | --- | 205.9 | --- | 98 | 203.1514 | 98.5725
|  | 1: All of the information requested in this field may not be available, but values for all Design | [15 empty] | SDS-DCBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [70 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L |  | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  | Parameters must be entered in cells E14:E23, since these parameters are used in calculations. | [15 empty] | SDS-HAA5 | mg/L | NR | 251.6 | 251.6 | #VALUE! | [70 empty] | SDS-DBAA* | mg/L | 1.5 | 1.9 | 1.7 | 23.5294 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DBAA* | mg/L |  | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DBAA* | mg/L | 1.4 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DBAA* | mg/L | 1.4 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | Blended Water Quality if HAA5 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if HAA5 Controls the Blend Ratio
[18 empty] | SDS-HAA6 | mg/L | NR | 259.3 | 259.3 | #VALUE! | [70 empty] | SDS-BCAA* | mg/L | 3.4 | 3.6 | 3.5 | 5.7143 | --- | 15.2647 | --- | 53.3333 | 15.1079 | 76.8333 | SDS-BCAA* | mg/L |  | --- | 7.5 | --- | 100 | #DIV/0! | #DIV/0! | SDS-BCAA* | mg/L | 2.7 | --- | 12.1118 | --- | 64 | 11.9794 | 77.4612 | SDS-BCAA* | mg/L | 2.6 | --- | 9.6 | --- | 65.3333 | 9.5052 | 72.6466 | Qp/QT (HAA5), % | 82.1451 | 78.5374 | 81.05 | 80.818 | Qp/QT (HAA5), % | 93.3694 | 89.2687 | 92.1247 | 91.8609
[18 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [75 empty] | SDS-TBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-THM4b, ug/L | 51.3594 | 35.5207 | 45.1407 | 45.0004 | SDS-THM4b, ug/L | 35.7633 | 17.7603 | 28.6948 | 28.5353
[18 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, | [75 empty] | SDS-CDBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-HAA5b, ug/L | 54 | 54 | 54 | 54 | SDS-HAA5b, ug/L | 27 | 27 | 27 | 27
[18 empty] | should be reported if measured. | [75 empty] | SDS-DCBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TOXb, ug Cl- /L | 225.5901 | 183.2909 | 212.4079 | 202.2029 | SDS-TOXb, ug Cl- /L | 139.7244 | 91.6455 | 124.7409 | 113.1415
[94 empty] | SDS-HAA5 | mg/L | 11.5 | 10.6 | 11.05 | 8.1448 | --- | 718.55 | --- | 95.6081 | 709.1201 | 98.4417 | SDS-HAA5 | mg/L | 0 | --- | 251.6 | --- | 100 | #DIV/0! | #DIV/0! | SDS-HAA5 | mg/L | 7.8 | --- | 485.8392 | --- | 96.8998 | 479.1141 | 98.372 | SDS-HAA5 | mg/L | 7.1 | --- | 356.3857 | --- | 97.1781 | 351.6563 | 97.981 | SDS-CDb, mg/L | 4.3811 | 2.23 | 3.9222 | 3.7548 | SDS-CDb, mg/L | 3.56 | 1.115 | 3.0384 | 2.8482
[94 empty] | SDS-HAA6 | mg/L | 14.9 | 14.2 | 14.55 | 4.811 | --- | 734.4029 | --- | 94.3887 | 724.8084 | 97.9926 | SDS-HAA6 | mg/L | 0 | --- | 259.3 | --- | 100 | #DIV/0! | #DIV/0! | SDS-HAA6 | mg/L | 10.5 | --- | 498.3431 | --- | 95.9506 | 491.4801 | 97.8636 | SDS-HAA6 | mg/L | 9.7 | --- | 366.2714 | --- | 96.2592 | 361.4434 | 97.3163 | TOCb, mg/L | 2.5239 | 2.1946 | 2.4726 | 2.317 | TOCb, mg/L | 1.4716 | 1.0973 | 1.4133 | 1.2364
[94 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | UV254 b, cm-1 | 0.081457 | 0.071256 | 0.081555 | 0.07904 | UV254 b, cm-1 | 0.047223 | 0.035628 | 0.047335 | 0.044475
[94 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | Bromideb, ug/L | 92.4817 | 23.287 | 69.596 | 65.8895 | Bromideb, ug/L | 90.293 | 11.6435 | 64.2801 | 60.0672
[133 empty] | Alkb, mg/L CaCO3 | 3.1357 | 0.70827 | 1.9221 | 2.2494 | Alkb, mg/L CaCO3 | 3.1133 | 0.35413 | 1.7339 | 2.1058
[133 empty] | T-Hdb, mg/L CaCO3 | 158.6581 | 54.9444 | 136.8564 | 130.7321 | T-Hdb, mg/L CaCO3 | 145.3573 | 27.4722 | 120.5767 | 113.6155
[133 empty] | Ca-Hdb, mg/L CaCO3 | 150.8546 | 52.4762 | 129.8142 | 124.5661 | Ca-Hdb, mg/L CaCO3 | 138.0589 | 26.2381 | 114.1436 | 108.1784
[133 empty] | Notes: |  |  |  |  | Notes:
[133 empty] | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to |  |  |  |  | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to
[133 empty] | determine the percentage of total flow that must be treated by the membrane process to meet the |  |  |  |  | determine the percentage of total flow that must be treated by the membrane process to meet the
[133 empty] | Stage 1 DBP MCLs. |  |  |  |  | Stage 2 DBP MCLs.
[133 empty] | A 10% factor of safety has been applied all the MCLs. i.e., 72 / 54 mg/L for THM4 and HAA5. |  |  |  |  | A 10% factor of safety has been applied all the MCLs. i.e., 36 / 27 mg/L for THM4 and HAA5.
[133 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for |  |  |  |  | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for
[133 empty] | both parameters and the maximum (Qp/QT) ratio controls the design. |  |  |  |  | both parameters and the maximum (Qp/QT) ratio controls the design.
[133 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. |  |  |  |  | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[133 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. |  |  |  |  | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[133 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. |  |  |  |  | The subscript "b" refers to the blended water quality for a given blend ratio.
[133 empty] | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL. |  |  |  |  | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL.
[133 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. |  |  |  |  | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
Note on Z27: C. Hill (11/15/99): Verified by the utility.
Note on AA27: C. Hill (11/15/99): Verified by the utility.
Note on CY29: TSC_ADM: Reported SDS temperature is a measured value - the consultant used an incubator for SDS testing.
Note on DL10: TSC_ADM: Consultant was unable to operate the RBSMT system at 90% recovery for this membrane without exceeding 150 psi; thus, no water quality data at 90% recovery was collected.
Note on DL29: TSC_ADM: Reported SDS temperature is a measured value - the consultant used an incubator for SDS testing.
Note on DV29: TSC_ADM: Reported SDS temperature is a measured value - the consultant used an incubator for SDS testing.
Note on EF29: TSC_ADM: Reported SDS temperature is a measured value - the consultant used an incubator for SDS testing.
Print All Fields

## DCSS1. 4th Quarter
FIELD-SET 4: Membrane D, Run 1 (FILE: Delray1.xls)
Field 4-1: PWS And Treatment Plant Data |  | Field 4-2: Manufacturer Reported Membrane Characteristics1 |  | Field 4-3: RBSMT Design Parameters | [8 empty] | Field 4-4: Foulants And Fouling Indices1 |  | Field 4-5: Pretreatment Used Prior To Membranes1 |  |  | Field 4-6: Feed Water Quality After Pretreatment | [5 empty] | Field 4-7: Membrane Setting Data | [20 empty] | Field 4-8: Membrane Performance Data During Operation With The Test Water | [16 empty] | Field 4-8: Membrane Performance Data During Operation With The Test Water (continued) | [19 empty] | Field 4-8: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 4-9: Permeate And Concentrate Water Quality For Run 1 | [11 empty] | Field 4-10: Permeate And Concentrate Water Quality For Run 2 | [8 empty] | Field 4-11: Permeate And Concentrate Water Quality For Run 3 | [8 empty] | Field 4-12: Permeate And Concentrate Water Quality For Run 4 | [8 empty] | Field 4-13: Blending Calculations For Stage 1 D-DBP MCLs |  |  |  |  | Field 4-14: Blending Calculations For Proposed Stage 2 D-DBP MCLs |  |  |  |  | Field 4-15: Membrane Cost Parameters
|  | General Information |  | Input Design Parameters | [8 empty] | Parameters Evaluated Prior to Pretreatment | [80 empty] | Operating Parameters During Sample Collection | [11 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Feed and Permeate Water Quality Parameters |  |  |  |  | Feed and Permeate Water Quality Parameters |  |  |  |  | General Cost Parameters
PWS Name | Delray Beach Water Department | Membrane manufacturer | Fluid Systems | [5 empty] | Active membrane area in bench-scale cell, Acell (ft2) | 0.16667 |  |  | Alkalinity (mg/L as CaCO3) | 243 | Process | Description | Scale | Parameter | Units | CF-1 | CF-2 | Average | RPD |  |  |  | Average TDS rejection (decimal fraction) | 0.7 | [5 empty] | TDS concentration of setting solution (mg/L) | 50 | [12 empty] | Average bulk TDS rejection (decimal fraction) | 0.71965 | [45 empty] | Recovery during sample collection (decimal) | 0.69 | [10 empty] | Recovery during sample collection (decimal) | 0.91 | [7 empty] | Recovery during sample collection (decimal) | 0.79 | [7 empty] | Recovery during sample collection (decimal) | 0.38 | [8 empty] | RUN ID # |  |  |  |  | RUN ID # |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | FL4500351 | Membrane trade name | TFC 8921S-400 | [5 empty] | Active width of membrane in the bench-scale cell, wcell (ft) | 0.33333 |  |  | Calcium Hardness (mg/L as CaCO3) | 295 | Acidification | Hydrochloric acid to pH 6.5 | Bench | Sampling date | MM/DD/YY | 1999-03-23 | 1999-03-26 | --- | --- | [71 empty] | Feed flow rate during sample collection (mL/min) | 9.4 | [10 empty] | Feed flow rate during sample collection (mL/min) | 7.13 | [7 empty] | Feed flow rate during sample collection (mL/min) | 13.1 | [7 empty] | Feed flow rate during sample collection (mL/min) | 22.8 | [6 empty] | Parameter | 1 | 2 | 3 | 4 | Parameter | 1 | 2 | 3 | 4 | Capital Recovery Interest Rate (%) | 5.75
Water Industry Data Base Number (optional) | NA | Molecular weight cutoff (Daltons) | 200 | [5 empty] | Average yearly temperature of feed water, TavgoC (oC) | 22 |  |  | LSI |  | Antiscalant addition | King Lee PreTreat 0100, 3 ppm by volume | Bench | Sampling time | hh:mm | 13:45 | 10:12 | --- | --- | Date | Time | Setting time | Influent | PI | PC | QI | Qp | QW | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) | Date | Time | Operation time | Influent | PI | PC | QI | Qp | QW | Cleaning Event | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1) | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Influent flow rate during sample collection (mL/min) | 300 | [10 empty] | Influent flow rate during sample collection (mL/min) | 300 | [7 empty] | Influent flow rate during sample collection (mL/min) | 300 | [7 empty] | Influent flow rate during sample collection (mL/min) | 300 | [6 empty] | SDS-THM4F, ug/L | 174.4 | 174.4 | 174.4 | 174.4 | SDS-THM4F, ug/L | 174.4 | 174.4 | 174.4 | 174.4 | Capital Recovery Period (years) | 25
|  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide | [5 empty] | Approximate feed water TDS, TDSF (mg/L) | 545 |  |  | Dissolved iron (mg/L) |  | Cartridge filtration | 5 micron nominal | Bench | Operation time | hh.hh | 43.1 | 110 | --- | --- | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | Indicate with "X" | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) | [39 empty] | SDS-THM4p, ug/L | 39.05 | 62.8 | 22.9 | 14.3 | SDS-THM4p, ug/L | 39.05 | 62.8 | 22.9 | 14.3 | Overhead & Profit Factor (% of construction costs) | 15
Official ICR Contact Person |  | Membrane construction (e.g., thin-film composite) | Thin-Film Composite | [5 empty] | Manufacturer reported TDS rejection, RejTDS (decimal fraction) | 0.7 |  |  | Total iron (mg/L) |  |  |  |  | pH | --- | 6.2 | 6.9 | 6.55 | 10.687 | 1999-03-16 | 18:30 | 0 | [18 empty] | 1999-03-21 | 21:05 | 0.8 | 22 | 83.6 | 83.4 | 300 | 6.7 | 2.8 |  | 9.5 | 0.24449 | 0.70526 | 30.5789 | 15.2924 | 15.2924 | 955.5297 | 263.5473 | 940.0754 | 6.8426 | 76.6574 | 0.19949 | [27 empty] | Permeate and Concentrate Water Quality | [11 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | SDS-HAA5F, ug/L | 197.25 | 197.25 | 197.25 | 197.25 | SDS-HAA5F, ug/L | 197.25 | 197.25 | 197.25 | 197.25 | Special Sitework Factor (% of construction costs) | 5
Mailing Address |  | Membrane hydrophobicity | Hydrophilic | [5 empty] | Temperature normalized MTCW (gfd/psi) | 0.24251 |  |  | Dissolved aluminum (mg/L) |  |  |  |  | Temperature | oC | NR | NR | #DIV/0! | #VALUE! | 1999-03-16 | 19:20 | 0.83333 | 22.6 | 75.4 | 75.2 | 300 | 6.7 | 2.7 | 9.4 | 0.24449 | 0.71277 | 30.9149 | 15.2924 | 15.0236 | 100.4624 | 29.6644 | 98.8813 | 0.70007 | 74.5999 | 0.20139 | 1999-03-22 | 10:10 | 14 | 23 | 113.3 | 113.1 | 300 | 6.5 | 2.8 |  | 9.3 | 0.24449 | 0.69892 | 31.2581 | 14.8359 | 14.4038 | 946.4658 | 261.1763 | 931.6179 | 6.7787 | 106.4213 | 0.13535 | 5.84 |  |  | 318.16 |  |  | 814.1821 |  | 31.9444 | 808.8086 | 60.6631 | 0.136 |  |  | 0.79364 |  | 59.2814 | 0.78652 | 82.7086 | [8 empty] | Parameter | Units | Cp-1 | Cp-1 (dup) | Average | RPD | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | SDS-HAA5p, ug/L | 17.7 | 37.6 | 10 | 7 | SDS-HAA5p, ug/L | 17.7 | 37.6 | 10 | 7 | Construction Contingencies (% of construction costs) | 15
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Negative | [9 empty] | Total aluminum (mg/L) |  |  |  |  | Alkalinity | mg/L as CaCO3 | 9.8 | 5 | 7.4 | 64.8649 | 1999-03-17 | 16:35 | 22.0833 | 23.6 | 74.1 | 73.7 | 300 | 6.7 | 2.7 | 9.4 | 0.24449 | 0.71277 | 30.9149 | 15.2924 | 14.586 | 100.4624 | 29.6644 | 98.8813 | 0.70007 | 73.1999 | 0.19926 | 1999-03-22 | 12:59 | 16.7 | 23.5 | 104.2 | 103.8 | 300 | 6.8 | 2.8 |  | 9.6 | 0.24449 | 0.70833 | 30.25 | 15.5206 | 14.8475 | 959.9869 | 264.7113 | 944.2273 | 6.874 | 97.126 | 0.15287 | 5.78 |  |  | 247.64 |  |  | 1001.4457 |  | 47.0289 | 992.9026 | 75.059 | 0.065 |  |  | 0.98729 |  | 80.5389 | 0.97683 | 93.3458 | [8 empty] | Sampling date | MM/DD/YY | 1999-03-23 | 1999-03-23 | --- | --- | 1999-03-23 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-03-24 | 1999-03-24 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-03-25 | 1999-03-25 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-03-26 | 1999-03-26 | --- | --- | --- | --- | --- | SDS-TOXF, ug Cl- /L | 939.5 | 939.5 | 939.5 | 939.5 | SDS-TOXF, ug Cl- /L | 939.5 | 939.5 | 939.5 | 939.5 | Engineering Fee Factor (% of construction costs) | 10
Phone Number |  |  |  | Experimental Design1,2 | [8 empty] | Fluoride (mg/L) |  |  |  |  | Total dissolved solids | mg/L | 449 | 486 | 467.5 | 7.9144 | 1999-03-17 | 18:26 | 23.9333 | 23.3 | 72 | 71.8 | 300 | 6.6 | 2.8 | 9.4 | 0.24449 | 0.70213 | 30.9149 | 15.0641 | 14.4963 | 98.9618 | 29.2283 | 97.4277 | 0.68966 | 71.2103 | 0.20357 | 1999-03-22 | 15:58 | 19.7 | 23.8 | 101.8 | 101.6 | 300 | 6.5 | 2.9 |  | 9.4 | 0.24449 | 0.69149 | 30.9149 | 14.8359 | 14.0672 | 936.2613 | 258.3603 | 921.5735 | 6.7056 | 94.9944 | 0.14808 | 5.66 | 5.97 | 6.43 | 241.08 | 468.272 | 1659.921 | 974.9931 | 41.2627 | 48.4321 | 967.0424 | 75.0704 | 0.032 | 0.355 | 1.018 | 1.0109 | 0.69778 | 90.4192 | 1.0003 | 96.8009 | [8 empty] | Sampling time | hh:mm | NR | NR | --- | --- | NR | --- | --- | --- | --- | --- | Sampling time | hh:mm | NR | NR | --- | --- | --- | --- | --- | Sampling time | hh:mm | NR | NR | --- | --- | --- | --- | --- | Sampling time | hh:mm | NR | NR | --- | --- | --- | --- | --- | SDS-TOXp, ug Cl- /L | 134 | 211 | 104 | 46.7 | SDS-TOXp, ug Cl- /L | 134 | 211 | 104 | 46.7 | 1998 ENR Construction Cost Index (CCI base year 1913) | 5875
FAX Number |  | Design Parameters |  | ID# | Recovery | FW-design | Dp | PI | QI-cell | Qp | QF | QW | Phosphate (mg/L) |  |  |  |  | Total hardness | mg/L as CaCO3 | 225 | 218 | 221.5 | 3.1603 | 1999-03-18 | 11:35 | 41.0833 | 23.4 | 74.6 | 74.3 | 300 | 6.7 | 2.9 | 9.6 | 0.24449 | 0.69792 | 30.25 | 15.2924 | 14.6725 | 98.3936 | 29.0535 | 96.845 | 0.68566 | 73.7643 | 0.19891 | 1999-03-23 | 10:53 | 38.6 | 23.3 | 124 | 123.7 | 300 | 6.7 | 0.7 |  | 7.4 | 0.24449 | 0.90541 | 39.5405 | 15.2924 | 14.7159 | 1357.7605 | 374.4877 | 1335.8008 | 9.7229 | 114.1271 | 0.12894 | 5.78 |  |  | 343.36 |  |  | 1655.6971 |  | 26.554 | 1641.0427 | 79.0767 | 0.076 |  |  | 2.8034 |  | 77.2455 | 2.773 | 97.2593 | [8 empty] | Operation time | hh.hh | 28.4 | 28.4 | --- | --- | 28.4 | --- | --- | --- | --- | --- | Operation time | hh.hh | 52.2 | 52.2 | --- | --- | --- | --- | --- | Operation time | hh.hh | 76.4 | 76.4 | --- | --- | --- | --- | --- | Cumulative time | hr | 99.8 | 99.8 | --- | --- | --- | --- | --- | SDS-CDF, mg/L | 11.195 | 11.195 | 11.195 | 11.195 | SDS-CDF, mg/L | 11.195 | 11.195 | 11.195 | 11.195 | 1998 Producers Price Index (PPI base year 1967 = 100) | 369
E-Mail Address (optional) |  | Design flux, FW (gfd) | 15 |  | (decimal) | (gfd) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | Sulfate (mg/L) | 26.5 |  |  |  | Calcium hardness | mg/L as CaCO3 | 214 | 207 | 210.5 | 3.3254 | [21 empty] | 1999-03-23 | 14:27 | 42.2 | 24.1 | 132.9 | 132.6 | 300 | 6.7 | 0.63 |  | 7.33 | 0.24449 | 0.91405 | 39.9277 | 15.2924 | 14.372 | 1382.9097 | 381.4242 | 1360.5432 | 9.903 | 122.847 | 0.11699 | 5.752 |  |  | 386.048 |  |  | 1333.7356 |  | 17.4229 | 1323.153 | 70.8236 | 0.08 |  |  | 3.0353 |  | 76.0479 | 3.0023 | 97.3353 | [8 empty] | pH | --- | 6.39 | 6.25 | 6.32 | 2.2152 | 7.28 | --- | --- | --- | --- | --- | pH | --- | 6.35 | 8.34 | --- | --- | --- | --- | --- | pH | --- | 6.85 | 6.98 | --- | --- | --- | --- | --- | pH | --- | 6.7 | 6.5 | --- | --- | --- | --- | --- | SDS-CDp, mg/L | 2.97 | 4.88 | 3.13 | 2.02 | SDS-CDp, mg/L | 2.97 | 4.88 | 3.13 | 2.02 | Labor Rate + Fringe ($/work-hour) | 19.89
|  | Net driving pressure at the design flux, NDP (psi) | 56.5 | 1 | 0.7 | 15 | 14.3517 | 76.2041 | 299.4788 | 6.5712 | 9.3874 | 2.8162 | Calcium (mg/L) |  |  |  |  | Turbidity | ntu | 0.39 | 0.17 | 0.28 | 78.5714 | [21 empty] | 1999-03-23 | 16:04 | 43.8 | 24.3 | 133.3 | 133.1 | 300 | 6.5 | 0.63 |  | 7.13 | 0.24449 | 0.91164 | 41.0757 | 14.8359 | 13.8608 | 1375.3017 | 379.5131 | 1353.7263 | 9.85 | 123.35 | 0.11237 | 6.14 | 6.13 | 6.6 | 401.824 | 483.301 | 2819.915 | 1145.1095 | 59.3921 | 14.0483 | 1137.0573 | 64.6611 | 0.078 | 0.348 | 0.726 | 2.9753 | -309.8168 | 76.6467 | 2.9439 | 97.3504 | [8 empty] | Temperature | oC | NR | NR | #DIV/0! | #VALUE! | NR | --- | --- | --- | --- | --- | Temperature | oC | NR | NR | --- | --- | --- | --- | --- | Temperature | oC | NR | NR | --- | --- | --- | --- | --- | Temperature | oC | NR | NR | --- | --- | --- | --- | --- | TOCF, mg/L | 10.74 | 10.74 | 10.74 | 10.74 | TOCF, mg/L | 10.74 | 10.74 | 10.74 | 10.74 | Labor Overhead Factor (% of labor) | 6
Technical ICR Contact Person |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.265 | 2 | 0.9 | 15 | 39.785 | 101.6375 | 299.4788 | 6.5712 | 7.3013 | 0.73013 | Barium (mg/L) | 0.018 |  |  |  | Ammonia | mg NH3-N / L | 0.39 | 0.44 | 0.415 | 12.0482 | [21 empty] | 1999-03-24 | 9:07 | 60.9 | 24 | 154.1 | 153.9 | 300 | 6.8 | 6.4 |  | 13.2 | 0.24449 | 0.51515 | 21.7273 | 15.5206 | 14.6297 | 745.7344 | 205.6323 | 733.4921 | 5.3398 | 148.6602 | 0.09841 | 6.01 |  |  | 342.912 |  |  | 599.8747 |  | 26.6498 | 596.9625 | 42.5572 | 0.074 |  |  | 0.61025 |  | 77.8443 | 0.60417 | 87.7518 | [8 empty] | Alkalinity | mg/L as CaCO3 | 5.2 | 5 | 5.1 | 3.9216 | 29.5 | 12.5194 | 57.5615 | 31.0811 | 12.4392 | 59.0004 | Alkalinity | mg/L as CaCO3 | 6.3 | NR | 18.5222 | #VALUE! | 14.8649 | 18.3901 | 65.7424 | Alkalinity | mg/L as CaCO3 | 2.6 | 9.5 | 25.4571 | -167.9699 | 64.8649 | 25.0629 | 89.6261 | Alkalinity | mg/L as CaCO3 | 0.5 | 2 | 11.629 | -481.4516 | 93.2432 | 11.4683 | 95.6402 | TOCp, mg/L | 1.745 | 2.81 | 1.13 | 0.61 | TOCp, mg/L | 1.745 | 2.81 | 1.13 | 0.61 | Electric Rate ($/kW-h) | 0.05
Mailing Address |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | 3 | 0.5 | 15 | 9.265 | 71.1175 | 299.4788 | 6.5712 | 13.1424 | 6.5712 | Strontium (mg/L) |  |  |  |  | Total organic carbon | mg/L | 11.08 | 10.4 | 10.74 | 6.3315 | [21 empty] | 1999-03-24 | 13:38 | 65.4167 | 24.8 | 132.1 | 131.8 | 300 | 6.8 | 6.4 |  | 13.2 | 0.24449 | 0.51515 | 21.7273 | 15.5206 | 14.2878 | 745.7344 | 205.6323 | 733.4921 | 5.3398 | 126.6102 | 0.11285 | 5.93 |  |  | 204.288 |  |  | 747.1627 |  | 56.302 | 741.0102 | 72.4311 | 0.031 |  |  | 0.65594 |  | 90.7186 | 0.64885 | 95.2224 | [8 empty] | Total dissolved solids | mg/L | 238 | 244 | 241 | 2.4896 | 1660 | 971.6452 | 41.4672 | 48.4492 | 963.7469 | 74.9934 | Total dissolved solids | mg/L | 402 | 2820 | 1129.7778 | 59.937 | 14.0107 | 1121.9077 | 64.1682 | Total dissolved solids | mg/L | 197 | 1280 | 1485.0952 | -16.0231 | 57.861 | 1462.8777 | 86.5334 | Total dissolved solids | mg/L | 102 | 659 | 691.5161 | -4.9342 | 78.1818 | 683.0035 | 85.066 | UV254 F, cm-1 | 0.334 | 0.334 | 0.334 | 0.334 | UV254 F, cm-1 | 0.334 | 0.334 | 0.334 | 0.334 | Fuel Oil Rate ($/gal) | NA
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 400 | 4 | 0.3 | 15 | 7.085 | 68.9375 | 299.4788 | 6.5712 | 21.9039 | 15.3328 | Reactive silica (mg/L as SiO2) | 32.8 |  |  |  | UV254 | cm-1 | 0.33 | 0.338 | 0.334 | 2.3952 | [21 empty] | 1999-03-24 | 16:35 | 68.3667 | 24.7 | 121.2 | 121 | 300 | 6.5 | 6.6 |  | 13.1 | 0.24449 | 0.49618 | 21.9008 | 14.8359 | 13.6979 | 729.6274 | 201.3399 | 718.1811 | 5.2256 | 115.8744 | 0.11821 | 6.07 | 6.32 | 7.84 | 196.992 | 470.645 | 1280.4 | 733.9094 | 42.6812 | 57.8627 | 728.0928 | 72.9441 | 0.028 | 0.344 | 2.76 | 0.63536 | 76.9796 | 91.6168 | 0.62878 | 95.547 | [8 empty] | Total hardness | mg/L as CaCO3 | 104 | 103 | 103.5 | 0.96618 | 765 | 484.1452 | 36.7131 | 53.2731 | 480.0304 | 78.4389 | Total hardness | mg/L as CaCO3 | 162 | 1390 | 823.1111 | 40.7834 | 26.8623 | 815.962 | 80.1461 | Total hardness | mg/L as CaCO3 | 75.2 | 653 | 771.8667 | -18.2032 | 66.0497 | 759.8503 | 90.1033 | Total hardness | mg/L as CaCO3 | 33.4 | 332 | 336.7871 | -1.4419 | 84.921 | 332.4062 | 89.9521 | UV254 p, cm-1 | 0.0515 | 0.081 | 0.037 | 0.018 | UV254 p, cm-1 | 0.0515 | 0.081 | 0.037 | 0.018 | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Purchase price for an equivalent 8" x 40 " element ($) | 846 | 1: For experimental matrix see Table 4-2 in Part 3 of the ICR Treatment Studies Manual. | [8 empty] | Turbidity (ntu) |  |  |  |  | SUVA | L/(mg*m) | 2.9783 | 3.25 | 3.1142 | 8.7234 | [21 empty] | 1999-03-25 | 8:43 | 84.5 | 23.4 | 127.2 | 126.9 | 300 | 6.9 | 15.4 |  | 22.3 | 0.24449 | 0.30942 | 12.4529 | 15.7489 | 15.1105 | 602.5401 | 166.1062 | 592.5021 | 4.3141 | 122.7359 | 0.12311 | 6.78 |  |  | 117.955 |  |  | 624.1143 |  | 74.769 | 618.2935 | 80.9225 | 0.031 |  |  | 0.46976 |  | 90.7186 | 0.46471 | 93.3292 | [8 empty] | Calcium hardness | mg/L as CaCO3 | 99.1 | 98.6 | 98.85 | 0.50582 | 729 | 459.0113 | 37.0355 | 53.0404 | 455.1179 | 78.2804 | Calcium hardness | mg/L as CaCO3 | 155 | 1320 | 771.6667 | 41.5404 | 26.3658 | 764.9981 | 79.7385 | Calcium hardness | mg/L as CaCO3 | 71.9 | 621 | 731.9 | -17.8583 | 65.8432 | 720.5161 | 90.021 | Calcium hardness | mg/L as CaCO3 | 33.4 | 317 | 319.0452 | -0.64516 | 84.133 | 314.9204 | 89.3941 | BromideF, ug/L | 116.5 | 116.5 | 116.5 | 116.5 | BromideF, ug/L | 116.5 | 116.5 | 116.5 | 116.5 | Current Process Water Rate ($/1000 gal) | 0.41
FAX Number |  | Maximum flow rate to the 8" x 40" element, QI, max (gpm) | 70 | 2: Flow rates and pressures may need to be adjusted in order to obtain the desired operating conditions. | [8 empty] | SDI |  |  |  |  | Bromide | mg/L | 128 | 105 | 116.5 | 19.7425 | [21 empty] | 1999-03-25 | 14:23 | 90.1667 | 23.7 | 118.3 | 118.1 | 300 | 6.9 | 15.2 |  | 22.1 | 0.24449 | 0.31222 | 12.5747 | 15.7489 | 14.9771 | 604.1193 | 166.5415 | 594.055 | 4.3255 | 113.8745 | 0.13152 | 6.81 |  |  | 91.32 |  |  | 638.2659 |  | 80.4663 | 631.976 | 85.5501 | 0.02 |  |  | 0.47654 |  | 94.012 | 0.47129 | 95.7563 | [8 empty] | Turbidity | ntu | BMRL | BMRL | #DIV/0! | #VALUE! | 0.3 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu | BMRL | 1.11 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | 0.2 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | 0.24 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Bromidep, ug/L | 73.7 | 90.74 | 54.082 | 22 | Bromidep, ug/L | 73.7 | 90.74 | 54.082 | 22 | Modifications to Existing Plant (% of construction costs) | 10
E-Mail Address (optional) |  | Minimum flow rate to the 8" x 40" element, QI, min (gpm) | 15 | [9 empty] | MFI |  |  |  |  | SDS-Cl2 dose | mg/L | 14.85 | 12.5 | 13.675 | 17.1846 | [21 empty] | 1999-03-25 | 16:24 | 92.1833 | 23.8 | 118.4 | 118.2 | 300 | 7 | 15.8 |  | 22.8 | 0.24449 | 0.30702 | 12.1579 | 15.9771 | 15.1493 | 601.2096 | 165.6984 | 591.0476 | 4.3043 | 113.9957 | 0.13289 | [27 empty] | Ammonia | mg NH3-N / L | 0.24 | 0.25 | 0.245 | 4.0816 | 0.68 | 0.79339 | -16.6746 | 40.9639 | 0.78746 | 68.8873 | Ammonia | mg NH3-N / L | 0.6 | NR | -1.4556 | #VALUE! | -44.5783 | -1.4333 | 141.8606 | Ammonia | mg NH3-N / L | 0.28 | 0.87 | 0.92286 | -6.0755 | 32.5301 | 0.91177 | 69.2905 | Ammonia | mg NH3-N / L | 0.18 | 0.63 | 0.55903 | 11.2647 | 56.6265 | 0.55356 | 67.4831 | AlkF, mg/L CaCO3 | 7.4 | 7.4 | 7.4 | 7.4 | AlkF, mg/L CaCO3 | 7.4 | 7.4 | 7.4 | 7.4
|  | Total width of all membrane envelopes in the 8" x 40" element, w (ft) | 63.2 | [9 empty] | MPFI |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | SDS-Free Cl2 residual | mg/L | 3.42 | 1.54 | 2.48 | 75.8065 | [21 empty] | 1999-03-27 | 8:40 | 132.45 | 22.6 | 108.3 | 107.8 | 300 | 6.7 | 14.5 | X | 21.2 | 0.24449 | 0.31604 | 13.1509 | 15.2924 | 15.0236 | 606.2535 | 167.2125 | 596.4483 | 4.3414 | 103.7086 | 0.14486 | 6.36 | 6.42 | 6.37 | 101.974 | 492.793 | 658.86 | 636.3982 | 3.4092 | 78.1874 | 630.4305 | 83.8247 | 0.02 | 0.33 | 0.491 | 0.47909 | 2.4257 | 94.012 | 0.47396 | 95.7803 | [8 empty] | Total organic carbon | mg/L | 1.76 | 1.73 | 1.745 | 1.7192 | 48.2 | 30.7611 | 36.1802 | 83.7523 | 30.4475 | 94.2688 | Total organic carbon | mg/L | 2.81 | 122.7 | 90.9211 | 25.8997 | 73.8361 | 89.9683 | 96.8767 | Total organic carbon | mg/L | 1.13 | 44.6 | 46.8919 | -5.1388 | 89.4786 | 46.1026 | 97.5489 | Total organic carbon | mg/L | 0.61 | 16.22 | 16.9487 | -4.4927 | 94.3203 | 16.7128 | 96.3501 | Alkp, mg/L CaCO3 | 5.1 | 6.3 | 2.6 | 0.5 | Alkp, mg/L CaCO3 | 5.1 | 6.3 | 2.6 | 0.5
Plant Name | Lime Softening Plant | Feed spacer thickness in the 8" x 40" element, T (ft) | 0.0021667 | [9 empty] | pH | 7.2 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | SDS-Cl2 demand | mg/L | 11.43 | 10.96 | 11.195 | 4.1983 | [70 empty] | UV254 | cm-1 | 0.051 | 0.052 | 0.0515 | 1.9417 | 1.51 | 0.96279 | 36.2391 | 84.5808 | 0.95294 | 94.5957 | UV254 | cm-1 | 0.081 | 3.61 | 2.8921 | 19.8861 | 75.7485 | 2.8617 | 97.1695 | UV254 | cm-1 | 0.037 | 1.28 | 1.4513 | -13.3817 | 88.9222 | 1.4269 | 97.407 | UV254 | cm-1 | 0.018 | 0.516 | 0.52768 | -2.2631 | 94.6108 | 0.52032 | 96.5406 | T-HdF, mg/L CaCO3 | 221.5 | 221.5 | 221.5 | 221.5 | T-HdF, mg/L CaCO3 | 221.5 | 221.5 | 221.5 | 221.5
Treatment Plant Category | SOFT | [11 empty] | Chloride (mg/L) | 59.9 | is to list the pretreatment processes used in this particular RBSMT run. |  |  | SDS-Chlorination temp. | oC | 20 | 20 | 20 | 0 | [70 empty] | SUVA | L/(mg*m) | 2.8977 | 3.0058 | 2.9518 | 3.6606 | 3.1328 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 2.8826 | 2.9421 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 3.2743 | 2.87 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 2.9508 | 3.1813 | --- | --- | --- | --- | --- | T-Hdp, mg/L CaCO3 | 103.5 | 162 | 75.2 | 33.4 | T-Hdp, mg/L CaCO3 | 103.5 | 162 | 75.2 | 33.4
Process Train Name | NA | Additional Information | [10 empty] | Mg (mg/L) | 44 |  |  |  | SDS-Chlorination pH | --- | 7.42 | 7.52 | 7.47 | 1.3387 | [70 empty] | Bromide | mg/L | 70.2 | 77.2 | 73.7 | 9.498 | --- | 211.7645 | --- | 36.7382 | 210.272 | 64.9502 | Bromide | mg/L | 90.74 | --- | 376.9622 | --- | 22.1116 | 373.8671 | 75.7293 | Bromide | mg/L | 54.082 | --- | 351.3106 | --- | 53.5777 | 346.1839 | 84.3777 | Bromide | mg/L | 22 | --- | 174.4194 | --- | 81.1159 | 172.2184 | 87.2255 | Ca-HdF, mg/L CaCO3 | 210.5 | 210.5 | 210.5 | 210.5 | Ca-HdF, mg/L CaCO3 | 210.5 | 210.5 | 210.5 | 210.5
ICR Treatment Plant Identification Number | 1086 | Design cross-flow velocity (fps) | .7 ft/sec @ 15 gfd, 10% recovery | [9 empty] | Potassium (mg/L) | 25.1 |  |  |  | SDS-Incubation time | hours | 22.9 | 21.6 | 22.25 | 5.8427 | [70 empty] | SDS-Cl2 dose | mg/L | 4 | 4 | 4 | 0 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 5.8 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 3.5 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2.95 | --- | --- | --- | --- | --- | --- | Ca-Hdp, mg/L CaCO3 | 98.85 | 155 | 71.9 | 33.4 | Ca-Hdp, mg/L CaCO3 | 98.85 | 155 | 71.9 | 33.4
PWSID Number of Plant (if assigned) | 45-00351 | Required influent flow to permeate flow rate ratio, QI:Qp | 6:1 | [9 empty] | Strontium (mg/L) | 1.14 |  |  |  | SDS-TOX | mg Cl- /L | 970 | 909 | 939.5 | 6.4928 | [70 empty] | SDS-Free Cl2 residual | mg/L | 1.06 | 1 | 1.03 | 5.8252 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.92 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.37 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.93 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 18 | Maximum element recovery (%) | 17 | [14 empty] | SDS-CHCl3 | mg/L | 155 | 138 | 146.5 | 11.6041 | [70 empty] | SDS-Cl2 demand | mg/L | 2.94 | 3 | 2.97 | 2.0202 | --- | 29.5023 | --- | 73.4703 | 29.2154 | 89.8341 | SDS-Cl2 demand | mg/L | 4.88 | --- | 75.0467 | --- | 56.4091 | 74.2879 | 93.431 | SDS-Cl2 demand | mg/L | 3.13 | --- | 41.5348 | --- | 72.0411 | 40.8723 | 92.342 | SDS-Cl2 demand | mg/L | 2.02 | --- | 16.8184 | --- | 81.9562 | 16.6047 | 87.8348 | Blended Water Quality if THM4 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if THM4 Controls the Blend Ratio
Historical Average Water Temperature (oC) | 20 | Variability of design flux (%) | 15 | [14 empty] | SDS-BDCM | mg/L | 27.6 | 22.8 | 25.2 | 19.0476 | [70 empty] | SDS-Chlorination temp. | oC | 20 | 20 | 20 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 20 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 20 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 20 | --- | --- | --- | --- | --- | --- | Qp/QT (THM4), % | 75.6557 | 91.7563 | 67.5908 | 63.96 | Qp/QT (THM4), % | 102.2534 | 124.0143 | 91.3531 | 86.446
State Approved Plant Capacity (MGD) | 22.4 | Rejection of reference solute and conditions of test | 0.85 | [14 empty] | SDS-DBCM | mg/L | 2.8 | 2.6 | 2.7 | 7.4074 | [70 empty] | SDS-Chlorination pH | --- | 7.59 | 7.47 | 7.53 | 1.5936 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.42 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.54 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.58 | --- | --- | --- | --- | --- | --- | SDS-THM4b, ug/L | 72 | 72 | 72 | 72 | SDS-THM4b, ug/L | NA | NA | 36 | 36
|  | (e.g., solute type and concentration) | 500 mg/L NaCl @ 80 psi | [9 empty] | Sodium (mg/L) | 32.8 |  |  |  | SDS-CHBr3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [70 empty] | SDS-Incubation time | hours | 24.9 | 24.9 | 24.9 | 0 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24.9 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24.8 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 22 | --- | --- | --- | --- | --- | --- | SDS-HAA5b, ug/L | 61.4102 | 50.7611 | 70.6863 | 75.5661 | SDS-HAA5b, ug/L | NA | NA | 26.1913 | 32.7865
|  | Variability of rejection of reference solute (%) | 5 | [9 empty] | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | SDS-THM4 | mg/L | 185.4 | 163.4 | 174.4 | 12.6147 | [70 empty] | SDS-TOX | mg Cl- /L | 129 | 139 | 134 | 7.4627 | --- | 2732.3871 | --- | 85.7371 | 2704.2985 | 95.0449 | SDS-TOX | mg Cl- /L | 211 | --- | 8305.4444 | --- | 77.5412 | 8217.9125 | 97.4324 | SDS-TOX | mg Cl- /L | 104 | --- | 4082.5714 | --- | 88.9303 | 4013.9477 | 97.409 | SDS-TOX | mg Cl- /L | 46.7 | --- | 1486.7 | --- | 95.0293 | 1465.9064 | 96.8143 | SDS-TOXb, ug Cl- /L | 330.0933 | 271.0556 | 374.7792 | 368.4649 | SDS-TOXb, ug Cl- /L | NA | NA | 176.2446 | 167.7104
|  | Standard testing recovery (%) | 10 | [9 empty] | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | SDS-MCAA* | mg/L | 6.9 | 5.7 | 6.3 | 19.0476 | [70 empty] | SDS-CHCl3 | mg/L | 20.2 | 18.8 | 19.5 | 7.1795 | --- | 429.1774 | --- | 86.6894 | 424.7488 | 95.4091 | SDS-CHCl3 | mg/L | 34.5 | --- | 1278.9444 | --- | 76.4505 | 1265.4872 | 97.2738 | SDS-CHCl3 | mg/L | 9.2 | --- | 663.0095 | --- | 93.7201 | 651.7324 | 98.5884 | SDS-CHCl3 | mg/L | 7 | --- | 232 | --- | 95.2218 | 228.751 | 96.9399 | SDS-CDb, mg/L | 4.9723 | 5.4006 | 5.7438 | 5.3267 | SDS-CDb, mg/L | NA | NA | 3.8274 | 3.2636
|  | Standard testing pH | 7.5 | [14 empty] | SDS-DCAA* | mg/L | 70.4 | 55.5 | 62.95 | 23.6696 | [70 empty] | SDS-BDCM | mg/L | 13.9 | 13.1 | 13.5 | 5.9259 | --- | 51.2419 | --- | 46.4286 | 50.8339 | 73.4429 | SDS-BDCM | mg/L | 20.2 | --- | 75.7556 | --- | 19.8413 | 75.1548 | 73.1221 | SDS-BDCM | mg/L | 7.4 | --- | 92.1619 | --- | 70.6349 | 90.6999 | 91.8412 | SDS-BDCM | mg/L | 5 | --- | 37.5806 | --- | 80.1587 | 37.1102 | 86.5266 | TOCb, mg/L | 3.9348 | 3.4637 | 4.2445 | 4.2608 | TOCb, mg/L | NA | NA | 1.961 | 1.983
|  | Acceptable range of operating pressures | 0-350 | [14 empty] | SDS-TCAA* | mg/L | 138 | 118 | 128 | 15.625 | [70 empty] | SDS-DBCM | mg/L | 6.1 | 6 | 6.05 | 1.6529 | --- | -4.7565 | --- | -124.0741 | -4.6396 | 230.3982 | SDS-DBCM | mg/L | 8.1 | --- | -51.9 | --- | -200 | -51.2512 | 115.8045 | SDS-DBCM | mg/L | 6.3 | --- | -10.8429 | --- | -133.3333 | -10.5472 | 159.7317 | SDS-DBCM | mg/L | 2.3 | --- | 2.9452 | --- | 14.8148 | 2.9358 | 21.658 | UV254 b, cm-1 | 0.12027 | 0.10186 | 0.13326 | 0.13189 | UV254 b, cm-1 | NA | NA | 0.062681 | 0.060831
|  | Acceptable range of operating pH values | 4-11 | [14 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [70 empty] | SDS-CHBr3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | Bromideb, ug/L | 84.1194 | 92.8636 | 74.3112 | 56.0578 | Bromideb, ug/L | NA | NA | 59.4792 | 34.8086
|  | Typical pressure drop across a single element (psi) | 5 | [14 empty] | SDS-DBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [70 empty] | SDS-THM4 | mg/L | 40.2 | 37.9 | 39.05 | 5.8899 | --- | 475.6629 | --- | 77.6089 | 470.9431 | 91.7081 | SDS-THM4 | mg/L | 62.8 | --- | 1302.8 | --- | 63.9908 | 1289.3908 | 95.1295 | SDS-THM4 | mg/L | 22.9 | --- | 744.3286 | --- | 86.8693 | 731.8851 | 96.8711 | SDS-THM4 | mg/L | 14.3 | --- | 272.5258 | --- | 91.8005 | 268.797 | 94.68 | Alkb, mg/L CaCO3 | 5.6599 | 6.3907 | 4.1556 | 2.9868 | Alkb, mg/L CaCO3 | NA | NA | 3.015 | 1.4352
|  | Maximum permissible SDI | 5 | [14 empty] | SDS-BCAA* | mg/L | 8.6 | 7.6 | 8.1 | 12.3457 | [70 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | 2.2 | --- | 47.7556 | --- | 65.0794 | 47.2629 | 95.3452 | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | T-Hdb, mg/L CaCO3 | 132.2263 | 166.905 | 122.6147 | 101.1912 | T-Hdb, mg/L CaCO3 | NA | NA | 87.8504 | 58.8951
|  | Maximum permissible turbidity (ntu) | 1 | [14 empty] | SDS-TBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [70 empty] | SDS-DCAA* | mg/L | 7.6 | 7.8 | 7.7 | 2.5974 | --- | 185.9258 | --- | 87.7681 | 183.9992 | 95.8152 | SDS-DCAA* | mg/L | 13.3 | --- | 564.9667 | --- | 78.8721 | 559.001 | 97.6208 | SDS-DCAA* | mg/L | 5 | --- | 280.9524 | --- | 92.0572 | 276.1927 | 98.1897 | SDS-DCAA* | mg/L | 3.2 | --- | 99.571 | --- | 94.9166 | 98.1794 | 96.7407 | Ca-Hdb, mg/L CaCO3 | 126.0304 | 159.5753 | 116.8192 | 97.2268 | Ca-Hdb, mg/L CaCO3 | NA | NA | 83.8846 | 57.4042
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | <0.1 mg/L extended | [14 empty] | SDS-CDBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [70 empty] | SDS-TCAA* | mg/L | 7.6 | 10 | 8.8 | 27.2727 | --- | 393.3161 | --- | 93.125 | 389.1595 | 97.7387 | SDS-TCAA* | mg/L | 20.6 | --- | 1213.9333 | --- | 83.9062 | 1201.0288 | 98.2848 | SDS-TCAA* | mg/L | 5 | --- | 590.7143 | --- | 96.0938 | 580.6117 | 99.1388 | SDS-TCAA* | mg/L | 3.8 | --- | 204.1226 | --- | 97.0312 | 201.2299 | 98.1116
|  | 1: All of the information requested in this field may not be available, but values for all Design | [15 empty] | SDS-DCBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [70 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  | Parameters must be entered in cells E14:E23, since these parameters are used in calculations. | [15 empty] | SDS-HAA5 | mg/L | 215.3 | 179.2 | 197.25 | 18.3016 | [70 empty] | SDS-DBAA* | mg/L | 1.2 | 1.2 | 1.2 | 0 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DBAA* | mg/L | 1.5 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | Blended Water Quality if HAA5 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if HAA5 Controls the Blend Ratio
[18 empty] | SDS-HAA6 | mg/L | 223.9 | 186.8 | 205.35 | 18.0667 | [70 empty] | SDS-BCAA* | mg/L | 4.2 | 4 | 4.1 | 4.878 | --- | 17.0032 | --- | 49.3827 | 16.8637 | 75.6875 | SDS-BCAA* | mg/L | 6.1 | --- | 28.3222 | --- | 24.6914 | 28.0819 | 78.2778 | SDS-BCAA* | mg/L | 2.9 | --- | 27.6619 | --- | 64.1975 | 27.2348 | 89.3519 | SDS-BCAA* | mg/L | 1.6 | --- | 12.0839 | --- | 80.2469 | 11.9325 | 86.5912 | Qp/QT (HAA5), % | 79.7828 | 89.7275 | 76.502 | 75.2957 | Qp/QT (HAA5), % | 94.8204 | 106.6395 | 90.9212 | 89.4875
[18 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [75 empty] | SDS-TBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-THM4b, ug/L | 66.414 | 74.2641 | 58.4995 | 53.8516 | SDS-THM4b, ug/L | 46.0606 | NA | 36.6543 | 31.1305
[18 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, | [75 empty] | SDS-CDBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-HAA5b, ug/L | 54 | 54 | 54 | 54 | SDS-HAA5b, ug/L | 27 | NA | 27 | 27
[18 empty] | should be reported if measured. | [75 empty] | SDS-DCBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TOXb, ug Cl- /L | 296.8496 | 285.835 | 300.3258 | 267.2603 | SDS-TOXb, ug Cl- /L | 175.7218 | NA | 179.8531 | 140.5555
[94 empty] | SDS-HAA5 | mg/L | 16.4 | 19 | 17.7 | 14.6893 | --- | 596.8935 | --- | 91.0266 | 590.6325 | 97.0032 | SDS-HAA5 | mg/L | 37.6 | --- | 1811.4889 | --- | 80.9379 | 1792.3064 | 97.9021 | SDS-HAA5 | mg/L | 10 | --- | 901.6667 | --- | 94.9303 | 886.2869 | 98.8717 | SDS-HAA5 | mg/L | 7 | --- | 313.8548 | --- | 96.4512 | 309.4239 | 97.7377 | SDS-CDb, mg/L | 4.6329 | 5.5287 | 5.0251 | 4.2866 | SDS-CDb, mg/L | 3.396 | NA | 3.8622 | 2.9845
[94 empty] | SDS-HAA6 | mg/L | 20.6 | 23 | 21.8 | 11.0092 | --- | 613.8968 | --- | 89.384 | 607.4962 | 96.4115 | SDS-HAA6 | mg/L | 43.7 | --- | 1839.8111 | --- | 78.7193 | 1820.3883 | 97.5994 | SDS-HAA6 | mg/L | 12.9 | --- | 929.3286 | --- | 93.718 | 913.5217 | 98.5879 | SDS-HAA6 | mg/L | 8.6 | --- | 325.9387 | --- | 95.812 | 321.3563 | 97.3238 | TOCb, mg/L | 3.5635 | 3.6246 | 3.3882 | 3.1125 | TOCb, mg/L | 2.2109 | NA | 2.0025 | 1.6749
[94 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | UV254 b, cm-1 | 0.10861 | 0.10699 | 0.10679 | 0.096066 | UV254 b, cm-1 | 0.066132 | NA | 0.063964 | 0.051219
[94 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | Bromideb, ug/L | 82.353 | 93.3862 | 68.749 | 45.3456 | Bromideb, ug/L | 75.9169 | NA | 59.7488 | 31.9343
[133 empty] | Alkb, mg/L CaCO3 | 5.565 | 6.413 | 3.7279 | 2.2046 | Alkb, mg/L CaCO3 | 5.2191 | NA | 3.0358 | 1.2254
[133 empty] | T-Hdb, mg/L CaCO3 | 127.3563 | 168.1121 | 109.5776 | 79.8689 | T-Hdb, mg/L CaCO3 | 109.6119 | NA | 88.4822 | 53.174
[133 empty] | Ca-Hdb, mg/L CaCO3 | 121.4225 | 160.7012 | 104.4682 | 77.1514 | Ca-Hdb, mg/L CaCO3 | 104.633 | NA | 84.4832 | 52.0176
[133 empty] | Notes: |  |  |  |  | Notes:
[133 empty] | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to |  |  |  |  | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to
[133 empty] | determine the percentage of total flow that must be treated by the membrane process to meet the |  |  |  |  | determine the percentage of total flow that must be treated by the membrane process to meet the
[133 empty] | Stage 1 DBP MCLs. |  |  |  |  | Stage 2 DBP MCLs.
[133 empty] | A 10% factor of safety has been applied all the MCLs. i.e., 72 / 54 mg/L for THM4 and HAA5. |  |  |  |  | A 10% factor of safety has been applied all the MCLs. i.e., 36 / 27 mg/L for THM4 and HAA5.
[133 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for |  |  |  |  | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for
[133 empty] | both parameters and the maximum (Qp/QT) ratio controls the design. |  |  |  |  | both parameters and the maximum (Qp/QT) ratio controls the design.
[133 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. |  |  |  |  | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[133 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. |  |  |  |  | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[133 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. |  |  |  |  | The subscript "b" refers to the blended water quality for a given blend ratio.
[133 empty] | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL. |  |  |  |  | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL.
[133 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. |  |  |  |  | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
Note on X24: TSC_ADM: Reported SDS temperature is a measured value - the consultant used an incubator for SDS testing.
Note on CY16: C. Hill (11/15/99): Utility verified the data responsible for the high mass balance closure errors for alkalinity (all four runs), and TDS, total hardness, calcium hardness, TOC and UV (runs 1 and 2). It is believed these errors might be partially due to the incorrect recoveries reported for runs 3 and 4.
Note on CY17: C. Hill (11/15/99): Utility verified the data responsible for the high mass balance closure errors for alkalinity (all four runs), and TDS, total hardness, calcium hardness, TOC and UV (runs 1 and 2). It is believed these errors might be partially due to the incorrect recoveries reported for runs 3 and 4.
Note on CY18: C. Hill (11/15/99): Utility verified the data responsible for the high mass balance closure errors for alkalinity (all four runs), and TDS, total hardness, calcium hardness, TOC and UV (runs 1 and 2). It is believed these errors might be partially due to the incorrect recoveries reported for runs 3 and 4.
Note on CY19: C. Hill (11/15/99): Utility verified the data responsible for the high mass balance closure errors for alkalinity (all four runs), and TDS, total hardness, calcium hardness, TOC and UV (runs 1 and 2). It is believed these errors might be partially due to the incorrect recoveries reported for runs 3 and 4.
Note on CY23: C. Hill (11/15/99): Utility verified the data responsible for the high mass balance closure errors for alkalinity (all four runs), and TDS, total hardness, calcium hardness, TOC and UV (runs 1 and 2). It is believed these errors might be partially due to the incorrect recoveries reported for runs 3 and 4.
Note on CY29: TSC_ADM: Reported SDS temperature is a measured value - the consultant used an incubator for SDS testing.
Note on DL16: C. Hill (11/15/99): Utility verified the data responsible for the high mass balance closure errors for alkalinity (all four runs), and TDS, total hardness, calcium hardness, TOC and UV (runs 1 and 2). It is believed these errors might be partially due to the incorrect recoveries reported for runs 3 and 4.
Note on DL17: C. Hill (11/15/99): Utility verified the data responsible for the high mass balance closure errors for alkalinity (all four runs), and TDS, total hardness, calcium hardness, TOC and UV (runs 1 and 2). It is believed these errors might be partially due to the incorrect recoveries reported for runs 3 and 4.
Note on DL18: C. Hill (11/15/99): Utility verified the data responsible for the high mass balance closure errors for alkalinity (all four runs), and TDS, total hardness, calcium hardness, TOC and UV (runs 1 and 2). It is believed these errors might be partially due to the incorrect recoveries reported for runs 3 and 4.
Note on DL19: C. Hill (11/15/99): Utility verified the data responsible for the high mass balance closure errors for alkalinity (all four runs), and TDS, total hardness, calcium hardness, TOC and UV (runs 1 and 2). It is believed these errors might be partially due to the incorrect recoveries reported for runs 3 and 4.
Note on DL23: C. Hill (11/15/99): Utility verified the data responsible for the high mass balance closure errors for alkalinity (all four runs), and TDS, total hardness, calcium hardness, TOC and UV (runs 1 and 2). It is believed these errors might be partially due to the incorrect recoveries reported for runs 3 and 4.
Note on DL29: TSC_ADM: Reported SDS temperature is a measured value - the consultant used an incubator for SDS testing.
Note on DO21: C. Hill (10/19/99): No value reported by consultant. Reviewer inserted NR.
Note on DV16: C. Hill (11/15/99): Utility verified the data responsible for the high mass balance closure errors for alkalinity (all four runs), and TDS, total hardness, calcium hardness, TOC and UV (runs 1 and 2). It is believed these errors might be partially due to the incorrect recoveries reported for runs 3 and 4.
Note on DV29: TSC_ADM: Reported SDS temperature is a measured value - the consultant used an incubator for SDS testing.
Note on DX5: The recovery reported for Run 3 and 4 was calculated from the weights of the composite sample taken over 16 hours. The recoveries reported in Field 4-8 were measured flow rates for one minute. In this case, the flow rate varied significantly over the course of composite sampling.
Note on EF16: C. Hill (11/15/99): Utility verified the data responsible for the high mass balance closure errors for alkalinity (all four runs), and TDS, total hardness, calcium hardness, TOC and UV (runs 1 and 2). It is believed these errors might be partially due to the incorrect recoveries reported for runs 3 and 4.
Note on EF29: TSC_ADM: Reported SDS temperature is a measured value - the consultant used an incubator for SDS testing.
Note on EH5: The recovery reported for Run 3 and 4 was calculated from the weights of the composite sample taken over 16 hours. The recoveries reported in Field 4-8 were measured flow rates for one minute. In this case, the flow rate varied significantly over the course of composite sampling.
Print All Fields

## DCSS2. 1st Quarter
FIELD-SET 1: Membrane A, Run 2 (FILE: Delray2.xls)
Field 1-1: PWS And Treatment Plant Data |  | Field 1-2: Manufacturer Reported Membrane Characteristics1 |  | Field 1-3: RBSMT Design Parameters | [8 empty] | Field 1-4: Foulants And Fouling Indices1 |  | Field 1-5: Pretreatment Used Prior To Membranes1 |  |  | Field 1-6: Feed Water Quality After Pretreatment | [5 empty] | Field 1-7: Membrane Setting Data | [20 empty] | Field 1-8: Membrane Performance Data During Operation With The Test Water | [16 empty] | Field 1-8: Membrane Performance Data During Operation With The Test Water (continued) | [19 empty] | Field 1-8: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 1-9: Permeate And Concentrate Water Quality For Run 1 | [11 empty] | Field 1-10: Permeate And Concentrate Water Quality For Run 2 | [8 empty] | Field 1-11: Permeate And Concentrate Water Quality For Run 3 | [8 empty] | Field 1-12: Permeate And Concentrate Water Quality For Run 4 | [8 empty] | Field 1-13: Blending Calculations For Stage 1 D-DBP MCLs |  |  |  |  | Field 1-14: Blending Calculations For Proposed Stage 2 D-DBP MCLs |  |  |  |  | Field 1-15: Membrane Cost Parameters
|  | General Information |  | Input Design Parameters | [8 empty] | Parameters Evaluated Prior to Pretreatment | [80 empty] | Operating Parameters During Sample Collection | [11 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Feed and Permeate Water Quality Parameters |  |  |  |  | Feed and Permeate Water Quality Parameters |  |  |  |  | General Cost Parameters
PWS Name | Delray Beach Water Department | Membrane manufacturer | Film Tec | [5 empty] | Active membrane area in bench-scale cell, Acell (ft2) | 0.16667 |  |  | Alkalinity (mg/L as CaCO3) | 243 | Process | Description | Scale | Parameter | Units | CF-1 | CF-2 | Average | RPD |  |  |  | Average TDS rejection (decimal fraction) | 0.7 | [5 empty] | TDS concentration of setting solution (mg/L) | 50 | [12 empty] | Average bulk TDS rejection (decimal fraction) | 0.87832 | [45 empty] | Recovery during sample collection (decimal) | 0.68 | [10 empty] | Recovery during sample collection (decimal) | 0.9 | [7 empty] | Recovery during sample collection (decimal) | 0.5 | [7 empty] | Recovery during sample collection (decimal) | 0.3 | [8 empty] | RUN ID # |  |  |  |  | RUN ID # |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | FL4500351 | Membrane trade name | NF70 | [5 empty] | Active width of membrane in the bench-scale cell, wcell (ft) | 0.33333 |  |  | Calcium Hardness (mg/L as CaCO3) | 295 | Aeration | Fine Bubble diffuwer in barrel overnight | Bench | Sampling date | MM/DD/YY | 1999-05-11 | 1999-05-14 | --- | --- | [71 empty] | Feed flow rate during sample collection (mL/min) | 9.5 | [10 empty] | Feed flow rate during sample collection (mL/min) | 7.2 | [7 empty] | Feed flow rate during sample collection (mL/min) | 13.1 | [7 empty] | Feed flow rate during sample collection (mL/min) | 21.9 | [6 empty] | Parameter | 1 | 2 | 3 | 4 | Parameter | 1 | 2 | 3 | 4 | Capital Recovery Interest Rate (%) | 5.75
Water Industry Data Base Number (optional) | NA | Molecular weight cutoff (Daltons) | 200 | [5 empty] | Average yearly temperature of feed water, TavgoC (oC) | 22 |  |  | LSI |  | Acidification | Hydrochloric acid to pH 6.5 | Bench | Sampling time | hh:mm | NR | NR | --- | --- | Date | Time | Setting time | Influent | PI | PC | QI | Qp | QW | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) | Date | Time | Operation time | Influent | PI | PC | QI | Qp | QW | Cleaning Event | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1) | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Influent flow rate during sample collection (mL/min) | 300 | [10 empty] | Influent flow rate during sample collection (mL/min) | 300 | [7 empty] | Influent flow rate during sample collection (mL/min) | 300 | [7 empty] | Influent flow rate during sample collection (mL/min) | 300 | [6 empty] | SDS-THM4F, ug/L | 234.3 | 234.3 | 234.3 | 234.3 | SDS-THM4F, ug/L | 234.3 | 234.3 | 234.3 | 234.3 | Capital Recovery Period (years) | 25
|  | Membrane material (e.g., PVD, polyamide, etc.) | polyamide | [5 empty] | Approximate feed water TDS, TDSF (mg/L) | 545 |  |  | Dissolved iron (mg/L) |  | Antiscalant addition | King Lee PreTreat 0100, 3 ppm by volume | Bench | Operation time | hh.hh | 61.9 | 133 | --- | --- | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | Indicate with "X" | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) | [39 empty] | SDS-THM4p, ug/L | 3.75 | 5.5 | 0 | 0 | SDS-THM4p, ug/L | 3.75 | 5.5 | 0 | 0 | Overhead & Profit Factor (% of construction costs) | 15
Official ICR Contact Person |  | Membrane construction (e.g., thin-film composite) | thin-film composite | [5 empty] | Manufacturer reported TDS rejection, RejTDS (decimal fraction) | 0.7 |  |  | Total iron (mg/L) |  | Membrane Filtration | 0.1 micron Pall Microza cartridge | Bench | pH | --- | 6.19 | 6.14 | 6.165 | 0.81103 | 1999-05-08 | 11:43 | 0 | [18 empty] | 1999-05-10 | 10:45 | 0 | [46 empty] | Permeate and Concentrate Water Quality | [11 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | SDS-HAA5F, ug/L | 182.4 | 182.4 | 182.4 | 182.4 | SDS-HAA5F, ug/L | 182.4 | 182.4 | 182.4 | 182.4 | Special Sitework Factor (% of construction costs) | 5
Mailing Address |  | Membrane hydrophobicity | Hydrophobic | [5 empty] | Temperature normalized MTCW (gfd/psi) | 0.32671 |  |  | Dissolved aluminum (mg/L) |  |  |  |  | Temperature | oC | NR | NR | #DIV/0! | #VALUE! | 1999-05-08 | 12:15 | 0.5 | 23.1 | 56 | 55.9 | 300 | 6.3 | 2.9 | 9.2 | 0.22702 | 0.68478 | 31.6087 | 14.3794 | 13.9194 | 96.5972 | 28.5505 | 95.1683 | 0.67332 | 55.2767 | 0.25181 | 1999-05-10 | 11:35 | 0.8 | 22.9 | 58.2 | 57.9 | 300 | 7 | 2.9 |  | 9.9 | 0.22702 | 0.70707 | 29.303 | 15.9771 | 15.5577 | 1247.3559 | 148.6597 | 1221.7197 | 10.8588 | 47.1912 | 0.32967 | [27 empty] | Parameter | Units | Cp-1 | Cp-1 (dup) | Average | RPD | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | SDS-HAA5p, ug/L | 0 | 0 | 0 | 0 | SDS-HAA5p, ug/L | 0 | 0 | 0 | 0 | Construction Contingencies (% of construction costs) | 15
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Slightly negative charge | [9 empty] | Total aluminum (mg/L) |  |  |  |  | Alkalinity | mg/L as CaCO3 | 25.5 | 24.7 | 25.1 | 3.1873 | 1999-05-08 | 16:30 | 4.7 | 23 | 56 | 55.9 | 300 | 6.7 | 2.8 | 9.5 | 0.22702 | 0.70526 | 30.5789 | 15.2924 | 14.847 | 99.4064 | 29.3526 | 97.8419 | 0.69272 | 55.2573 | 0.26869 | 1999-05-10 | 14:13 | 3.5 | 23.5 | 65 | 64.7 | 300 | 6.6 | 3 |  | 9.6 | 0.22702 | 0.6875 | 30.25 | 15.0641 | 14.4108 | 1192.5441 | 142.2981 | 1169.4387 | 10.3869 | 54.4631 | 0.2646 | 5.75 |  |  | 102.6 |  |  | 1279.88 |  | 78.1934 | 1266.9299 | 91.9017 | 0 | [15 empty] | Sampling date | MM/DD/YY | 1999-05-11 | 1999-05-11 | --- | --- | 1999-05-11 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-05-12 | 1999-05-12 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-05-13 | 1999-05-13 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-05-14 | 1999-05-14 | --- | --- | --- | --- | --- | SDS-TOXF, ug Cl- /L | 1059 | 1059 | 1059 | 1059 | SDS-TOXF, ug Cl- /L | 1059 | 1059 | 1059 | 1059 | Engineering Fee Factor (% of construction costs) | 10
Phone Number |  |  |  | Experimental Design1,2 | [8 empty] | Fluoride (mg/L) |  |  |  |  | Total dissolved solids | mg/L | 454.5 | 486.5 | 470.5 | 6.8013 | 1999-05-09 | 10:00 | 22.3 | 23.2 | 56.3 | 55.7 | 300 | 7.2 | 2.9 | 10.1 | 0.22702 | 0.71287 | 28.703 | 16.4336 | 15.8609 | 100.5285 | 29.6482 | 98.8274 | 0.7003 | 55.2997 | 0.28682 | 1999-05-10 | 15:42 | 4.9 | 23.7 | 64.8 | 64.7 | 300 | 6.5 | 3 |  | 9.5 | 0.22702 | 0.68421 | 30.5789 | 14.8359 | 14.1088 | 1183.7784 | 141.2946 | 1161.1913 | 10.3119 | 54.4381 | 0.25917 | 5.71 |  |  | 85.975 |  |  | 1303.6375 |  | 81.7269 | 1290.4462 | 93.3376 | 0 | [15 empty] | Sampling time | hh:mm | NR | NR | --- | --- | NR | --- | --- | --- | --- | --- | Sampling time | hh:mm | NR | NR | --- | --- | --- | --- | --- | Sampling time | hh:mm | NR | NR | --- | --- | --- | --- | --- | Sampling time | hh:mm | NR | NR | --- | --- | --- | --- | --- | SDS-TOXp, ug Cl- /L | #DIV/0! | BMRL | BMRL | BMRL | SDS-TOXp, ug Cl- /L | #DIV/0! | BMRL | BMRL | BMRL | 1998 ENR Construction Cost Index (CCI base year 1913) | 5875
FAX Number |  | Design Parameters |  | ID# | Recovery | FW-design | Dp | PI | QI-cell | Qp | QF | QW | Phosphate (mg/L) |  |  |  |  | Total hardness | mg/L as CaCO3 | 238 | 251 | 244.5 | 5.317 | 1999-05-09 | 13:20 | 25.6 | 23.4 | 56.5 | 55.9 | 300 | 7.1 | 2.9 | 10 | 0.22702 | 0.71 | 29 | 16.2054 | 15.5484 | 100.1109 | 29.5322 | 98.4405 | 0.69744 | 55.5026 | 0.28014 | 1999-05-10 | 17:56 | 7.2 | 23.9 | 64.5 | 64 | 300 | 6.5 | 3 |  | 9.5 | 0.22702 | 0.68421 | 30.5789 | 14.8359 | 14.0257 | 1183.7784 | 141.2946 | 1161.1913 | 10.3119 | 53.9381 | 0.26003 | 5.77 | 6.22 |  | 75.525 | 495.166 |  | 1326.2792 |  | 83.9479 | 1312.7293 | 94.2467 | 0 | 0.365 | [14 empty] | Operation time | hh.hh | 61.9 | 61.9 | --- | --- | 61.9 | --- | --- | --- | --- | --- | Operation time | hh.hh | 85.6 | 85.6 | --- | --- | --- | --- | --- | Operation time | hh.hh | 109.1 | 109.1 | --- | --- | --- | --- | --- | Cumulative time | hr | 133 | 133 | --- | --- | --- | --- | --- | SDS-CDF, mg/L | 11.97 | 11.97 | 11.97 | 11.97 | SDS-CDF, mg/L | 11.97 | 11.97 | 11.97 | 11.97 | 1998 Producers Price Index (PPI base year 1967 = 100) | 369
E-Mail Address (optional) |  | Design flux, FW (gfd) | 25 |  | (decimal) | (gfd) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | Sulfate (mg/L) | 26.5 |  |  |  | Calcium hardness | mg/L as CaCO3 | 226 | 238 | 232 | 5.1724 | 1999-05-09 | 19:03 | 31.3 | 23.2 | 56.6 | 56.5 | 300 | 7.2 | 2.9 | 10.1 | 0.22702 | 0.71287 | 28.703 | 16.4336 | 15.8609 | 100.5285 | 29.6482 | 98.8274 | 0.7003 | 55.8497 | 0.28399 | 1999-05-11 | 11:28 | 24.7 | 24.1 | 71.5 | 71.1 | 299 | 6.6 | 0.7 |  | 7.3 | 0.22627 | 0.90411 | 39.9589 | 15.0641 | 14.1575 | 2309.0385 | 275.5035 | 2264.1512 | 20.1109 | 51.1891 | 0.27657 | 5.58 |  |  | 267.631 |  |  | 2383.2649 |  | 43.1177 | 2359.9151 | 88.6593 | 0 | [15 empty] | pH | --- | 6.14 | 6.04 | 6.09 | 1.642 | 6.75 | --- | --- | --- | --- | --- | pH | --- | 6.09 | 7.33 | --- | --- | --- | --- | --- | pH | --- | 5.88 | 6.55 | --- | --- | --- | --- | --- | pH | --- | 5.72 | 6.37 | --- | --- | --- | --- | --- | SDS-CDp, mg/L | 3.455 | 3.59 | 2.81 | 2.39 | SDS-CDp, mg/L | 3.455 | 3.59 | 2.81 | 2.39 | Labor Rate + Fringe ($/work-hour) | 19.89
|  | Net driving pressure at the design flux, NDP (psi) | 70 | 1 | 0.7 | 25 | 14.3517 | 90.8732 | 531.2481 | 10.952 | 15.6457 | 4.6937 | Calcium (mg/L) |  |  |  |  | Turbidity | ntu | 0.05 | 0.04 | 0.045 | 22.2222 | [21 empty] | 1999-05-11 | 15:27 | 28.7 | 24.7 | 79.3 | 79.1 | 299 | 6.6 | 0.7 |  | 7.3 | 0.22627 | 0.90411 | 39.9589 | 15.0641 | 13.9086 | 2309.0385 | 275.5035 | 2264.1512 | 20.1109 | 59.0891 | 0.23538 | 5.78 |  |  | 304.759 |  |  | 2033.2009 |  | 35.2266 | 2014.1244 | 84.8689 | 0 | [15 empty] | Temperature | oC | NR | NR | #DIV/0! | #VALUE! | NR | --- | --- | --- | --- | --- | Temperature | oC | NR | NR | --- | --- | --- | --- | --- | Temperature | oC | NR | NR | --- | --- | --- | --- | --- | Temperature | oC | NR | NR | --- | --- | --- | --- | --- | TOCF, mg/L | 11.05 | 11.05 | 11.05 | 11.05 | TOCF, mg/L | 11.05 | 11.05 | 11.05 | 11.05 | Labor Overhead Factor (% of labor) | 6
Technical ICR Contact Person |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.357 | 2 | 0.9 | 25 | 39.785 | 116.3065 | 531.2481 | 10.952 | 12.1689 | 1.2169 | Barium (mg/L) | 0.018 |  |  |  | Ammonia | mg NH3-N / L | 0.59 | 0.57 | 0.58 | 3.4483 | [21 empty] | 1999-05-11 | 17:06 | 30.3 | 24.9 | 79.4 | 79.1 | 299 | 6.5 | 0.7 |  | 7.2 | 0.22627 | 0.90278 | 40.5278 | 14.8359 | 13.6171 | 2295.46 | 273.9658 | 2251.5145 | 19.9952 | 59.2548 | 0.22981 | 5.62 | 6.36 | 7.67 | 297.024 | 499.912 | 2184.74 | 2081.3486 | 4.7324 | 36.8706 | 2061.9537 | 85.595 | 0 | 0.378 | 3.294 |  | #VALUE! | [11 empty] | Alkalinity | mg/L as CaCO3 | 5.7 | 6.5 | 6.1 | 13.1148 | 67.2 | 65.475 | 2.567 | 75.6972 | 64.8357 | 90.5916 | Alkalinity | mg/L as CaCO3 | 12.5 | 130 | 138.5 | -6.5385 | 50.1992 | 137.1392 | 90.8852 | Alkalinity | mg/L as CaCO3 | 4.5 | 47.2 | 45.7 | 3.178 | 82.0717 | 45.2502 | 90.0553 | Alkalinity | mg/L as CaCO3 | 3.5 | 34.7 | 34.3571 | 0.98806 | 86.0558 | 34.0193 | 89.7117 | TOCp, mg/L | #DIV/0! | 1.17 | BMRL | BMRL | TOCp, mg/L | #DIV/0! | 1.17 | BMRL | BMRL | Electric Rate ($/kW-h) | 0.05
Mailing Address |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | 3 | 0.5 | 25 | 9.265 | 85.7865 | 531.2481 | 10.952 | 21.9039 | 10.952 | Strontium (mg/L) |  |  |  |  | Total organic carbon | mg/L | 10.6 | 11.5 | 11.05 | 8.1448 | [21 empty] | 1999-05-12 | 10:41 | 47.9 | 23.9 | 73.3 | 72.9 | 299 | 6.8 | 6.5 |  | 13.3 | 0.22627 | 0.51128 | 21.4812 | 15.5206 | 14.673 | 855.9396 | 102.0651 | 838.7946 | 7.453 | 65.647 | 0.22351 | 5.44 |  |  | 64.608 |  |  | 895.1255 |  | 86.2682 | 885.6815 | 92.7053 | 0 | [15 empty] | Total dissolved solids | mg/L | 76 | 75 | 75.5 | 1.3245 | 1236.5 | 1309.875 | -5.9341 | 83.9532 | 1296.5849 | 94.177 | Total dissolved solids | mg/L | 297 | 2184 | 2032 | 6.9597 | 36.8757 | 2013.262 | 85.2478 | Total dissolved solids | mg/L | 66 | 817 | 875 | -7.0991 | 85.9724 | 866.1684 | 92.3802 | Total dissolved solids | mg/L | 65.5 | 751.5 | 644.0714 | 14.2952 | 86.0786 | 637.7361 | 89.7293 | UV254 F, cm-1 | 0.3585 | 0.3585 | 0.3585 | 0.3585 | UV254 F, cm-1 | 0.3585 | 0.3585 | 0.3585 | 0.3585 | Fuel Oil Rate ($/gal) | NA
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 400 | 4 | 0.3 | 25 | 7.085 | 83.6065 | 531.2481 | 10.952 | 36.5066 | 25.5546 | Reactive silica (mg/L as SiO2) | 32.8 |  |  |  | UV254 | cm-1 | 0.35 | 0.367 | 0.3585 | 4.742 | [21 empty] | 1999-05-12 | 13:58 | 51.2 | 24.3 | 64.4 | 64 | 299 | 6.6 | 6.5 |  | 13.1 | 0.22627 | 0.50382 | 21.8244 | 15.0641 | 14.074 | 845.7724 | 100.9135 | 829.3307 | 7.3664 | 56.8336 | 0.24764 | 5.44 |  |  | 62.589 |  |  | 884.6866 |  | 86.6973 | 875.6132 | 92.852 | 0 | [15 empty] | Total hardness | mg/L as CaCO3 | 28.9 | 28.7 | 28.8 | 0.69444 | 691 | 702.8625 | -1.7167 | 88.2209 | 695.6051 | 95.8597 | Total hardness | mg/L as CaCO3 | 107 | 1110 | 1482 | -33.5135 | 56.2372 | 1467.15 | 92.7069 | Total hardness | mg/L as CaCO3 | 20.5 | 488 | 468.5 | 3.9959 | 91.6155 | 463.6093 | 95.5782 | Total hardness | mg/L as CaCO3 | 17.3 | 334 | 341.8714 | -2.3567 | 92.9243 | 338.3174 | 94.8865 | UV254 p, cm-1 | #DIV/0! | 0.0415 | BMRL | BMRL | UV254 p, cm-1 | #DIV/0! | 0.0415 | BMRL | BMRL | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Purchase price for an equivalent 8" x 40 " element ($) | 600 | 1: For experimental matrix see Table 4-2 in Part 3 of the ICR Treatment Studies Manual. | [8 empty] | Turbidity (ntu) |  |  |  |  | SUVA | L/(mg*m) | 3.3019 | 3.1913 | 3.2466 | 3.4061 | [21 empty] | 1999-05-12 | 16:21 | 53.6 | 24.1 | 64.8 | 64.6 | 299 | 6.6 | 6.5 |  | 13.1 | 0.22627 | 0.50382 | 21.8244 | 15.0641 | 14.1575 | 845.7724 | 100.9135 | 829.3307 | 7.3664 | 57.3336 | 0.24693 | 5.54 | 6.29 | 6.4 | 65.954 | 497.539 | 817.3 | 881.2698 | -7.827 | 85.9821 | 872.2713 | 92.4388 | 0 | 0.401 | 0.725 |  | #VALUE! | [11 empty] | Calcium hardness | mg/L as CaCO3 | 28.9 | 28.7 | 28.8 | 0.69444 | 656 | 663.8 | -1.189 | 87.5862 | 656.9632 | 95.6162 | Calcium hardness | mg/L as CaCO3 | 102 | 1050 | 1402 | -33.5238 | 56.0345 | 1387.96 | 92.6511 | Calcium hardness | mg/L as CaCO3 | 20.5 | 464 | 443.5 | 4.4181 | 91.1638 | 438.8822 | 95.329 | Calcium hardness | mg/L as CaCO3 | 17.3 | 317 | 324.0143 | -2.2127 | 92.5431 | 320.6558 | 94.6048 | BromideF, ug/L | 130 | 130 | 130 | 130 | BromideF, ug/L | 130 | 130 | 130 | 130 | Current Process Water Rate ($/1000 gal) | 0.41
FAX Number |  | Maximum flow rate to the 8" x 40" element, QI, max (gpm) | 75 | 2: Flow rates and pressures may need to be adjusted in order to obtain the desired operating conditions. | [8 empty] | SDI |  |  |  |  | Bromide | mg/L | 138 | 122 | 130 | 12.3077 | [21 empty] | 1999-05-13 | 11:15 | 72.2 | 22 | 67.6 | 67.3 | 299 | 6.7 | 15.3 |  | 22 | 0.22627 | 0.30455 | 12.5909 | 15.2924 | 15.2924 | 642.9523 | 76.6909 | 630.2635 | 5.5992 | 61.8508 | 0.24725 | 5.42 |  |  | 240.13 |  |  | 571.381 |  | 48.9628 | 567.6696 | 57.699 | 0 | [15 empty] | Turbidity | ntu | BMRL | BMRL | #DIV/0! | #VALUE! | 0.12 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu | BMRL | 0.63 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | 0.07 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | 0.1 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Bromidep, ug/L | 25.5 | 71 | BMRL | BMRL | Bromidep, ug/L | 25.5 | 71 | BMRL | BMRL | Modifications to Existing Plant (% of construction costs) | 10
E-Mail Address (optional) |  | Minimum flow rate to the 8" x 40" element, QI, min (gpm) | 24.7 | [9 empty] | MFI |  |  |  |  | SDS-Cl2 dose | mg/L | 12.6 | 12.7 | 12.65 | 0.79051 | [21 empty] | 1999-05-13 | 13:55 | 74.9 | 22.2 | 64.6 | 64.3 | 299 | 6.5 | 15.4 |  | 21.9 | 0.22627 | 0.2968 | 12.653 | 14.8359 | 14.7485 | 636.9985 | 76.0265 | 624.8035 | 5.5487 | 58.9013 | 0.25039 | 5.55 |  |  | 63.602 |  |  | 642.2427 |  | 86.482 | 635.9531 | 89.9989 | 0 | [15 empty] | Ammonia | mg NH3-N / L | 0.45 | 0.41 | 0.43 | 9.3023 | 0.66 | 0.89875 | -36.1742 | 25.8621 | 0.8937 | 51.8856 | Ammonia | mg NH3-N / L | 0.43 | 1.19 | 1.93 | -62.1849 | 25.8621 | 1.9138 | 77.5316 | Ammonia | mg NH3-N / L | 0.44 | 0.7 | 0.72 | -2.8571 | 24.1379 | 0.71694 | 38.6283 | Ammonia | mg NH3-N / L | 0.41 | 0.63 | 0.65286 | -3.6281 | 29.3103 | 0.6502 | 36.9423 | AlkF, mg/L CaCO3 | 25.1 | 25.1 | 25.1 | 25.1 | AlkF, mg/L CaCO3 | 25.1 | 25.1 | 25.1 | 25.1
|  | Total width of all membrane envelopes in the 8" x 40" element, w (ft) | 58.6667 | [9 empty] | MPFI |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | SDS-Free Cl2 residual | mg/L | 0.6 | 0.76 | 0.68 | 23.5294 | [21 empty] | 1999-05-13 | 16:45 | 77.7 | 22.5 | 64.2 | 63.9 | 299 | 6.5 | 15.4 |  | 21.9 | 0.22627 | 0.2968 | 12.653 | 14.8359 | 14.6182 | 636.9985 | 76.0265 | 624.8035 | 5.5487 | 58.5013 | 0.24988 | 5.48 | 6.12 | 6.19 | 65.549 | 511.777 | 751.424 | 641.4209 | 14.6393 | 86.0682 | 635.1614 | 89.6799 | 0 | 0.384 | 0.494 |  | #VALUE! | [11 empty] | Total organic carbon | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | 33.1 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L | 1.17 | 82.2 | 99.97 | -21.618 | 89.4118 | 98.903 | 98.817 | Total organic carbon | mg/L | BMRL | 21.1 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 13.4 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkp, mg/L CaCO3 | 6.1 | 12.5 | 4.5 | 3.5 | Alkp, mg/L CaCO3 | 6.1 | 12.5 | 4.5 | 3.5
Plant Name | Lime Softening Plant | Feed spacer thickness in the 8" x 40" element, T (ft) | 0.0023333 | [9 empty] | pH | 7.2 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | SDS-Cl2 demand | mg/L | 12 | 11.94 | 11.97 | 0.50125 | [21 empty] | 1999-05-14 | 9:47 | 94.7 | [6 empty] | X | [39 empty] | UV254 | cm-1 | BMRL | BMRL | #DIV/0! | #VALUE! | 1.1625 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | UV254 | cm-1 | 0.0415 | 3.188 | 3.2115 | -0.73714 | 88.424 | 3.1773 | 98.6938 | UV254 | cm-1 | BMRL | 0.153 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.5415 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | T-HdF, mg/L CaCO3 | 244.5 | 244.5 | 244.5 | 244.5 | T-HdF, mg/L CaCO3 | 244.5 | 244.5 | 244.5 | 244.5
Treatment Plant Category | SOFT | [11 empty] | Chloride (mg/L) | 59.9 | is to list the pretreatment processes used in this particular RBSMT run. |  |  | SDS-Chlorination temp. | oC | 20 | 20 | 20 | 0 | [21 empty] | 1999-05-14 | 20:00 | 96.5 | 22.8 | 76.3 | 76 | 299 | 6.7 | 14.8 |  | 21.5 | 0.22627 | 0.31163 | 12.907 | 15.2924 | 14.935 | 648.48 | 77.3502 | 635.6821 | 5.6473 | 70.5027 | 0.21184 | [27 empty] | SUVA | L/(mg*m) | NR | NR | #DIV/0! | #VALUE! | 3.5121 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 3.547 | 3.8783 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 0.72512 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 4.041 | --- | --- | --- | --- | --- | T-Hdp, mg/L CaCO3 | 28.8 | 107 | 20.5 | 17.3 | T-Hdp, mg/L CaCO3 | 28.8 | 107 | 20.5 | 17.3
Process Train Name | NA | Additional Information | [10 empty] | Mg (mg/L) | 44 |  |  |  | SDS-Chlorination pH | --- | 7.48 | 7.53 | 7.505 | 0.66622 | [21 empty] | 1999-05-14 | 21:59 | 98.5 | 22.8 | 70.8 | 70.4 | 299 | 6.6 | 15.3 |  | 21.9 | 0.22627 | 0.30137 | 12.653 | 15.0641 | 14.7121 | 640.4949 | 76.4208 | 628.0438 | 5.5785 | 65.0215 | 0.22627 | [27 empty] | Bromide | mg/L | 26 | 25 | 25.5 | 3.9216 | --- | 352.0625 | --- | 80.3846 | 348.5465 | 92.6839 | Bromide | mg/L | 71 | --- | 661 | --- | 45.3846 | 654.628 | 89.1541 | Bromide | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Bromide | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Ca-HdF, mg/L CaCO3 | 232 | 232 | 232 | 232 | Ca-HdF, mg/L CaCO3 | 232 | 232 | 232 | 232
ICR Treatment Plant Identification Number | 1086 | Design cross-flow velocity (fps) | Unknown | [9 empty] | Potassium (mg/L) | 25.1 |  |  |  | SDS-Incubation time | hours | 24.2 | 23.63 | 23.915 | 2.3834 | [21 empty] | 1999-05-15 | 11:40 | 112.1833 | 22.3 | 66.5 | 66.3 | 299 | 6.7 | 15 |  | 21.7 | 0.22627 | 0.30876 | 12.7788 | 15.2924 | 15.1574 | 646.2269 | 77.0815 | 633.4735 | 5.6277 | 60.7723 | 0.24941 | [27 empty] | SDS-Cl2 dose | mg/L | 4 | 4 | 4 | 0 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 4.6 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 4 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2.85 | --- | --- | --- | --- | --- | --- | Ca-Hdp, mg/L CaCO3 | 28.8 | 102 | 20.5 | 17.3 | Ca-Hdp, mg/L CaCO3 | 28.8 | 102 | 20.5 | 17.3
PWSID Number of Plant (if assigned) | 45-00351 | Required influent flow to permeate flow rate ratio, QI:Qp | 1.54 | [9 empty] | Strontium (mg/L) | 1.14 |  |  |  | SDS-TOX | mg Cl- /L | 1058 | 1060 | 1059 | 0.18886 | [70 empty] | SDS-Free Cl2 residual | mg/L | 0.82 | 0.27 | 0.545 | 100.9174 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.01 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.19 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.46 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 18 | Maximum element recovery (%) | 15 | [14 empty] | SDS-CHCl3 | mg/L | 177 | 211 | 194 | 17.5258 | [70 empty] | SDS-Cl2 demand | mg/L | 3.18 | 3.73 | 3.455 | 15.919 | --- | 30.0644 | --- | 71.1362 | 29.7779 | 88.3974 | SDS-Cl2 demand | mg/L | 3.59 | --- | 87.39 | --- | 70.0084 | 86.485 | 95.849 | SDS-Cl2 demand | mg/L | 2.81 | --- | 21.13 | --- | 76.5246 | 20.93 | 86.5743 | SDS-Cl2 demand | mg/L | 2.39 | --- | 16.0757 | --- | 80.0334 | 15.9259 | 84.993 | Blended Water Quality if THM4 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if THM4 Controls the Blend Ratio
Historical Average Water Temperature (oC) | 20 | Variability of design flux (%) | 10 | [14 empty] | SDS-BDCM | mg/L | 36.7 | 36.5 | 36.6 | 0.54645 | [70 empty] | SDS-Chlorination temp. | oC | 20 | 20 | 20 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 20 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 20 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 20 | --- | --- | --- | --- | --- | --- | Qp/QT (THM4), % | 70.3969 | 70.9353 | 69.2702 | 69.2702 | Qp/QT (THM4), % | 86.0117 | 86.6696 | 84.6351 | 84.6351
State Approved Plant Capacity (MGD) | 22.4 | Rejection of reference solute and conditions of test | 95% | [14 empty] | SDS-DBCM | mg/L | 3.8 | 3.6 | 3.7 | 5.4054 | [70 empty] | SDS-Chlorination pH | --- | 7.59 | 7.59 | 7.59 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.49 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.46 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.55 | --- | --- | --- | --- | --- | --- | SDS-THM4b, ug/L | 72 | 72 | 72 | 72 | SDS-THM4b, ug/L | 36 | 36 | 36 | 36
|  | (e.g., solute type and concentration) | 2000 ppm MgSO4 | [9 empty] | Sodium (mg/L) | 32.8 |  |  |  | SDS-CHBr3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [70 empty] | SDS-Incubation time | hours | 24.3 | 24.4 | 24.35 | 0.41068 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24.2 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 23.7 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-HAA5b, ug/L | 53.9961 | 53.014 | 56.0512 | 56.0512 | SDS-HAA5b, ug/L | 25.5146 | 24.3147 | 28.0256 | 28.0256
|  | Variability of rejection of reference solute (%) | 3 | [9 empty] | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | SDS-THM4 | mg/L | 217.5 | 251.1 | 234.3 | 14.3406 | [70 empty] | SDS-TOX | mg Cl- /L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOXb, ug Cl- /L | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | SDS-TOXb, ug Cl- /L | #DIV/0! | #VALUE! | #VALUE! | #VALUE!
|  | Standard testing recovery (%) | 15 | [9 empty] | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | SDS-MCAA* | mg/L | 7.2 | 7 | 7.1 | 2.8169 | [70 empty] | SDS-CHCl3 | mg/L | 1.2 | 1.1 | 1.15 | 8.6957 | --- | 603.8062 | --- | 99.4072 | 597.3177 | 99.8075 | SDS-CHCl3 | mg/L | 1.5 | --- | 1926.5 | --- | 99.2268 | 1905.71 | 99.9213 | SDS-CHCl3 | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHCl3 | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDb, mg/L | 5.9757 | 6.0256 | 5.6249 | 5.3339 | SDS-CDb, mg/L | 4.6461 | 4.7071 | 4.2174 | 3.862
|  | Standard testing pH | 7 | [14 empty] | SDS-DCAA* | mg/L | 52.3 | 53.3 | 52.8 | 1.8939 | [70 empty] | SDS-BDCM | mg/L | 1.3 | 1.2 | 1.25 | 8 | --- | 111.7188 | --- | 96.5847 | 110.5294 | 98.8691 | SDS-BDCM | mg/L | 1.9 | --- | 348.9 | --- | 94.8087 | 345.1524 | 99.4495 | SDS-BDCM | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | TOCb, mg/L | #DIV/0! | 4.0416 | #VALUE! | #VALUE! | TOCb, mg/L | #DIV/0! | 2.487 | #VALUE! | #VALUE!
|  | Acceptable range of operating pressures | <250 psi | [14 empty] | SDS-TCAA* | mg/L | 121 | 124 | 122.5 | 2.449 | [70 empty] | SDS-DBCM | mg/L | 1.4 | 1.3 | 1.35 | 7.4074 | --- | 8.6937 | --- | 63.5135 | 8.6147 | 84.3291 | SDS-DBCM | mg/L | 2.1 | --- | 18.1 | --- | 43.2432 | 17.9272 | 88.286 | SDS-DBCM | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 b, cm-1 | #DIV/0! | 0.13364 | #VALUE! | #VALUE! | UV254 b, cm-1 | #DIV/0! | 0.083757 | #VALUE! | #VALUE!
|  | Acceptable range of operating pH values | 3-9 | [14 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [70 empty] | SDS-CHBr3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | Bromideb, ug/L | 56.4353 | 88.1482 | #VALUE! | #VALUE! | Bromideb, ug/L | 40.1178 | 78.8649 | #VALUE! | #VALUE!
|  | Typical pressure drop across a single element (psi) | 5 | [14 empty] | SDS-DBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [70 empty] | SDS-THM4 | mg/L | 3.9 | 3.6 | 3.75 | 8 | --- | 724.2188 | --- | 98.3995 | 716.4617 | 99.4766 | SDS-THM4 | mg/L | 5.5 | --- | 2293.5 | --- | 97.6526 | 2268.7896 | 99.7576 | SDS-THM4 | mg/L | 0 | --- | 468.6 | --- | 100 | 463.4844 | 100 | SDS-THM4 | mg/L | 0 | --- | 334.7143 | --- | 100 | 331.0492 | 100 | Alkb, mg/L CaCO3 | 11.7246 | 16.1622 | 10.8303 | 10.1376 | Alkb, mg/L CaCO3 | 8.7578 | 14.1796 | 7.6652 | 6.8188
|  | Maximum permissible SDI | 5 | [14 empty] | SDS-BCAA* | mg/L | 8.3 | 7.5 | 7.9 | 10.1266 | [70 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | T-Hdb, mg/L CaCO3 | 92.6539 | 146.9639 | 89.3348 | 87.1182 | T-Hdb, mg/L CaCO3 | 58.9727 | 125.3293 | 54.9174 | 52.2091
|  | Maximum permissible turbidity (ntu) | 1 | [14 empty] | SDS-TBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [70 empty] | SDS-DCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Ca-Hdb, mg/L CaCO3 | 88.9535 | 139.7841 | 85.4936 | 83.277 | Ca-Hdb, mg/L CaCO3 | 57.2242 | 119.3295 | 52.9968 | 50.2885
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | 1000 ppm-hrs | [14 empty] | SDS-CDBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [70 empty] | SDS-TCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | 1: All of the information requested in this field may not be available, but values for all Design | [15 empty] | SDS-DCBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [70 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  | Parameters must be entered in cells E14:E23, since these parameters are used in calculations. | [15 empty] | SDS-HAA5 | mg/L | 180.5 | 184.3 | 182.4 | 2.0833 | [70 empty] | SDS-DBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | Blended Water Quality if HAA5 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if HAA5 Controls the Blend Ratio
[18 empty] | SDS-HAA6 | mg/L | 188.8 | 191.8 | 190.3 | 1.5765 | [70 empty] | SDS-BCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-BCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Qp/QT (HAA5), % | 70.3947 | 70.3947 | 70.3947 | 70.3947 | Qp/QT (HAA5), % | 85.1974 | 85.1974 | 85.1974 | 85.1974
[18 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [75 empty] | SDS-TBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-THM4b, ug/L | 72.0049 | 73.2368 | 69.3651 | 69.3651 | SDS-THM4b, ug/L | 37.8775 | 39.3684 | 34.6826 | 34.6826
[18 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, | [75 empty] | SDS-CDBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-HAA5b, ug/L | 54 | 54 | 54 | 54 | SDS-HAA5b, ug/L | 27 | 27 | 27 | 27
[18 empty] | should be reported if measured. | [75 empty] | SDS-DCBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TOXb, ug Cl- /L | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | SDS-TOXb, ug Cl- /L | #DIV/0! | #VALUE! | #VALUE! | #VALUE!
[94 empty] | SDS-HAA5 | mg/L | 0 | 0 | 0 | #DIV/0! | --- | 570 | --- | 100 | 563.863 | 100 | SDS-HAA5 | mg/L | 0 | --- | 1824 | --- | 100 | 1804.3008 | 100 | SDS-HAA5 | mg/L | 0 | --- | 364.8 | --- | 100 | 360.8176 | 100 | SDS-HAA5 | mg/L | 0 | --- | 260.5714 | --- | 100 | 257.7182 | 100 | SDS-CDb, mg/L | 5.9759 | 6.0709 | 5.5218 | 5.2262 | SDS-CDb, mg/L | 4.7154 | 4.8305 | 4.1659 | 3.8081
[94 empty] | SDS-HAA6 | mg/L | 0 | 0 | 0 | #DIV/0! | --- | 594.6875 | --- | 100 | 588.2847 | 100 | SDS-HAA6 | mg/L | 0 | --- | 1903 | --- | 100 | 1882.4476 | 100 | SDS-HAA6 | mg/L | 0 | --- | 380.6 | --- | 100 | 376.4451 | 100 | SDS-HAA6 | mg/L | 0 | --- | 271.8571 | --- | 100 | 268.8803 | 100 | TOCb, mg/L | #DIV/0! | 4.095 | #VALUE! | #VALUE! | TOCb, mg/L | #DIV/0! | 2.6325 | #VALUE! | #VALUE!
[94 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | UV254 b, cm-1 | #DIV/0! | 0.13535 | #VALUE! | #VALUE! | UV254 b, cm-1 | #DIV/0! | 0.088424 | #VALUE! | #VALUE!
[94 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | Bromideb, ug/L | 56.4375 | 88.4671 | #VALUE! | #VALUE! | Bromideb, ug/L | 40.9688 | 79.7336 | #VALUE! | #VALUE!
[133 empty] | Alkb, mg/L CaCO3 | 11.725 | 16.2303 | 10.5987 | 9.8947 | Alkb, mg/L CaCO3 | 8.9125 | 14.3651 | 7.5493 | 6.6974
[133 empty] | T-Hdb, mg/L CaCO3 | 92.6586 | 147.7072 | 86.8158 | 84.5632 | T-Hdb, mg/L CaCO3 | 60.7293 | 127.3536 | 53.6579 | 50.9316
[133 empty] | Ca-Hdb, mg/L CaCO3 | 88.9579 | 140.4868 | 83.1151 | 80.8625 | Ca-Hdb, mg/L CaCO3 | 58.8789 | 121.2434 | 51.8076 | 49.0812
[133 empty] | Notes: |  |  |  |  | Notes:
[133 empty] | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to |  |  |  |  | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to
[133 empty] | determine the percentage of total flow that must be treated by the membrane process to meet the |  |  |  |  | determine the percentage of total flow that must be treated by the membrane process to meet the
[133 empty] | Stage 1 DBP MCLs. |  |  |  |  | Stage 2 DBP MCLs.
[133 empty] | A 10% factor of safety has been applied all the MCLs. i.e., 72 / 54 mg/L for THM4 and HAA5. |  |  |  |  | A 10% factor of safety has been applied all the MCLs. i.e., 36 / 27 mg/L for THM4 and HAA5.
[133 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for |  |  |  |  | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for
[133 empty] | both parameters and the maximum (Qp/QT) ratio controls the design. |  |  |  |  | both parameters and the maximum (Qp/QT) ratio controls the design.
[133 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. |  |  |  |  | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[133 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. |  |  |  |  | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[133 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. |  |  |  |  | The subscript "b" refers to the blended water quality for a given blend ratio.
[133 empty] | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL. |  |  |  |  | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL.
[133 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. |  |  |  |  | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
Note on X24: TSC_ADM: Reported SDS temperature is a measured value - the consultant used an incubator for SDS testing.
Note on CY29: TSC_ADM: Reported SDS temperature is a measured value - the consultant used an incubator for SDS testing.
Note on DL29: TSC_ADM: Reported SDS temperature is a measured value - the consultant used an incubator for SDS testing.
Note on DV29: TSC_ADM: Reported SDS temperature is a measured value - the consultant used an incubator for SDS testing.
Note on EF29: TSC_ADM: Reported SDS temperature is a measured value - the consultant used an incubator for SDS testing.
Print All Fields

## DCSS2. 2nd Quarter
FIELD-SET 2: Membrane B, Run 2 (FILE: Delray2.xls)
Field 2-1: PWS And Treatment Plant Data |  | Field 2-2: Manufacturer Reported Membrane Characteristics1 |  | Field 2-3: RBSMT Design Parameters | [8 empty] | Field 2-4: Foulants And Fouling Indices1 |  | Field 2-5: Pretreatment Used Prior To Membranes1 |  |  | Field 2-6: Feed Water Quality After Pretreatment | [5 empty] | Field 2-7: Membrane Setting Data | [20 empty] | Field 2-8: Membrane Performance Data During Operation With The Test Water | [16 empty] | Field 1-8: Membrane Performance Data During Operation With The Test Water (continued) | [19 empty] | Field 2-8: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 2-9: Permeate And Concentrate Water Quality For Run 1 | [11 empty] | Field 2-10: Permeate And Concentrate Water Quality For Run 2 | [8 empty] | Field 2-11: Permeate And Concentrate Water Quality For Run 3 | [8 empty] | Field 2-12: Permeate And Concentrate Water Quality For Run 4 | [8 empty] | Field 2-13: Blending Calculations For Stage 1 D-DBP MCLs |  |  |  |  | Field 2-14: Blending Calculations For Proposed Stage 2 D-DBP MCLs |  |  |  |  | Field 2-15: Membrane Cost Parameters
|  | General Information |  | Input Design Parameters | [8 empty] | Parameters Evaluated Prior to Pretreatment | [80 empty] | Operating Parameters During Sample Collection | [11 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Feed and Permeate Water Quality Parameters |  |  |  |  | Feed and Permeate Water Quality Parameters |  |  |  |  | General Cost Parameters
PWS Name | Delray Beach Water Department | Membrane manufacturer | Film Tec | [5 empty] | Active membrane area in bench-scale cell, Acell (ft2) | 0.16667 |  |  | Alkalinity (mg/L as CaCO3) | 243 | Process | Description | Scale | Parameter | Units | CF-1 | CF-2 | Average | RPD |  |  |  | Average TDS rejection (decimal fraction) | 0.7 | [5 empty] | TDS concentration of setting solution (mg/L) | 50 | [12 empty] | Average bulk TDS rejection (decimal fraction) | 0.46252 | [45 empty] | Recovery during sample collection (decimal) | 0.7 | [10 empty] | Recovery during sample collection (decimal) | 0.9 | [7 empty] | Recovery during sample collection (decimal) | 0.5 | [7 empty] | Recovery during sample collection (decimal) | 0.3 | [8 empty] | RUN ID # |  |  |  |  | RUN ID # |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | FL4500351 | Membrane trade name | NF200B-400 | [5 empty] | Active width of membrane in the bench-scale cell, wcell (ft) | 0.33333 |  |  | Calcium Hardness (mg/L as CaCO3) | 295 | Aeration | Fine Bubble diffuwer in barrel overnight | Bench | Sampling date | MM/DD/YY | 1999-05-18 | 1999-05-21 | --- | --- | [71 empty] | Feed flow rate during sample collection (mL/min) | 9.2 | [10 empty] | Feed flow rate during sample collection (mL/min) | 7.3 | [7 empty] | Feed flow rate during sample collection (mL/min) | 13.1 | [7 empty] | Feed flow rate during sample collection (mL/min) | 29.2 | [6 empty] | Parameter | 1 | 2 | 3 | 4 | Parameter | 1 | 2 | 3 | 4 | Capital Recovery Interest Rate (%) | 5.75
Water Industry Data Base Number (optional) | NA | Molecular weight cutoff (Daltons) | 200-400 | [5 empty] | Average yearly temperature of feed water, TavgoC (oC) | 22 |  |  | LSI |  | Acidification | Hydrochloric acid to pH 6.5 | Bench | Sampling time | hh:mm | NR | NR | --- | --- | Date | Time | Setting time | Influent | PI | PC | QI | Qp | QW | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) | Date | Time | Operation time | Influent | PI | PC | QI | Qp | QW | Cleaning Event | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1) | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Influent flow rate during sample collection (mL/min) | 299 | [10 empty] | Influent flow rate during sample collection (mL/min) | 299 | [7 empty] | Influent flow rate during sample collection (mL/min) | 299 | [7 empty] | Influent flow rate during sample collection (mL/min) | 299 | [6 empty] | SDS-THM4F, ug/L | 245.65 | 245.65 | 245.65 | 245.65 | SDS-THM4F, ug/L | 245.65 | 245.65 | 245.65 | 245.65 | Capital Recovery Period (years) | 25
|  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide | [5 empty] | Approximate feed water TDS, TDSF (mg/L) | 545 |  |  | Dissolved iron (mg/L) |  | Antiscalant addition | King Lee PreTreat 0100, 3 ppm by volume | Bench | Operation time | hh.hh | 58.1 | 129.8 | --- | --- | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | Indicate with "X" | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) | [39 empty] | SDS-THM4p, ug/L | 32.85 | 37.5 | 42.1 | 27.7 | SDS-THM4p, ug/L | 32.85 | 37.5 | 42.1 | 27.7 | Overhead & Profit Factor (% of construction costs) | 15
Official ICR Contact Person |  | Membrane construction (e.g., thin-film composite) | Thin-Film Composite | [5 empty] | Manufacturer reported TDS rejection, RejTDS (decimal fraction) | 0.7 |  |  | Total iron (mg/L) |  | Membrane Filtration | 0.1 micron Pall Microza cartridge | Bench | pH | --- | 6.31 | 6 | 6.155 | 5.0366 | 1999-05-15 | 15:10 | 0 | [18 empty] | 1999-05-17 | 9:15 | 0 | [46 empty] | Permeate and Concentrate Water Quality | [11 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | SDS-HAA5F, ug/L | 179.5 | 179.5 | 179.5 | 179.5 | SDS-HAA5F, ug/L | 179.5 | 179.5 | 179.5 | 179.5 | Special Sitework Factor (% of construction costs) | 5
Mailing Address |  | Membrane hydrophobicity | Hydrophilic | [5 empty] | Temperature normalized MTCW (gfd/psi) | 0.2599 |  |  | Dissolved aluminum (mg/L) |  |  |  |  | Temperature | oC | NR | NR | #DIV/0! | #VALUE! | 1999-05-15 | 16:03 | 0.8 | 24.3 | 108.7 | 108.3 | 299 | 6.7 | 2.7 | 9.4 | 0.22627 | 0.71277 | 30.8085 | 15.2924 | 14.2873 | 100.4647 | 29.6635 | 98.8782 | 0.70008 | 107.7999 | 0.13254 | 1999-05-17 | 11:14 | 2 | 25.4 | 114.1 | 113.9 | 299 | 6.6 | 2.8 |  | 9.4 | 0.22627 | 0.70213 | 30.8085 | 15.0641 | 13.6238 | 714.233 | 379.9163 | 706.8534 | 3.3063 | 110.6937 | 0.12308 | 6.39 |  |  | 316.938 |  |  | 862.6819 |  | 33.9024 | 856.6586 | 63.003 | 0.023 |  |  | 1.2198 |  | 93.9394 | 1.2066 | 98.0938 | [8 empty] | Parameter | Units | Cp-1 | Cp-1 (dup) | Average | RPD | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | SDS-HAA5p, ug/L | 7.95 | 12.7 | 10.4 | 6.8 | SDS-HAA5p, ug/L | 7.95 | 12.7 | 10.4 | 6.8 | Construction Contingencies (% of construction costs) | 15
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Highly Negative | [9 empty] | Total aluminum (mg/L) |  |  |  |  | Alkalinity | mg/L as CaCO3 | 12.2 | 26.2 | 19.2 | 72.9167 | 1999-05-15 | 18:00 | 2.8 | 24.8 | 108.6 | 108.2 | 299 | 6.7 | 2.8 | 9.5 | 0.22627 | 0.70526 | 30.4737 | 15.2924 | 14.0777 | 99.4086 | 29.3516 | 97.8388 | 0.69272 | 107.7073 | 0.1307 | 1999-05-17 | 13:24 | 4.2 | 25.9 | 113.6 | 113.3 | 299 | 6.6 | 2.8 |  | 9.4 | 0.22627 | 0.70213 | 30.8085 | 15.0641 | 13.4239 | 714.233 | 379.9163 | 706.8534 | 3.3063 | 110.1437 | 0.12188 | 6.32 |  |  | 321.18 |  |  | 852.6829 |  | 33.0177 | 846.8168 | 62.0721 | 0.022 |  |  | 1.2222 |  | 94.2029 | 1.2089 | 98.1802 | [8 empty] | Sampling date | MM/DD/YY | 1999-05-18 | 1999-05-18 | --- | --- | 1999-05-18 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-05-19 | 1999-05-19 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-05-20 | 1999-05-20 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-05-21 | 1999-05-21 | --- | --- | --- | --- | --- | SDS-TOXF, ug Cl- /L | 1001 | 1001 | 1001 | 1001 | SDS-TOXF, ug Cl- /L | 1001 | 1001 | 1001 | 1001 | Engineering Fee Factor (% of construction costs) | 10
Phone Number |  |  |  | Experimental Design1,2 | [8 empty] | Fluoride (mg/L) |  |  |  |  | Total dissolved solids | mg/L | 538 | 421 | 479.5 | 24.4004 | 1999-05-16 | 12:00 | 20.8 | 24.6 | 107.1 | 106.8 | 299 | 6.6 | 2.8 | 9.4 | 0.22627 | 0.70213 | 30.8085 | 15.0641 | 13.9498 | 98.964 | 29.2274 | 97.4247 | 0.68967 | 106.2603 | 0.13128 | 1999-05-17 | 16:33 | 7.3 | 26.1 | 113.8 | 113.4 | 299 | 6.7 | 2.8 |  | 9.5 | 0.22627 | 0.70526 | 30.4737 | 15.2924 | 13.547 | 715.862 | 380.7219 | 708.3521 | 3.3139 | 110.2861 | 0.12283 | 6.09 | 6.28 | 6.65 | 324.21 | 488.838 | 712.124 | 851.0868 | -19.5138 | 32.3858 | 845.1837 | 61.6403 | 0.021 | 0.366 | 1.031 | 1.2373 | -20.0135 | 94.4664 | 1.2237 | 98.2839 | [8 empty] | Sampling time | hh:mm | NR | NR | --- | --- | NR | --- | --- | --- | --- | --- | Sampling time | hh:mm | NR | NR | --- | --- | --- | --- | --- | Sampling time | hh:mm | NR | NR | --- | --- | --- | --- | --- | Sampling time | hh:mm | NR | NR | --- | --- | --- | --- | --- | SDS-TOXp, ug Cl- /L | 67.4 | 98.15 | 100.5 | 54.1 | SDS-TOXp, ug Cl- /L | 67.4 | 98.15 | 100.5 | 54.1 | 1998 ENR Construction Cost Index (CCI base year 1913) | 5875
FAX Number |  | Design Parameters |  | ID# | Recovery | FW-design | Dp | PI | QI-cell | Qp | QF | QW | Phosphate (mg/L) |  |  |  |  | Total hardness | mg/L as CaCO3 | 246 | 219 | 232.5 | 11.6129 | 1999-05-16 | 14:24 | 23.2 | 25.2 | 105.4 | 105.3 | 299 | 6.6 | 2.8 | 9.4 | 0.22627 | 0.70213 | 30.8085 | 15.0641 | 13.7046 | 98.964 | 29.2274 | 97.4247 | 0.68967 | 104.6603 | 0.13094 | 1999-05-18 | 14:15 | 29 | 25.8 | 114.1 | 113.7 | 299 | 6.6 | 0.7 |  | 7.3 | 0.22627 | 0.90411 | 39.9589 | 15.0641 | 13.4637 | 831.3016 | 442.1877 | 822.7124 | 3.8482 | 110.0518 | 0.12234 | 6.21 |  |  | 421.728 |  |  | 1024.2074 |  | 12.0484 | 1017.558 | 58.5549 | 0.022 |  |  | 3.7502 |  | 94.2029 | 3.7091 | 99.4069 | [8 empty] | Operation time | hh.hh | 58.1 | 58.1 | --- | --- | 58.1 | --- | --- | --- | --- | --- | Operation time | hh.hh | 84.2 | 84.2 | --- | --- | --- | --- | --- | Operation time | hh.hh | 106.8 | 106.8 | --- | --- | --- | --- | --- | Cumulative time | hr | 129.8 | 129.8 | --- | --- | --- | --- | --- | SDS-CDF, mg/L | 11.92 | 11.92 | 11.92 | 11.92 | SDS-CDF, mg/L | 11.92 | 11.92 | 11.92 | 11.92 | 1998 Producers Price Index (PPI base year 1967 = 100) | 369
E-Mail Address (optional) |  | Design flux, FW (gfd) | 21.1 |  | (decimal) | (gfd) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | Sulfate (mg/L) | 26.5 |  |  |  | Calcium hardness | mg/L as CaCO3 | 233 | 208 | 220.5 | 11.3379 | 1999-05-16 | 18:10 | 26.9 | 25.5 | 106.5 | 106.2 | 299 | 6.6 | 2.8 | 9.4 | 0.22627 | 0.70213 | 30.8085 | 15.0641 | 13.5836 | 98.964 | 29.2274 | 97.4247 | 0.68967 | 105.6603 | 0.12856 | 1999-05-18 | 18:30 | 33.3 | 25.8 | 114.3 | 114 | 299 | 6.6 | 0.7 |  | 7.3 | 0.22627 | 0.90411 | 39.9589 | 15.0641 | 13.4637 | 831.3016 | 442.1877 | 822.7124 | 3.8482 | 110.3018 | 0.12206 | 6.23 |  |  | 428.352 |  |  | 961.7526 |  | 10.6669 | 955.8655 | 55.187 | 0.026 |  |  | 3.7125 |  | 93.1489 | 3.6718 | 99.2919 | [8 empty] | pH | --- | 6.59 | 6.64 | 6.615 | 0.75586 | 6.73 | --- | --- | --- | --- | --- | pH | --- | 6.27 | 6.59 | --- | --- | --- | --- | --- | pH | --- | 6.19 | 6.38 | --- | --- | --- | --- | --- | pH | --- | 6 | 6.3 | --- | --- | --- | --- | --- | SDS-CDp, mg/L | 3.915 | 4.45 | 3.98 | 3.49 | SDS-CDp, mg/L | 3.915 | 4.45 | 3.98 | 3.49 | Labor Rate + Fringe ($/work-hour) | 19.89
|  | Net driving pressure at the design flux, NDP (psi) | 71 | 1 | 0.7 | 21.1 | 14.3517 | 95.5367 | 344.1283 | 9.2435 | 13.2049 | 3.9615 | Calcium (mg/L) |  |  |  |  | Turbidity | ntu | 0.21 | 0.3 | 0.255 | 35.2941 | [21 empty] | 1999-05-18 | 19:50 | 34.6 | 25.9 | 114.3 | 114.1 | 299 | 6.6 | 0.7 |  | 7.3 | 0.22627 | 0.90411 | 39.9589 | 15.0641 | 13.4239 | 831.3016 | 442.1877 | 822.7124 | 3.8482 | 110.3518 | 0.12165 | 6.22 | 6.46 | 7.06 | 429.824 | 507.822 | 907.885 | 947.8737 | -4.4046 | 10.36 | 942.1561 | 54.3787 | 0.026 | 0.366 | 2 | 3.7125 | -85.625 | 93.1489 | 3.6718 | 99.2919 | [8 empty] | Temperature | oC | NR | NR | #DIV/0! | #VALUE! | NR | --- | --- | --- | --- | --- | Temperature | oC | NR | NR | --- | --- | --- | --- | --- | Temperature | oC | NR | NR | --- | --- | --- | --- | --- | Temperature | oC | NR | NR | --- | --- | --- | --- | --- | TOCF, mg/L | 9.675 | 9.675 | 9.675 | 9.675 | TOCF, mg/L | 9.675 | 9.675 | 9.675 | 9.675 | Labor Overhead Factor (% of labor) | 6
Technical ICR Contact Person |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.284 | 2 | 0.9 | 21.1 | 39.785 | 120.97 | 344.1283 | 9.2435 | 10.2705 | 1.0271 | Barium (mg/L) | 0.018 |  |  |  | Ammonia | mg NH3-N / L | 0.59 | 0.37 | 0.48 | 45.8333 | [21 empty] | 1999-05-19 | 10:42 | 49.5 | 25.6 | 115.5 | 114.9 | 299 | 6.6 | 6.5 |  | 13.1 | 0.22627 | 0.50382 | 21.8244 | 15.0641 | 13.5435 | 627.4745 | 333.7676 | 620.9913 | 2.9047 | 112.2953 | 0.12061 | 6.4 |  |  | 298.944 |  |  | 662.8338 |  | 37.6551 | 658.8176 | 54.6242 | 0.029 |  |  | 0.73539 |  | 92.3584 | 0.7276 | 96.0143 | [8 empty] | Alkalinity | mg/L as CaCO3 | 19.1 | 19.5 | 19.3 | 2.0725 | 41 | 18.9667 | 53.7398 | -0.52083 | 18.9703 | -1.7382 | Alkalinity | mg/L as CaCO3 | 5 | 26 | 147 | -465.3846 | 73.9583 | 145.4399 | 96.5622 | Alkalinity | mg/L as CaCO3 | 14 | 31 | 24.4 | 21.2903 | 27.0833 | 24.2861 | 42.3538 | Alkalinity | mg/L as CaCO3 | 13 | 30.5 | 21.8571 | 28.3372 | 32.2917 | 21.7274 | 40.1677 | TOCp, mg/L | 0.695 | 0.95 | 1.18 | 0.83 | TOCp, mg/L | 0.695 | 0.95 | 1.18 | 0.83 | Electric Rate ($/kW-h) | 0.05
Mailing Address |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | 3 | 0.5 | 21.1 | 9.265 | 90.45 | 344.1283 | 9.2435 | 18.4869 | 9.2435 | Strontium (mg/L) |  |  |  |  | Total organic carbon | mg/L | 9.65 | 9.7 | 9.675 | 0.5168 | [21 empty] | 1999-05-19 | 13:09 | 51.9 | 25.8 | 115.6 | 115.2 | 299 | 6.7 | 6.5 |  | 13.2 | 0.22627 | 0.50758 | 21.6515 | 15.2924 | 13.6677 | 628.9582 | 334.5032 | 622.3601 | 2.9116 | 112.4884 | 0.1215 | 6.42 |  |  | 289.728 |  |  | 675.1111 |  | 39.5771 | 670.7933 | 56.8082 | 0.029 |  |  | 0.74078 |  | 92.3584 | 0.73281 | 96.0426 | [8 empty] | Total dissolved solids | mg/L | 398 | 435 | 416.5 | 8.8836 | 712 | 626.5 | 12.0084 | 13.1387 | 624.2385 | 33.2787 | Total dissolved solids | mg/L | 430 | 908 | 925 | -1.8722 | 10.3233 | 919.5616 | 53.2386 | Total dissolved solids | mg/L | 293 | 558 | 666 | -19.3548 | 38.8947 | 661.9145 | 55.7345 | Total dissolved solids | mg/L | 377.5 | 455 | 523.2143 | -14.9922 | 21.2722 | 521.0797 | 27.5543 | UV254 F, cm-1 | 0.3795 | 0.3795 | 0.3795 | 0.3795 | UV254 F, cm-1 | 0.3795 | 0.3795 | 0.3795 | 0.3795 | Fuel Oil Rate ($/gal) | NA
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 400 | 4 | 0.3 | 21.1 | 7.085 | 88.27 | 344.1283 | 9.2435 | 30.8115 | 21.5681 | Reactive silica (mg/L as SiO2) | 32.8 |  |  |  | UV254 | cm-1 | 0.388 | 0.371 | 0.3795 | 4.4796 | [21 empty] | 1999-05-19 | 16:12 | 54.8 | 25.7 | 115.4 | 114.9 | 299 | 6.7 | 6.5 |  | 13.2 | 0.22627 | 0.50758 | 21.6515 | 15.2924 | 13.7081 | 628.9582 | 334.5032 | 622.3601 | 2.9116 | 112.2384 | 0.12213 | 6.76 | 6.69 | 6.71 | 293.184 | 501.494 | 558 | 671.5488 | -20.3492 | 38.8563 | 667.3096 | 56.0648 | 0.03 | 0.364 | 0.691 | 0.73975 | -7.0555 | 92.0949 | 0.7318 | 95.9005 | [8 empty] | Total hardness | mg/L as CaCO3 | 200 | 197 | 198.5 | 1.5113 | 353 | 311.8333 | 11.6619 | 14.6237 | 310.6128 | 36.0941 | Total hardness | mg/L as CaCO3 | 213 | 445 | 408 | 8.3146 | 8.3871 | 405.8576 | 47.5185 | Total hardness | mg/L as CaCO3 | 176 | 312 | 289 | 7.3718 | 24.3011 | 287.7623 | 38.8384 | Total hardness | mg/L as CaCO3 | 149 | 253 | 268.2857 | -6.0418 | 35.914 | 266.5383 | 44.0981 | UV254 p, cm-1 | 0.021 | 0.032 | 0.034 | 0.0205 | UV254 p, cm-1 | 0.021 | 0.032 | 0.034 | 0.0205 | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Purchase price for an equivalent 8" x 40 " element ($) | 800 | 1: For experimental matrix see Table 4-2 in Part 3 of the ICR Treatment Studies Manual. | [8 empty] | Turbidity (ntu) |  |  |  |  | SUVA | L/(mg*m) | 4.0207 | 3.8247 | 3.9227 | 4.9961 | [21 empty] | 1999-05-20 | 12:00 | 74.6 | 25.2 | 117.5 | 117.3 | 299 | 6.8 | 6.8 |  | 13.6 | 0.22627 | 0.5 | 20.9853 | 15.5206 | 14.1199 | 626.0806 | 332.9194 | 619.4133 | 2.8983 | 114.5017 | 0.12332 | [27 empty] | Calcium hardness | mg/L as CaCO3 | 192 | 189 | 190.5 | 1.5748 | 332 | 290.5 | 12.5 | 13.6054 | 289.4231 | 34.1794 | Calcium hardness | mg/L as CaCO3 | 203 | 414 | 378 | 8.6957 | 7.9365 | 376.0773 | 46.0217 | Calcium hardness | mg/L as CaCO3 | 168 | 294 | 273 | 7.1429 | 23.8095 | 271.8499 | 38.2012 | Calcium hardness | mg/L as CaCO3 | 143 | 239 | 253.7143 | -6.1566 | 35.1474 | 252.0925 | 43.2748 | BromideF, ug/L | 190.5 | 190.5 | 190.5 | 190.5 | BromideF, ug/L | 190.5 | 190.5 | 190.5 | 190.5 | Current Process Water Rate ($/1000 gal) | 0.41
FAX Number |  | Maximum flow rate to the 8" x 40" element, QI, max (gpm) | 70 | 2: Flow rates and pressures may need to be adjusted in order to obtain the desired operating conditions. | [8 empty] | SDI |  |  |  |  | Bromide | mg/L | 243 | 138 | 190.5 | 55.1181 | [21 empty] | 1999-05-20 | 14:29 | 76.7 | 24.3 | 115.4 | 115.1 | 299 | 6.5 | 15.8 |  | 22.3 | 0.22627 | 0.29148 | 12.4081 | 14.8359 | 13.8608 | 555.2406 | 295.392 | 549.5917 | 2.5702 | 112.6798 | 0.12301 | 6.07 |  |  | 377.66 |  |  | 521.3962 |  | 21.2388 | 519.8339 | 27.3499 | 0.022 |  |  | 0.52657 |  | 94.2029 | 0.52109 | 95.7781 | [8 empty] | Turbidity | ntu | 0.1 | 0.12 | 0.11 | 18.1818 | 0.27 | 0.59333 | -119.7531 | 56.8627 | 0.58813 | 81.2966 | Turbidity | ntu | 0.02 | 0.25 | 2.37 | -848 | 92.1569 | 2.3442 | 99.1468 | Turbidity | ntu | 0.04 | 0.15 | 0.47 | -213.3333 | 84.3137 | 0.46529 | 91.4032 | Turbidity | ntu | 0.19 | 0.13 | 0.28286 | -117.5824 | 25.4902 | 0.2815 | 32.5037 | Bromidep, ug/L | 119 | 124 | 118 | 113 | Bromidep, ug/L | 119 | 124 | 118 | 113 | Modifications to Existing Plant (% of construction costs) | 10
E-Mail Address (optional) |  | Minimum flow rate to the 8" x 40" element, QI, min (gpm) | 16 | [9 empty] | MFI |  |  |  |  | SDS-Cl2 dose | mg/L | 12.7 | 12.72 | 12.71 | 0.15736 | [21 empty] | 1999-05-20 | 16:20 | 78.6 | 24.5 | 115.6 | 115.4 | 299 | 6.5 | 15.7 |  | 22.2 | 0.22627 | 0.29279 | 12.4685 | 14.8359 | 13.7791 | 555.636 | 295.6024 | 549.9831 | 2.5721 | 112.9279 | 0.12202 | 6.29 |  |  | 379.302 |  |  | 520.9832 |  | 20.8964 | 519.4432 | 26.9791 | 0.018 |  |  | 0.52917 |  | 95.2569 | 0.52361 | 96.5623 | [8 empty] | Ammonia | mg NH3-N / L | 0.51 | 0.51 | 0.51 | 0 | 0.67 | 0.41 | 38.806 | -6.25 | 0.41108 | -24.0644 | Ammonia | mg NH3-N / L | 0.5 | 0.67 | 0.3 | 55.2239 | -4.1667 | 0.3022 | -65.4548 | Ammonia | mg NH3-N / L | 0.47 | 0.66 | 0.49 | 25.7576 | 2.0833 | 0.48978 | 4.0387 | Ammonia | mg NH3-N / L | 0.28 | 0.37 | 0.56571 | -52.8958 | 41.6667 | 0.56153 | 50.1361 | AlkF, mg/L CaCO3 | 19.2 | 19.2 | 19.2 | 19.2 | AlkF, mg/L CaCO3 | 19.2 | 19.2 | 19.2 | 19.2
|  | Total width of all membrane envelopes in the 8" x 40" element, w (ft) | 58.6667 | [9 empty] | MPFI |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | SDS-Free Cl2 residual | mg/L | 0.8 | 0.78 | 0.79 | 2.5316 | [21 empty] | 1999-05-20 | 18:01 | 80.2 | 24.6 | 115.6 | 115.4 | 299 | 6.4 | 15 |  | 21.4 | 0.22627 | 0.29907 | 12.972 | 14.6077 | 13.5271 | 557.516 | 296.65 | 551.9322 | 2.5807 | 112.9193 | 0.11979 | 6.32 | 6.27 | 6.34 | 377.66 | 489.629 | 454.92 | 522.9517 | -14.9547 | 21.2388 | 521.3968 | 27.5676 | 0.019 | 0.362 | 0.524 | 0.53331 | -1.7774 | 94.9934 | 0.52781 | 96.4002 | [8 empty] | Total organic carbon | mg/L | 0.69 | 0.7 | 0.695 | 1.4388 | 29.7 | 30.6283 | -3.1257 | 92.8165 | 30.306 | 97.7067 | Total organic carbon | mg/L | 0.95 | 69.1 | 88.2 | -27.6411 | 90.1809 | 87.2414 | 98.9111 | Total organic carbon | mg/L | 1.18 | 21.1 | 18.17 | 13.8863 | 87.8036 | 17.9839 | 93.4386 | Total organic carbon | mg/L | 0.83 | 14.1 | 13.4657 | 4.4985 | 91.4212 | 13.2806 | 93.7503 | Alkp, mg/L CaCO3 | 19.3 | 5 | 14 | 13 | Alkp, mg/L CaCO3 | 19.3 | 5 | 14 | 13
Plant Name | Lime Softening Plant | Feed spacer thickness in the 8" x 40" element, T (ft) | 0.0023333 | [9 empty] | pH | 7.2 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | SDS-Cl2 demand | mg/L | 11.9 | 11.94 | 11.92 | 0.33557 | [21 empty] | 1999-05-21 | 10:06 | 96.3 | [6 empty] | X | [39 empty] | UV254 | cm-1 | 0.021 | 0.021 | 0.021 | 0 | 1.031 | 1.216 | -17.9437 | 94.4664 | 1.2031 | 98.2546 | UV254 | cm-1 | 0.032 | 2.36 | 3.507 | -48.6017 | 91.5679 | 3.4688 | 99.0775 | UV254 | cm-1 | 0.034 | 0.693 | 0.725 | -4.6176 | 91.0408 | 0.71743 | 95.2609 | UV254 | cm-1 | 0.0205 | 0.5925 | 0.53336 | 9.9819 | 94.5982 | 0.52584 | 96.1015 | T-HdF, mg/L CaCO3 | 232.5 | 232.5 | 232.5 | 232.5 | T-HdF, mg/L CaCO3 | 232.5 | 232.5 | 232.5 | 232.5
Treatment Plant Category | SOFT | [11 empty] | Chloride (mg/L) | 59.9 | is to list the pretreatment processes used in this particular RBSMT run. |  |  | SDS-Chlorination temp. | oC | 20 | 20 | 20 | 0 | [21 empty] | 1999-05-21 | 18:54 | 96.9 | 23.1 | 61.6 | 61.3 | 299 | 6.7 | 15.6 |  | 22.3 | 0.22627 | 0.30045 | 12.4081 | 15.2924 | 14.8032 | 557.9856 | 296.7574 | 552.132 | 2.583 | 58.867 | 0.25147 | 6.56 |  |  | 406.395 |  |  | 510.8977 |  | 15.2461 | 509.7268 | 20.272 | 0.057 |  |  | 0.51801 |  | 84.9802 | 0.51284 | 88.8855 | [8 empty] | SUVA | L/(mg*m) | 3.0435 | 3 | 3.0217 | 1.4388 | 3.4714 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 3.3684 | 3.4153 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 2.8814 | 3.2844 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 2.4699 | 4.2021 | --- | --- | --- | --- | --- | T-Hdp, mg/L CaCO3 | 198.5 | 213 | 176 | 149 | T-Hdp, mg/L CaCO3 | 198.5 | 213 | 176 | 149
Process Train Name | NA | Additional Information | [10 empty] | Mg (mg/L) | 44 |  |  |  | SDS-Chlorination pH | --- | 7.49 | 7.55 | 7.52 | 0.79787 | [21 empty] | 1999-05-22 | 11:50 | 114.2 | 23 | 61.5 | 61.2 | 299 | 6.3 | 15.3 |  | 21.6 | 0.22627 | 0.29167 | 12.8426 | 14.3794 | 13.9606 | 555.2649 | 295.4995 | 549.7916 | 2.5703 | 58.7797 | 0.23751 | 6.42 | 6.14 | 6.24 | 394.901 | 507.031 | 458.934 | 514.3349 | -12.0716 | 17.6432 | 513.0766 | 23.0327 | 0.012 | 0.375 | 0.514 | 0.53082 | -3.2731 | 96.8379 | 0.52536 | 97.7158 | [8 empty] | Bromide | mg/L | 118 | 120 | 119 | 1.6807 | --- | 357.3333 | --- | 37.5328 | 354.7667 | 66.4568 | Bromide | mg/L | 124 | --- | 789 | --- | 34.9081 | 781.6939 | 84.137 | Bromide | mg/L | 118 | --- | 263 | --- | 38.0577 | 261.4118 | 54.8605 | Bromide | mg/L | 113 | --- | 223.7143 | --- | 40.6824 | 222.0925 | 49.1203 | Ca-HdF, mg/L CaCO3 | 220.5 | 220.5 | 220.5 | 220.5 | Ca-HdF, mg/L CaCO3 | 220.5 | 220.5 | 220.5 | 220.5
ICR Treatment Plant Identification Number | 1086 | Design cross-flow velocity (fps) | - | [9 empty] | Potassium (mg/L) | 25.1 |  |  |  | SDS-Incubation time | hours | 23.53 | 24 | 23.765 | 1.9777 | [70 empty] | SDS-Cl2 dose | mg/L | 4.84 | 4.84 | 4.84 | 0 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 5.6 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 4.6 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 3.8 | --- | --- | --- | --- | --- | --- | Ca-Hdp, mg/L CaCO3 | 190.5 | 203 | 168 | 143 | Ca-Hdp, mg/L CaCO3 | 190.5 | 203 | 168 | 143
PWSID Number of Plant (if assigned) | 45-00351 | Required influent flow to permeate flow rate ratio, QI:Qp | - | [9 empty] | Strontium (mg/L) | 1.14 |  |  |  | SDS-TOX | mg Cl- /L | 1115 | 887 | 1001 | 22.7772 | [70 empty] | SDS-Free Cl2 residual | mg/L | 0.98 | 0.87 | 0.925 | 11.8919 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.15 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.62 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.31 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 18 | Maximum element recovery (%) | 19 | [14 empty] | SDS-CHCl3 | mg/L | 196 | 216 | 206 | 9.7087 | [70 empty] | SDS-Cl2 demand | mg/L | 3.86 | 3.97 | 3.915 | 2.8097 | --- | 30.5983 | --- | 67.156 | 30.311 | 87.0839 | SDS-Cl2 demand | mg/L | 4.45 | --- | 79.15 | --- | 62.6678 | 78.3293 | 94.3189 | SDS-Cl2 demand | mg/L | 3.98 | --- | 19.86 | --- | 66.6107 | 19.6861 | 79.7827 | SDS-Cl2 demand | mg/L | 3.49 | --- | 15.5329 | --- | 70.7215 | 15.3564 | 77.2734 | Blended Water Quality if THM4 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if THM4 Controls the Blend Ratio
Historical Average Water Temperature (oC) | 20 | Variability of design flux (%) | -10%, +25% | [14 empty] | SDS-BDCM | mg/L | 33.5 | 38.4 | 35.95 | 13.63 | [70 empty] | SDS-Chlorination temp. | oC | 20 | 20 | 20 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 20 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 20 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 20 | --- | --- | --- | --- | --- | --- | Qp/QT (THM4), % | 81.6024 | 83.4254 | 85.3107 | 79.6742 | Qp/QT (THM4), % | 98.5197 | 100.7206 | 102.9968 | 96.1918
State Approved Plant Capacity (MGD) | 22.4 | Rejection of reference solute and conditions of test | >99% of 2,000 ppm MgSO4 | [14 empty] | SDS-DBCM | mg/L | 3.5 | 3.9 | 3.7 | 10.8108 | [70 empty] | SDS-Chlorination pH | --- | 7.56 | 7.56 | 7.56 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.46 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.58 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.44 | --- | --- | --- | --- | --- | --- | SDS-THM4b, ug/L | 72 | 72 | 72 | 72 | SDS-THM4b, ug/L | 36 | NA | NA | 36
|  | (e.g., solute type and concentration) | <50% 500 ppm CaCl2 | [9 empty] | Sodium (mg/L) | 32.8 |  |  |  | SDS-CHBr3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [70 empty] | SDS-Incubation time | hours | 24.85 | 24.75 | 24.8 | 0.40323 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24.67 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24.55 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24.25 | --- | --- | --- | --- | --- | --- | SDS-HAA5b, ug/L | 39.511 | 40.3464 | 35.2395 | 41.9026 | SDS-HAA5b, ug/L | 10.4894 | NA | NA | 13.3768
|  | Variability of rejection of reference solute (%) | - | [9 empty] | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | SDS-THM4 | mg/L | 233 | 258.3 | 245.65 | 10.2992 | [70 empty] | SDS-TOX | mg Cl- /L | 63.8 | 71 | 67.4 | 10.6825 | --- | 3179.4 | --- | 93.2667 | 3145.8862 | 97.8575 | SDS-TOX | mg Cl- /L | 98.15 | --- | 9126.65 | --- | 90.1948 | 9027.4573 | 98.9128 | SDS-TOX | mg Cl- /L | 100.5 | --- | 1901.5 | --- | 89.96 | 1881.7733 | 94.6593 | SDS-TOX | mg Cl- /L | 54.1 | --- | 1406.8143 | --- | 94.5954 | 1386.9986 | 96.0995 | SDS-TOXb, ug Cl- /L | 239.1596 | 247.7936 | 232.7768 | 246.5646 | SDS-TOXb, ug Cl- /L | 81.2197 | NA | NA | 90.16
|  | Standard testing recovery (%) | 15 | [9 empty] | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | SDS-MCAA* | mg/L | BMRL | 5.7 | 5.7 | #VALUE! | [70 empty] | SDS-CHCl3 | mg/L | 4.7 | 4.9 | 4.8 | 4.1667 | --- | 675.4667 | --- | 97.6699 | 668.2441 | 99.2817 | SDS-CHCl3 | mg/L | 7.4 | --- | 1993.4 | --- | 96.4078 | 1971.5806 | 99.6247 | SDS-CHCl3 | mg/L | 7.5 | --- | 404.5 | --- | 96.3592 | 400.1516 | 98.1257 | SDS-CHCl3 | mg/L | 2.8 | --- | 293.0857 | --- | 98.6408 | 288.8334 | 99.0306 | SDS-CDb, mg/L | 5.3877 | 5.6881 | 5.1463 | 5.2035 | SDS-CDb, mg/L | 4.0335 | NA | NA | 3.811
|  | Standard testing pH | 6.7-7.3 | [14 empty] | SDS-DCAA* | mg/L | 52 | 68 | 60 | 26.6667 | [70 empty] | SDS-BDCM | mg/L | 9.8 | 9.8 | 9.8 | 0 | --- | 96.9667 | --- | 72.7399 | 96.0279 | 89.7946 | SDS-BDCM | mg/L | 12.6 | --- | 246.1 | --- | 64.9513 | 243.5346 | 94.8262 | SDS-BDCM | mg/L | 13.7 | --- | 58.2 | --- | 61.8915 | 57.7126 | 76.2617 | SDS-BDCM | mg/L | 6.8 | --- | 48.4429 | --- | 81.0848 | 47.8328 | 85.7838 | TOCb, mg/L | 2.3471 | 2.3961 | 2.4279 | 2.6278 | TOCb, mg/L | 0.82793 | NA | NA | 1.1668
|  | Acceptable range of operating pressures | <105 psi | [14 empty] | SDS-TCAA* | mg/L | 116 | 116 | 116 | 0 | [70 empty] | SDS-DBCM | mg/L | 14 | 13.8 | 13.9 | 1.4388 | --- | -20.1 | --- | -275.6757 | -19.7338 | 170.4374 | SDS-DBCM | mg/L | 14.8 | --- | -96.2 | --- | -300 | -94.9805 | 115.5821 | SDS-DBCM | mg/L | 16.7 | --- | -9.3 | --- | -351.3514 | -9.0152 | 285.2423 | SDS-DBCM | mg/L | 12.1 | --- | 0.1 | --- | -227.027 | 0.27579 | -4287.4606 | UV254 b, cm-1 | 0.086955 | 0.089597 | 0.084751 | 0.093469 | UV254 b, cm-1 | 0.026307 | NA | NA | 0.034171
|  | Acceptable range of operating pH values | 3-10 | [14 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [70 empty] | SDS-CHBr3 | mg/L | 4.5 | 4.2 | 4.35 | 6.8966 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 2.7 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 4.2 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 6 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | Bromideb, ug/L | 132.1543 | 135.0221 | 128.6497 | 128.7525 | Bromideb, ug/L | 120.0584 | NA | NA | 115.9514
|  | Typical pressure drop across a single element (psi) | 3 | [14 empty] | SDS-DBAA* | mg/L | BMRL | 1.3 | 1.3 | #VALUE! | [70 empty] | SDS-THM4 | mg/L | 33 | 32.7 | 32.85 | 0.91324 | --- | 742.1833 | --- | 86.6273 | 734.5444 | 95.5278 | SDS-THM4 | mg/L | 37.5 | --- | 2119 | --- | 84.7344 | 2096.1313 | 98.211 | SDS-THM4 | mg/L | 42.1 | --- | 449.2 | --- | 82.8618 | 444.741 | 90.5338 | SDS-THM4 | mg/L | 27.7 | --- | 339.0571 | --- | 88.7238 | 334.4961 | 91.7189 | Alkb, mg/L CaCO3 | 19.2816 | 7.3536 | 14.7638 | 14.2602 | Alkb, mg/L CaCO3 | 19.2985 | NA | NA | 13.2361
|  | Maximum permissible SDI | 5 | [14 empty] | SDS-BCAA* | mg/L | 8.1 | 10.1 | 9.1 | 21.978 | [70 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | T-Hdb, mg/L CaCO3 | 204.7552 | 216.232 | 184.2994 | 165.972 | T-Hdb, mg/L CaCO3 | 199.0033 | NA | NA | 152.1799
|  | Maximum permissible turbidity (ntu) | 1 | [14 empty] | SDS-TBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [70 empty] | SDS-DCAA* | mg/L | 2.3 | 2.4 | 2.35 | 4.2553 | --- | 194.5167 | --- | 96.0833 | 192.4472 | 98.7789 | SDS-DCAA* | mg/L | 4.3 | --- | 561.3 | --- | 92.8333 | 555.1805 | 99.2255 | SDS-DCAA* | mg/L | 3.5 | --- | 116.5 | --- | 94.1667 | 115.2623 | 96.9634 | SDS-DCAA* | mg/L | 1.6 | --- | 85.0286 | --- | 97.3333 | 83.8064 | 98.0908 | Ca-Hdb, mg/L CaCO3 | 196.0193 | 205.9006 | 175.7119 | 158.7525 | Ca-Hdb, mg/L CaCO3 | 190.9441 | NA | NA | 145.9514
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | 1000 ppm-hr | [14 empty] | SDS-CDBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [70 empty] | SDS-TCAA* | mg/L | 2.2 | 2.3 | 2.25 | 4.4444 | --- | 381.4167 | --- | 98.0603 | 377.3333 | 99.4037 | SDS-TCAA* | mg/L | 4.6 | --- | 1118.6 | --- | 96.0345 | 1106.3609 | 99.5842 | SDS-TCAA* | mg/L | 3.1 | --- | 228.9 | --- | 97.3276 | 226.4268 | 98.6309 | SDS-TCAA* | mg/L | 1.5 | --- | 165.0714 | --- | 98.7069 | 162.6753 | 99.0779
|  | 1: All of the information requested in this field may not be available, but values for all Design | [15 empty] | SDS-DCBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [70 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  | Parameters must be entered in cells E14:E23, since these parameters are used in calculations. | [15 empty] | SDS-HAA5 | mg/L | 168 | 191 | 179.5 | 12.8134 | [70 empty] | SDS-DBAA* | mg/L | 3.4 | 3.3 | 3.35 | 2.9851 | --- | -3.4833 | --- | -157.6923 | -3.4097 | 198.2479 | SDS-DBAA* | mg/L | 3.8 | --- | -21.2 | --- | -192.3077 | -20.9253 | 118.1598 | SDS-DBAA* | mg/L | 3.8 | --- | -1.2 | --- | -192.3077 | -1.1452 | 431.8099 | SDS-DBAA* | mg/L | 3.7 | --- | 0.27143 | --- | -184.6154 | 0.32165 | -1050.3075 | Blended Water Quality if HAA5 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if HAA5 Controls the Blend Ratio
[18 empty] | SDS-HAA6 | mg/L | 176.1 | 201.1 | 188.6 | 13.2556 | [70 empty] | SDS-BCAA* | mg/L | 3.4 | 3.4 | 3.4 | 0 | --- | 22.4 | --- | 62.6374 | 22.1954 | 84.6815 | SDS-BCAA* | mg/L | 5.2 | --- | 44.2 | --- | 42.8571 | 43.7715 | 88.1201 | SDS-BCAA* | mg/L | 4.6 | --- | 13.6 | --- | 49.4505 | 13.5014 | 65.9295 | SDS-BCAA* | mg/L | 2.8 | --- | 11.8 | --- | 69.2308 | 11.6682 | 76.0031 | Qp/QT (HAA5), % | 73.1565 | 75.2398 | 74.2164 | 72.6694 | Qp/QT (HAA5), % | 88.8954 | 91.4269 | 90.1833 | 88.3034
[18 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [75 empty] | SDS-TBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-THM4b, ug/L | 89.9729 | 89.0383 | 94.5824 | 87.2671 | SDS-THM4b, ug/L | 56.4807 | 55.345 | 62.0818 | 53.1927
[18 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, | [75 empty] | SDS-CDBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-HAA5b, ug/L | 54 | 54 | 54 | 54 | SDS-HAA5b, ug/L | 27 | 27 | 27 | 27
[18 empty] | should be reported if measured. | [75 empty] | SDS-DCBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TOXb, ug Cl- /L | 318.0108 | 321.6974 | 332.681 | 312.8937 | SDS-TOXb, ug Cl- /L | 171.0729 | 175.5526 | 188.8992 | 164.855
[94 empty] | SDS-HAA5 | mg/L | 7.9 | 8 | 7.95 | 1.2579 | --- | 579.7833 | --- | 95.571 | 573.6251 | 98.6141 | SDS-HAA5 | mg/L | 12.7 | --- | 1680.7 | --- | 92.9248 | 1662.3743 | 99.236 | SDS-HAA5 | mg/L | 10.4 | --- | 348.6 | --- | 94.2061 | 344.8956 | 96.9846 | SDS-HAA5 | mg/L | 6.8 | --- | 253.5143 | --- | 96.2117 | 249.9002 | 97.2789 | SDS-CDb, mg/L | 6.0638 | 6.2996 | 6.0272 | 5.794 | SDS-CDb, mg/L | 4.8039 | 5.0904 | 4.7594 | 4.476
[94 empty] | SDS-HAA6 | mg/L | 11.3 | 11.4 | 11.35 | 0.88106 | --- | 602.1833 | --- | 93.982 | 595.8205 | 98.0951 | SDS-HAA6 | mg/L | 17.9 | --- | 1724.9 | --- | 90.509 | 1706.1458 | 98.9509 | SDS-HAA6 | mg/L | 15 | --- | 362.2 | --- | 92.0467 | 358.3971 | 95.8147 | SDS-HAA6 | mg/L | 9.6 | --- | 265.3143 | --- | 94.9099 | 261.5684 | 96.3298 | TOCb, mg/L | 3.1055 | 3.1103 | 3.3703 | 3.2474 | TOCb, mg/L | 1.6922 | 1.698 | 2.0139 | 1.8646
[94 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | UV254 b, cm-1 | 0.11723 | 0.11804 | 0.12308 | 0.11862 | UV254 b, cm-1 | 0.06081 | 0.061792 | 0.067917 | 0.062491
[94 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | Bromideb, ug/L | 138.1931 | 140.4655 | 136.6931 | 134.1812 | Bromideb, ug/L | 126.9398 | 129.7011 | 125.1171 | 122.0649
[133 empty] | Alkb, mg/L CaCO3 | 19.2732 | 8.5159 | 15.3407 | 14.6945 | Alkb, mg/L CaCO3 | 19.2889 | 6.2174 | 14.5105 | 13.7252
[133 empty] | T-Hdb, mg/L CaCO3 | 207.6268 | 217.8282 | 190.5677 | 171.8211 | T-Hdb, mg/L CaCO3 | 202.2756 | 214.6718 | 181.5464 | 158.7666
[133 empty] | Ca-Hdb, mg/L CaCO3 | 198.553 | 207.333 | 181.5364 | 164.1812 | Ca-Hdb, mg/L CaCO3 | 193.8314 | 204.5003 | 173.1538 | 152.0649
[133 empty] | Notes: |  |  |  |  | Notes:
[133 empty] | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to |  |  |  |  | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to
[133 empty] | determine the percentage of total flow that must be treated by the membrane process to meet the |  |  |  |  | determine the percentage of total flow that must be treated by the membrane process to meet the
[133 empty] | Stage 1 DBP MCLs. |  |  |  |  | Stage 2 DBP MCLs.
[133 empty] | A 10% factor of safety has been applied all the MCLs. i.e., 72 / 54 mg/L for THM4 and HAA5. |  |  |  |  | A 10% factor of safety has been applied all the MCLs. i.e., 36 / 27 mg/L for THM4 and HAA5.
[133 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for |  |  |  |  | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for
[133 empty] | both parameters and the maximum (Qp/QT) ratio controls the design. |  |  |  |  | both parameters and the maximum (Qp/QT) ratio controls the design.
[133 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. |  |  |  |  | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[133 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. |  |  |  |  | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[133 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. |  |  |  |  | The subscript "b" refers to the blended water quality for a given blend ratio.
[133 empty] | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL. |  |  |  |  | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL.
[133 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. |  |  |  |  | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
Note on X24: TSC_ADM: Reported SDS temperature is a measured value - the consultant used an incubator for SDS testing.
Note on Z20: C. Hill (11/16/99): Bromide feed concentrations verified by the utility.
Note on AA20: C. Hill (11/16/99): Bromide feed concentrations verified by the utility.
Note on BA24: C. Hill (11/16/99): The sharp drop in NDP (and rise is MTCw) was verified by the consultant with operational log sheets. Note that the same observation was made for both runs with this particular membrane.
Note on CY16: C. Hill (11/16/99): Results verified by the utility.
Note on CY17: C. Hill (11/16/99): Utility verified the reported permeate concentration for this parameter.
Note on CY22: C. Hill (11/16/99): Utility verified the reported permeate concentration for this parameter.
Note on CY23: C. Hill (11/16/99): Utility verified the reported permeate concentration for this parameter.
Note on CY29: TSC_ADM: Reported SDS temperature is a measured value - the consultant used an incubator for SDS testing.
Note on CY33: C. Hill (11/16/99): Utility verified the reported permeate concentration for this parameter.
Note on CY34: C. Hill (11/16/99): Utility verified the reported permeate concentration for this parameter.
Note on CY35: C. Hill (11/16/99): Utility verified the reported permeate concentration for this parameter.
Note on CY36: C. Hill (11/16/99): Utility verified the reported permeate concentration for this parameter.
Note on CY38: C. Hill (11/16/99): Utility verified the reported permeate concentration for this parameter.
Note on CY39: C. Hill (11/16/99): Utility verified the reported permeate concentration for this parameter.
Note on CY40: C. Hill (11/16/99): Utility verified the reported permeate concentration for this parameter.
Note on CY41: C. Hill (11/16/99): Utility verified the reported permeate concentration for this parameter.
Note on CY42: C. Hill (11/16/99): Utility verified the reported permeate concentration for this parameter.
Note on CY43: C. Hill (11/16/99): Utility verified the reported permeate concentration for this parameter.
Note on DL16: C. Hill (11/16/99): Results verified by the utility.
Note on DL23: C. Hill (11/16/99): Results verified by the utility.
Note on DL29: TSC_ADM: Reported SDS temperature is a measured value - the consultant used an incubator for SDS testing.
Note on DV16: C. Hill (11/16/99): Results verified by the utility.
Note on DV17: C. Hill (11/16/99): Utility verified the reported permeate concentration for this parameter.
Note on DV22: C. Hill (11/16/99): Utility verified the reported permeate concentration for this parameter.
Note on DV23: C. Hill (11/16/99): Utility verified the reported permeate concentration for this parameter.
Note on DV29: TSC_ADM: Reported SDS temperature is a measured value - the consultant used an incubator for SDS testing.
Note on DV33: C. Hill (11/16/99): Utility verified the reported permeate concentration for this parameter.
Note on DV34: C. Hill (11/16/99): Utility verified the reported permeate concentration for this parameter.
Note on DV35: C. Hill (11/16/99): Utility verified the reported permeate concentration for this parameter.
Note on DV36: C. Hill (11/16/99): Utility verified the reported permeate concentration for this parameter.
Note on DV38: C. Hill (11/16/99): Utility verified the reported permeate concentration for this parameter.
Note on DV39: C. Hill (11/16/99): Utility verified the reported permeate concentration for this parameter.
Note on DV40: C. Hill (11/16/99): Utility verified the reported permeate concentration for this parameter.
Note on DV41: C. Hill (11/16/99): Utility verified the reported permeate concentration for this parameter.
Note on DV42: C. Hill (11/16/99): Utility verified the reported permeate concentration for this parameter.
Note on DV43: C. Hill (11/16/99): Utility verified the reported permeate concentration for this parameter.
Note on EF16: C. Hill (11/16/99): Results verified by the utility.
Note on EF29: TSC_ADM: Reported SDS temperature is a measured value - the consultant used an incubator for SDS testing.
Print All Fields

## DCSS2. 3rd Quarter
FIELD-SET 3: Membrane C, Run 2 (FILE: Delray2.xls)
Field 3-1: PWS And Treatment Plant Data |  | Field 3-2: Manufacturer Reported Membrane Characteristics1 |  | Field 3-3: RBSMT Design Parameters | [8 empty] | Field 3-4: Foulants And Fouling Indices1 |  | Field 3-5: Pretreatment Used Prior To Membranes1 |  |  | Field 3-6: Feed Water Quality After Pretreatment | [5 empty] | Field 3-7: Membrane Setting Data | [20 empty] | Field 3-8: Membrane Performance Data During Operation With The Test Water | [16 empty] | Field 3-8: Membrane Performance Data During Operation With The Test Water (continued) | [19 empty] | Field 3-8: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 3-9: Permeate And Concentrate Water Quality For Run 1 | [11 empty] | Field 3-10: Permeate And Concentrate Water Quality For Run 2 | [8 empty] | Field 3-11: Permeate And Concentrate Water Quality For Run 3 | [8 empty] | Field 3-12: Permeate And Concentrate Water Quality For Run 4 | [8 empty] | Field 3-13: Blending Calculations For Stage 1 D-DBP MCLs |  |  |  |  | Field 3-14: Blending Calculations For Proposed Stage 2 D-DBP MCLs |  |  |  |  | Field 3-15: Membrane Cost Parameters
|  | General Information |  | Input Design Parameters | [8 empty] | Parameters Evaluated Prior to Pretreatment | [80 empty] | Operating Parameters During Sample Collection | [11 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Feed and Permeate Water Quality Parameters |  |  |  |  | Feed and Permeate Water Quality Parameters |  |  |  |  | General Cost Parameters
PWS Name | Delray Beach Water Department | Membrane manufacturer | Hydranautics | [5 empty] | Active membrane area in bench-scale cell, Acell (ft2) | 0.16667 |  |  | Alkalinity (mg/L as CaCO3) | 243 | Process | Description | Scale | Parameter | Units | CF-1 | CF-2 | Average | RPD |  |  |  | Average TDS rejection (decimal fraction) | 0.7 | [5 empty] | TDS concentration of setting solution (mg/L) | 50 | [12 empty] | Average bulk TDS rejection (decimal fraction) | 0.52018 | [45 empty] | Recovery during sample collection (decimal) | 0.76 | [10 empty] | Recovery during sample collection (decimal) | 0.9 | [7 empty] | Recovery during sample collection (decimal) | 0.5 | [7 empty] | Recovery during sample collection (decimal) | 0.35 | [8 empty] | RUN ID # |  |  |  |  | RUN ID # |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | FL4500351 | Membrane trade name | ESNA1 | [5 empty] | Active width of membrane in the bench-scale cell, wcell (ft) | 0.33333 |  |  | Calcium Hardness (mg/L as CaCO3) | 295 | Aeration | Fine Bubble diffuwer in barrel overnight | Bench | Sampling date | MM/DD/YY | 1999-05-18 | 1999-05-21 | --- | --- | [71 empty] | Feed flow rate during sample collection (mL/min) | 9.2 | [10 empty] | Feed flow rate during sample collection (mL/min) | 7.3 | [7 empty] | Feed flow rate during sample collection (mL/min) | 13 | [7 empty] | Feed flow rate during sample collection (mL/min) | 22.3 | [6 empty] | Parameter | 1 | 2 | 3 | 4 | Parameter | 1 | 2 | 3 | 4 | Capital Recovery Interest Rate (%) | 5.75
Water Industry Data Base Number (optional) | NA | Molecular weight cutoff (Daltons) | 180 | [5 empty] | Average yearly temperature of feed water, TavgoC (oC) | 22 |  |  | LSI |  | Acidification | Hydrochloric acid to pH 6.5 | Bench | Sampling time | hh:mm | NR | NR | --- | --- | Date | Time | Setting time | Influent | PI | PC | QI | Qp | QW | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) | Date | Time | Operation time | Influent | PI | PC | QI | Qp | QW | Cleaning Event | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1) | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Influent flow rate during sample collection (mL/min) | 299 | [10 empty] | Influent flow rate during sample collection (mL/min) | 299 | [7 empty] | Influent flow rate during sample collection (mL/min) | 299 | [7 empty] | Influent flow rate during sample collection (mL/min) | 299 | [6 empty] | SDS-THM4F, ug/L | 245.65 | 245.65 | 245.65 | 245.65 | SDS-THM4F, ug/L | 245.65 | 245.65 | 245.65 | 245.65 | Capital Recovery Period (years) | 25
|  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide | [5 empty] | Approximate feed water TDS, TDSF (mg/L) | 545 |  |  | Dissolved iron (mg/L) |  | Antiscalant addition | King Lee PreTreat 0100, 3 ppm by volume | Bench | Operation time | hh.hh | 58.1 | 129.8 | --- | --- | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | Indicate with "X" | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) | [39 empty] | SDS-THM4p, ug/L | 43.45 | 67.7 | 35 | 32 | SDS-THM4p, ug/L | 43.45 | 67.7 | 35 | 32 | Overhead & Profit Factor (% of construction costs) | 15
Official ICR Contact Person |  | Membrane construction (e.g., thin-film composite) | Thin-Film Composite | [5 empty] | Manufacturer reported TDS rejection, RejTDS (decimal fraction) | 0.7 |  |  | Total iron (mg/L) |  | Membrane Filtration | 0.1 micron Pall Microza cartridge | Bench | pH | --- | 6.31 | 6 | 6.155 | 5.0366 | 1999-05-22 | 13:15 | 0 | Start | [17 empty] | 1999-05-24 | 11:30 | 0 | [46 empty] | Permeate and Concentrate Water Quality | [11 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | SDS-HAA5F, ug/L | 179.5 | 179.5 | 179.5 | 179.5 | SDS-HAA5F, ug/L | 179.5 | 179.5 | 179.5 | 179.5 | Special Sitework Factor (% of construction costs) | 5
Mailing Address |  | Membrane hydrophobicity | Hydrophilic | [5 empty] | Temperature normalized MTCW (gfd/psi) | 0.32945 |  |  | Dissolved aluminum (mg/L) |  |  |  |  | Temperature | oC | NR | NR | #DIV/0! | #VALUE! | 1999-05-22 | 13:40 | 0.3 | 23 | 79.8 | 79.5 | 299 | 6.7 | 2.7 | 9.4 | 0.22627 | 0.71277 | 30.8085 | 15.2924 | 14.847 | 100.4647 | 29.6635 | 98.8782 | 0.70008 | 78.9499 | 0.18806 | 1999-05-24 | 12:10 | 0.7 | 24.6 | 78.6 | 78.2 | 299 | 6.5 | 2.8 |  | 9.3 | 0.22627 | 0.69892 | 31.1505 | 14.8359 | 13.7384 | 757.9797 | 359.5395 | 749.3179 | 3.9411 | 74.4589 | 0.18451 | 5.95 |  |  | 526.682 |  |  | 369.9704 |  | NR | 371.6737 | NR | 0.021 |  |  | 1.2117 |  | 94.4664 | 1.1988 | 98.2482 | [8 empty] | Parameter | Units | Cp-1 | Cp-1 (dup) | Average | RPD | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | SDS-HAA5p, ug/L | 19.95 | 40.5 | 13.2 | 14 | SDS-HAA5p, ug/L | 19.95 | 40.5 | 13.2 | 14 | Construction Contingencies (% of construction costs) | 15
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Negative | [9 empty] | Total aluminum (mg/L) |  |  |  |  | Alkalinity | mg/L as CaCO3 | 12.2 | 26.2 | 19.2 | 72.9167 | 1999-05-23 | 12:31 | 23.2 | 26.3 | 74.4 | 74.1 | 299 | 6.9 | 2.6 | 9.5 | 0.22627 | 0.72632 | 30.4737 | 15.7489 | 13.8691 | 102.4518 | 30.2356 | 100.7852 | 0.71383 | 73.5362 | 0.1886 | 1999-05-24 | 13:22 | 2 | 24.9 | 78.8 | 78.2 | 299 | 6.4 | 2.8 |  | 9.2 | 0.22627 | 0.69565 | 31.5 | 14.6077 | 13.4076 | 755.8534 | 358.5954 | 747.3502 | 3.9301 | 74.5699 | 0.1798 | 5.76 |  |  | 431 |  |  | 590.3571 |  | 10.1147 | 588.6516 | 26.7818 | 0.052 |  |  | 1.1281 |  | 86.2978 | 1.1166 | 95.3428 | [8 empty] | Sampling date | MM/DD/YY | 1999-05-25 | 1999-05-25 | --- | --- | 1999-05-25 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-05-26 | 1999-05-26 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-05-27 | 1999-05-27 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-05-28 | 1999-05-28 | --- | --- | --- | --- | --- | SDS-TOXF, ug Cl- /L | 1001 | 1001 | 1001 | 1001 | SDS-TOXF, ug Cl- /L | 1001 | 1001 | 1001 | 1001 | Engineering Fee Factor (% of construction costs) | 10
Phone Number |  |  |  | Experimental Design1,2 | [8 empty] | Fluoride (mg/L) |  |  |  |  | Total dissolved solids | mg/L | 538 | 421 | 479.5 | 24.4004 | 1999-05-23 | 14:01 | 24.7 | 26.9 | 74.2 | 73.9 | 299 | 6.9 | 2.6 | 9.5 | 0.22627 | 0.72632 | 30.4737 | 15.7489 | 13.6253 | 102.4518 | 30.2356 | 100.7852 | 0.71383 | 73.3362 | 0.18579 | 1999-05-24 | 17:43 | 6.3 | 24.3 | 82 | 81.9 | 299 | 6.3 | 2.9 |  | 9.2 | 0.22627 | 0.68478 | 31.5 | 14.3794 | 13.4343 | 749.0392 | 355.4264 | 740.7457 | 3.8947 | 78.0553 | 0.17211 | 6.58 | 6.04 | 6.66 | 400.83 | 503.867 | 871.65 | 650.4038 | 25.3825 | 16.4067 | 647.7745 | 38.122 | 0.056 | 0.365 | 1.089 | 1.0823 | 0.61746 | 85.2437 | 1.0715 | 94.7735 | [8 empty] | Sampling time | hh:mm | NR | NR | --- | --- | NR | --- | --- | --- | --- | --- | Sampling time | hh:mm | NR | NR | --- | --- | --- | --- | --- | Sampling time | hh:mm | NR | NR | --- | --- | --- | --- | --- | Sampling time | hh:mm | NR | NR | --- | --- | --- | --- | --- | SDS-TOXp, ug Cl- /L | 119 | 298 | 108 | 116.5 | SDS-TOXp, ug Cl- /L | 119 | 298 | 108 | 116.5 | 1998 ENR Construction Cost Index (CCI base year 1913) | 5875
FAX Number |  | Design Parameters |  | ID# | Recovery | FW-design | Dp | PI | QI-cell | Qp | QF | QW | Phosphate (mg/L) |  |  |  |  | Total hardness | mg/L as CaCO3 | 246 | 219 | 232.5 | 11.6129 | 1999-05-23 | 17:45 | 28.4 | 28 | 73 | 72.8 | 299 | 6.8 | 2.8 | 9.6 | 0.22627 | 0.70833 | 30.1458 | 15.5206 | 12.9983 | 99.8481 | 29.4743 | 98.2477 | 0.69574 | 72.2043 | 0.18002 | 1999-05-25 | 10:01 | 22.6 | 24.1 | 86.1 | 85.8 | 299 | 6.4 | 0.7 |  | 7.1 | 0.22627 | 0.90141 | 41.1127 | 14.6077 | 13.7285 | 911.1781 | 432.2852 | 900.9276 | 4.7377 | 81.2123 | 0.16904 | 6.19 |  |  | 396.206 |  |  | 1241.0451 |  | 17.371 | 1232.0034 | 67.8405 | 0.06 |  |  | 3.3006 |  | 84.1897 | 3.266 | 98.1629 | [8 empty] | Operation time | hh.hh | 60 | 60 | --- | --- | 60 | --- | --- | --- | --- | --- | Operation time | hh.hh | 83.5 | 83.5 | --- | --- | --- | --- | --- | Operation time | hh.hh | 107.7 | 107.7 | --- | --- | --- | --- | --- | Cumulative time | hr | 132.3 | 132.3 | --- | --- | --- | --- | --- | SDS-CDF, mg/L | 11.92 | 11.92 | 11.92 | 11.92 | SDS-CDF, mg/L | 11.92 | 11.92 | 11.92 | 11.92 | 1998 Producers Price Index (PPI base year 1967 = 100) | 369
E-Mail Address (optional) |  | Design flux, FW (gfd) | 27 |  | (decimal) | (gfd) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | Sulfate (mg/L) | 26.5 |  |  |  | Calcium hardness | mg/L as CaCO3 | 233 | 208 | 220.5 | 11.3379 | [21 empty] | 1999-05-25 | 13:43 | 26.3 | 24.7 | 90.1 | 89.9 | 299 | 6.6 | 0.7 |  | 7.3 | 0.22627 | 0.90411 | 39.9589 | 15.0641 | 13.9086 | 913.9113 | 433.4261 | 903.3053 | 4.7518 | 85.2482 | 0.16315 | 5.88 |  |  | 438.288 |  |  | 868.0703 |  | 8.5948 | 863.3269 | 49.2327 | 0.088 |  |  | 3.1279 |  | 76.8116 | 3.0944 | 97.1561 | [8 empty] | pH | --- | 6.73 | 6.56 | 6.645 | 2.5583 | 6.74 | --- | --- | --- | --- | --- | pH | --- | 6.54 | 6.86 | --- | --- | --- | --- | --- | pH | --- | 6.3 | 6.9 | --- | --- | --- | --- | --- | pH | --- | 6.1 | 6.1 | --- | --- | --- | --- | --- | SDS-CDp, mg/L | 4.09 | 5.42 | 3.28 | 3.27 | SDS-CDp, mg/L | 4.09 | 5.42 | 3.28 | 3.27 | Labor Rate + Fringe ($/work-hour) | 19.89
|  | Net driving pressure at the design flux, NDP (psi) | 68 | 1 | 0.7 | 27 | 14.3517 | 96.3062 | 411.456 | 11.8281 | 16.8973 | 5.0692 | Calcium (mg/L) |  |  |  |  | Turbidity | ntu | 0.21 | 0.3 | 0.255 | 35.2941 | [21 empty] | 1999-05-25 | 16:11 | 28.8 | 24.3 | 88.5 | 88.2 | 299 | 6.6 | 0.7 |  | 7.3 | 0.22627 | 0.90411 | 39.9589 | 15.0641 | 14.074 | 913.9113 | 433.4261 | 903.3053 | 4.7518 | 83.5982 | 0.16835 | 6.03 | 6.34 | 7.1 | 454.168 | 494.375 | 1160.277 | 718.3446 | 38.0885 | 5.283 | 715.4289 | 36.5181 | 0.125 | 0.348 | 2.397 | 2.7791 | -15.9396 | 67.0619 | 2.7498 | 95.4542 | [8 empty] | Temperature | oC | NR | NR | #DIV/0! | #VALUE! | NR | --- | --- | --- | --- | --- | Temperature | oC | NR | NR | --- | --- | --- | --- | --- | Temperature | oC | NR | NR | --- | --- | --- | --- | --- | Temperature | oC | NR | NR | --- | --- | --- | --- | --- | TOCF, mg/L | 9.675 | 9.675 | 9.675 | 9.675 | TOCF, mg/L | 9.675 | 9.675 | 9.675 | 9.675 | Labor Overhead Factor (% of labor) | 6
Technical ICR Contact Person |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.36 | 2 | 0.9 | 27 | 39.785 | 121.7395 | 411.456 | 11.8281 | 13.1424 | 1.3142 | Barium (mg/L) | 0.018 |  |  |  | Ammonia | mg NH3-N / L | 0.59 | 0.37 | 0.48 | 45.8333 | [21 empty] | 1999-05-26 | 10:27 | 47 | 24.6 | 91.2 | 91 | 299 | 6.8 | 6.6 |  | 13.4 | 0.22627 | 0.50746 | 21.3134 | 15.5206 | 14.3725 | 654.0566 | 310.0774 | 646.2337 | 3.4007 | 87.6993 | 0.16388 | 6.17 |  |  | 322.392 |  |  | 641.3688 |  | 32.765 | 637.7417 | 49.4479 | 0.056 |  |  | 0.7128 |  | 85.2437 | 0.70533 | 92.0605 | [8 empty] | Alkalinity | mg/L as CaCO3 | 4.5 | 4.8 | 4.65 | 6.4516 | 13.5 | 65.275 | -383.5185 | 75.7812 | 64.5662 | 92.7981 | Alkalinity | mg/L as CaCO3 | 5.7 | 20.7 | 140.7 | -579.7101 | 70.3125 | 139.2168 | 95.9057 | Alkalinity | mg/L as CaCO3 | NR | NR | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 6 | 16 | 26.3077 | -64.4231 | 68.75 | 26.0426 | 76.9609 | TOCp, mg/L | 1.325 | 2.94 | 1 | 1.08 | TOCp, mg/L | 1.325 | 2.94 | 1 | 1.08 | Electric Rate ($/kW-h) | 0.05
Mailing Address |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | 3 | 0.5 | 27 | 9.265 | 91.2195 | 411.456 | 11.8281 | 23.6562 | 11.8281 | Strontium (mg/L) |  |  |  |  | Total organic carbon | mg/L | 9.65 | 9.7 | 9.675 | 0.5168 | [21 empty] | 1999-05-26 | 13:07 | 49.7 | 25 | 88 | 87.8 | 299 | 6.6 | 6.6 |  | 13.2 | 0.22627 | 0.5 | 21.6515 | 15.0641 | 13.7858 | 650.4985 | 308.5015 | 642.9494 | 3.3822 | 84.5178 | 0.16311 | 6.05 |  |  | 295.26 |  |  | 663.74 |  | 38.4234 | 659.6732 | 55.2415 | 0.029 |  |  | 0.73 |  | 92.3584 | 0.72226 | 95.9848 | [8 empty] | Total dissolved solids | mg/L | 406 | 396 | 401 | 2.4938 | 872 | 728.0833 | 16.5042 | 16.3712 | 724.259 | 44.6331 | Total dissolved solids | mg/L | 454 | 1160 | 709 | 38.8793 | 5.318 | 706.1984 | 35.7121 | Total dissolved solids | mg/L | 296 | 716 | 663 | 7.4022 | 38.269 | 659.0109 | 55.0842 | Total dissolved solids | mg/L | 250 | 692 | 603.0769 | 12.8502 | 47.8624 | 598.4686 | 58.2267 | UV254 F, cm-1 | 0.3795 | 0.3795 | 0.3795 | 0.3795 | UV254 F, cm-1 | 0.3795 | 0.3795 | 0.3795 | 0.3795 | Fuel Oil Rate ($/gal) | NA
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 400 | 4 | 0.3 | 27 | 7.085 | 89.0395 | 411.456 | 11.8281 | 39.4271 | 27.599 | Reactive silica (mg/L as SiO2) | 32.8 |  |  |  | UV254 | cm-1 | 0.388 | 0.371 | 0.3795 | 4.4796 | [21 empty] | 1999-05-26 | 17:10 | 53.7 | 24.7 | 88.5 | 88.2 | 299 | 6.5 | 6.5 |  | 13 | 0.22627 | 0.5 | 22 | 14.8359 | 13.6979 | 650.4609 | 308.5391 | 643.0278 | 3.3821 | 84.9679 | 0.16121 | 6.11 | 6.37 | 6.45 | 296.058 | 507.822 | 716.292 | 662.942 | 7.4481 | 38.2569 | 658.9541 | 55.0715 | 0.036 | 0.352 | 0.732 | 0.723 | 1.2295 | 90.5138 | 0.71553 | 94.9688 | [8 empty] | Total hardness | mg/L as CaCO3 | 149 | 141 | 145 | 5.5172 | 347 | 509.5833 | -46.854 | 37.6344 | 505.3205 | 71.3053 | Total hardness | mg/L as CaCO3 | 199 | 518 | 534 | -3.0888 | 14.4086 | 530.3195 | 62.4754 | Total hardness | mg/L as CaCO3 | 117 | 364 | 348 | 4.3956 | 49.6774 | 345.4891 | 66.135 | Total hardness | mg/L as CaCO3 | 109 | 286 | 299 | -4.5455 | 53.1183 | 296.5202 | 63.2403 | UV254 p, cm-1 | 0.04775 | 0.1015 | 0.037 | 0.036 | UV254 p, cm-1 | 0.04775 | 0.1015 | 0.037 | 0.036 | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Purchase price for an equivalent 8" x 40 " element ($) | 875 | 1: For experimental matrix see Table 4-2 in Part 3 of the ICR Treatment Studies Manual. | [8 empty] | Turbidity (ntu) |  |  |  |  | SUVA | L/(mg*m) | 4.0207 | 3.8247 | 3.9227 | 4.9961 | [21 empty] | 1999-05-27 | 9:23 | 69.7 | 23.9 | 90 | 89.6 | 299 | 6.7 | 15.5 |  | 22.2 | 0.22627 | 0.3018 | 12.4685 | 15.2924 | 14.4572 | 569.9491 | 270.252 | 563.2335 | 2.9634 | 86.8366 | 0.16649 | 6.07 |  |  | 257.866 |  |  | 575.3031 |  | 46.2219 | 571.7465 | 54.8985 | 0.042 |  |  | 0.52539 |  | 88.9328 | 0.51997 | 91.9226 | [8 empty] | Calcium hardness | mg/L as CaCO3 | 141 | 133 | 137 | 5.8394 | 329 | 484.9167 | -47.3911 | 37.8685 | 480.8487 | 71.5087 | Calcium hardness | mg/L as CaCO3 | 189 | 491 | 504 | -2.6477 | 14.2857 | 500.5392 | 62.2407 | Calcium hardness | mg/L as CaCO3 | 110 | 347 | 331 | 4.611 | 50.1134 | 328.5978 | 66.5244 | Calcium hardness | mg/L as CaCO3 | 104 | 272 | 283.2308 | -4.129 | 52.8345 | 280.8915 | 62.975 | BromideF, ug/L | 190.5 | 190.5 | 190.5 | 190.5 | BromideF, ug/L | 190.5 | 190.5 | 190.5 | 190.5 | Current Process Water Rate ($/1000 gal) | 0.41
FAX Number |  | Maximum flow rate to the 8" x 40" element, QI, max (gpm) | 75 | 2: Flow rates and pressures may need to be adjusted in order to obtain the desired operating conditions. | [8 empty] | SDI |  |  |  |  | Bromide | mg/L | 243 | 138 | 190.5 | 55.1181 | [21 empty] | 1999-05-27 | 12:45 | 73.1 | 24.2 | 90.4 | 90.1 | 299 | 6.6 | 15.4 |  | 22 | 0.22627 | 0.3 | 12.5909 | 15.0641 | 14.1157 | 569.2907 | 269.9884 | 562.684 | 2.96 | 87.29 | 0.16171 | 6.08 |  |  | 246.001 |  |  | 579.571 |  | 48.6964 | 575.8895 | 57.2833 | 0.022 |  |  | 0.53271 |  | 94.2029 | 0.52708 | 95.826 | [8 empty] | Turbidity | ntu | BMRL | BMRL | #DIV/0! | #VALUE! | 0.1 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu | BMRL | 0.24 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | 0.11 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | 0.09 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Bromidep, ug/L | 113.5 | 112 | 77 | 75 | Bromidep, ug/L | 113.5 | 112 | 77 | 75 | Modifications to Existing Plant (% of construction costs) | 10
E-Mail Address (optional) |  | Minimum flow rate to the 8" x 40" element, QI, min (gpm) | 25 | [9 empty] | MFI |  |  |  |  | SDS-Cl2 dose | mg/L | 12.7 | 12.72 | 12.71 | 0.15736 | [21 empty] | 1999-05-27 | 18:55 | 79.3 | 23.8 | 91 | 90.8 | 299 | 6.9 | 15.4 |  | 22.3 | 0.22627 | 0.30942 | 12.4081 | 15.7489 | 14.9328 | 572.711 | 271.4639 | 565.7591 | 2.9777 | 87.9223 | 0.16984 | 6.15 |  | 6.32 | 249.956 |  | 692.307 | 582.3476 | 15.883 | 47.8715 | 578.5123 | 56.7933 | 0.036 |  | 0.533 | 0.53341 | -0.076143 | 90.5138 | 0.52767 | 93.1775 | [8 empty] | Ammonia | mg NH3-N / L | 0.28 | 0.3 | 0.29 | 6.8966 | 0.52 | 1.0817 | -108.0128 | 39.5833 | 1.0724 | 72.9581 | Ammonia | mg NH3-N / L | 0.2 | 0.36 | 3 | -733.3333 | 58.3333 | 2.9692 | 93.2643 | Ammonia | mg NH3-N / L | 0.16 | 0.29 | 0.8 | -175.8621 | 66.6667 | 0.79304 | 79.8246 | Ammonia | mg NH3-N / L | 0.14 | 0.27 | 0.66308 | -145.584 | 70.8333 | 0.65625 | 78.6667 | AlkF, mg/L CaCO3 | 19.2 | 19.2 | 19.2 | 19.2 | AlkF, mg/L CaCO3 | 19.2 | 19.2 | 19.2 | 19.2
|  | Total width of all membrane envelopes in the 8" x 40" element, w (ft) | 76.667 | [9 empty] | MPFI |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | SDS-Free Cl2 residual | mg/L | 0.8 | 0.78 | 0.79 | 2.5316 | [21 empty] | 1999-05-28 | 9:34 | 93.9 | [6 empty] | X | [39 empty] | Total organic carbon | mg/L | 1.45 | 1.2 | 1.325 | 18.8679 | 28.6 | 36.1167 | -26.2821 | 86.3049 | 35.7099 | 96.2895 | Total organic carbon | mg/L | 2.94 | 62.1 | 70.29 | -13.1884 | 69.6124 | 69.5501 | 95.7728 | Total organic carbon | mg/L | 1 | 18.4 | 18.35 | 0.27174 | 89.6641 | 18.1614 | 94.4938 | Total organic carbon | mg/L | 1.08 | 14.3 | 14.3031 | -0.021517 | 88.8372 | 14.1305 | 92.357 | Alkp, mg/L CaCO3 | 4.65 | 5.7 | NR | 6 | Alkp, mg/L CaCO3 | 4.65 | 5.7 | NR | 6
Plant Name | Lime Softening Plant | Feed spacer thickness in the 8" x 40" element, T (ft) | 0.0023333 | [9 empty] | pH | 7.2 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | SDS-Cl2 demand | mg/L | 11.9 | 11.94 | 11.92 | 0.33557 | [21 empty] | 1999-05-28 | 18:43 | 94.2 | 23 | 87.6 | 87.4 | 299 | 6.6 | 15.4 |  | 22 | 0.22627 | 0.3 | 12.5909 | 15.0641 | 14.6254 | 569.2907 | 269.9884 | 562.684 | 2.96 | 84.54 | 0.173 | 5.85 |  |  | 246.001 |  |  | 579.571 |  | 48.6964 | 575.8895 | 57.2833 | 0.096 |  |  | 0.501 |  | 74.7036 | 0.49653 | 80.6658 | [8 empty] | UV254 | cm-1 | 0.0475 | 0.048 | 0.04775 | 1.0471 | 1.044 | 1.43 | -36.9772 | 87.4177 | 1.4139 | 96.6228 | UV254 | cm-1 | 0.1015 | 2.417 | 2.8815 | -19.218 | 73.2543 | 2.851 | 96.4398 | UV254 | cm-1 | 0.037 | 0.678 | 0.722 | -6.4897 | 90.2503 | 0.71455 | 94.8219 | UV254 | cm-1 | 0.036 | 0.556 | 0.56446 | -1.5219 | 90.5138 | 0.55756 | 93.5433 | T-HdF, mg/L CaCO3 | 232.5 | 232.5 | 232.5 | 232.5 | T-HdF, mg/L CaCO3 | 232.5 | 232.5 | 232.5 | 232.5
Treatment Plant Category | SOFT | [11 empty] | Chloride (mg/L) | 59.9 | is to list the pretreatment processes used in this particular RBSMT run. |  |  | SDS-Chlorination temp. | oC | 20 | 20 | 20 | 0 | [21 empty] | 1999-05-29 | 12:39 | 112.2 | 23.4 | 80.4 | 80.1 | 299 | 6.9 | 14.9 |  | 21.8 | 0.22627 | 0.31651 | 12.7156 | 15.7489 | 15.1105 | 575.2759 | 272.6796 | 568.2929 | 2.991 | 77.259 | 0.19558 | 5.92 |  |  | 230.181 |  |  | 594.9564 |  | 51.9956 | 590.7475 | 61.0356 | 0.032 |  |  | 0.54042 |  | 91.5679 | 0.53456 | 94.0137 | [8 empty] | SUVA | L/(mg*m) | 3.2759 | 4 | 3.6379 | 19.9052 | 3.6503 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 3.4524 | 3.8921 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 3.7 | 3.6848 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 3.3333 | 3.8881 | --- | --- | --- | --- | --- | T-Hdp, mg/L CaCO3 | 145 | 199 | 117 | 109 | T-Hdp, mg/L CaCO3 | 145 | 199 | 117 | 109
Process Train Name | NA | Additional Information | [10 empty] | Mg (mg/L) | 44 |  |  |  | SDS-Chlorination pH | --- | 7.49 | 7.55 | 7.52 | 0.79787 | [21 empty] | 1999-05-29 | 13:50 | 113.4 | 23.6 | 80.4 | 80.2 | 299 | 6.9 | 14.7 |  | 21.6 | 0.22627 | 0.31944 | 12.8426 | 15.7489 | 15.0214 | 576.3418 | 273.1849 | 569.3459 | 2.9966 | 77.3034 | 0.19432 | 5.83 | 5.98 | 6.03 | 222.271 | 420.021 | 582.714 | 600.2401 | -3.0077 | 53.6453 | 595.879 | 62.6986 | 0.032 | 0.371 | 0.534 | 0.54261 | -1.6128 | 91.5679 | 0.53672 | 94.0379 | [8 empty] | Bromide | mg/L | 127 | 100 | 113.5 | 23.7885 | --- | 434.3333 | --- | 40.4199 | 430.5821 | 73.6403 | Bromide | mg/L | 112 | --- | 897 | --- | 41.2073 | 888.3755 | 87.3927 | Bromide | mg/L | 77 | --- | 304 | --- | 59.5801 | 301.5326 | 74.4638 | Bromide | mg/L | 75 | --- | 252.6923 | --- | 60.6299 | 250.3731 | 70.0447 | Ca-HdF, mg/L CaCO3 | 220.5 | 220.5 | 220.5 | 220.5 | Ca-HdF, mg/L CaCO3 | 220.5 | 220.5 | 220.5 | 220.5
ICR Treatment Plant Identification Number | 1086 | Design cross-flow velocity (fps) | Unknown | [9 empty] | Potassium (mg/L) | 25.1 |  |  |  | SDS-Incubation time | hours | 23.53 | 24 | 23.765 | 1.9777 | [70 empty] | SDS-Cl2 dose | mg/L | 5.52 | 5.52 | 5.52 | 0 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 6 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 3.8 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 4.4 | --- | --- | --- | --- | --- | --- | Ca-Hdp, mg/L CaCO3 | 137 | 189 | 110 | 104 | Ca-Hdp, mg/L CaCO3 | 137 | 189 | 110 | 104
PWSID Number of Plant (if assigned) | 45-00351 | Required influent flow to permeate flow rate ratio, QI:Qp | 5 | [9 empty] | Strontium (mg/L) | 1.14 |  |  |  | SDS-TOX | mg Cl- /L | 1115 | 887 | 1001 | 22.7772 | [70 empty] | SDS-Free Cl2 residual | mg/L | 1.42 | 1.44 | 1.43 | 1.3986 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.58 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.52 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.13 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 18 | Maximum element recovery (%) | 20 | [14 empty] | SDS-CHCl3 | mg/L | 196 | 216 | 206 | 9.7087 | [70 empty] | SDS-Cl2 demand | mg/L | 4.1 | 4.08 | 4.09 | 0.489 | --- | 36.715 | --- | 65.6879 | 36.3335 | 88.7432 | SDS-Cl2 demand | mg/L | 5.42 | --- | 70.42 | --- | 54.5302 | 69.7059 | 92.2245 | SDS-Cl2 demand | mg/L | 3.28 | --- | 20.56 | --- | 72.4832 | 20.3722 | 83.8996 | SDS-Cl2 demand | mg/L | 3.27 | --- | 16.5777 | --- | 72.5671 | 16.404 | 80.0658 | Blended Water Quality if THM4 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if THM4 Controls the Blend Ratio
Historical Average Water Temperature (oC) | 20 | Variability of design flux (%) | 15 | [14 empty] | SDS-BDCM | mg/L | 33.5 | 38.4 | 35.95 | 13.63 | [70 empty] | SDS-Chlorination temp. | oC | 20 | 20 | 20 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 20 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 20 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 20 | --- | --- | --- | --- | --- | --- | Qp/QT (THM4), % | 85.8803 | 97.5836 | 82.4353 | 81.2778 | Qp/QT (THM4), % | 103.6845 | 117.814 | 99.5253 | 98.1278
State Approved Plant Capacity (MGD) | 22.4 | Rejection of reference solute and conditions of test | min 70% avg 80% | [14 empty] | SDS-DBCM | mg/L | 3.5 | 3.9 | 3.7 | 10.8108 | [70 empty] | SDS-Chlorination pH | --- | 7.53 | 7.55 | 7.54 | 0.26525 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.54 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.42 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.49 | --- | --- | --- | --- | --- | --- | SDS-THM4b, ug/L | 72 | 72 | 72 | 72 | SDS-THM4b, ug/L | NA | NA | 36 | 36
|  | (e.g., solute type and concentration) | 500 ppm NaCl | [9 empty] | Sodium (mg/L) | 32.8 |  |  |  | SDS-CHBr3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [70 empty] | SDS-Incubation time | hours | 23.9 | 23.9 | 23.9 | 0 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24.75 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 28.88 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 20 | --- | --- | --- | --- | --- | --- | SDS-HAA5b, ug/L | 42.478 | 43.8588 | 42.4101 | 44.9853 | SDS-HAA5b, ug/L | NA | NA | 13.9895 | 17.0985
|  | Variability of rejection of reference solute (%) | 10 | [9 empty] | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | SDS-THM4 | mg/L | 233 | 258.3 | 245.65 | 10.2992 | [70 empty] | SDS-TOX | mg Cl- /L | 126 | 112 | 119 | 11.7647 | --- | 3794 | --- | 88.1119 | 3751.0308 | 96.8275 | SDS-TOX | mg Cl- /L | 298 | --- | 7328 | --- | 70.2298 | 7250.764 | 95.8901 | SDS-TOX | mg Cl- /L | 108 | --- | 1894 | --- | 89.2108 | 1874.587 | 94.2387 | SDS-TOX | mg Cl- /L | 116.5 | --- | 1477.2692 | --- | 88.3616 | 1459.5087 | 92.0179 | SDS-TOXb, ug Cl- /L | 243.5356 | 314.9874 | 264.8526 | 282.0979 | SDS-TOXb, ug Cl- /L | NA | NA | 112.2393 | 133.0598
|  | Standard testing recovery (%) | 15 | [9 empty] | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | SDS-MCAA* | mg/L | BMRL | 5.7 | 5.7 | #VALUE! | [70 empty] | SDS-CHCl3 | mg/L | 15 | 15.5 | 15.25 | 3.2787 | --- | 810.0417 | --- | 92.5971 | 800.7487 | 98.0955 | SDS-CHCl3 | mg/L | 36.5 | --- | 1731.5 | --- | 82.2816 | 1712.8777 | 97.8691 | SDS-CHCl3 | mg/L | 11 | --- | 401 | --- | 94.6602 | 396.7609 | 97.2275 | SDS-CHCl3 | mg/L | 10.7 | --- | 311.1615 | --- | 94.8058 | 307.24 | 96.5174 | SDS-CDb, mg/L | 5.1956 | 5.5771 | 4.7976 | 4.8895 | SDS-CDb, mg/L | NA | NA | 3.321 | 3.4319
|  | Standard testing pH | 6.5-7 | [14 empty] | SDS-DCAA* | mg/L | 52 | 68 | 60 | 26.6667 | [70 empty] | SDS-BDCM | mg/L | 15.9 | 15.8 | 15.85 | 0.63091 | --- | 99.6 | --- | 55.911 | 98.6208 | 83.9283 | SDS-BDCM | mg/L | 21.8 | --- | 163.3 | --- | 39.3602 | 161.7454 | 86.522 | SDS-BDCM | mg/L | 12.8 | --- | 59.1 | --- | 64.395 | 58.5967 | 78.1558 | SDS-BDCM | mg/L | 11.6 | --- | 49.0615 | --- | 67.733 | 48.5726 | 76.1182 | TOCb, mg/L | 2.504 | 3.1027 | 2.5237 | 2.6892 | TOCb, mg/L | NA | NA | 1.0412 | 1.2409
|  | Acceptable range of operating pressures | <400 psi | [14 empty] | SDS-TCAA* | mg/L | 116 | 116 | 116 | 0 | [70 empty] | SDS-DBCM | mg/L | 11.2 | 11.1 | 11.15 | 0.89686 | --- | -19.8917 | --- | -201.3514 | -19.5287 | 157.0954 | SDS-DBCM | mg/L | 9.4 | --- | -47.6 | --- | -154.0541 | -46.9738 | 120.0112 | SDS-DBCM | mg/L | 10 | --- | -2.6 | --- | -170.2703 | -2.463 | 506.0018 | SDS-DBCM | mg/L | 8.7 | --- | 1.0077 | --- | -135.1351 | 1.1081 | -685.134 | UV254 b, cm-1 | 0.094592 | 0.10822 | 0.097159 | 0.10031 | UV254 b, cm-1 | NA | NA | 0.038626 | 0.042431
|  | Acceptable range of operating pH values | 3-10 | [14 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [70 empty] | SDS-CHBr3 | mg/L | 1.2 | 1.2 | 1.2 | 0 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 1.2 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 1 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | Bromideb, ug/L | 124.3722 | 113.8969 | 96.9359 | 96.6242 | Bromideb, ug/L | NA | NA | 77.5388 | 77.1624
|  | Typical pressure drop across a single element (psi) | 3-5 | [14 empty] | SDS-DBAA* | mg/L | BMRL | 1.3 | 1.3 | #VALUE! | [70 empty] | SDS-THM4 | mg/L | 43.3 | 43.6 | 43.45 | 0.69045 | --- | 885.95 | --- | 82.3122 | 876.0992 | 95.0405 | SDS-THM4 | mg/L | 67.7 | --- | 1847.2 | --- | 72.4405 | 1827.6493 | 96.2958 | SDS-THM4 | mg/L | 35 | --- | 456.3 | --- | 85.7521 | 451.7207 | 92.2518 | SDS-THM4 | mg/L | 32 | --- | 360.6923 | --- | 86.9733 | 356.4023 | 91.0214 | Alkb, mg/L CaCO3 | 6.7044 | 6.0262 | #VALUE! | 8.4713 | Alkb, mg/L CaCO3 | NA | NA | #VALUE! | 6.2471
|  | Maximum permissible SDI | 5 | [14 empty] | SDS-BCAA* | mg/L | 8.1 | 10.1 | 9.1 | 21.978 | [70 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | T-Hdb, mg/L CaCO3 | 157.3547 | 199.8095 | 137.2872 | 132.1219 | T-Hdb, mg/L CaCO3 | NA | NA | 117.5483 | 111.3122
|  | Maximum permissible turbidity (ntu) | 1 | [14 empty] | SDS-TBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [70 empty] | SDS-DCAA* | mg/L | 7.3 | 7.5 | 7.4 | 2.7027 | --- | 226.5667 | --- | 87.6667 | 224.0041 | 96.6965 | SDS-DCAA* | mg/L | 15.2 | --- | 463.2 | --- | 74.6667 | 458.278 | 96.6832 | SDS-DCAA* | mg/L | 4.9 | --- | 115.1 | --- | 91.8333 | 113.9022 | 95.6981 | SDS-DCAA* | mg/L | 5.2 | --- | 89.5077 | --- | 91.3333 | 88.4073 | 94.1181 | Ca-Hdb, mg/L CaCO3 | 148.7899 | 189.7612 | 129.409 | 125.8114 | Ca-Hdb, mg/L CaCO3 | NA | NA | 110.5246 | 106.1811
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | <0.1 mg/L | [14 empty] | SDS-CDBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [70 empty] | SDS-TCAA* | mg/L | 9.5 | 10.2 | 9.85 | 7.1066 | --- | 452.1417 | --- | 91.5086 | 446.9703 | 97.7963 | SDS-TCAA* | mg/L | 23 | --- | 953 | --- | 80.1724 | 942.7824 | 97.5604 | SDS-TCAA* | mg/L | 5.6 | --- | 226.4 | --- | 95.1724 | 224 | 97.5 | SDS-TCAA* | mg/L | 6.5 | --- | 174.9615 | --- | 94.3966 | 172.7628 | 96.2376
|  | 1: All of the information requested in this field may not be available, but values for all Design | [15 empty] | SDS-DCBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [70 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  | Parameters must be entered in cells E14:E23, since these parameters are used in calculations. | [15 empty] | SDS-HAA5 | mg/L | 168 | 191 | 179.5 | 12.8134 | [70 empty] | SDS-DBAA* | mg/L | 2.7 | 2.7 | 2.7 | 0 | --- | -3.1333 | --- | -107.6923 | -3.0651 | 188.0877 | SDS-DBAA* | mg/L | 2.3 | --- | -7.7 | --- | -76.9231 | -7.5901 | 130.3025 | SDS-DBAA* | mg/L | 2.7 | --- | -0.1 | --- | -107.6923 | -0.069565 | 3981.25 | SDS-DBAA* | mg/L | 2.3 | --- | 0.76154 | --- | -76.9231 | 0.78162 | -194.2613 | Blended Water Quality if HAA5 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if HAA5 Controls the Blend Ratio
[18 empty] | SDS-HAA6 | mg/L | 176.1 | 201.1 | 188.6 | 13.2556 | [70 empty] | SDS-BCAA* | mg/L | 5.5 | 5.5 | 5.5 | 0 | --- | 20.5 | --- | 39.5604 | 20.3246 | 72.9392 | SDS-BCAA* | mg/L | 7.5 | --- | 23.5 | --- | 17.5824 | 23.3242 | 67.8446 | SDS-BCAA* | mg/L | 4.5 | --- | 13.7 | --- | 50.5495 | 13.6 | 66.9118 | SDS-BCAA* | mg/L | 4.1 | --- | 11.7923 | --- | 54.9451 | 11.6919 | 64.933 | Qp/QT (HAA5), % | 78.6587 | 90.2878 | 75.466 | 75.8308 | Qp/QT (HAA5), % | 95.5813 | 109.7122 | 91.7017 | 92.145
[18 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [75 empty] | SDS-TBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-THM4b, ug/L | 86.6021 | 84.9829 | 86.6808 | 83.6375 | SDS-THM4b, ug/L | 52.3846 | NA | 52.4803 | 48.7822
[18 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, | [75 empty] | SDS-CDBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-HAA5b, ug/L | 54 | 54 | 54 | 54 | SDS-HAA5b, ug/L | 27 | NA | 27 | 27
[18 empty] | should be reported if measured. | [75 empty] | SDS-DCBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TOXb, ug Cl- /L | 307.23 | 366.277 | 327.0884 | 330.2764 | SDS-TOXb, ug Cl- /L | 157.9727 | NA | 182.1034 | 185.9773
[94 empty] | SDS-HAA5 | mg/L | 19.5 | 20.4 | 19.95 | 4.5113 | --- | 684.7417 | --- | 88.8858 | 676.9687 | 97.053 | SDS-HAA5 | mg/L | 40.5 | --- | 1430.5 | --- | 77.4373 | 1415.2286 | 97.1383 | SDS-HAA5 | mg/L | 13.2 | --- | 345.8 | --- | 92.6462 | 342.1848 | 96.1424 | SDS-HAA5 | mg/L | 14 | --- | 268.6154 | --- | 92.2006 | 265.2922 | 94.7228 | SDS-CDb, mg/L | 5.761 | 6.0513 | 5.3997 | 5.3606 | SDS-CDb, mg/L | 4.436 | NA | 3.997 | 3.9495
[94 empty] | SDS-HAA6 | mg/L | 25 | 25.9 | 25.45 | 3.5363 | --- | 705.2417 | --- | 86.5058 | 697.2933 | 96.3502 | SDS-HAA6 | mg/L | 48 | --- | 1454 | --- | 74.5493 | 1438.5528 | 96.6633 | SDS-HAA6 | mg/L | 17.7 | --- | 359.5 | --- | 90.6151 | 355.7848 | 95.0251 | SDS-HAA6 | mg/L | 18.1 | --- | 280.4077 | --- | 90.403 | 276.9841 | 93.4653 | TOCb, mg/L | 3.107 | 3.5941 | 3.1283 | 3.1573 | TOCb, mg/L | 1.694 | NA | 1.7199 | 1.7551
[94 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | UV254 b, cm-1 | 0.11855 | 0.1285 | 0.12103 | 0.11902 | UV254 b, cm-1 | 0.062409 | NA | 0.065422 | 0.062982
[94 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | Bromideb, ug/L | 129.9328 | 119.6241 | 104.8461 | 102.9154 | Bromideb, ug/L | 116.9024 | NA | 86.4185 | 84.0725
[133 empty] | Alkb, mg/L CaCO3 | 7.7552 | 7.0112 | #VALUE! | 9.1903 | Alkb, mg/L CaCO3 | 5.2929 | NA | #VALUE! | 7.0369
[133 empty] | T-Hdb, mg/L CaCO3 | 163.6736 | 202.2536 | 145.3367 | 138.8489 | T-Hdb, mg/L CaCO3 | 148.8663 | NA | 126.5845 | 118.7009
[133 empty] | Ca-Hdb, mg/L CaCO3 | 154.82 | 192.0594 | 137.11 | 132.1571 | Ca-Hdb, mg/L CaCO3 | 140.6896 | NA | 119.1696 | 113.1511
[133 empty] | Notes: |  |  |  |  | Notes:
[133 empty] | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to |  |  |  |  | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to
[133 empty] | determine the percentage of total flow that must be treated by the membrane process to meet the |  |  |  |  | determine the percentage of total flow that must be treated by the membrane process to meet the
[133 empty] | Stage 1 DBP MCLs. |  |  |  |  | Stage 2 DBP MCLs.
[133 empty] | A 10% factor of safety has been applied all the MCLs. i.e., 72 / 54 mg/L for THM4 and HAA5. |  |  |  |  | A 10% factor of safety has been applied all the MCLs. i.e., 36 / 27 mg/L for THM4 and HAA5.
[133 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for |  |  |  |  | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for
[133 empty] | both parameters and the maximum (Qp/QT) ratio controls the design. |  |  |  |  | both parameters and the maximum (Qp/QT) ratio controls the design.
[133 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. |  |  |  |  | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[133 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. |  |  |  |  | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[133 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. |  |  |  |  | The subscript "b" refers to the blended water quality for a given blend ratio.
[133 empty] | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL. |  |  |  |  | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL.
[133 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. |  |  |  |  | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
Note on X24: TSC_ADM: Reported SDS temperature is a measured value - the consultant used an incubator for SDS testing.
Note on Z20: C. Hill (11/16/99): Bromide feed concentrations verified by the utility.
Note on AA20: C. Hill (11/16/99): Bromide feed concentrations verified by the utility.
Note on CY16: C. Hill (11/16/99): Utility verfied the reported permeate and concentrate values for this parameter.
Note on CY21: C. Hill (11/16/99): Utility verfied the reported permeate and concentrate values for this parameter.
Note on CY29: TSC_ADM: Reported SDS temperature is a measured value - the consultant used an incubator for SDS testing.
Note on DL16: C. Hill (11/16/99): Utility verfied the reported permeate and concentrate values for this parameter.
Note on DL21: C. Hill (11/16/99): Utility verfied the reported permeate and concentrate values for this parameter.
Note on DL29: TSC_ADM: Reported SDS temperature is a measured value - the consultant used an incubator for SDS testing.
Note on DV16: C. Hill (11/16/99): Utility verfied the reported permeate and concentrate values for this parameter.
Note on DV21: C. Hill (11/16/99): Utility verfied the reported permeate and concentrate values for this parameter.
Note on DV29: TSC_ADM: Reported SDS temperature is a measured value - the consultant used an incubator for SDS testing.
Note on EF16: C. Hill (11/16/99): Utility verfied the reported permeate and concentrate values for this parameter.
Note on EF21: C. Hill (11/16/99): Utility verfied the reported permeate and concentrate values for this parameter.
Note on EF29: TSC_ADM: Reported SDS temperature is a measured value - the consultant used an incubator for SDS testing.
Print All Fields

## DCSS2. 4th Quarter
FIELD-SET 4: Membrane D, Run 2 (FILE: Delray2.xls)
Field 4-1: PWS And Treatment Plant Data |  | Field 4-2: Manufacturer Reported Membrane Characteristics1 |  | Field 4-3: RBSMT Design Parameters | [8 empty] | Field 4-4: Foulants And Fouling Indices1 |  | Field 4-5: Pretreatment Used Prior To Membranes1 |  |  | Field 4-6: Feed Water Quality After Pretreatment | [5 empty] | Field 4-7: Membrane Setting Data | [20 empty] | Field 4-8: Membrane Performance Data During Operation With The Test Water | [16 empty] | Field 4-8: Membrane Performance Data During Operation With The Test Water (continued) | [19 empty] | Field 4-8: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 4-9: Permeate And Concentrate Water Quality For Run 1 | [11 empty] | Field 4-10: Permeate And Concentrate Water Quality For Run 2 | [8 empty] | Field 4-11: Permeate And Concentrate Water Quality For Run 3 | [8 empty] | Field 4-12: Permeate And Concentrate Water Quality For Run 4 | [8 empty] | Field 4-13: Blending Calculations For Stage 1 D-DBP MCLs |  |  |  |  | Field 4-14: Blending Calculations For Proposed Stage 2 D-DBP MCLs |  |  |  |  | Field 4-15: Membrane Cost Parameters
|  | General Information |  | Input Design Parameters | [8 empty] | Parameters Evaluated Prior to Pretreatment | [80 empty] | Operating Parameters During Sample Collection | [11 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Feed and Permeate Water Quality Parameters |  |  |  |  | Feed and Permeate Water Quality Parameters |  |  |  |  | General Cost Parameters
PWS Name | Delray Beach Water Department | Membrane manufacturer | Fluid Systems | [5 empty] | Active membrane area in bench-scale cell, Acell (ft2) | 0.16667 |  |  | Alkalinity (mg/L as CaCO3) | 243 | Process | Description | Scale | Parameter | Units | CF-1 | CF-2 | Average | RPD |  |  |  | Average TDS rejection (decimal fraction) | 0.7 | [5 empty] | TDS concentration of setting solution (mg/L) | 50 | [12 empty] | Average bulk TDS rejection (decimal fraction) | 0.85329 | [45 empty] | Recovery during sample collection (decimal) | 0.69 | [10 empty] | Recovery during sample collection (decimal) | 0.89 | [7 empty] | Recovery during sample collection (decimal) | 0.5 | [7 empty] | Recovery during sample collection (decimal) | 0.32 | [8 empty] | RUN ID # |  |  |  |  | RUN ID # |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | FL4500351 | Membrane trade name | TFC 8921S-400 | [5 empty] | Active width of membrane in the bench-scale cell, wcell (ft) | 0.33333 |  |  | Calcium Hardness (mg/L as CaCO3) | 295 | Aeration | Fine Bubble diffuwer in barrel overnight | Bench | Sampling date | MM/DD/YY | 1999-05-11 | 1999-05-14 | --- | --- | [71 empty] | Feed flow rate during sample collection (mL/min) | 9.1 | [10 empty] | Feed flow rate during sample collection (mL/min) | 7.2 | [7 empty] | Feed flow rate during sample collection (mL/min) | 13 | [7 empty] | Feed flow rate during sample collection (mL/min) | 21.8 | [6 empty] | Parameter | 1 | 2 | 3 | 4 | Parameter | 1 | 2 | 3 | 4 | Capital Recovery Interest Rate (%) | 5.75
Water Industry Data Base Number (optional) | NA | Molecular weight cutoff (Daltons) | 200 | [5 empty] | Average yearly temperature of feed water, TavgoC (oC) | 22 |  |  | LSI |  | Acidification | Hydrochloric acid to pH 6.5 | Bench | Sampling time | hh:mm | NR | NR | --- | --- | Date | Time | Setting time | Influent | PI | PC | QI | Qp | QW | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) | Date | Time | Operation time | Influent | PI | PC | QI | Qp | QW | Cleaning Event | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1) | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Influent flow rate during sample collection (mL/min) | 300 | [10 empty] | Influent flow rate during sample collection (mL/min) | 300 | [7 empty] | Influent flow rate during sample collection (mL/min) | 300 | [7 empty] | Influent flow rate during sample collection (mL/min) | 300 | [6 empty] | SDS-THM4F, ug/L | 234.3 | 234.3 | 234.3 | 234.3 | SDS-THM4F, ug/L | 234.3 | 234.3 | 234.3 | 234.3 | Capital Recovery Period (years) | 25
|  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide | [5 empty] | Approximate feed water TDS, TDSF (mg/L) | 545 |  |  | Dissolved iron (mg/L) |  | Antiscalant addition | King Lee PreTreat 0100, 3 ppm by volume | Bench | Operation time | hh.hh | 61.9 | 133 | --- | --- | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | Indicate with "X" | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) | [39 empty] | SDS-THM4p, ug/L | 23.55 | 33.7 | 12.4 | 8.4 | SDS-THM4p, ug/L | 23.55 | 33.7 | 12.4 | 8.4 | Overhead & Profit Factor (% of construction costs) | 15
Official ICR Contact Person |  | Membrane construction (e.g., thin-film composite) | Thin-Film Composite | [5 empty] | Manufacturer reported TDS rejection, RejTDS (decimal fraction) | 0.7 |  |  | Total iron (mg/L) |  | Membrane Filtration | 0.1 micron Pall Microza cartridge | Bench | pH | --- | 6.19 | 6.14 | 6.165 | 0.81103 | 1999-05-08 | 11:43 | 0 | [18 empty] | 1999-05-10 | 10:45 | 0 | [46 empty] | Permeate and Concentrate Water Quality | [11 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | SDS-HAA5F, ug/L | 182.4 | 182.4 | 182.4 | 182.4 | SDS-HAA5F, ug/L | 182.4 | 182.4 | 182.4 | 182.4 | Special Sitework Factor (% of construction costs) | 5
Mailing Address |  | Membrane hydrophobicity | Hydrophilic | [5 empty] | Temperature normalized MTCW (gfd/psi) | 0.24251 |  |  | Dissolved aluminum (mg/L) |  |  |  |  | Temperature | oC | NR | NR | #DIV/0! | #VALUE! | 1999-05-08 | 12:17 | 0.5 | 22.7 | 95.6 | 95.3 | 299 | 6.8 | 2.7 | 9.5 | 0.24367 | 0.71579 | 30.4737 | 15.5206 | 15.2028 | 100.9071 | 29.7869 | 99.2896 | 0.70311 | 94.7469 | 0.16046 | 1999-05-10 | 11:39 | 0.9 | 23.9 | 95.5 | 94 | 300 | 6.3 | 2.6 |  | 8.9 | 0.24449 | 0.70787 | 32.7079 | 14.3794 | 13.5941 | 1193.8018 | 171.9945 | 1172.3438 | 10.1108 | 84.6392 | 0.16061 | [27 empty] | Parameter | Units | Cp-1 | Cp-1 (dup) | Average | RPD | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | SDS-HAA5p, ug/L | 8.8 | 15.7 | 4 | 2.5 | SDS-HAA5p, ug/L | 8.8 | 15.7 | 4 | 2.5 | Construction Contingencies (% of construction costs) | 15
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Negative | [9 empty] | Total aluminum (mg/L) |  |  |  |  | Alkalinity | mg/L as CaCO3 | 25.5 | 24.7 | 25.1 | 3.1873 | 1999-05-08 | 16:30 | 4.8 | 23.6 |  |  | 300 | 6.8 | 2.8 | 9.6 | 0.24449 | 0.70833 | 30.25 | 15.5206 | 14.8037 | 99.8459 | 29.4752 | 98.2508 | 0.69573 | -0.69573 |  | 1999-05-10 | 14:17 | 3.5 | 24 | 106.9 | 106.5 | 300 | 6.6 | 2.9 |  | 9.5 | 0.24449 | 0.69474 | 30.5789 | 15.0641 | 14.1994 | 1160.959 | 167.1165 | 1139.0945 | 9.8291 | 96.8709 | 0.14658 | 6.2 |  |  | 211.2 |  |  | 1060.631 |  | 55.1116 | 1051.2873 | 79.9103 | 0.043 |  |  | 1.0765 |  | 88.0056 | 1.0652 | 95.9631 | [8 empty] | Sampling date | MM/DD/YY | 1999-05-11 | 1999-05-11 | --- | --- | 1999-05-11 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-05-12 | 1999-05-12 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-05-13 | 1999-05-13 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-05-14 | 1999-05-14 | --- | --- | --- | --- | --- | SDS-TOXF, ug Cl- /L | 1059 | 1059 | 1059 | 1059 | SDS-TOXF, ug Cl- /L | 1059 | 1059 | 1059 | 1059 | Engineering Fee Factor (% of construction costs) | 10
Phone Number |  |  |  | Experimental Design1,2 | [8 empty] | Fluoride (mg/L) |  |  |  |  | Total dissolved solids | mg/L | 454.5 | 486.5 | 470.5 | 6.8013 | 1999-05-09 |  | 22.3 | 24 | 97.4 | 97.1 | 300 | 7.2 | 2.6 | 9.8 | 0.24449 | 0.73469 | 29.6122 | 16.4336 | 15.4903 | 103.7378 | 30.5947 | 101.9823 | 0.72265 | 96.5273 | 0.16048 | 1999-05-10 | 15:49 | 5.1 | 24.3 | 106.5 | 105.9 | 300 | 6.4 | 2.8 |  | 9.2 | 0.24449 | 0.69565 | 31.6087 | 14.6077 | 13.6476 | 1163.04 | 167.5137 | 1141.8022 | 9.8491 | 96.3509 | 0.14164 | 5.99 |  |  | 165.55 |  |  | 1167.5286 |  | 64.814 | 1156.8408 | 85.6895 | 0.039 |  |  | 1.0888 |  | 89.1213 | 1.0776 | 96.3808 | [8 empty] | Sampling time | hh:mm | NR | NR | --- | --- | NR | --- | --- | --- | --- | --- | Sampling time | hh:mm | NR | NR | --- | --- | --- | --- | --- | Sampling time | hh:mm | NR | NR | --- | --- | --- | --- | --- | Sampling time | hh:mm | NR | NR | --- | --- | --- | --- | --- | SDS-TOXp, ug Cl- /L | 74.35 | 139.5 | 52.75 | 27.9 | SDS-TOXp, ug Cl- /L | 74.35 | 139.5 | 52.75 | 27.9 | 1998 ENR Construction Cost Index (CCI base year 1913) | 5875
FAX Number |  | Design Parameters |  | ID# | Recovery | FW-design | Dp | PI | QI-cell | Qp | QF | QW | Phosphate (mg/L) |  |  |  |  | Total hardness | mg/L as CaCO3 | 238 | 251 | 244.5 | 5.317 | 1999-05-09 | 13:20 | 25.6 | 24 | 97 | 96.7 | 300 | 7.2 | 2.6 | 9.8 | 0.24449 | 0.73469 | 29.6122 | 16.4336 | 15.4903 | 103.7378 | 30.5947 | 101.9823 | 0.72265 | 96.1273 | 0.16114 | 1999-05-10 | 17:57 | 7.2 | 24.4 | 105.8 | 105 | 300 | 6.4 | 2.7 |  | 9.1 | 0.24449 | 0.7033 | 31.967 | 14.6077 | 13.6073 | 1182.1615 | 170.2678 | 1160.5744 | 10.011 | 95.389 | 0.14265 | 6.12 | 6.26 | 7.53 | 167.75 | 495.166 | 1018.08 | 1188.1296 | -16.703 | 64.3464 | 1177.2456 | 85.7506 | 0.034 | 0.365 | 1.052 | 1.1277 | -7.1944 | 90.516 | 1.116 | 96.9535 | [8 empty] | Operation time | hh.hh | 61.9 | 61.9 | --- | --- | 61.9 | --- | --- | --- | --- | --- | Operation time | hh.hh | 85.6 | 85.6 | --- | --- | --- | --- | --- | Operation time | hh.hh | 109.1 | 109.1 | --- | --- | --- | --- | --- | Cumulative time | hr | 133 | 133 | --- | --- | --- | --- | --- | SDS-CDF, mg/L | 11.97 | 11.97 | 11.97 | 11.97 | SDS-CDF, mg/L | 11.97 | 11.97 | 11.97 | 11.97 | 1998 Producers Price Index (PPI base year 1967 = 100) | 369
E-Mail Address (optional) |  | Design flux, FW (gfd) | 15 |  | (decimal) | (gfd) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | Sulfate (mg/L) | 26.5 |  |  |  | Calcium hardness | mg/L as CaCO3 | 226 | 238 | 232 | 5.1724 | 1999-05-09 | 18:51 | 31.2 | 23.9 | 97.6 | 97.1 | 300 | 7.2 | 2.6 | 9.8 | 0.24449 | 0.73469 | 29.6122 | 16.4336 | 15.5361 | 103.7378 | 30.5947 | 101.9823 | 0.72265 | 96.6273 | 0.16078 | 1999-05-11 | 11:25 | 24.7 | 24.5 | 118.6 | 118.4 | 299 | 6.6 | 0.7 |  | 7.3 | 0.24367 | 0.90411 | 39.9589 | 15.0641 | 13.9911 | 2081.6205 | 299.6236 | 2042.2855 | 17.6233 | 100.8767 | 0.13869 | 5.79 |  |  | 124.271 |  |  | 3734.9449 |  | 73.5875 | 3695.0946 | 96.6369 | 0.038 |  |  | 3.3804 |  | 89.4003 | 3.3435 | 98.8635 | [8 empty] | pH | --- | 6.15 | 6.16 | 6.155 | 0.16247 | 6.77 | --- | --- | --- | --- | --- | pH | --- | 6.01 | 7.61 | --- | --- | --- | --- | --- | pH | --- | 5.91 | 6.8 | --- | --- | --- | --- | --- | pH | --- | 0.066667 | 6.48 | --- | --- | --- | --- | --- | SDS-CDp, mg/L | 2.79 | 4.13 | 1.86 | 1.42 | SDS-CDp, mg/L | 2.79 | 4.13 | 1.86 | 1.42 | Labor Rate + Fringe ($/work-hour) | 19.89
|  | Net driving pressure at the design flux, NDP (psi) | 56.5 | 1 | 0.7 | 15 | 14.3517 | 76.2041 | 299.4788 | 6.5712 | 9.3874 | 2.8162 | Calcium (mg/L) |  |  |  |  | Turbidity | ntu | 0.05 | 0.04 | 0.045 | 22.2222 | [21 empty] | 1999-05-11 | 15:21 | 28.6 | 24.9 | 122.7 | 122.5 | 299 | 6.7 | 0.8 |  | 7.5 | 0.24367 | 0.89333 | 38.8667 | 15.2924 | 14.0361 | 2000.3118 | 287.8359 | 1961.9386 | 16.9329 | 105.6671 | 0.13283 | 6 |  |  | 141.158 |  |  | 3228.7393 |  | 69.9983 | 3194.1459 | 95.5807 | 0.045 |  |  | 2.9841 |  | 87.4477 | 2.9511 | 98.4752 | [8 empty] | Temperature | oC | NR | NR | #DIV/0! | #VALUE! | NR | --- | --- | --- | --- | --- | Temperature | oC | NR | NR | --- | --- | --- | --- | --- | Temperature | oC | NR | NR | --- | --- | --- | --- | --- | Temperature | oC | NR | NR | --- | --- | --- | --- | --- | TOCF, mg/L | 11.05 | 11.05 | 11.05 | 11.05 | TOCF, mg/L | 11.05 | 11.05 | 11.05 | 11.05 | Labor Overhead Factor (% of labor) | 6
Technical ICR Contact Person |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.265 | 2 | 0.9 | 15 | 39.785 | 101.6375 | 299.4788 | 6.5712 | 7.3013 | 0.73013 | Barium (mg/L) | 0.018 |  |  |  | Ammonia | mg NH3-N / L | 0.59 | 0.57 | 0.58 | 3.4483 | [21 empty] | 1999-05-11 | 17:13 | 30.5 | 25.1 | 122.3 | 122.2 | 299 | 6.5 | 0.7 |  | 7.2 | 0.24367 | 0.90278 | 40.5278 | 14.8359 | 13.5369 | 2070.8264 | 298.1572 | 2032.2901 | 17.534 | 104.716 | 0.12927 | 5.97 | 6.36 | 7.55 | 142.024 | 499.912 | 3527.16 | 3520.6343 | 0.18501 | 69.8142 | 3483.9103 | 95.9234 | 0.044 | 0.378 | 2.506 | 3.2789 | -30.8403 | 87.7266 | 3.2437 | 98.6435 | [8 empty] | Alkalinity | mg/L as CaCO3 | 8.1 | 8.4 | 8.25 | 3.6364 | 62 | 62.6048 | -0.97555 | 67.1315 | 62.036 | 86.7013 | Alkalinity | mg/L as CaCO3 | 8 | 170 | 163.4545 | 3.8503 | 68.1275 | 161.7943 | 95.0554 | Alkalinity | mg/L as CaCO3 | 5.5 | 46.7 | 44.7 | 4.2827 | 78.0876 | 44.2753 | 87.5777 | Alkalinity | mg/L as CaCO3 | 4.8 | 36 | 34.6529 | 3.7418 | 80.8765 | 34.3059 | 86.0082 | TOCp, mg/L | 0.81 | BMRL | 0.41 | BMRL | TOCp, mg/L | 0.81 | BMRL | 0.41 | BMRL | Electric Rate ($/kW-h) | 0.05
Mailing Address |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | 3 | 0.5 | 15 | 9.265 | 71.1175 | 299.4788 | 6.5712 | 13.1424 | 6.5712 | Strontium (mg/L) |  |  |  |  | Total organic carbon | mg/L | 10.6 | 11.5 | 11.05 | 8.1448 | [21 empty] | 1999-05-12 | 10:55 | 48.1 | 24.4 | 132.6 | 132.4 | 299 | 6.5 | 6.6 |  | 13.1 | 0.24367 | 0.49618 | 21.8244 | 14.8359 | 13.8199 | 817.8951 | 117.7604 | 802.6748 | 6.9252 | 125.5748 | 0.11005 | 5.92 |  |  | 235.84 |  |  | 701.6045 |  | 49.8746 | 696.5419 | 66.1413 | 0.046 |  |  | 0.66627 |  | 87.1688 | 0.65952 | 93.0253 | [8 empty] | Total dissolved solids | mg/L | 161.5 | 174 | 167.75 | 7.4516 | 1017.5 | 1144.3629 | -12.4681 | 64.3464 | 1134.1426 | 85.2091 | Total dissolved solids | mg/L | 142 | 3526 | 3128.3636 | 11.2773 | 69.8193 | 3096.4693 | 95.4141 | Total dissolved solids | mg/L | 121.5 | 909 | 819.5 | 9.846 | 74.1764 | 811.9383 | 85.0358 | Total dissolved solids | mg/L | 95 | 644.5 | 647.2059 | -0.41984 | 79.8087 | 640.7856 | 85.1744 | UV254 F, cm-1 | 0.3585 | 0.3585 | 0.3585 | 0.3585 | UV254 F, cm-1 | 0.3585 | 0.3585 | 0.3585 | 0.3585 | Fuel Oil Rate ($/gal) | NA
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 400 | 4 | 0.3 | 15 | 7.085 | 68.9375 | 299.4788 | 6.5712 | 21.9039 | 15.3328 | Reactive silica (mg/L as SiO2) | 32.8 |  |  |  | UV254 | cm-1 | 0.35 | 0.367 | 0.3585 | 4.742 | [21 empty] | 1999-05-12 | 14:14 | 48.5 | 24.9 | 116.8 | 116.4 | 299 | 6.5 | 6.5 |  | 13 | 0.24367 | 0.5 | 22 | 14.8359 | 13.6171 | 822.567 | 118.433 | 807.2597 | 6.9648 | 109.6352 | 0.1242 | 5.72 |  |  | 122.32 |  |  | 818.68 |  | 74.0021 | 811.1109 | 84.9194 | 0.018 |  |  | 0.699 |  | 94.9791 | 0.6916 | 97.3973 | [8 empty] | Total hardness | mg/L as CaCO3 | 71.8 | 72.8 | 72.3 | 1.3831 | 609 | 627.7839 | -3.0844 | 70.4294 | 621.9707 | 88.3757 | Total hardness | mg/L as CaCO3 | 45.9 | 1690 | 1851.3545 | -9.5476 | 81.227 | 1832.0723 | 97.4946 | Total hardness | mg/L as CaCO3 | 41.5 | 441 | 447.5 | -1.4739 | 83.0266 | 443.1017 | 90.6342 | Total hardness | mg/L as CaCO3 | 29.2 | 329 | 345.8176 | -5.1117 | 88.0573 | 342.1364 | 91.4654 | UV254 p, cm-1 | 0.02825 | 0.041 | 0.0155 | 0.011 | UV254 p, cm-1 | 0.02825 | 0.041 | 0.0155 | 0.011 | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Purchase price for an equivalent 8" x 40 " element ($) | 846 | 1: For experimental matrix see Table 4-2 in Part 3 of the ICR Treatment Studies Manual. | [8 empty] | Turbidity (ntu) |  |  |  |  | SUVA | L/(mg*m) | 3.3019 | 3.1913 | 3.2466 | 3.4061 | [21 empty] | 1999-05-12 | 16:25 | 53.7 | 24.8 | 116.7 | 116.6 | 299 | 6.5 | 6.5 |  | 13 | 0.24367 | 0.5 | 22 | 14.8359 | 13.6575 | 822.567 | 118.433 | 807.2597 | 6.9648 | 109.6852 | 0.12452 | 5.61 | 6.29 | 6.46 | 121.44 | 497.539 | 909.36 | 819.56 | 9.8751 | 74.1892 | 811.9717 | 85.0438 | 0.016 | 0.401 | 0.748 | 0.701 | 6.2834 | 95.537 | 0.69355 | 97.693 | [8 empty] | Calcium hardness | mg/L as CaCO3 | 68.4 | 69.4 | 68.9 | 1.4514 | 579 | 595.029 | -2.7684 | 70.3017 | 589.5231 | 88.3126 | Calcium hardness | mg/L as CaCO3 | 45.9 | 1600 | 1737.7182 | -8.6074 | 80.2155 | 1719.6496 | 97.3309 | Calcium hardness | mg/L as CaCO3 | 39.4 | 419 | 424.6 | -1.3365 | 83.0172 | 420.427 | 90.6286 | Calcium hardness | mg/L as CaCO3 | 29.2 | 312 | 327.4353 | -4.9472 | 87.4138 | 323.9678 | 90.9868 | BromideF, ug/L | 130 | 130 | 130 | 130 | BromideF, ug/L | 130 | 130 | 130 | 130 | Current Process Water Rate ($/1000 gal) | 0.41
FAX Number |  | Maximum flow rate to the 8" x 40" element, QI, max (gpm) | 70 | 2: Flow rates and pressures may need to be adjusted in order to obtain the desired operating conditions. | [8 empty] | SDI |  |  |  |  | Bromide | mg/L | 138 | 122 | 130 | 12.3077 | [21 empty] | 1999-05-13 | 11:35 | 72.5 | 22.9 | 121.9 | 121.7 | 299 | 6.5 | 15.4 |  | 21.9 | 0.24367 | 0.2968 | 12.653 | 14.8359 | 14.4464 | 630.7562 | 90.8161 | 619.0183 | 5.3407 | 116.4593 | 0.12405 | [27 empty] | Turbidity | ntu | BMRL | BMRL | #DIV/0! | #VALUE! | 0.18 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu | BMRL | 1.38 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | 0.11 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | 0.15 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Bromidep, ug/L | 48.5 | 43 | 27 | 20 | Bromidep, ug/L | 48.5 | 43 | 27 | 20 | Modifications to Existing Plant (% of construction costs) | 10
E-Mail Address (optional) |  | Minimum flow rate to the 8" x 40" element, QI, min (gpm) | 15 | [9 empty] | MFI |  |  |  |  | SDS-Cl2 dose | mg/L | 12.6 | 12.7 | 12.65 | 0.79051 | [21 empty] | 1999-05-13 | 14:24 | 75.3 | 23.1 | 120.9 | 120.6 | 299 | 6.5 | 15.1 |  | 21.6 | 0.24367 | 0.30093 | 12.8426 | 14.8359 | 14.3613 | 633.7543 | 91.2478 | 621.9606 | 5.3661 | 115.3839 | 0.12447 | 5.6 |  |  | 132.396 |  |  | 616.0415 |  | 71.8606 | 610.7844 | 78.3236 | 0.015 |  |  | 0.50636 |  | 95.8159 | 0.50102 | 97.0061 | [8 empty] | Ammonia | mg NH3-N / L | 0.33 | 0.46 | 0.395 | 32.9114 | 0.99 | 0.99177 | -0.17921 | 31.8966 | 0.98553 | 59.92 | Ammonia | mg NH3-N / L | 0.6 | 0.63 | 0.41818 | 33.6219 | -3.4483 | 0.42012 | -42.8151 | Ammonia | mg NH3-N / L | 0.3 | 0.88 | 0.86 | 2.2727 | 48.2759 | 0.85393 | 64.8685 | Ammonia | mg NH3-N / L | 0.22 | 0.76 | 0.74941 | 1.3932 | 62.069 | 0.74326 | 70.4005 | AlkF, mg/L CaCO3 | 25.1 | 25.1 | 25.1 | 25.1 | AlkF, mg/L CaCO3 | 25.1 | 25.1 | 25.1 | 25.1
|  | Total width of all membrane envelopes in the 8" x 40" element, w (ft) | 63.2 | [9 empty] | MPFI |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | SDS-Free Cl2 residual | mg/L | 0.6 | 0.76 | 0.68 | 23.5294 | [21 empty] | 1999-05-13 | 17:16 | 78.2 | 23.3 | 119.2 | 119 | 299 | 6.4 | 15.4 |  | 21.8 | 0.24367 | 0.29358 | 12.7156 | 14.6077 | 14.057 | 628.4195 | 90.5062 | 616.9056 | 5.3216 | 113.7784 | 0.12355 | 5.59 | 6.12 | 6.19 | 94.996 | 511.777 | 644.76 | 626.5536 | 2.8237 | 79.8096 | 620.8647 | 84.6994 | 0.011 | 0.384 | 0.494 | 0.50292 | -1.8048 | 96.9317 | 0.49765 | 97.7896 | [8 empty] | Total organic carbon | mg/L | 0.87 | 0.75 | 0.81 | 14.8148 | 30 | 33.8423 | -12.8075 | 92.6697 | 33.4966 | 97.5818 | Total organic carbon | mg/L | BMRL | 101 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.41 | 19.7 | 21.69 | -10.1015 | 96.2896 | 21.4595 | 98.0894 | Total organic carbon | mg/L | BMRL | 14.2 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkp, mg/L CaCO3 | 8.25 | 8 | 5.5 | 4.8 | Alkp, mg/L CaCO3 | 8.25 | 8 | 5.5 | 4.8
Plant Name | Lime Softening Plant | Feed spacer thickness in the 8" x 40" element, T (ft) | 0.0021667 | [9 empty] | pH | 7.2 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | SDS-Cl2 demand | mg/L | 12 | 11.94 | 11.97 | 0.50125 | [21 empty] | 1999-05-14 | 9:47 | 94.7 | [6 empty] | X | [39 empty] | UV254 | cm-1 | 0.0285 | 0.028 | 0.02825 | 1.7699 | 0.9865 | 1.0936 | -10.8538 | 92.1199 | 1.0824 | 97.3901 | UV254 | cm-1 | 0.041 | 2.919 | 2.9274 | -0.28652 | 88.5635 | 2.8965 | 98.5845 | UV254 | cm-1 | 0.0155 | 0.696 | 0.7015 | -0.79023 | 95.6764 | 0.69407 | 97.7668 | UV254 | cm-1 | 0.011 | 0.5765 | 0.52203 | 9.4485 | 96.9317 | 0.51609 | 97.8686 | T-HdF, mg/L CaCO3 | 244.5 | 244.5 | 244.5 | 244.5 | T-HdF, mg/L CaCO3 | 244.5 | 244.5 | 244.5 | 244.5
Treatment Plant Category | SOFT | [11 empty] | Chloride (mg/L) | 59.9 | is to list the pretreatment processes used in this particular RBSMT run. |  |  | SDS-Chlorination temp. | oC | 20 | 20 | 20 | 0 | [21 empty] | 1999-05-14 | 20:24 | 96.9 | 23.4 | 95.5 | 95.3 | 299 | 6.5 | 15.4 |  | 21.9 | 0.24367 | 0.2968 | 12.653 | 14.8359 | 14.2345 | 630.7562 | 90.8161 | 619.0183 | 5.3407 | 90.0593 | 0.15806 | [27 empty] | SUVA | L/(mg*m) | 3.2759 | 3.7333 | 3.5046 | 13.0535 | 3.2883 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 2.8901 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 3.7805 | 3.533 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 4.0599 | --- | --- | --- | --- | --- | T-Hdp, mg/L CaCO3 | 72.3 | 45.9 | 41.5 | 29.2 | T-Hdp, mg/L CaCO3 | 72.3 | 45.9 | 41.5 | 29.2
Process Train Name | NA | Additional Information | [10 empty] | Mg (mg/L) | 44 |  |  |  | SDS-Chlorination pH | --- | 7.48 | 7.53 | 7.505 | 0.66622 | [21 empty] | 1999-05-14 | 22:12 | 98.7 | 23.1 | 96.8 | 96.5 | 299 | 6.5 | 15.3 |  | 21.8 | 0.24367 | 0.29817 | 12.7156 | 14.8359 | 14.3613 | 631.7432 | 90.9583 | 619.987 | 5.3491 | 91.3009 | 0.1573 | [27 empty] | Bromide | mg/L | 49 | 48 | 48.5 | 2.0619 | --- | 311.4032 | --- | 62.6923 | 308.6519 | 84.2865 | Bromide | mg/L | 43 | --- | 833.9091 | --- | 66.9231 | 825.4622 | 94.7908 | Bromide | mg/L | 27 | --- | 233 | --- | 79.2308 | 230.7683 | 88.3 | Bromide | mg/L | 20 | --- | 181.7647 | --- | 84.6154 | 179.8839 | 88.8817 | Ca-HdF, mg/L CaCO3 | 232 | 232 | 232 | 232 | Ca-HdF, mg/L CaCO3 | 232 | 232 | 232 | 232
ICR Treatment Plant Identification Number | 1086 | Design cross-flow velocity (fps) | .7 ft/sec @ 15 gfd, 10% recovery | [9 empty] | Potassium (mg/L) | 25.1 |  |  |  | SDS-Incubation time | hours | 24.2 | 23.63 | 23.915 | 2.3834 | [21 empty] | 1999-05-15 | 12:01 | 112.6 | 22.7 | 100.2 | 100 | 299 | 6.6 | 15 |  | 21.6 | 0.24367 | 0.30556 | 12.8426 | 15.0641 | 14.7557 | 637.1666 | 91.7123 | 625.1265 | 5.3943 | 94.7057 | 0.15581 | [27 empty] | SDS-Cl2 dose | mg/L | 3.92 | 3.92 | 3.92 | 0 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 5.8 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2.8 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2.1 | --- | --- | --- | --- | --- | --- | Ca-Hdp, mg/L CaCO3 | 68.9 | 45.9 | 39.4 | 29.2 | Ca-Hdp, mg/L CaCO3 | 68.9 | 45.9 | 39.4 | 29.2
PWSID Number of Plant (if assigned) | 45-00351 | Required influent flow to permeate flow rate ratio, QI:Qp | 6:1 | [9 empty] | Strontium (mg/L) | 1.14 |  |  |  | SDS-TOX | mg Cl- /L | 1058 | 1060 | 1059 | 0.18886 | [70 empty] | SDS-Free Cl2 residual | mg/L | 1.12 | 1.14 | 1.13 | 1.7699 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.67 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.94 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.68 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 18 | Maximum element recovery (%) | 17 | [14 empty] | SDS-CHCl3 | mg/L | 177 | 211 | 194 | 17.5258 | [70 empty] | SDS-Cl2 demand | mg/L | 2.8 | 2.78 | 2.79 | 0.71685 | --- | 32.4029 | --- | 76.6917 | 32.093 | 91.3065 | SDS-Cl2 demand | mg/L | 4.13 | --- | 75.4027 | --- | 65.4971 | 74.6415 | 94.4669 | SDS-Cl2 demand | mg/L | 1.86 | --- | 22.08 | --- | 84.4612 | 21.8609 | 91.4917 | SDS-Cl2 demand | mg/L | 1.42 | --- | 16.9347 | --- | 88.137 | 16.7543 | 91.5246 | Blended Water Quality if THM4 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if THM4 Controls the Blend Ratio
Historical Average Water Temperature (oC) | 20 | Variability of design flux (%) | 15 | [14 empty] | SDS-BDCM | mg/L | 36.7 | 36.5 | 36.6 | 0.54645 | [70 empty] | SDS-Chlorination temp. | oC | 20 | 20 | 20 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 20 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 20 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 20 | --- | --- | --- | --- | --- | --- | Qp/QT (THM4), % | 77.0107 | 80.9073 | 73.1411 | 71.8459 | Qp/QT (THM4), % | 94.0925 | 98.8534 | 89.3646 | 87.7822
State Approved Plant Capacity (MGD) | 22.4 | Rejection of reference solute and conditions of test | 0.85 | [14 empty] | SDS-DBCM | mg/L | 3.8 | 3.6 | 3.7 | 5.4054 | [70 empty] | SDS-Chlorination pH | --- | 7.49 | 7.43 | 7.46 | 0.80429 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.52 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.55 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.54 | --- | --- | --- | --- | --- | --- | SDS-THM4b, ug/L | 72 | 72 | 72 | 72 | SDS-THM4b, ug/L | 36 | 36 | 36 | 36
|  | (e.g., solute type and concentration) | 500 mg/L NaCl @ 80 psi | [9 empty] | Sodium (mg/L) | 32.8 |  |  |  | SDS-CHBr3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [70 empty] | SDS-Incubation time | hours | 24.3 | 24.2 | 24.25 | 0.41237 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 23.3 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 26 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 23.68 | --- | --- | --- | --- | --- | --- | SDS-HAA5b, ug/L | 48.7095 | 47.5276 | 51.9164 | 53.1491 | SDS-HAA5b, ug/L | 19.0554 | 17.6113 | 22.9736 | 24.4798
|  | Variability of rejection of reference solute (%) | 5 | [9 empty] | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | SDS-THM4 | mg/L | 217.5 | 251.1 | 234.3 | 14.3406 | [70 empty] | SDS-TOX | mg Cl- /L | 76.3 | 72.4 | 74.35 | 5.2455 | --- | 3250.6403 | --- | 92.9792 | 3217.4004 | 97.6891 | SDS-TOX | mg Cl- /L | 139.5 | --- | 8498.5909 | --- | 86.8272 | 8409.3158 | 98.3411 | SDS-TOX | mg Cl- /L | 52.75 | --- | 2065.25 | --- | 95.0189 | 2043.4479 | 97.4186 | SDS-TOX | mg Cl- /L | 27.9 | --- | 1544.2235 | --- | 97.3654 | 1526.5937 | 98.1724 | SDS-TOXb, ug Cl- /L | 300.7144 | 315.0576 | 323.0181 | 318.1964 | SDS-TOXb, ug Cl- /L | 132.5179 | 150.0426 | 159.7689 | 153.8777
|  | Standard testing recovery (%) | 10 | [9 empty] | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | SDS-MCAA* | mg/L | 7.2 | 7 | 7.1 | 2.8169 | [70 empty] | SDS-CHCl3 | mg/L | 9 | 9.1 | 9.05 | 1.105 | --- | 605.6629 | --- | 95.3351 | 599.4193 | 98.4902 | SDS-CHCl3 | mg/L | 13.2 | --- | 1656.8364 | --- | 93.1959 | 1639.2823 | 99.1948 | SDS-CHCl3 | mg/L | 4.7 | --- | 383.3 | --- | 97.5773 | 379.1985 | 98.7605 | SDS-CHCl3 | mg/L | 2.9 | --- | 283.9294 | --- | 98.5052 | 280.662 | 98.9667 | SDS-CDb, mg/L | 4.9004 | 5.6269 | 4.5754 | 4.3903 | SDS-CDb, mg/L | 3.3323 | 4.2199 | 2.9352 | 2.709
|  | Standard testing pH | 7.5 | [14 empty] | SDS-DCAA* | mg/L | 52.3 | 53.3 | 52.8 | 1.8939 | [70 empty] | SDS-BDCM | mg/L | 8.8 | 8.7 | 8.75 | 1.1429 | --- | 98.5887 | --- | 76.0929 | 97.6485 | 91.0393 | SDS-BDCM | mg/L | 12.4 | --- | 232.4 | --- | 66.1202 | 230.0504 | 94.6099 | SDS-BDCM | mg/L | 4.6 | --- | 68.6 | --- | 87.4317 | 67.9067 | 93.226 | SDS-BDCM | mg/L | 3.1 | --- | 52.3647 | --- | 91.5301 | 51.7919 | 94.0145 | TOCb, mg/L | 3.1641 | #VALUE! | 3.2678 | #VALUE! | TOCb, mg/L | 1.4149 | #VALUE! | 1.5416 | #VALUE!
|  | Acceptable range of operating pressures | 0-350 | [14 empty] | SDS-TCAA* | mg/L | 121 | 124 | 122.5 | 2.449 | [70 empty] | SDS-DBCM | mg/L | 5.9 | 5.6 | 5.75 | 5.2174 | --- | -0.8629 | --- | -55.4054 | -0.7937 | 824.4558 | SDS-DBCM | mg/L | 8.1 | --- | -31.9 | --- | -118.9189 | -31.4728 | 125.7365 | SDS-DBCM | mg/L | 3.1 | --- | 4.3 | --- | 16.2162 | 4.287 | 27.6884 | SDS-DBCM | mg/L | 2.4 | --- | 4.3118 | --- | 35.1351 | 4.2895 | 44.0499 | UV254 b, cm-1 | 0.10417 | 0.10162 | 0.10763 | 0.10884 | UV254 b, cm-1 | 0.047759 | 0.04464 | 0.051979 | 0.053457
|  | Acceptable range of operating pH values | 4-11 | [14 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [70 empty] | SDS-CHBr3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | Bromideb, ug/L | 67.2363 | 59.6107 | 54.6647 | 50.9695 | Bromideb, ug/L | 53.3146 | 43.9975 | 37.9545 | 33.4396
|  | Typical pressure drop across a single element (psi) | 5 | [14 empty] | SDS-DBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [70 empty] | SDS-THM4 | mg/L | 23.7 | 23.4 | 23.55 | 1.2739 | --- | 703.3887 | --- | 89.9488 | 696.2742 | 96.6177 | SDS-THM4 | mg/L | 33.7 | --- | 1857.3364 | --- | 85.6167 | 1837.8599 | 98.1663 | SDS-THM4 | mg/L | 12.4 | --- | 456.2 | --- | 94.7076 | 451.3922 | 97.2529 | SDS-THM4 | mg/L | 8.4 | --- | 340.6059 | --- | 96.4149 | 336.7434 | 97.5055 | Alkb, mg/L CaCO3 | 12.1237 | 11.2649 | 10.7644 | 10.5153 | Alkb, mg/L CaCO3 | 9.2454 | 8.1961 | 7.5845 | 7.2802
|  | Maximum permissible SDI | 5 | [14 empty] | SDS-BCAA* | mg/L | 8.3 | 7.5 | 7.9 | 10.1266 | [70 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | T-Hdb, mg/L CaCO3 | 111.8876 | 83.8181 | 96.0237 | 89.8157 | T-Hdb, mg/L CaCO3 | 82.4727 | 48.1771 | 63.0899 | 55.5049
|  | Maximum permissible turbidity (ntu) | 1 | [14 empty] | SDS-TBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [70 empty] | SDS-DCAA* | mg/L | 3.5 | 3.8 | 3.65 | 8.2192 | --- | 162.1984 | --- | 93.0871 | 160.5392 | 97.7264 | SDS-DCAA* | mg/L | 6.1 | --- | 430.6455 | --- | 88.447 | 426.1113 | 98.5684 | SDS-DCAA* | mg/L | 1.8 | --- | 103.8 | --- | 96.5909 | 102.695 | 98.2472 | SDS-DCAA* | mg/L | 1.3 | --- | 77.0353 | --- | 97.5379 | 76.1547 | 98.2929 | Ca-Hdb, mg/L CaCO3 | 106.3956 | 81.4316 | 91.1303 | 86.2964 | Ca-Hdb, mg/L CaCO3 | 78.5351 | 48.0337 | 59.8838 | 53.9777
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | <0.1 mg/L extended | [14 empty] | SDS-CDBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [70 empty] | SDS-TCAA* | mg/L | 3.8 | 4.3 | 4.05 | 12.3457 | --- | 386.1468 | --- | 96.6939 | 382.1481 | 98.9402 | SDS-TCAA* | mg/L | 8.2 | --- | 1047.2909 | --- | 93.3061 | 1036.1934 | 99.2086 | SDS-TCAA* | mg/L | 2.2 | --- | 242.8 | --- | 98.2041 | 240.1935 | 99.0841 | SDS-TCAA* | mg/L | 1.2 | --- | 179.5824 | --- | 99.0204 | 177.5084 | 99.324
|  | 1: All of the information requested in this field may not be available, but values for all Design | [15 empty] | SDS-DCBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [70 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  | Parameters must be entered in cells E14:E23, since these parameters are used in calculations. | [15 empty] | SDS-HAA5 | mg/L | 180.5 | 184.3 | 182.4 | 2.0833 | [70 empty] | SDS-DBAA* | mg/L | 1.1 | 1.1 | 1.1 | 0 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DBAA* | mg/L | 1.4 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | Blended Water Quality if HAA5 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if HAA5 Controls the Blend Ratio
[18 empty] | SDS-HAA6 | mg/L | 188.8 | 191.8 | 190.3 | 1.5765 | [70 empty] | SDS-BCAA* | mg/L | 2.6 | 2.7 | 2.65 | 3.7736 | --- | 19.5855 | --- | 66.4557 | 19.4083 | 86.346 | SDS-BCAA* | mg/L | 3.9 | --- | 40.2636 | --- | 50.6329 | 39.8753 | 90.2195 | SDS-BCAA* | mg/L | 1.4 | --- | 14.4 | --- | 82.2785 | 14.2592 | 90.1818 | SDS-BCAA* | mg/L | 1.1 | --- | 11.1 | --- | 86.0759 | 10.9837 | 89.9852 | Qp/QT (HAA5), % | 73.9631 | 77.0246 | 71.9731 | 71.373 | Qp/QT (HAA5), % | 89.5161 | 93.2214 | 87.1076 | 86.3813
[18 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [75 empty] | SDS-TBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-THM4b, ug/L | 78.4227 | 79.7887 | 74.5917 | 73.0684 | SDS-THM4b, ug/L | 45.6448 | 47.298 | 41.0082 | 39.1646
[18 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, | [75 empty] | SDS-CDBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-HAA5b, ug/L | 54 | 54 | 54 | 54 | SDS-HAA5b, ug/L | 27 | 27 | 27 | 27
[18 empty] | should be reported if measured. | [75 empty] | SDS-DCBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TOXb, ug Cl- /L | 330.722 | 350.7588 | 334.7707 | 323.0732 | SDS-TOXb, ug Cl- /L | 177.5794 | 201.8296 | 182.4795 | 168.3222
[94 empty] | SDS-HAA5 | mg/L | 8.4 | 9.2 | 8.8 | 9.0909 | --- | 568.8 | --- | 95.1754 | 562.9396 | 98.4368 | SDS-HAA5 | mg/L | 15.7 | --- | 1531.1545 | --- | 91.3925 | 1514.9695 | 98.9637 | SDS-HAA5 | mg/L | 4 | --- | 360.8 | --- | 97.807 | 356.9347 | 98.8793 | SDS-HAA5 | mg/L | 2.5 | --- | 267.0588 | --- | 98.6294 | 263.9829 | 99.053 | SDS-CDb, mg/L | 5.1802 | 5.9313 | 4.6935 | 4.4402 | SDS-CDb, mg/L | 3.7524 | 4.6614 | 3.1634 | 2.8568
[94 empty] | SDS-HAA6 | mg/L | 11 | 11.9 | 11.45 | 7.8603 | --- | 588.3855 | --- | 93.9832 | 582.3479 | 98.0338 | SDS-HAA6 | mg/L | 19.6 | --- | 1571.4182 | --- | 89.7005 | 1554.8448 | 98.7394 | SDS-HAA6 | mg/L | 5.4 | --- | 375.2 | --- | 97.1624 | 371.1938 | 98.5452 | SDS-HAA6 | mg/L | 3.6 | --- | 278.1588 | --- | 98.1083 | 274.9666 | 98.6908 | TOCb, mg/L | 3.4762 | #VALUE! | 3.3921 | #VALUE! | TOCb, mg/L | 1.8835 | #VALUE! | 1.7817 | #VALUE!
[94 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | UV254 b, cm-1 | 0.11424 | 0.11395 | 0.11163 | 0.11048 | UV254 b, cm-1 | 0.062873 | 0.062522 | 0.059721 | 0.058325
[94 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | Bromideb, ug/L | 69.72 | 62.9886 | 55.8677 | 51.4897 | Bromideb, ug/L | 57.0444 | 48.8974 | 40.2791 | 34.9805
[133 empty] | Alkb, mg/L CaCO3 | 12.6372 | 11.9288 | 10.9933 | 10.6113 | Alkb, mg/L CaCO3 | 10.0165 | 9.1591 | 8.0269 | 7.5646
[133 empty] | T-Hdb, mg/L CaCO3 | 117.1355 | 91.5292 | 98.3946 | 90.834 | T-Hdb, mg/L CaCO3 | 90.3532 | 59.3624 | 67.6715 | 58.521
[133 empty] | Ca-Hdb, mg/L CaCO3 | 111.3661 | 88.6572 | 93.3798 | 87.2556 | Ca-Hdb, mg/L CaCO3 | 85.9992 | 58.5151 | 64.2307 | 56.8187
[133 empty] | Notes: |  |  |  |  | Notes:
[133 empty] | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to |  |  |  |  | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to
[133 empty] | determine the percentage of total flow that must be treated by the membrane process to meet the |  |  |  |  | determine the percentage of total flow that must be treated by the membrane process to meet the
[133 empty] | Stage 1 DBP MCLs. |  |  |  |  | Stage 2 DBP MCLs.
[133 empty] | A 10% factor of safety has been applied all the MCLs. i.e., 72 / 54 mg/L for THM4 and HAA5. |  |  |  |  | A 10% factor of safety has been applied all the MCLs. i.e., 36 / 27 mg/L for THM4 and HAA5.
[133 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for |  |  |  |  | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for
[133 empty] | both parameters and the maximum (Qp/QT) ratio controls the design. |  |  |  |  | both parameters and the maximum (Qp/QT) ratio controls the design.
[133 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. |  |  |  |  | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[133 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. |  |  |  |  | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[133 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. |  |  |  |  | The subscript "b" refers to the blended water quality for a given blend ratio.
[133 empty] | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL. |  |  |  |  | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL.
[133 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. |  |  |  |  | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
Note on X24: TSC_ADM: Reported SDS temperature is a measured value - the consultant used an incubator for SDS testing.
Note on CY16: C. Hill (11/16/99): Utility verified reported permeate concentrations for this parameter.
Note on CY17: C. Hill (11/16/99): Utility verified reported permeate concentrations for this parameter.
Note on CY18: C. Hill (11/16/99): Utility verified reported permeate concentrations for this parameter.
Note on CY19: C. Hill (11/16/99): Utility verified reported permeate concentrations for this parameter.
Note on CY22: C. Hill (11/16/99): Utility verified reported permeate concentrations for this parameter.
Note on CY25: C. Hill (11/16/99): Utility verified reported permeate concentrations for this parameter.
Note on CY29: TSC_ADM: Reported SDS temperature is a measured value - the consultant used an incubator for SDS testing.
Note on DL29: TSC_ADM: Reported SDS temperature is a measured value - the consultant used an incubator for SDS testing.
Note on DV29: TSC_ADM: Reported SDS temperature is a measured value - the consultant used an incubator for SDS testing.
Note on EF29: TSC_ADM: Reported SDS temperature is a measured value - the consultant used an incubator for SDS testing.
Print All Fields