## Sheet1. 1st Pilot Study
FIELD-SET 1: RESULTS FROM 1st PILOT-SCALE STUDY (FILE: gacpilot.xls)
Field 1-1: PWS And Treatment Plant Data |  | Field 1-2: Pilot-Scale GAC Design Parameters |  |  |  | Field 1-3: Pretreatment Used Prior To GAC1 |  |  | Field 1-4: Influent Water Quality For The 10- And 20-Minute, Pilot-Scale GAC Contactors1 | [14 empty] | Field 1-4: Influent Water Quality For The 10- And 20-Minute, Pilot-Scale GAC Contactors (continued) | [15 empty] | Field 1-4: Influent Water Quality For The 10- And 20-Minute, Pilot-Scale GAC Contactors (continued) | [9 empty] | Field 1-5: Effluent Water Quality For The 10-Minute, Pilot-Scale GAC Contactor1 | [16 empty] | Field 1-5: Effluent Water Quality For The 10-Minute, Pilot-Scale GAC Contactor (continued) | [18 empty] | Field 1-6: Effluent Water Quality For The 20-Minute, Pilot-Scale GAC Contactor1 | [16 empty] | Field 1-6: Effluent Water Quality For The 20-Minute, Pilot-Scale GAC Contactor (continued) | [18 empty] | Field 1-7: GAC Cost Parameters
|  | Input Design Parameters |  | US Standard Mesh Sizes |  |  |  |  | Group A, 15 influent samples per run | [40 empty] | Group B, 15 effluent samples per run | [35 empty] | Group C, 15 effluent samples per run
PWS Name | Miami Dade WSD | Carbon manufacturer | Calgon Carbon Manufacturer | US standard | Opening | Process | Description | Scale | Sample | Was sample | Sampling | Sampling | Operation | Bed | Bed | pH | Turbidity | Alkalinity | Temp. | Total | Calcium | Ammonia | Bromide | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Cost Parameter | Parameter value
Public Water System Identification Number | PWISD # FL 4130871 | Carbon trade name | Filtrasorb 300 | mesh size | (mm) | Activated Silica | Added to raw water, 1 mg/L | full | ID | duplicated? | date | time | time | volumes | volumes |  |  |  |  | Hardness | Hardness | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | Capital Recovery Interest Rate (%) | 5
Water Industry Data Base Number (optional) | NA | Carbon type | Bituminous-based granular activated | 4 | 4.75 | Lime Softening | Added to raw water in softening units, tp pH 10.0 | full |  | Y/N | MM/DD/YY | hh:mm | hh.hh | ( 20 minute) | ( 10 minute) | --- | ntu | mg/L as CaCO3 | oC | mg/L as CaCO3 | mg/L as CaCO3 | mg NH3-N / L | mg/L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | Capital Recovery Period (years) | 30
|  | Pilot GAC influent TOC (mg/L) | 15 | 6 | 3.35 | Sedimentation | Within softening units, Turbidity 17 NTU | pilot | START | --- | 1997-11-03 | 17:30 | 0 | 0 | 0 | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | START | --- | 1997-11-03 | 17:30 | 0 | 0 | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | START | --- | 1997-11-03 | 17:30 | 0 | 0 | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | Overhead & Profit Factor (% of construction costs) | 25
Official ICR Contact Person |  | Inner diameter of the pilot GAC column, D (mm) | 76.2 | 8 | 2.36 | pH adjustment | acid added to reduce the pH of the softened water from pH = 9.8 to 10.2 (not adjusted) | pilot | A1 | N | 1997-11-04 | 17:30 | 24 | 72 | 144 | 9.99 | 0.38 | 55 | 25 | 58 | 37 | 0.3 | 170 | 15.3 | 0.429 | 2.8039 | 14 | 1.02 | 12.98 | 29 | 8.8 | 9 | 945 | 260 | 55 | 10 | BMRL | 325 | 8.9 | 84 | 48 | 1.3 | 2.3 | 16 | BMRL | 4.6 | 11 | 144.5 | 160.5 | B1-10 | N | 1997-11-04 | 17:30 | 24 | 144 | 10.19 | 0.24 | 25 | 0.2 | BMRL | BMRL |  | 3 | 0.51 | 2.49 | 29 | 8.8 | 9 | BMRL | BMRL | 0.9 | 1.9 | NA | 2.8 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | 0 | C1-20 | N | 1997-11-04 | 17:30 | 24 | 72 | 10.01 | 0.11 | 23 | 0.2 | 0.6 | BMRL |  | 4 | 1.04 | 2.96 | 29 | 8.8 | 9 | 25 | BMRL | 0.7 | 1.7 | 2.4 | 4.8 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | 0 | Special Sitework Factor (% of construction costs) | 5
Mailing Address |  | Manufacturer reported dry bed density, r (kg/m3) | 500 | 10 | 2 | Filtration | Dual Media Filtration - Pilot Scale @ 5 gal/min/ft^2. 12" of Sand and 24" of Anthracite | pilot | A2 | N | 1997-11-05 | 16:06 | 46.6 | 139.8 | 279.6 | 10.84 | 0.33 | 70 | 25.2 | 77 | 67 | 0.3 | 170 | 13.8 | 0.354 | 2.5652 | 13.5 | 0.85 | 12.65 | 29 | 8.8 | 9 | 790 | 240 | 59 | 14 | NA | 313 | 9.8 | 77 | 42 | 1.4 | 3.4 | 18 | BMRL | 3 | 13 | 133.6 | 151.6 | B2-10 | N | 1997-11-05 | 16:06 | 46.6 | 279.6 | 9.76 | 0.29 | 25.8 | 0.2 | BMRL | BMRL |  | 3.5 | 0.74 | 2.76 | 29 | 8.8 | 9 | 25 | 0.7 | 2.4 | 6.9 | NA | 10 | BMRL | BMRL | BMRL | BMRL | 3.2 | BMRL | 4 | BMRL | BMRL | 3.2 | 3.2 | C2-20 | N | 1997-11-05 | 16:06 | 46.6 | 139.8 | 9.73 | 0.13 | 25.7 | 0.2 | 0.7 | 0.009 | 1.2857 | 3.5 | 1.04 | 2.46 | 29 | 8.9 | 9 | BMRL | BMRL | 0.7 | 1.8 | 2.1 | 4.6 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | 0 | Construction Contingencies (% of construction costs) | 10
|  | Pilot GAC mesh size, upper (US standard mesh) | 8 | 12 | 1.68 |  |  |  | A3 | N | 1997-11-06 | 17:35 | 72.0833 | 216.25 | 432.5 | 10.08 | 0.49 | 55 | 25.8 | 59 | 40 | 0.3 | 170 | 15.3 | 0.418 | 2.732 | 14 | 0.95 | 13.05 | 29 | 8.9 | 9 | 865 | 250 | 55 | 11 | BMRL | 316 | 7.8 | 83 | 48 | 1.3 | 2.5 | 17 | BMRL | 3.7 | 11 | 142.6 | 159.6 | B3-10 | Y | 1997-11-06 | 17:35 | 72.0833 | 432.5 | 10.18 | 0.49 | 26.6 | 0.2 | 3.5 | 0.069 | 1.9714 | 5 | 0.67 | 4.33 | 29 | 8.8 | 9 | 140 | 17 | 31 | 34 | NA | 82 | BMRL | 5.7 | 2.6 | BMRL | 8.3 | 7.7 | 5.6 | 3.6 | 4 | 16.6 | 24.3 | C3-20 | N | 1997-11-06 | 17:35 | 72.0833 | 216.25 | 10.09 | 0.35 | 26.2 | 0.2 | 1.7 | 0.029 | 1.7059 | 4 | 0.82 | 3.18 | 29 | 8.9 | 9 | 50 | 2.5 | 6.5 | 15 | 26 | 50 | BMRL | 1.3 | BMRL | BMRL | 6.6 | 2.7 | BMRL | 2.3 | 1.3 | 7.9 | 10.6 | Engineering Fee Factor (% of construction costs) | 15
Phone Number |  | Pilot GAC mesh size, lower (US standard mesh) | 30 | 16 | 1.18 |  |  |  | A4 | N | 1997-11-07 | 18:49 | 97.3167 | 291.95 | 583.9 | 10.04 | 0.23 | 55 | 24.5 | 60 | 40 | 0.3 | 170 | 15.7 | 0.4194 | 2.6713 | 14 | 0.85 | 13.15 | 29 | 8.8 | 9 | 925 | 250 | 56 | 11 | BMRL | 317 | 7.9 | 82 | 49 | 1.3 | 2.6 | 17 | BMRL | 3.7 | 11 | 142.8 | 159.8 | B4-10 | N | 1997-11-07 | 18:49 | 97.3167 | 583.9 | 9.77 | 0.34 | 25.4 | 0.2 | 3.6 | 0.0723 | 2.0083 | 5.5 | 0.95 | 4.55 | 29 | 8.9 | 9 | 150 | NA | NA | NA | NA | 0 | BMRL | 7.9 | 3.1 | 1 | 9.4 | 9.3 | NR | 4.1 | 4.3 | 21.4 | 30.7 | C4-20 | N | 1997-11-07 | 18:49 | 97.3167 | 291.95 | 9.52 | 0.28 | 25 | 0.2 | 1.9 | 0.0287 | 1.5105 | 4 | 0.9 | 3.1 | 29 | 8.9 | 9 | 59 | 2.3 | 7 | 19 | 24 | 52.3 | BMRL | 1.3 | BMRL | BMRL | 6.8 | 2.8 | NR | 2.7 | 1.7 | 8.1 | 10.9 | 1998 ENR Construction Cost Index (CCI base year 1913) | 5986
FAX Number |  | Flow rate, Q (L/hr) | 29.5 | 20 | 0.85 |  |  |  | A5 | Y | 1997-11-08 | 17:05 | 119.5833 | 358.75 | 717.5 | 8.66 | 0.3 | 115 | 23.3 | 125 | 95 | 0.3 | 170 | 16.5 | 0.4371 | 2.6491 | 15 | 0.47 | 14.53 | 29 | 8.9 | 9 | 1090 | 290 | 58 | 9.7 | BMRL | 357.7 | 8.1 | 91 | 57 | 1 | 2.3 | 18 | BMRL | 3.9 | 12 | 159.4 | 177.4 | B5-10 | N | 1997-11-08 | 8:30 | 111 | 666 | 10.28 | 0.28 | 21.4 | 0.2 | 3.8 | 0.0726 | 1.9105 | 6 | 1.04 | 4.96 | 29 | 8.9 | 9 | 140 | 18 | 25 | 27 | 8 | 78 | BMRL | 7.4 | 3 | BMRL | 8.5 | 8.4 | NR | 4.2 | 4.3 | 18.9 | 27.3 | C5-20 | Y | 1997-11-08 | 17:05 | 119.5833 | 358.75 | 9.54 | 0.16 | 22.7 | 0.2 | 3 | 0.034 | 1.1333 | 4 | 0.72 | 3.28 | 29 | 8.8 | 9 | NR | 5.1 | 11 | 19 | 18 | 53.1 | BMRL | 2.2 | BMRL | BMRL | 6.4 | 3.6 | BMRL | 2.5 | 1.8 | 8.6 | 12.2 | 1998 Producers Price Index (PPI base year 1967 = 100) | 367
E-Mail Address (optional) |  |  |  | 30 | 0.6 |  |  |  | A6 | N | 1997-11-10 | 8:15 | 158.75 | 476.25 | 952.5 | 10.37 | 0.4 | 60 | 23.7 | 62 | 42 | 0.3 | 160 | 15.6 | 0.398 | 2.5513 | 13 | 0.96 | 12.04 | 29 | 8.9 | 9 | 845 | 287 | 53 | 14.2 | BMRL | 354.2 | 8.8 | 85.3 | 36 | BMRL | 2.8 | 15 | BMRL | 2.9 | 10 | 132.9 | 147.9 | B6-10 | N | 1997-11-10 | 8:15 | 158.75 | 952.5 | 10.66 | 0.16 | 21.6 | 0.3 | 7.1 | 0.154 | 2.169 | 6.5 | 0.59 | 5.91 | 29 | 8.9 | 9 | 295 | 57 | 35 | 21 | 2.6 | 115.6 | 3.5 | 20 | 8.6 | BMRL | 7 | 13 | 4 | 3.9 | 6.2 | 39.1 | 52.1 | C6-20 | N | 1997-11-10 | 8:15 | 158.75 | 476.25 | 10.36 | 0.17 | 20.9 | 0.2 | 4.9 | 0.096 | 1.9592 | 5 | 0.49 | 4.51 | 29 | 8.9 | 9 | 150 | 25 | 28 | 26 | 5.7 | 84.7 | BMRL | 9.1 | 3.9 | BMRL | 8 | 8 | BMRL | 3.5 | 4.2 | 21 | 29 | Labor Rate + Fringe ($/work-hour) | 24
|  | Estimated Run Length |  | 40 | 0.425 |  |  |  | A7 | N | 1997-11-11 | 8:10 | 182.6667 | 548 | 1096 | 10.21 | 0.2 | 55 | 23.7 | 58 | 37 | 0.3 | 170 | 15.2 | NR |  | 14 | 0.82 | 13.18 | 29 | 8.9 | 9 | 945 | 220 | 55 | 12 | BMRL | 287 | 11 | 77 | 47 | 1 | 2.9 | 17 | BMRL | 4 | 12 | 138.9 | 155.9 | B7-10 | N | 1997-11-11 | 8:10 | 182.6667 | 1096 | 9.86 | 0.15 | 23.9 | 0.2 | 2.9 | 0.067 | 2.3103 | 5.5 | 0.67 | 4.83 | 29 | 8.9 | 9 | 165 | 25 | 31 | 32 | 8.6 | 96.6 | BMRL | 8.4 | 3.8 | 1.1 | 8.5 | 9.2 | NR | 3.9 | 5.1 | 21.8 | 31 | C7-20 | N | 1997-11-11 | 8:10 | 182.6667 | 548 | 8.55 | 0.16 | 24 | 0.2 | 1.1 | 0.016 | 1.4545 | 3.5 | 0.96 | 2.54 | 29 | 8.9 | 9 | NR | 3.7 | 7.5 | 13 | 8.7 | 32.9 | BMRL | 1.5 | BMRL | BMRL | 3.1 | 2.2 | NR | 2.2 | 1.8 | 4.6 | 6.8 | Labor Overhead Factor (% of labor) | 67
Technical ICR Contact Person |  | Bed volumes to 50% TOC breakthrough, BV50 | 642.009 | 50 | 0.3 |  |  |  | A8 | N | 1997-11-12 | 14:30 | 213 | 639 | 1278 | 10.74 | 0.11 | 65 | 26.2 | 66 | 55 | 0.2 | 170 | 14.4 | 0.371 | 2.5764 | 13 | 0.87 | 12.13 | 29 | 8.9 | 9 | 895 | 278 | 59.3 | 13.9 | BMRL | 351.2 | 8.9 | 57 | 38 | BMRL | 2.7 | 16 | BMRL | 3.6 | 10 | 106.6 | 122.6 | B8-10 | Y | 1997-11-12 | 19:19 | 217.8167 | 1306.9 | 10.54 | 0.11 | 24.5 | 0.2 | 6.2 | 0.138 | 2.2258 | 7 | 0.8 | 6.2 | 29 | 8.9 | 9 | 315 | 62 | 41 | 25 | 3.3 | 131.3 | 5 | 22 | 9.6 | BMRL | 7.6 | 14 | 4 | 4.1 | 7.3 | 44.2 | 58.2 | C8-20 | N | 1997-11-12 | 14:30 | 213 | 639 | 10.17 | 0.12 | 26.9 | 0.2 | 6.1 | 0.11 | 1.8033 | 5.5 | 0.54 | 4.96 | 29 | 8.9 | 9 | 200 | 32 | 36 | 33 | 6.5 | 107.5 | 2.3 | 11 | 4.8 | BMRL | 9.3 | 9.9 | BMRL | 4.2 | 5.2 | 27.4 | 37.3 | Electric Rate ($/kW-h) | 0.05
Mailing Address |  | Estimated run length, BVT (= 2 x BV50) | 1284.0179 | 60 | 0.25 |  |  |  | A9 | N | 1997-11-14 | 8:40 | 255.1667 | 765.5 | 1531 | 10.48 | 0.34 | 55 | 24.8 | 58 | 42 | 0.3 | 170 | 14.5 | 0.379 | 2.6138 | 14 | 1.04 | 12.96 | 29 | 8.8 | 9 | 905 | 220 | 55 | 13 | BMRL | 288 | 9.1 | 65 | 36 | BMRL | 2.4 | 13 | BMRL | 2.9 | 10 | 112.5 | 125.5 | B9-10 | N | 1997-11-13 | 9:15 | 231.75 | 1390.5 | 10.55 | 0.16 | 27 | 0.2 | 5.9 | 0.137 | 2.322 | 6.5 | 0.95 | 5.55 | 29 | 9 | 9 | 280 | 55 | 39 | 21 | 2.2 | 117.2 | BMRL | 18 | 9.9 | BMRL | 5.4 | 11 | NR | 3.7 | 6.9 | 33.3 | 44.3 | C9-20 | N | 1997-11-14 | 8:40 | 255.1667 | 765.5 | 10.3 | 0.15 | 24.7 | 0.2 | 4.3 | 0.0856 | 1.9907 | 5.5 | 0.7 | 4.8 | 29 | 8.9 | 9 | 160 | 24 | 39 | 34 | 12 | 109 | BMRL | 7.8 | 3.6 | BMRL | 8.8 | 9.5 | 4.3 | 4.2 | 4.5 | 20.2 | 29.7 | Fuel Oil Rate ($/gal) | 0.95
|  |  |  | 70 | 0.21 |  |  |  | A10 | N | 1997-11-16 | 16:49 | 311.3167 | 933.95 | 1867.9 | 10.58 | 0.16 | 60 | 24.7 | 59 | 45 | 0.3 | 170 | 14.7 | 0.3773 | 2.5667 | 14 | 1.04 | 12.96 | 29 | 8.9 | 9 | 900 | 278 | 61.5 | 13 | BMRL | 352.5 | 11 | 83 | 51 | 1.4 | 2.8 | 17 | BMRL | 3.6 | 12 | 149.2 | 166.2 | B10-10 | N | 1997-11-14 | 8:40 | 255.1667 | 1531 | 10.39 | 0.17 | 24.9 | 0.2 | 7.6 | 0.175 | 2.3026 | 8 | 0.92 | 7.08 | 29 | 8.9 | 9 | 385 | 73 | 49 | 26 | 2.3 | 150.3 | 3.1 | 29 | 15 | BMRL | 6.2 | 15 | BMRL | 4.4 | 8.8 | 53.3 | 68.3 | C10-20 | N | 1997-11-16 | 16:49 | 311.3167 | 933.95 | 10.35 | 0.1 | 24.6 | 0.2 | 6.3 | 0.1334 | 2.1175 | 6.5 | 0.62 | 5.88 | 29 | 8.9 | 9 | 270 | 49 | 45 | 34 | 4.7 | 132.7 | 4.1 | 17 | 7.8 | BMRL | 7.6 | 13 | BMRL | 4.4 | 6.3 | 36.5 | 49.5 | Natural Gas Rate ($/ft3) | 0.0055
Phone Number |  | General Pilot Design Parameters |  | 80 | 0.18 |  |  |  | A11 | N | 1997-11-18 | 9:00 | 351.5 | 1054.5 | 2109 | 10.29 | 8.47 | 50 | 24.5 | 69 | 50 | 0.3 | 160 | 14.3 | 0.376 | 2.6294 | 14 | 0.91 | 13.09 | 29 | 8.8 | 9 | 875 | 277 | 62.2 | 13.7 | BMRL | 352.9 | 11 | 82 | 49 | 1.4 | 2.9 | 18 | BMRL | 3.1 | 13 | 146.3 | 164.3 | B11-10 | N | 1997-11-16 | 16:49 | 311.3167 | 1867.9 | 10.47 | 0.12 | 24.6 | 0.3 | 9 | 0.214 | 2.3778 | 8.5 | 0.54 | 7.96 | 29 | 8.9 | 9 | 525 | 110 | 49 | 21 | 1.5 | 181.5 | 4.3 | 38 | 18 | BMRL | 5 | 15 | BMRL | 3.9 | 8.7 | 65.3 | 80.3 | C11-20 | N | 1997-11-18 | 9:00 | 351.5 | 1054.5 | 10.36 | 0.22 | 22.9 | 0.3 | 6 | 0.137 | 2.2833 | 7 | 0.7 | 6.3 | 29 | 8.9 | 9 | 265 | 48 | 43 | 31 | 4.1 | 126.1 | 2.3 | 17 | 9.4 | BMRL | 6.9 | 13 | BMRL | 4.1 | 6.9 | 35.6 | 48.6 | Current Process Water Rate ($/1000 gal) | 0.2
FAX Number |  | Carbon particle diameter, d (mm) | 1.48 | [5 empty] | A12 | Y | 1997-11-20 | 11:49 | 402.3167 | 1206.95 | 2413.9 | 10.43 | 0.15 | 50 | 25 | 59 | 40 | 0.3 | 170 | 14.7 | 0.411 | 2.7959 | 14 | 0.91 | 13.09 | 29 | 8.9 | 9 | 920 | 284 | 59.7 | 12.8 | BMRL | 356.5 | 12 | 76 | 49 | 1.4 | 2.7 | 17 | BMRL | 3.4 | 13 | 141.1 | 158.1 | B12-10 | N | 1997-11-17 | 14:49 | 333.3167 | 1999.9 | 10.15 | 0.11 | 24.5 | 0.3 | 9.3 | 0.227 | 2.4409 | 8.5 | 0.52 | 7.98 | 29 | 8.9 | 9 | 495 | 93 | 48 | 19 | 1.3 | 161.3 | 4.1 | 40 | 20 | BMRL | 5 | 14 | BMRL | 3.9 | 9 | 69.1 | 83.1 | C12-20 | Y | 1997-11-20 | 11:49 | 402.3167 | 1206.95 | 10.4 | 0.12 | 25.4 | 0.3 | 10.2 | 0.26 | 2.549 | 7.5 | 0.53 | 6.97 | 29 | 8.9 | 9 | 365 | 66 | 49 | 30 | 3.1 | 148.1 | 3.2 | 25 | 12 | BMRL | 7 | 15 | BMRL | 4.2 | 8.2 | 47.2 | 62.2 | Modifications to Existing Plant (% of construction costs) | 30
E-Mail Address (optional) |  | Column cross-sectional area, A (m2) | 0.0045604 | [5 empty] | A13 | N | 1997-11-24 | 9:20 | 495.8333 | 1487.5 | 2975 | 10.37 | 0.22 | 50 | 24.7 | 58 | 40 | 0.3 | 160 | 15 | 0.418 | 2.7867 | 14 | 0.85 | 13.15 | 29 | 8.8 | 9 | 880 | 220 | 49 | 11 | NA | 280 | 9.8 | 85 | 52 | 1.4 | 2.5 | 18 | BMRL | 3.4 | 13 | 150.7 | 168.7 | B13-10 | N | 1997-11-18 | 9:00 | 351.5 | 2109 | 10.27 | 8.47 | 24.5 | 0.3 | 9 | 0.228 | 2.5333 | 9 | 0.49 | 8.51 | 29 | 8.9 | 9 | 520 | 110 | 42 | 22 | 1.3 | 175.3 | 4.5 | 40 | 20 | BMRL | 4.9 | 16 | BMRL | 4 | 9.6 | 69.4 | 85.4 | C13-20 | N | 1997-11-24 | 9:20 | 495.8333 | 1487.5 | 10.23 | 0.14 | 24.2 | 0.2 | 7.5 | 0.184 | 2.4533 | 8 | 1.01 | 6.99 | 29 | 8.9 | 9 | 375 | 74 | 44 | 23 | 2.6 | 143.6 | 3.7 | 26 | 14 | BMRL | 6.2 | 16 | 14 | NR | NR | 49.9 | 65.9
|  | Hydraulic loading rate1, v (m/hr) | 6.4688 |  |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | A14 | N | 1997-11-26 | 9:00 | 543.5 | 1630.5 | 3261 | 10.06 | 0.29 | 50 | 24.7 | 66 | 42 | 0.3 | 160 | 15.3 | 0.435 | 2.8431 | 7 | 0.84 | 6.16 | 29 | 8.9 | 9 | 995 | 399 | 79.6 | 13 | BMRL | 491.6 | 9.7 | NR | 43 | BMRL | 2.4 | 15 | BMRL | 2.9 | 11 | 55.1 | 70.1 | B14-10 | N | 1997-11-19 | 9:00 | 375.5 | 2253 | 10.59 | 0.17 | 24.3 | 0.3 | 9.1 | 0.226 | 2.4835 | 9.5 | 0.95 | 8.55 | 29 | 8.9 | 9 | 495 | 110 | 49 | 23 | 1.7 | 183.7 | 4.7 | 37 | 22 | BMRL | 5.1 | 18 | NR | NR | NR | 68.8 | 86.8 | C14-20 | N | 1997-11-26 | 9:00 | 543.5 | 1630.5 | 10.1 | 0.2 | 24.5 | 0.2 | 7.5 | 0.186 | 2.48 | 5.6 | 1 | 4.6 | 29 | 8.9 | 9 | 315 | 75 | 38 | 20 | 2.4 | 135.4 | 2.6 | 24 | 13 | 1.1 | 6.4 | 14 | BMRL | 4.7 | 8.2 | 47.1 | 61.1
Plant Name | John E. Preston Water Treatment Plant | 1: If v is not in the range from 5 to 15 m/hr (2 to 6 gpm/ft2) then either Q or D must be adjusted. |  |  |  | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | A15 | N | 1997-12-08 | 9:00 | 831.5 | 2494.5 | 4989 | 10.08 | 4.1 | 55 | 19.5 | 67 | 45 | 0.2 | 150 | 14.3 | 0.406 | 2.8392 | 7 | 1.04 | 5.96 | 29 | 8.9 | 9 | 975 | 320 | 59 | 12.6 | BMRL | 391.6 | 9.8 | 71 | 45 | BMRL | 2.4 | 14 | BMRL | 3 | 11 | 128.2 | 142.2 | B15-10 | Y | 1997-11-20 | 11:49 | 402.3167 | 2413.9 | 10.4 | 0.12 | 25.4 | 0.3 | 7.2 | 0.17 | 2.3611 | 10 | 0.81 | 9.19 | 29 | 8.9 | 9 | 590 | 120 | 50 | 17 | 0.9 | 187.9 | 5.3 | 49 | 39 | BMRL | 4.2 | 18 | NR | NR | NR | 97.5 | 115.5 | C15-20 | N | 1997-12-08 | 9:00 | 831.5 | 2494.5 | 10.02 | 0.21 | 17.7 | 0.2 | 8.5 | 0.218 | 2.5647 | 7.5 | 0.65 | 6.85 | 29 | 8.9 | 9 | 360 | 77 | 40 | 17 | 1.3 | 135.3 | 2.7 | 31 | 16 | BMRL | 4.6 | 14 | BMRL | 4.3 | 8.1 | 54.3 | 68.3
Treatment Plant Category | Ammonia and Chlorine |  |  |  |  | is to list the pretreatment processes used in this particular pilot GAC run. |  |  | A16 | N | 1997-12-09 | 15:45 | 862.25 | 2586.75 | 5173.5 | 10.36 | 0.45 | 50 | 25.1 | 64 | 47 | 0.3 | 150 | 12.3 | 0.333 | 2.7073 | 11.5 | 1 | 10.5 | 29 | 8.9 | 9 | 675 | 266 | 62.5 | 14.1 | BMRL | 342.6 | 5.4 | 52 | 29 | BMRL | 2.4 | 12 | BMRL | 3 | 9.4 | 88.8 | 100.8 | B16-10 | N | 1997-11-21 | 9:40 | 424.1667 | 2545 | 10.5 | 0.18 | 26.4 | 0.3 | 10.3 | 0.337 | 3.2718 | 10 | 1.04 | 8.96 | 29 | 9 | 9 | 605 | 150 | 58 | 21 | 1.2 | 230.2 | 4.9 | 40 | 23 | 1.1 | 4.2 | 15 | NR | 4.6 | 9.8 | 73.2 | 88.2 | C16-20 | N | 1997-12-09 | 15:45 | 862.25 | 2586.75 | 10.16 | 0.55 | 26.5 | 0.3 | 8.5 | 0.21 | 2.4706 | 7.5 | 0.86 | 6.64 | 29 | 8.9 | 9 | 410 | 94 | 48 | 21 | 1.4 | 164.4 | 2.8 | 31 | 18 | 1 | 4.4 | 13 | BMRL | 4.3 | 8.2 | 57.2 | 70.2
Process Train Name | NA | 10-Minute EBCT Run | [6 empty] | A17 | Y | 1997-12-17 | 9:30 | 1048 | 3144 | 6288 | 10.09 | 0.65 | 55 | 19.6 | 59 | 37 | 0.2 | 150 | 15.1 | 0.414 | 2.7417 | 13 | 0.65 | 12.35 | 29 | 8.9 | 9 | 860 | 346 | 64.2 | 12.1 | BMRL | 422.3 | 7.6 | 75 | 47 | BMRL | 2.1 | 15 | BMRL | 2.8 | 10 | 131.7 | 146.7 | B17-10 | N | 1997-11-26 | 9:00 | 543.5 | 3261 | 10.04 | 0.23 | 25.1 | 0.2 | 10.8 | 0.284 | 2.6296 | 10 | 0.91 | 9.09 | 29 | 8.9 | 9 | 610 | 150 | 51 | 18 | 0.9 | 219.9 | 4.2 | 34 | 23 | 1 | 3.9 | 15 | NR | 4 | 9.2 | 66.1 | 81.1 | C17-20 | Y | 1997-12-17 | 9:30 | 1048 | 3144 | 9.91 | 0.17 | 17.1 | 0.2 | 9.5 | 0.246 | 2.5895 | 8 | 0.6 | 7.4 | 29 | 8.9 | 9 | 470 | 162 | 57.2 | 19.8 | BMRL | 239 | 3 | 36 | 23 | BMRL | 3.7 | 14 | BMRL | 3.2 | 9.5 | 65.7 | 79.7
ICR Treatment Plant Identification Number | 301 | Empty bed contact time, EBCT (min) | 10 | [5 empty] | A18 | N | 1997-12-22 | 9:08 | 1167.6333 | 3502.9 | 7005.8 | 10.11 | 0.18 | 50 | 24.3 | 53 | 32 | 0.2 | 150 | 15 | 0.416 | 2.7733 | 11.5 | 0.97 | 10.53 | 29 | 8.9 | 9 | NR | 143 | 41.3 | 11.8 | BMRL | 196.1 | 12 | 110 | 51 | 1 | 3.1 | 19 | BMRL | 3.7 | 14 | 177.1 | 196.1 | B18-10 | N | 1997-12-08 | 9:00 | 831.5 | 4989 | 9.92 | 0.41 | 18.4 | 0.2 | 11 | 0.296 | 2.6909 | 11 | 1.03 | 9.97 | 29 | 8.9 | 9 | 750 | 210 | 61 | 16 | 0.5 | 287.5 | 5.5 | 60 | 39 | 1.2 | 3 | 16 | BMRL | 4.3 | 11 | 108.7 | 124.7 | C18-20 | N | 1997-12-22 | 9:08 | 1167.6333 | 3502.9 | 10.2 | 0.33 | 24.3 | 0.2 | 10.2 | 0.266 | 2.6078 | 8.5 | 0.73 | 7.77 | 29 | 8.9 | 9 | 560 | 245 | 64.4 | 16.9 | BMRL | 326.3 | 3.2 | 43 | 22 | BMRL | 3.8 | 14 | BMRL | 4.1 | 9.1 | 72 | 86
PWSID Number of Plant (if assigned) | PWISD # FL 4130871 | Estimated run time, t (days) | 8.9168 | [5 empty] | A19 | N | 1997-12-29 | 9:30 | 1336 | 4008 | 8016 | 10.29 | 1.57 | 50 | 21.1 | 50 | 35 | 0.2 | 140 | 14.8 | 0.393 | 2.6554 | 12.5 | 1.01 | 11.49 | 29 | 8.9 | 9 | 765 | 306 | 58.8 | 11.3 | BMRL | 376.1 | 7.3 | 67 | 42 | BMRL | 2.4 | 15 | BMRL | 3.2 | 12 | 118.7 | 133.7 | B19-10 | N | 1997-12-17 | 9:30 | 1048 | 6288 | 10.04 | 0.21 | 18.2 | 0.3 | 12.2 | 0.3268 | 2.6787 | 10.5 | 0.8 | 9.7 | 29 | 8.9 | 9 | 640 | 160 | 44 | 14 | BMRL | 218 | 6 | 44 | 31 | 1 | 3.2 | 15 | 31 | 4 | 9.6 | 85.2 | 100.2 | C19-20 | N | 1997-12-29 | 9:30 | 1336 | 4008 | 10.09 | 0.17 | 19.6 | 0.2 | 10.6 | 0.272 | 2.566 | 8.5 | 0.78 | 7.72 | 29 | 9 | 9 | 540 | 233 | 62.2 | 16.7 | BMRL | 311.9 | 3.5 | 44 | 23 | BMRL | 3.7 | 14 | BMRL | 4.3 | 9.1 | 74.2 | 88.2
Historical Minimum Water Temperature (oC) | 19 | Pilot column bed length, l (m) | 1.0781 | [5 empty] | A20 | N | 1998-01-02 | 9:42 | 1432.2 | 4296.6 | 8593.2 | 10.45 | 0.19 | 55 | 22.5 | 57 | 37 | 0.3 | 140 | 14.7 | 0.378 | 2.5714 | 12.5 | 0.84 | 11.66 | 29 | 9 | 9 | 840 | 325 | 61.7 | 11 | BMRL | 397.7 | 7.6 | 68 | 30 | BMRL | 1.8 | 12 | BMRL | 3.3 | 7.9 | 107.4 | 119.4 | [36 empty] | C20-20 | N | 1998-01-02 | 9:42 | 1432.2 | 4296.6 | 10.3 | 0.24 | 22.1 | 0.3 | 14.7 | 0.281 | 1.9116 | 9 | 0.8 | 8.2 | 29 | 9 | 9 | 615 | 284 | 70.3 | 18.7 | BMRL | 373 | 4.1 | 47 | 25 | BMRL | 3.3 | 14 | BMRL | 4.3 | 9.4 | 79.4 | 93.4
Historical Average Water Temperature (oC) | 24 | Mass GAC required, m (kg) | 2.4583 | [5 empty] | A21 | N | 1998-01-20 | 11:28 | 1883.4667 | 5650.4 | 11300.8 | 8.6 | 2.16 | 175 | 23.3 | 172 | 122 | 0.2 | 130 | 15.8 | NR |  | 9.5 | 0.48 | 9.02 | 29 | 8.9 | 9 | 780 | 329 | 47.7 | 12 | BMRL | 388.7 | 6.4 | 52 | 33 | BMRL | 2.4 | 13 | NR | 2 | 8.8 | 93.8 | 106.8 | [36 empty] | C21-20 | N | 1998-01-20 | 11:28 | 1865.9667 | 5597.9 | 9.26 | 0.22 | 23.7 | 0.1 | 13.9 | 0.393 | 2.8273 | 14 | 0.75 | 13.25 | 29 | 8.9 | 9 | 1130 | 374 | 48.9 | 8.9 | BMRL | 431.8 | 9.5 | 94 | 55 | BMRL | 1.8 | 15 | NR | 2.8 | 13 | 160.3 | 175.3
State Approved Plant Capacity (MGD) | 165
20-Minute EBCT Run
|  | Empty bed contact time, EBCT (min) | 20
|  | Estimated run time, t (days) | 17.8336
|  | Pilot column bed length, l (m) | 2.1563 | [5 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [18 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
|  | Mass GAC required, m (kg) | 4.9167 | [5 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [18 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
[9 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below. | [40 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below. | [35 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below.
[9 empty] | Group D, 3 duplicate influent samples per run | [40 empty] | Group D, 3 duplicate effluent samples per run | [35 empty] | Group D, 3 duplicate effluent samples per run
[9 empty] | Sample | Sample | Sampling | Sampling | Operation | Bed | Bed | pH | Turbidity | Alkalinity | Temp. | Total | Calcium | Ammonia | Bromide | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS
[9 empty] | ID | Type | date | time | time | volumes | volumes |  |  |  |  | Hardness | Hardness | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6
[11 empty] | MM/DD/YY | hh:mm | hh.hh | ( 20 minute) | ( 10 minute) | --- | ntu | mg/L as CaCO3 | oC | mg/L as CaCO3 | mg/L as CaCO3 | mg NH3-N / L | mg/L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L
[9 empty] | A5 | Primary | 1997-11-08 | 17:05 | 119.5833 | 358.75 | 717.5 | 8.66 | 0.3 | 115 | 23.3 | 125 | 95 | 0.3 | 170 | 16.5 | 0.4371 | 2.6491 | 15 | 0.47 | 14.53 | 29 | 8.9 | 9 | 1090 | 290 | 58 | 9.7 | BMRL | 357.7 | 8.1 | 91 | 57 | 1 | 2.3 | 18 | BMRL | 3.9 | 12 | 159.4 | 177.4 | B15-10 | Primary | 1997-11-20 | 11:49 | 402.3167 | 1206.95 | 10.4 | 0.12 | 25.4 | 0.3 | 7.2 | 0.17 | 2.3611 | 10 | 0.81 | 9.19 | 29 | 8.9 | 9 | 590 | 120 | 50 | 17 | 0.9 | 187.9 | 5.3 | 49 | 29 | BMRL | 4.2 | 18 | NR | NR | NR | 87.5 | 105.5 | C5-20 | Primary | 1997-11-08 | 17:05 | 119.5833 | 358.75 | 9.54 | 0.16 | 22.7 | 0.2 | 3 | 0.034 | 1.1333 | 4 | 0.72 | 3.28 | 29 | 8.8 | 9 | NR | 5.1 | 11 | 19 | 18 | 53.1 | BMRL | 2.2 | BMRL | BMRL | 6.4 | 3.6 | BMRL | 2.5 | 1.8 | 8.6 | 12.2
[9 empty] | D1 | Duplicate | 1997-11-08 | 17:05 | 119.5833 | 358.75 | 717.5 | 8.66 | 0.3 | 125 | 23.3 | 134 | 102 | 0.3 | 200 | 16.6 | 0.448 | 2.6988 | 15 | 0.6 | 14.4 | 29 | 9 | 9 | 1050 | 280 | 58 | 10 | BMRL | 348 | 8.3 | 80 | 58 | 1 | 2.4 | 19 | BMRL | 4.2 | 13 | 149.7 | 168.7 | D4 | Duplicate | 1997-11-20 | 11:49 | 402.3167 | 1206.95 | 10.46 | 0.13 | 25.5 | 0.3 | 7.4 | 0.169 | 2.2838 | 10 | 1.03 | 8.97 | 29 | 8.9 | 9 | 585 | 120 | 49 | 17 | 1 | 187 | 5 | 46 | 28 | BMRL | 4.2 | 18 | NR | NR | NR | 83.2 | 101.2 | D7 | Duplicate | 1997-11-08 | 17:05 | 119.5833 | 358.75 | 9.54 | 0.16 | 22.7 | 0.2 | 2 | 0.0339 | 1.695 | 4 | 0.73 | 3.27 | 29 | 8.9 | 9 | NR | NR | NR | NR | NR | 0 | BMRL | 2.2 | 1 | BMRL | 7.1 | 4 | NR | 2.9 | 2.1 | 10.3 | 14.3
[10 empty] | Average | --- | --- | --- | --- | --- | 8.66 | 0.3 | 120 | 23.3 | 129.5 | 98.5 | 0.3 | 185 | 16.55 | 0.44255 | 2.6739 | 15 | 0.535 | 14.465 | 29 | 8.95 | 9 | 1070 | 285 | 58 | 9.85 |  | 352.85 | 8.2 | 85.5 | 57.5 | 1 | 2.35 | 18.5 |  | 4.05 | 12.5 | 154.55 | 173.05 |  | Average | --- | --- | --- | --- | 10.43 | 0.125 | 25.45 | 0.3 | 7.3 | 0.1695 | 2.3224 | 10 | 0.92 | 9.08 | 29 | 8.9 | 9 | 587.5 | 120 | 49.5 | 17 | 0.95 | 187.45 | [9 empty] | 85.35 | 103.35 |  | Average | --- | --- | --- | --- | 9.54 | 0.16 | 22.7 | 0.2 | 2.5 | 0.03395 | 1.4142 | 4 | 0.725 | 3.275 | 29 | 8.85 | 9 |  | 5.1 | 11 | 19 | 18 | 26.55 |  | 2.2 | 1 |  | 6.75 | 3.8 |  | 2.7 | 1.95 | 9.45 | 13.25
[10 empty] | RPD | --- | --- | --- | --- | --- | 0 | 0 | 8.3333 | 0 | 6.9498 | 7.1066 | 0 | 16.2162 | 0.60423 | 2.463 | 1.8588 | 0 | 24.2991 | 0.89872 | 0 | 1.1173 | 0 | 3.7383 | 3.5088 | 0 | 3.0457 |  | 2.749 | 2.439 | 12.8655 | 1.7391 | 0 | 4.2553 | 5.4054 |  | 7.4074 | 8 | 6.2763 | 5.0274 |  | RPD | --- | --- | --- | --- | 0.57526 | 8 | 0.39293 | 0 | 2.7397 | 0.58997 | 3.3296 | 0 | 23.913 | 2.4229 | 0 | 0 | 0 | 0.85106 | 0 | 2.0202 | 0 | 10.5263 | 0.48013 | [12 empty] | RPD | --- | --- | --- | --- | 0 | 0 | 0 | 0 | 40 | 0.29455 | 39.7171 | 0 | 1.3793 | 0.30534 | 0 | 1.1299 | 0 | [7 empty] | 0 |  |  | 10.3704 | 10.5263 |  | 14.8148 | 15.3846 | 17.9894 | 15.8491
[9 empty] | A12 | Primary | 1997-11-20 | 11:49 | 402.3167 | 1206.95 | 2413.9 | 10.43 | 0.15 | 50 | 25 | 59 | 40 | 0.3 | 170 | 14.7 | 0.411 | 2.7959 | 14 | 0.91 | 13.09 | 29 | 8.9 | 9 | 920 | 284 | 59.7 | 12.8 | BMRL | 356.5 | 12 | 76 | 49 | 1.4 | 2.7 | 17 | BMRL | 3.4 | 13 | 141.1 | 158.1 | B3-10 | Primary | 1997-11-06 | 17:35 | 72.0833 | 432.5 | 10.18 | 0.49 | 26.6 | 0.2 | 3.5 | 0.069 | 1.9714 | 5 | 0.67 | 4.33 | 29 | 8.8 | 9 | 140 | 17 | 31 | 34 | NA | 82 | BMRL | 5.7 | 2.6 | BMRL | 8.3 | 7.7 | 5.6 | 3.6 | 4 | 16.6 | 24.3 | C12-20 | Primary | 1997-11-20 | 11:49 | 402.3167 | 2413.9 | 10.47 | 0.08 | 25.7 | 0.3 | 10.2 | 0.26 | 2.549 | 7.5 | 0.53 | 6.97 | 29 | 8.9 | 9 | 365 | 66 | 49 | 30 | 3.1 | 148.1 | 3.2 | 25 | 12 | BMRL | 7 | 15 | BMRL | 4.2 | 8.2 | 47.2 | 62.2
[9 empty] | D2 | Duplicate | 1997-11-20 | 11:49 | 402.3167 | 1206.95 | 2413.9 | 10.39 | 0.17 | 55 | 24.9 | 58 | 40 | 0.3 | 170 | 14.8 | 0.412 | 2.7838 | 14 | 0.95 | 13.05 | 29 | 8.8 | 9 | 955 | 210 | 49 | 11 | NA | 270 | 8.8 | 75 | 49 | 1.5 | 2.6 | 18 | BMRL | 3.5 | 13 | 136.9 | 154.9 | D5 | Duplicate | 1997-11-06 | 17:35 | 72.0833 | 432.5 | 10.18 | 0.49 | 26.6 | 0.2 | 3.5 | 0.069 | 1.9714 | 5 | 0.49 | 4.51 | 29 | 8.9 | 9 | 145 | 25 | 36 | 33 | NA | 94 | BMRL | 7.4 | 2.8 | BMRL | 8.5 | 8.6 | BMRL | 2.8 | 3.5 | 18.7 | 27.3 | D8 | Duplicate | 1997-11-20 | 11:49 | 402.3167 | 2413.9 | 10.48 | 0.1 | 25.9 | 0.3 | 10.4 | 0.271 | 2.6058 | 8 | 0.89 | 7.11 | 29 | 8.9 | 9 | 435 | 35 | 22 | 14 | 1.4 | 72.4 | 3.4 | 30 | 16 | 1 | 6.4 | 16 | BMRL | 4.5 | 9.5 | 56.8 | 72.8
[10 empty] | Average | --- | --- | --- | --- | --- | 10.41 | 0.16 | 52.5 | 24.95 | 58.5 | 40 | 0.3 | 170 | 14.75 | 0.4115 | 2.7899 | 14 | 0.93 | 13.07 | 29 | 8.85 | 9 | 937.5 | 247 | 54.35 | 11.9 |  | 313.25 | 10.4 | 75.5 | 49 | 1.45 | 2.65 | 17.5 |  | 3.45 | 13 | 139 | 156.5 |  | Average | --- | --- | --- | --- | 10.18 | 0.49 | 26.6 | 0.2 | 3.5 | 0.069 | 1.9714 | 5 | 0.58 | 4.42 | 29 | 8.85 | 9 | 142.5 | 21 | 33.5 | 33.5 |  | 88 |  | 6.55 | 2.7 |  | 8.4 | 8.15 | 5.6 | 3.2 | 3.75 | 17.65 | 25.8 |  | Average | --- | --- | --- | --- | 10.475 | 0.09 | 25.8 | 0.3 | 10.3 | 0.2655 | 2.5774 | 7.75 | 0.71 | 7.04 | 29 | 8.9 | 9 | 400 | 50.5 | 35.5 | 22 | 2.25 | 110.25 | 3.3 | 27.5 | 14 | 1 | 6.7 | 15.5 |  | 4.35 | 8.85 | 52 | 67.5
[10 empty] | RPD | --- | --- | --- | --- | --- | 0.38425 | 12.5 | 9.5238 | 0.4008 | 1.7094 | 0 | 0 | 0 | 0.67797 | 0.24301 | 0.43495 | 0 | 4.3011 | 0.30604 | 0 | 1.1299 | 0 | 3.7333 | 29.9595 | 19.6872 | 15.1261 |  | 27.6137 | 30.7692 | 1.3245 | 0 | 6.8966 | 3.7736 | 5.7143 |  | 2.8986 | 0 | 3.0216 | 2.0447 |  | RPD | --- | --- | --- | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.0345 | 4.0724 | 0 | 1.1299 | 0 | 3.5088 | 38.0952 | 14.9254 | 2.9851 |  | 13.6364 |  | 25.9542 | 7.4074 |  | 2.381 | 11.0429 |  | 25 | 13.3333 | 11.898 | 11.6279 |  | RPD | --- | --- | --- | --- | 0.095465 | 22.2222 | 0.77519 | 0 | 1.9417 | 4.1431 | 2.2018 | 6.4516 | 50.7042 | 1.9886 | 0 | 0 | 0 | 17.5 | 61.3861 | 76.0563 | 72.7273 | 75.5556 | 68.6621 | 6.0606 | 18.1818 | 28.5714 |  | 8.9552 | 6.4516 |  | 6.8966 | 14.6893 | 18.4615 | 15.7037
[9 empty] | A17 | Primary | 1997-12-17 | 9:30 | 1048 | 3144 | 6288 | 10.09 | 0.65 | 55 | 19.6 | 59 | 37 | 0.2 | 150 | 15.1 | 0.414 | 2.7417 | 13 | 0.65 | 12.35 | 29 | 8.9 | 9 | 860 | 346 | 64.2 | 12.1 | BMRL | 422.3 | 7.6 | 75 | 47 | BMRL | 2.1 | 15 | BMRL | 2.8 | 10 | 131.7 | 146.7 | B8-10 | Primary | 1997-11-12 | 19:19 | 217.8167 | 1306.9 | 10.54 | 0.11 | 24.5 | 0.2 | 6.2 | 0.138 | 2.2258 | 7 | 0.8 | 6.2 | 29 | 8.9 | 9 | 315 | 62 | 41 | 25 | 3.3 | 131.3 | 5 | 22 | 9.6 | BMRL | 7.6 | 14 | 4 | 4.1 | 7.3 | 44.2 | 58.2 | C17-20 | Primary | 1997-12-17 | 9:30 | 1048 | 3144 | 9.91 | 0.17 | 17.1 | 0.2 | 9.5 | 0.246 | 2.5895 | 8 | 0.6 | 7.4 | 29 | 8.9 | 9 | 470 | 162 | 57.2 | 19.8 | BMRL | 239 | 3 | 36 | 23 | BMRL | 3.7 | 14 | BMRL | 3.2 | 9.5 | 65.7 | 79.7
[9 empty] | D3 | Duplicate | 1997-12-17 | 9:30 | 1048 | 3144 | 6288 | 10.09 | 0.65 | 55 | 19.6 | 59 | 37 | 0.2 | 200 | 15 | 0.413 | 2.7533 | 13 | 0.57 | 12.43 | 29 | 8.8 | 9 | 830 | 357 | 63.9 | 11.8 | BMRL | 432.7 | 7.4 | 75 | 46 | BMRL | 2 | 15 | BMRL | 2.3 | 9.7 | 130.4 | 145.4 | D6 | Duplicate | 1997-11-12 | 19:19 | 217.8167 | 1306.9 | 10.41 | 0.13 | 24.15 | 0.2 | 6.1 | 0.139 | 2.2787 | 7.5 | 1.01 | 6.49 | 29 | 8.9 | 9 | 310 | 63 | 42 | 27 | 3.9 | 135.9 | 2.8 | 21 | 11 | BMRL | 7.4 | 14 | BMRL | 4.9 | 8.2 | 42.2 | 56.2 | D9 | Duplicate | 1997-12-17 | 9:30 | 1048 | 3144 | 9.91 | 0.17 | 17.1 | 0.2 | 9.9 | 0.251 | 2.5354 | 8.5 | 0.99 | 7.51 | 29 | 8.8 | 9 | 525 | 174 | 56.5 | 19.1 | 1.1 | 250.7 | 6.2 | 39 | 21 | BMRL | 4.3 | 13 | BMRL | 3.7 | 11 | 70.5 | 83.5
[10 empty] | Average | --- | --- | --- | --- | --- | 10.09 | 0.65 | 55 | 19.6 | 59 | 37 | 0.2 | 175 | 15.05 | 0.4135 | 2.7475 | 13 | 0.61 | 12.39 | 29 | 8.85 | 9 | 845 | 351.5 | 64.05 | 11.95 |  | 427.5 | 7.5 | 75 | 46.5 |  | 2.05 | 15 |  | 2.55 | 9.85 | 131.05 | 146.05 |  | Average | --- | --- | --- | --- | 10.475 | 0.12 | 24.325 | 0.2 | 6.15 | 0.1385 | 2.2522 | 7.25 | 0.905 | 6.345 | 29 | 8.9 | 9 | 312.5 | 62.5 | 41.5 | 26 | 3.6 | 133.6 | 3.9 | 21.5 | 10.3 |  | 7.5 | 14 | 4 | 4.5 | 7.75 | 43.2 | 57.2 |  | Average | --- | --- | --- | --- | 9.91 | 0.17 | 17.1 | 0.2 | 9.7 | 0.2485 | 2.5624 | 8.25 | 0.795 | 7.455 | 29 | 8.85 | 9 | 497.5 | 168 | 56.85 | 19.45 | 1.1 | 244.85 | 4.6 | 37.5 | 22 |  | 4 | 13.5 |  | 3.45 | 10.25 | 68.1 | 81.6
[10 empty] | RPD | --- | --- | --- | --- | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.5714 | 0.66445 | 0.24184 | 0.42262 | 0 | 13.1148 | 0.64568 | 0 | 1.1299 | 0 | 3.5503 | 3.1294 | 0.46838 | 2.5105 |  | 2.4327 | 2.6667 | 0 | 2.1505 |  | 4.878 | 0 |  | 19.6078 | 3.0457 | 0.99199 | 0.89011 |  | RPD | --- | --- | --- | --- | 1.2411 | 16.6667 | 1.4388 | 0 | 1.626 | 0.72202 | 2.348 | 6.8966 | 23.2044 | 4.5705 | 0 | 0 | 0 | 1.6 | 1.6 | 2.4096 | 7.6923 | 16.6667 | 3.4431 | 56.4103 | 4.6512 | 13.5922 |  | 2.6667 | 0 |  | 17.7778 | 11.6129 | 4.6296 | 3.4965 |  | RPD | --- | --- | --- | --- | 0 | 0 | 0 | 0 | 4.1237 | 2.0121 | 2.1121 | 6.0606 | 49.0566 | 1.4755 | 0 | 1.1299 | 0 | 11.0553 | 7.1429 | 1.2313 | 3.599 |  | 4.7784 | 69.5652 | 8 | 9.0909 |  | 15 | 7.4074 |  | 14.4928 | 14.6341 | 7.0485 | 4.6569
[9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [18 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [18 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
Note on L6: Reviewer M.H. (1/24/00): Reviewer changed scale from "pilot" to "full" based on pretreatment diagram in summary report.
Note on AI5: warathbu: Temperatures for the SDS are target values, the first set of corrections said that it was measured, but it is a target temperature.
Note on AI39: warathbu: Temperatures for the SDS are target values, the first set of corrections said that it was measured, but it is a target temperature.
Note on BT5: warathbu: Temperatures for the SDS are target values, the first set of corrections said that it was measured, but it is a target temperature.
Note on BT39: warathbu: Temperatures for the SDS are target values, the first set of corrections said that it was measured, but it is a target temperature.
Note on CY45: M.H. (8/13/99): High RPD results verified. Warthbu: mistype, or error in formula….
Note on DE39: warathbu: Temperatures for the SDS are target values, the first set of corrections said that it was measured, but it is a target temperature.

## Sheet2. 2nd Pilot Study
FIELD-SET 2: RESULTS FROM 2nd PILOT-SCALE STUDY (FILE: gacpilot.xls)
Field 2-1: PWS And Treatment Plant Data |  | Field 2-2: Pilot-Scale GAC Design Parameters |  |  |  | Field 2-3: Pretreatment Used Prior To GAC1 |  |  | Field 2-4: Influent Water Quality For The 10- And 20-Minute, Pilot-Scale GAC Contactors1 | [14 empty] | Field 2-4: Influent Water Quality For The 10- And 20-Minute, Pilot-Scale GAC Contactors (continued) | [15 empty] | Field 2-4: Influent Water Quality For The 10- And 20-Minute, Pilot-Scale GAC Contactors (continued) | [9 empty] | Field 2-5: Effluent Water Quality For The 10-Minute, Pilot-Scale GAC Contactor1 | [16 empty] | Field 2-5: Effluent Water Quality For The 10-Minute, Pilot-Scale GAC Contactor (continued) | [19 empty] | Field 2-6: Effluent Water Quality For The 20-Minute, Pilot-Scale GAC Contactor1 | [16 empty] | Field 2-6: Effluent Water Quality For The 20-Minute, Pilot-Scale GAC Contactor (continued) | [18 empty] | Field 2-7: GAC Cost Parameters
|  | Input Design Parameters |  | US Standard Mesh Sizes |  |  |  |  | Group A, 15 influent samples per run | [40 empty] | Group B, 15 effluent samples per run | [36 empty] | Group C, 15 effluent samples per run
PWS Name | Miami Dade WSD | Carbon manufacturer | Calgon Carbon Manufacturer | US standard | Opening | Process | Description | Scale | Sample | Was sample | Sampling | Sampling | Operation | Bed | Bed | pH | Turbidity | Alkalinity | Temp. | Total | Calcium | Ammonia | Bromide | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS |  | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Cost Parameter | Parameter value
Public Water System Identification Number | PWISD # FL 4130871 | Carbon trade name | Filtrasorb 300 | mesh size | (mm) | Activated Silica | Added to raw water, 1 mg/l | full | ID | duplicated? | date | time | time | volumes | volumes |  |  |  |  | Hardness | Hardness | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 |  | ID | duplicated? | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | Capital Recovery Interest Rate (%) | 5
Water Industry Data Base Number (optional) | NA | Carbon type | Bituminous-based granular activated | 4 | 4.75 | Lime Softening | Added to raw water in softening units, to pH 10.0 | full |  | Y/N | MM/DD/YY | hh:mm | hh.hh | ( 20 minute) | ( 10 minute) | --- | ntu | mg/L as CaCO3 | oC | mg/L as CaCO3 | mg/L as CaCO3 | mg NH3-N / L | mg/L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | Capital Recovery Period (years) | 30
|  | Pilot GAC influent TOC (mg/L) | 15 | 6 | 3.35 | Sedimentation | Within softening units, 17 NTU | pilot | START | --- | 1998-02-06 | 11:25 | 0 | 0 | 0 | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | START | --- | 1998-02-06 | 11:25 | 0 | 0 | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |  | START | --- | 1998-02-06 | 11:25 | 0 | 0 | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | Overhead & Profit Factor (% of construction costs) | 25
Official ICR Contact Person |  | Inner diameter of the pilot GAC column, D (mm) | 76.2 | 8 | 2.36 | pH adjustment | Acid added to reduce the pH of the softened water. Adjusted pH = 7.0 | pilot | A1 | N | 1998-02-06 | 11:30 | 0.083333 | 0.25 | 0.5 | 8.18 | 1.02 | 40 | 20.4 | 95 | 75 | 0.3 | 140 | 13.3 | 0.2695 | 2.0263 | 14 | 0.88 | 13.12 | 29 | 8.8 | 9 | 1170 | 330 | 76 | 22 | 1 | 429 | 11 | 84 | 42 | 1.1 | 4.5 | 20 | BMRL | 4.6 | 13 | 142.6 | 162.6 | B1-10 | N | 1998-02-06 | 11:30 | 0.083333 | 0.5 | 8.14 | 0.8 | 19.5 | 0.3 | 0.6 | 0.0029 | 0.48333 | 3.5 | 0.66 | 2.84 | 29 | 8.9 | 9 | BMRL | BMRL | BMRL | 1.5 | 3.8 | 5.3 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NR | BMRL | BMRL | 0 | 0 | C1-24 | C1-20 | N | 1998-02-06 | 11:30 | 0.083333 | 0.25 | 8.39 | 0.036 | 18.9 | 0.3 | BMRL | 0.0014 |  | 3.5 | 0.92 | 2.58 | 29 | 8.9 | 9 | BMRL | BMRL | BMRL | 1.1 | 1.5 | 2.6 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NR | BMRL | BMRL | 0 | 0 | Special Sitework Factor (% of construction costs) | 5
Mailing Address |  | Manufacturer reported dry bed density, r (kg/m3) | 500 | 10 | 2 | Ozone | ozone added to the pH-adjusted water prior to GAC @ 12 mg/l | pilot | A2 | N | 1998-02-07 | 11:32 | 24.1167 | 72.35 | 144.7 | 7.95 | 1.84 | 40 | 19.3 | 103 | 85 | 0.3 | 150 | 13.1 | 0.242 | 1.8473 | 13 | 0.65 | 12.35 | 29 | 9.1 | 9 | 1180 | 360 | 80 | 20 | BMRL | 460 | 15 | 77 | 34 | 1.7 | 4.6 | 20 | BMRL | 3.9 | 10 | 132.3 | 152.3 | B2-10 | N | 1998-02-07 | 11:32 | 24.1167 | 144.7 | 8.17 | 0.77 | 18 | 0.2 | 0.7 | 0.0032 | 0.45714 | 3.5 | 1.04 | 2.46 | 29 | 8.9 | 9 | BMRL | BMRL | BMRL | 1.5 | 3.3 | 4.8 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NR | BMRL | BMRL | 0 | 0 | C2-48 | C2-20 | N | 1998-02-07 | 11:32 | 24.1167 | 72.35 | 8.26 | 0.034 | 17.4 | 0.2 | 0.6 | 0.0024 | 0.4 | 3 | 0.71 | 2.29 | 29 | 8.9 | 9 | 57 | BMRL | BMRL | BMRL | 2 | 2 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | 0 | Construction Contingencies (% of construction costs) | 10
|  | Pilot GAC mesh size, upper (US standard mesh) | 8 | 12 | 1.68 | Filtration | Dual Media Filtration - Pilot Scale @ 5 gal/min/ft^2. 12" of Sand and 24" of Anthracite | pilot | A3 | Y | 1998-02-08 | 11:32 | 48.1167 | 144.35 | 288.7 | 8.19 | 2.327 | 40 | 20.3 | 102 | 85 | 0.3 | 140 | 12.9 | 0.2337 | 1.8116 | 13 | 0.82 | 12.18 | 29 | 9 | 9 | 960 | 350 | 78 | 22 | 1 | 451 | 13 | 79 | 34 | 1.7 | 4.7 | 21 | BMRL | 4.1 | 10 | 132.4 | 153.4 | B3-10 | Y | 1998-02-08 | 11:32 | 48.1167 | 288.7 | 8.13 | 1.3 | 19.2 | 0.2 | 0.7 | 0.0043 | 0.61429 | 3.5 | 0.73 | 2.77 | 29 | 8.9 | 9 | 34 | BMRL | 1.1 | 3.4 | 8 | 12.5 | BMRL | BMRL | BMRL | BMRL | 1.3 | BMRL | BMRL | BMRL | BMRL | 1.3 | 1.3 | C3-72 I | C3-20 | Y | 1998-02-08 | 11:32 | 48.1167 | 144.35 | 8.07 | 0.057 | 19 | 0.2 | BMRL | 0.0012 |  | 3.5 | 1.04 | 2.46 | 29 | 8.9 | 9 | BMRL | BMRL | BMRL | BMRL | 1.5 | 1.5 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NR | BMRL | BMRL | 0 | 0 | Engineering Fee Factor (% of construction costs) | 15
Phone Number |  | Pilot GAC mesh size, lower (US standard mesh) | 30 | 16 | 1.18 |  |  |  | A4 | N | 1998-02-09 | 11:30 | 72.0833 | 216.25 | 432.5 | 8 | 6.17 | 45 | 20.1 | 94 | 75 | 0.3 | 140 | 13.2 | 0.255 | 1.9318 | 13 | 0.9 | 12.1 | 29 | 9.1 | 9 | 1160 | 380 | 80 | 21 | BMRL | 481 | 16 | 100 | 45 | 1.9 | 4.7 | 21 | BMRL | 4.6 | 13 | 167.6 | 188.6 | B4-10 | N | 1998-02-09 | 11:30 | 72.0833 | 432.5 | 7.79 | 0.23 | 19 | 0.2 | 2.7 | 0.039 | 1.4444 | 4.5 | 0.69 | 3.81 | 29 | 8.9 | 9 | 125 | 8.1 | 17 | 32 | 24 | 81.1 | 2.2 | 3.4 | 1.4 | 1 | 8.6 | 5.5 | BMRL | 2.9 | 2.4 | 16.6 | 22.1 | C4-96 | C4-20 | N | 1998-02-09 | 11:30 | 72.0833 | 216.25 | 7.82 | 0.21 | 18.8 | 0.2 | 0.6 | BMRL |  | 3.5 | 0.86 | 2.64 | 29 | 8.9 | 9 | 25 | BMRL | BMRL | 1.3 | 2.8 | 4.1 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | 0 | 1998 ENR Construction Cost Index (CCI base year 1913) | 5986
FAX Number |  | Flow rate, Q (L/hr) | 29.5 | 20 | 0.85 |  |  |  | A5 | N | 1998-02-10 | 14:21 | 98.9333 | 296.8 | 593.6 | 8.02 | 6.032 | 60 | 23.4 | 103 | 82 | 0.5 | 130 | 10.9 | 0.211 | 1.9358 | 13 | 0.56 | 12.44 | 29 | 8.9 | 9 | 790 | 310 | 76 | 19 | 1 | 406 | 14 | 74 | 33 | 1.6 | 4.5 | 20 | BMRL | 4 | 11 | 127.1 | 147.1 | B5-10 | N | 1998-02-10 | 14:21 | 98.9333 | 593.6 | 7.79 | 0.26 | 23.3 | 0.4 | 3.1 | 0.05 | 1.6129 | 6 | 0.93 | 5.07 | 29 | 8.9 | 9 | 180 | 15 | 24 | 32 | 15 | 86 | BMRL | 6.6 | 1.9 | 1 | 8.4 | 7.1 | BMRL | 2.4 | 7.1 | 17.9 | 25 | C5-121.3 | C5-20 | N | 1998-02-10 | 14:21 | 98.9333 | 296.8 | 7.7 | 0.126 | 23 | 0.4 | BMRL | BMRL |  | 5 | 0.63 | 4.37 | 29 | 8.9 | 9 | 64 | BMRL | BMRL | 1.8 | 4.1 | 5.9 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | 0 | 1998 Producers Price Index (PPI base year 1967 = 100) | 367
E-Mail Address (optional) |  |  |  | 30 | 0.6 |  |  |  | A6 | N | 1998-02-11 | 10:48 | 119.3833 | 358.15 | 716.3 | 8.13 | 3.123 | 35 | 23.9 | 95 | 80 | 0.5 | 140 | 8.5 | 0.132 | 1.5529 | 12.5 | 0.96 | 11.54 | 29 | 8.9 | 9 | 630 | 230 | 73 | 25 | 1.7 | 329.7 | 11 | 60 | 25 | 1.5 | 5.5 | 19 | BMRL | 4.3 | 9.8 | 103 | 122 | B6-10 | N | 1998-02-11 | 10:48 | 119.3833 | 716.3 | 7.68 | 0.36 | 24.2 | 0.4 | 3.6 | 0.054 | 1.5 | 6.5 | 0.54 | 5.96 | 29 | 8.8 | 9 | 180 | 19 | 28 | 34 | 14 | 95 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | 0 | C6-141.7 | C6-20 | N | 1998-02-11 | 10:48 | 119.3833 | 358.15 | 7.67 | 0 | 24.4 | 0.4 | BMRL | BMRL |  | 5 | 0.78 | 4.22 | 29 | 8.8 | 9 | 38 | BMRL | BMRL | 1.7 | 3.1 | 4.8 | 2.8 | 8.6 | 3.2 | 1.1 | 9 | 9 | BMRL | 3.5 | 4.2 | 24.7 | 33.7 | Labor Rate + Fringe ($/work-hour) | 24
|  | Estimated Run Length |  | 40 | 0.425 |  |  |  | A7 | Y | 1998-02-12 | 14:40 | 147.25 | 441.75 | 883.5 | 8.27 | 2.916 | 40 | 25.7 | 130 | 112 | 0.7 | 140 | 6.15 | 0.089 | 1.4472 | 12 | 0.64 | 11.36 | 29 | 8.8 | 9 | 430 | 130 | 60 | 28 | 2.5 | 220.5 | 7.4 | 36 | 15 | 1.3 | 6.4 | 16 | BMRL | 3.7 | 7.4 | 66.1 | 82.1 | B7-10 | Y | 1998-02-12 | 14:40 | 147.25 | 883.5 | 7.66 | 0.27 | 25.5 | 0.7 | 3.9 | 0.059 | 1.5128 | 9 | 0.51 | 8.49 | 29 | 8.7 | 9 | 185 | 27 | 33 | 32 | 9.3 | 101.3 | BMRL | 10 | 3.3 | 1.2 | 7.6 | 8.6 | BMRL | 2.6 | 2.9 | 2.6 | 30.7 | C7-168.6 I | C7-20 | Y | 1998-02-12 | 14:40 | 147.25 | 441.75 | 7.66 | 0.12 | 25.4 | 0.6 | BMRL | BMRL |  | 7.5 | 0.57 | 6.93 | 29 | 8.8 | 9 | 50 | BMRL | BMRL | 1.3 | 3.5 | 4.8 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | 0 | Labor Overhead Factor (% of labor) | 67
Technical ICR Contact Person |  | Bed volumes to 50% TOC breakthrough, BV50 | 642.009 | 50 | 0.3 |  |  |  | A8 | N | 1998-02-13 | 12:00 | 168.5833 | 505.75 | 1011.5 | 8.06 | 13.28 | 50 | 23.3 | 100 | 80 | 0.3 | 150 | 12.2 | 0.2102 | 1.723 | 12.5 | 1 | 11.5 | 29 | 8.9 | 9 | 920 | 340 | 76 | 20 | BMRL | 436 | 11 | 85 | 40 | 1.7 | 4.6 | 21 | BMRL | 4.2 | 12 | 142.3 | 163.3 | B8-10 | N | 1998-02-13 | 12:00 | 168.5833 | 1011.5 | 7.6 | 0.38 | 23.9 | 0.2 | 6.1 | 0.0957 | 1.5689 | 6.5 | 0.7 | 5.8 | 29 | 8.8 | 9 | 350 | 78 | 53 | 37 | 5.2 | 173.2 | 3 | 23 | 9 | BMRL | 7.8 | 13 | BMRL | 4.4 | 6.7 | 42.8 | 55.8 | C8-190.9 | C8-20 | N | 1998-02-13 | 12:00 | 168.5833 | 505.75 | 7.68 | 0.23 | 23.8 | 0.3 | BMRL | 0.0044 |  | 4 | 1.04 | 2.96 | 29 | 9.1 | 9 | 26 | BMRL | 1.7 | 5.2 | 9.1 | 16 | BMRL | BMRL | BMRL | BMRL | 1.9 | BMRL | BMRL | BMRL | BMRL | 1.9 | 1.9 | Electric Rate ($/kW-h) | 0.05
Mailing Address |  | Estimated run length, BVT (= 2 x BV50) | 1284.0179 | 60 | 0.25 |  |  |  | A9 | N | 1998-02-14 | 10:30 | 191.0833 | 573.25 | 1146.5 | 8.07 | 2.85 | 45 | 22.4 | 107 | 87 | 0.3 | 150 | 12.1 | 0.2054 | 1.6975 | 13 | 0.62 | 12.38 | 29 | 8.9 | 9 | 985 | 330 | 78 | 21 | 1.1 | 430.1 | 15 | 81 | 39 | 1.7 | 4.7 | 20 | BMRL | 4.4 | 12 | 141.4 | 161.4 | B9-10 | N | 1998-02-14 | 10:30 | 191.0833 | 1146.5 | 7.68 | 0.03 | 22.7 | 0.3 | 6.1 | 0.0974 | 1.5967 | 6.5 | 0.54 | 5.96 | 29 | 9 | 9 | 325 | 86 | 56 | 36 | 4.9 | 182.9 | 3.5 | 25 | 7.6 | BMRL | 8.2 | 14 | BMRL | 4 | 6 | 44.3 | 58.3 | C9-213.4 | C9-20 | N | 1998-02-14 | 10:30 | 191.0833 | 573.25 | 7.75 | 0.03 | 22.3 | 0.3 | 0.9 | 0.0122 | 1.3556 | 4 | 1.01 | 2.99 | 29 | 9 | 9 | 43 | BMRL | 2.6 | 8.5 | 15 | 26.1 | BMRL | BMRL | BMRL | BMRL | 2.7 | 1.1 | BMRL | BMRL | BMRL | 2.7 | 3.8 | Fuel Oil Rate ($/gal) | 0.95
|  |  |  | 70 | 0.21 |  |  |  | A10 | N | 1998-02-17 | 13:30 | 266.0833 | 798.25 | 1596.5 | 8.12 | 6.43 | 45 | 23.7 | 121 | 102 | 0.2 | 150 | 12.1 | 0.204 | 1.686 | 13 | 1.04 | 11.96 | 29 | 9 | 9 | 990 | 330 | 75 | 21 | 1 | 427 | 12 | 88 | 39 | 1.8 | 4.7 | 21 | BMRL | 4.5 | 12 | 145.5 | 166.5 | B10-10 | N | 1998-02-16 | 13:45 | 242.3333 | 1454 | 7.62 | 0.3 | 25 | 0.2 | 7.5 | 0.12 | 1.6 | 7.5 | 1.02 | 6.48 | 29 | 8.8 | 9 | 435 | 130 | 67 | 38 | 2.9 | 237.9 | 4.8 | 37 | 17 | 1.4 | 7.3 | 16 | BMRL | 4.5 | 8.4 | 67.5 | 83.5 | C10-288.2 | C10-20 | N | 1998-02-17 | 13:30 | 266.0833 | 798.25 | 7.61 | 0.28 | 25.2 | 0.3 | 3.4 | 0.052 | 1.5294 | 4.5 | 0.54 | 3.96 | 29 | 8.9 | 9 | 120 | 9.4 | 20 | 32 | 18 | 79.4 | BMRL | 3.8 | 1.3 | BMRL | 9 | 6 | BMRL | 2.9 | 2.1 | 14.1 | 20.1 | Natural Gas Rate ($/ft3) | 0.0055
Phone Number |  | General Pilot Design Parameters |  | 80 | 0.18 |  |  |  | A11 | N | 1998-02-19 | 13:00 | 313.5833 | 940.75 | 1881.5 | 8.1 | 2.05 | 40 | 23.7 | 95 | 77 | 0.3 | 140 | 11.5 | 0.199 | 1.7304 | 13 | 0.76 | 12.24 | 29 | 8.9 | 9 | 985 | 310 | 78 | 21 | 1.1 | 410.1 | 15 | 75 | 35 | 1.7 | 4.8 | 20 | BMRL | 4.2 | 11 | 131.5 | 151.5 | B11-10 | Y | 1998-02-17 | 13:30 | 266.0833 | 1596.5 | 7.45 | 0.58 | 25.5 | 0.2 | 7.4 | 0.12 | 1.6216 | 7.5 | 1 | 6.5 | 29 | 8.8 | 9 | 480 | 120 | 66 | 37 | 3.6 | 226.6 | 4.6 | 36 | 17 | 1.4 | 7.4 | 16 | BMRL | 4.8 | 8.8 | 66.4 | 82.4 | C11-336.0 | C11-20 | N | 1998-02-19 | 13:00 | 313.5833 | 940.75 | 7.37 | 0.61 | 26.9 | 0.3 | 3.9 | 0.065 | 1.6667 | 5.5 | 0.65 | 4.85 | 29 | 8.8 | 9 | 230 | 19 | 32 | 41 | 15 | 107 | BMRL | 7.2 | 3.3 | 1.3 | 9.4 | 8.7 | BMRL | 3.7 | 3.4 | 21.2 | 29.9 | Current Process Water Rate ($/1000 gal) | 0.2
FAX Number |  | Carbon particle diameter, d (mm) | 1.48 | [5 empty] | A12 | Y | 1998-02-21 | 10:30 | 359.0833 | 1077.25 | 2154.5 | 7.99 | 0.74 | 35 | 22.3 | 95 | 77 | 0.2 | 140 | 11.7 | 0.1891 | 1.6162 | 13 | 1.03 | 11.97 | 29 | 8.9 | 9 | 975 | 330 | 76 | 20 | 1 | 427 | 15 | 80 | 38 | 1.8 | 4.6 | 20 | BMRL | 4.3 | 12 | 139.4 | 159.4 | B12-10 | N | 1998-02-18 | 15:00 | 291.5833 | 1749.5 | 7.68 | 0.82 | 24.6 | 0.2 | 7.3 | 0.123 | 1.6849 | 8 | 0.81 | 7.19 | 29 | 8.9 | 9 | 455 | 150 | 73 | 37 | 3.1 | 263.1 | 5.7 | 37 | 14 | 1.1 | 7.1 | 16 | BMRL | 4.1 | 7.8 | 64.9 | 80.9 | C12-381.5 I | C12-20 | Y | 1998-02-21 | 10:30 | 359.0833 | 1077.25 | 7.55 | 0.52 | 22 | 0.2 | 4.4 | 0.0733 | 1.6659 | 5.5 | 1.03 | 4.47 | 29 | 8.9 | 9 | 220 | 36 | 40 | 40 | 10 | 126 | 2.9 | 12 | 4.2 | 1.2 | 8.9 | 11 | BMRL | 4 | 4.6 | 29.2 | 40.2 | Modifications to Existing Plant (% of construction costs) | 30
E-Mail Address (optional) |  | Column cross-sectional area, A (m2) | 0.0045604 | [5 empty] | A13 | N | 1998-02-24 | 14:00 | 434.5833 | 1303.75 | 2607.5 | 8.02 | 8.75 | 50 | 21.1 | 131 | 110 | 0.2 | 140 | 11.5 | 0.188 | 1.6348 | 13 | 1 | 12 | 29 | 9 | 9 | 1200 | 340 | 76 | 20 | BMRL | 436 | 16 | 94 | 41 | 1.7 | 4.4 | 20 | BMRL | 4.2 | 11 | 157.1 | 177.1 | B13-10 | N | 1998-02-19 | 13:00 | 313.5833 | 1881.5 | 7.52 | 1.31 | 26.2 | 0.3 | 8.1 | 0.134 | 1.6543 | 8.5 | 0.6 | 7.9 | 29 | 8.9 | 9 | 495 | 150 | 66 | 33 | 2.7 | 251.7 | 5 | 39 | 16 | 1.1 | 6.7 | 17 | BMRL | 4.1 | 8.4 | 67.8 | 84.8 | C13-456.9 | C13-20 | N | 1998-02-24 | 14:00 | 434.5833 | 1303.75 | 7.65 | 0.39 | 21.3 | 0.2 | 4.1 | 0.061 | 1.4878 | 5.5 | 1.04 | 4.46 | 29 | 8.9 | 9 | 250 | 33 | 39 | 41 | 12 | 125 | 2.7 | 11 | 3.6 | 1.1 | 8.9 | 11 | BMRL | 3.9 | 4.4 | 27.3 | 38.3
|  | Hydraulic loading rate1, v (m/hr) | 6.4688 |  |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | A14 | N | 1998-02-27 | 14:00 | 506.5833 | 1519.75 | 3039.5 | 7.99 | 6.72 | 60 | 24.6 | 104 | 82 | 0.2 | 150 | 12.5 | 0.2414 | 1.9312 | 14 | 0.99 | 13.01 | 29 | 9 | 9 | 1080 | 340 | 72 | 19 | BMRL | 431 | 14 | 94 | 47 | 1.8 | 4.2 | 21 | BMRL | 4 | 12 | 161 | 182 | B14-10 | N | 1998-02-21 | 10:30 | 359.0833 | 2154.5 | 7.62 | 0.65 | 22.8 | 0.2 | 8.3 | 0.1349 | 1.6253 | 8.5 | 0.92 | 7.58 | 29 | 8.9 | 9 | 595 | 160 | 70 | 30 | 2.5 | 262.5 | 6.6 | 42 | 19 | 1.1 | 6.6 | 18 | BMRL | 4.1 | 9.3 | 75.3 | 93.3 | C14-529.0 | C14-20 | N | 1998-02-27 | 14:00 | 506.5833 | 1519.75 | 7.51 | 0.36 | 26.5 | 0.26 | 7.4 | 0.123 | 1.6622 | 7.5 | 1 | 6.5 | 29 | 8.8 | 9 | 450 | 120 | 65 | 39 | 5.1 | 229.1 | 4.5 | 31 | 11 | 1 | 8.2 | 17 | BMRL | 5 | 8 | 55.7 | 72.7
Plant Name | John E. Preston Water Treatment Plant | 1: If v is not in the range from 5 to 15 m/hr (2 to 6 gpm/ft2) then either Q or D must be adjusted. |  |  |  | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | A15 | N | 1998-03-03 | 13:40 | 602.25 | 1806.75 | 3613.5 | 8.07 | 0.97 | 50 | 21.1 | 101 | 80 | 0.21 | 140 | 13 | 0.223 | 1.7154 | 13 | 0.55 | 12.45 | 29 | 8.8 | 9 | 1100 | 380 | 78 | 19 | BMRL | 477 | 14 | 84 | 38 | 1.2 | 4.4 | 21 | BMRL | 3.6 | 11 | 141.6 | 162.6 | B15-10 | N | 1998-02-24 | 14:00 | 434.5833 | 2607.5 | 7.87 | 0.39 | 21.1 | 0.2 | 7 | 0.11 | 1.5714 | 7.5 | 1.02 | 6.48 | 29 | 8.9 | 9 | 560 | 140 | 68 | 35 | 2.8 | 245.8 | 5.5 | 39 | 14 | 1.2 | 7.1 | 17 | BMRL | 3.8 | 7.1 | 66.8 | 83.8 | C15-624.6 | C15-20 | N | 1998-03-03 | 13:40 | 602.25 | 1806.75 | 7.74 | 0.18 | 21.1 | 0.22 | 9 | 0.148 | 1.6444 | 7 | 0.98 | 6.02 | 29 | 8.8 | 9 | 415 | 110 | 65 | 40 | 5.1 | 220.1 | 5.1 | 29 | 11 | 1 | 8.2 | 15 | BMRL | 4.7 | 7.9 | 54.3 | 69.3
Treatment Plant Category | Ammonia and Chlorine |  |  |  |  | is to list the pretreatment processes used in this particular pilot GAC run. |  |  | A16 | N | 1998-03-06 | 12:40 | 673.25 | 2019.75 | 4039.5 | 8.07 | 0.98 | 85 | 22.9 | 132 | 107 | 0.19 | 150 | 13.9 | 0.2713 | 1.9518 | 13.5 | 0.98 | 12.52 | 29 | 8.9 | 9 | 1190 | 400 | 78 | 20 | BMRL | 498 | 13 | 92 | 42 | 1.1 | 4.4 | 23 | BMRL | 4 | 13 | 152.5 | 175.5 | B16-10 | N | 1998-02-26 | 14:00 | 482.5833 | 2895.5 | 7.58 | 0.26 | 22.9 | 0.22 | 8 | 0.132 | 1.65 | 9 | 1.01 | 7.99 | 29 | 8.7 | 9 | 745 | 200 | 74 | 31 | 2 | 307 | 7.2 | 58 | 23 | 1.5 | 6.3 | 18 | BMRL | 5.1 | 9.2 | 96 | 114 | C16-695.6 | C16-20 | N | 1998-03-06 | 12:40 | 673.25 | 2019.75 | 7.94 | 0.17 | 23.9 | 0.24 | 7 | 0.1089 | 1.5557 | 7 | 0.56 | 6.44 | 29 | 8.9 | 9 | 375 | 110 | 62 | 35 | 4.8 | 211.8 | 4.5 | 28 | 9.4 | 1.2 | 8.8 | 17 | BMRL | 3.5 | 6 | 51.9 | 68.9
Process Train Name | NA | 10-Minute EBCT Run | [6 empty] | A17 | Y | 1998-03-09 | 13:30 | 746.0833 | 2238.25 | 4476.5 | 8.06 | 7.32 | 40 | 20.5 | 141 | 122 | 0.17 | 140 | 11.8 | 0.186 | 1.5763 | 13 | 0.94 | 12.06 | 29 | 8.9 | 9 | 1100 | 360 | 80 | 21 | 1 | 462 | 13 | 79 | 35 | 1.1 | 4.5 | 21 | BMRL | 3.8 | 11 | 132.6 | 153.6 | B17-10 | N | 1998-02-28 | 10:46 | 527.35 | 3164.1 | 7.66 | 0.33 | 26.2 | 0.24 | 7.4 | 0.163 | 2.2027 | 9 | 1.01 | 7.99 | 29 | 8.7 | 9 | 810 | 230 | 77 | 30 | 1.7 | 338.7 | 7.8 | 55 | 24 | BMRL | 6.1 | 19 | BMRL | 4.2 | 9.7 | 92.9 | 111.9 | C17-792.3 | C17-20 | Y | 1998-03-09 | 13:30 | 746.0833 | 2238.25 | 7.73 | 0.17 | 20.2 | 0.23 | 5.8 | 0.085 | 1.4655 | 6.5 | 0.63 | 5.87 | 29 | 8.8 | 9 | 320 | 89 | 56 | 37 | 4.5 | 186.5 | 3.4 | 20 | 6.1 | 1.2 | 8.1 | 13 | BMRL | 3.4 | 4.8 | 38.8 | 51.8
ICR Treatment Plant Identification Number | 301 | Empty bed contact time, EBCT (min) | 10 | [5 empty] | A18 | N | 1998-03-17 | 13:30 | 938.0833 | 2814.25 | 5628.5 | 9.59 | 5.2 | 55 | 22.6 | 138 | 112 | 0.27 | 140 | 10.9 | 0.185 | 1.6972 | 12.5 | 0.77 | 11.73 | 29 | 8.9 | 9 | 810 | NR | 72 | 22 | 1.1 | 95.1 | 11 | 74 | 26 | BMRL | 5.2 | 20 | BMRL | 3.8 | 9.7 | 116.2 | 136.2 | B18-10 | N | 1998-03-03 | 13:40 | 602.25 | 3613.5 | 7.86 | 0.21 | 21.1 | 0.26 | 6.2 | 0.099 | 1.5968 | 9 | 0.7 | 8.3 | 29 | 8.9 | 9 | 685 | 190 | 73 | 30 | 2.1 | 295.1 | 8.5 | 55 | 22 | 1.4 | 6.4 | 19 | BMRL | 4 | 8.6 | 93.3 | 112.3 | C18-961.0 | C18-20 | N | 1998-03-17 | 13:30 | 938.0833 | 2814.25 | 8.1 | 0.28 | 25.1 | 0.34 | 12.6 | 0.204 | 1.619 | 12.5 | 1.05 | 11.45 | 29 | 8.9 | 9 | 605 | 190 | 76 | 32 | 2.2 | 300.2 | 11 | 73 | 31 | 1.6 | 7.8 | 24 | BMRL | 7.2 | 12 | 124.4 | 148.4
PWSID Number of Plant (if assigned) | PWISD # FL 4130871 | Estimated run time, t (days) | 8.9168 | [5 empty] | A19 | N | 1998-03-25 | 13:15 | 1129.8333 | 3389.5 | 6779 | 8.67 | 6.36 | 50 | 22.7 | 130 | 105 | 0.18 | 140 | 12.2 | 0.216 | 1.7705 | 13 | 0.91 | 12.09 | 29 | 8.8 | 9 | 1220 | NR | 55 | 20 | 0.8 | 75.8 | 16 | 100 | 36 | 4.7 | 4.2 | 19 | BMRL | 5.4 | 10 | 160.9 | 179.9 | B19-10 | N | 1998-03-17 | 13:30 | 938.0833 | 5628.5 | 8.29 | 0.47 | 24.6 | 0.39 | 12.4 | 0.225 | 1.8145 | 10.5 | 0.68 | 9.82 | 29 | 8.8 | 9 | 565 | 170 | 68 | 28 | 1.8 | 267.8 | 7.6 | 51 | 20 | BMRL | 6.8 | 20 | BMRL | 4 | 9.4 | 85.4 | 105.4 | C19-1147.0 | C19-20 | N | 1998-03-25 | 13:15 | 1129.8333 | 3389.5 | 8.73 | 0.28 | 24.2 | 0.23 | 11.1 | 0.238 | 2.1441 | 10.5 | 1 | 9.5 | 29 | 8.9 | 9 | 770 | 320 | 77 | 24 | 1.2 | 422.2 | 11 | 99 | 35 | 1.3 | 6.5 | 25 | BMRL | 6.2 | 11 | 152.8 | 177.8
Historical Minimum Water Temperature (oC) | 19 | Pilot column bed length, l (m) | 1.0781
Historical Average Water Temperature (oC) | 24 | Mass GAC required, m (kg) | 2.4583
State Approved Plant Capacity (MGD) | 165
20-Minute EBCT Run
|  | Empty bed contact time, EBCT (min) | 20
|  | Estimated run time, t (days) | 17.8336
|  | Pilot column bed length, l (m) | 2.1563
|  | Mass GAC required, m (kg) | 4.9167 | [5 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [19 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [19 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
[9 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below. | [40 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below. | [36 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below.
[9 empty] | Group D, 3 duplicate influent samples per run | [40 empty] | Group D, 3 duplicate effluent samples per run | [36 empty] | Group D, 3 duplicate effluent samples per run
[9 empty] | Sample | Sample | Sampling | Sampling | Operation | Bed | Bed | pH | Turbidity | Alkalinity | Temp. | Total | Calcium | Ammonia | Bromide | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS |  | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS
[9 empty] | ID | Type | date | time | time | volumes | volumes |  |  |  |  | Hardness | Hardness | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 |  | ID | Type | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6
[11 empty] | MM/DD/YY | hh:mm | hh.hh | ( 20 minute) | ( 10 minute) | --- | ntu | mg/L as CaCO3 | oC | mg/L as CaCO3 | mg/L as CaCO3 | mg NH3-N / L | mg/L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  |  | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L
[9 empty] | A3 | Primary | 1998-02-08 | 11:32 | 48.1167 | 144.35 | 288.7 | 8.19 | 2.33 | 40 | 20.3 | 102 | 85 | 0.3 | 140 | 12.9 | 0.2337 | 1.8116 | 13 | 0.82 | 12.18 | 29 | 9 | 9 | 960 | 360 | 78 | 22 | 1 | 461 | 13 | 79 | 34 | 1.7 | 4.7 | 21 | BMRL | 4.1 | 10 | 132.4 | 153.4 | B3-10 | Primary | 1998-02-08 | 11:32 | 48.1167 | 288.7 | 8.13 | 1.3 | 19.2 | 0.2 | 0.7 | 0.0043 | 0.61429 | 3.5 | 0.73 | 2.77 | 29 | 8.9 | 9 | 34 | BMRL | 1.1 | 3.4 | 8 | 12.5 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | 0 |  | C3-20 | Primary | 1998-02-08 | 11:32 | 48.1167 | 144.35 | 8.07 | 0.06 | 19 | 0.2 | BMRL | 0.0012 |  | 3.5 | 1.04 | 2.46 | 29 | 8.9 | 9 | BMRL | BMRL | BMRL | BMRL | 1.5 | 1.5 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | 0
[9 empty] | D1 | Duplicate | 1998-02-08 | 11:32 | 48.1167 | 144.35 | 288.7 | 8.19 | 2.33 | 40 | 20.3 | 102 | 85 | 0.3 | 140 | 13.1 | 0.2356 | 1.7985 | 13 | 0.99 | 12.01 | 29 | 9 | 9 | 1020 | 370 | 79 | 23 | 1 | 473 | 13 | 100 | 45 | 1.8 | 4.9 | 21 | BMRL | 4.8 | 13 | 164.7 | 185.7 | D4 | Duplicate | 1998-02-08 | 11:32 | 48.1167 | 288.7 | 8.13 | 1.3 | 19.2 | 0.2 | 0.6 | 0.0043 | 0.71667 | 3.5 | 0.73 | 2.77 | 29 | 8.8 | 9 | BMRL | BMRL | 1 | 3.5 | 7.9 | 12.4 | BMRL | BMRL | BMRL | BMRL | 1.2 | BMRL | BMRL | BMRL | BMRL | 1.2 | 1.2 |  | D7 | Duplicate | 1998-02-08 | 11:32 | 48.1167 | 144.35 | 8.07 | 0.06 | 19 | 0.2 | BMRL | 0.0018 |  | 3.5 | 1.03 | 2.47 | 29 | 8.9 | 9 | BMRL | BMRL | BMRL | BMRL | 1.4 | 1.4 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NR | BMRL | BMRL | 0 | 0
[10 empty] | Average | --- | --- | --- | --- | --- | 8.19 | 2.33 | 40 | 20.3 | 102 | 85 | 0.3 | 140 | 13 | 0.23465 | 1.8051 | 13 | 0.905 | 12.095 | 29 | 9 | 9 | 990 | 365 | 78.5 | 22.5 | 1 | 467 | 13 | 89.5 | 39.5 | 1.75 | 4.8 | 21 |  | 4.45 | 11.5 | 148.55 | 169.55 |  | Average | --- | --- | --- | --- | 8.13 | 1.3 | 19.2 | 0.2 | 0.65 | 0.0043 | 0.66548 | 3.5 | 0.73 | 2.77 | 29 | 8.85 | 9 | 34 |  | 1.05 | 3.45 | 7.95 | 12.45 | [9 empty] | 0.6 | 0.6 |  |  | Average | --- | --- | --- | --- | 8.07 | 0.06 | 19 | 0.2 |  | 0.0015 |  | 3.5 | 1.035 | 2.465 | 29 | 8.9 | 9 |  |  |  |  | 1.45 | 1.45 | [9 empty] | 0 | 0
[10 empty] | RPD | --- | --- | --- | --- | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5385 | 0.80972 | 0.72877 | 0 | 18.7845 | 1.4055 | 0 | 0 | 0 | 6.0606 | 2.7397 | 1.2739 | 4.4444 | 0 | 2.5696 | 0 | 23.4637 | 27.8481 | 5.7143 | 4.1667 | 0 |  | 15.7303 | 26.087 | 21.7435 | 19.0504 |  | RPD | --- | --- | --- | --- | 0 | 0 | 0 | 0 | 15.3846 | 0 | 15.3846 | 0 | 0 | 0 | 0 | 1.1299 | 0 |  |  | 9.5238 | 2.8986 | 1.2579 | 0.80321 | [9 empty] | 200 | 200 |  |  | RPD | --- | --- | --- | --- | 0 | 0 | 0 | 0 |  | 40 |  | 0 | 0.96618 | 0.40568 | 0 | 0 | 0 |  |  |  |  | 6.8966 | 6.8966
[9 empty] | A7 | Primary | 1998-02-12 | 14:40 | 147.25 | 441.75 | 883.5 | 8.27 | 2.92 | 40 | 25.7 | 130 | 112 | 0.7 | 140 | 6.15 | 0.089 | 1.4472 | 12 | 0.64 | 11.36 | 29 | 8.8 | 9 | 430 | 130 | 60 | 28 | 2.5 | 220.5 | 7.4 | 36 | 15 | 1.3 | 6.4 | 16 | BMRL | 3.7 | 7.4 | 66.1 | 82.1 | B7-10 | Primary | 1998-02-12 | 14:40 | 147.25 | 883.5 | 7.66 | 0.27 | 25.5 | 0.7 | 3.9 | NR | NR | 9 | 0.51 | 8.49 | 29 | 8.7 | 9 | 185 | 27 | 33 | 32 | 9.3 | 101.3 | BMRL | 10 | 3.3 | 1.2 | 7.6 | 8.6 | BMRL | 2.6 | 2.9 | 22.1 | 30.7 |  | C7-20 | Primary | 1998-02-12 | 14:40 | 147.25 | 441.75 | 7.66 | 0.12 | 25.4 | 0.6 | BMRL | NR | NR | 7.5 | 0.57 | 6.93 | 29 | 8.8 | 9 | 50 | BMRL | BMRL | 1.3 | 3.5 | 4.8 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | 0
[9 empty] | D2 | Duplicate | 1998-02-12 | 14:40 | 147.25 | 441.75 | 883.5 | 8.26 | 2.912 | 40 | 25.6 | 138 | 120 | 0.7 | 140 | 5.8 | 0.09 | 1.5517 | 12 | 1.04 | 10.96 | 29 | 8.8 | 9 | 445 | 120 | 59 | 28 | 3.1 | 210.1 | 5.5 | 34 | 16 | 1.3 | 6.1 | 15 | BMRL | 3.9 | 8 | 62.9 | 77.9 | D5 | Duplicate | 1998-02-12 | 14:40 | 147.25 | 883.5 | 7.69 | 0.25 | 25.4 | 0.7 | 3.7 | NR | NR | 9.5 | 1.03 | 8.47 | 29 | 8.9 | 9 | 235 | 22 | 30 | 33 | 9.2 | 94.2 | BMRL | 11 | 6.4 | 1 | 6.8 | 9.3 | BMRL | 4.8 | 6.8 | 25.2 | 34.5 |  | D8 | Duplicate | 1998-02-12 | 14:40 | 147.25 | 441.75 | 7.71 | 0.14 | 25.3 | 0.7 | BMRL | NR | NR | 7.5 | 0.89 | 6.61 | 29 | 8.8 | 9 | 30 | BMRL | BMRL | 2.1 | 3.5 | 5.6 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | 0
[10 empty] | Average | --- | --- | --- | --- | --- | 8.265 | 2.916 | 40 | 25.65 | 134 | 116 | 0.7 | 140 | 5.975 | 0.0895 | 1.4994 | 12 | 0.84 | 11.16 | 29 | 8.8 | 9 | 437.5 | 125 | 59.5 | 28 | 2.8 | 215.3 | 6.45 | 35 | 15.5 | 1.3 | 6.25 | 15.5 |  | 3.8 | 7.7 | 64.5 | 80 |  | Average | --- | --- | --- | --- | 7.675 | 0.26 | 25.45 | 0.7 | 3.8 | NR | NR | 9.25 | 0.77 | 8.48 | 29 | 8.8 | 9 | 210 | 24.5 | 31.5 | 32.5 | 9.25 | 97.75 |  | 10.5 | 4.85 | 1.1 | 7.2 | 8.95 |  | 3.7 | 4.85 | 23.65 | 32.6 |  |  | Average | --- | --- | --- | --- | 7.685 | 0.13 | 25.35 | 0.65 |  | NR | NR | 7.5 | 0.73 | 6.77 | 29 | 8.8 | 9 | 40 |  |  | 1.7 | 3.5 | 5.2 | [9 empty] | 0 | 0
[10 empty] | RPD | --- | --- | --- | --- | --- | 0.12099 | 0.27435 | 0 | 0.38986 | 5.9701 | 6.8966 | 0 | 0 | 5.8577 | 1.1173 | 6.9739 | 0 | 47.619 | 3.5842 | 0 | 0 | 0 | 3.4286 | 8 | 1.6807 | 0 | 21.4286 | 4.8305 | 29.4574 | 5.7143 | 6.4516 | 0 | 4.8 | 6.4516 |  | 5.2632 | 7.7922 | 4.9612 | 5.25 |  | RPD | --- | --- | --- | --- | 0.39088 | 7.6923 | 0.39293 | 0 | 5.2632 |  |  | 5.4054 | 67.5325 | 0.23585 | 0 | 2.2727 | 0 | 23.8095 | 20.4082 | 9.5238 | 3.0769 | 1.0811 | 7.2634 |  | 9.5238 |  | 18.1818 | 11.1111 | 7.8212 |  | 59.4595 | 80.4124 | 13.1078 | 11.6564 |  |  | RPD | --- | --- | --- | --- | 0.65062 | 15.3846 | 0.39448 | 15.3846 |  |  |  | 0 | 43.8356 | 4.7267 | 0 | 0 | 0 | 50 |  |  | 47.0588 | 0 | 15.3846
[9 empty] | A12 | Primary | 1998-02-21 | 10:30 | 359.0833 | 1077.25 | 2154.5 | 7.99 | 0.74 | 35 | 22.3 | 95 | 77 | 0.2 | 140 | 11.7 | 0.1891 | 1.6162 | 13 | 1.03 | 11.97 | 29 | 8.9 | 9 | 975 | 330 | 76 | 20 | 1 | 427 | 15 | 80 | 38 | 1.8 | 4.6 | 20 | BMRL | 4.3 | 12 | 139.4 | 159.4 | B11-10 | Primary | 1998-02-17 | 13:30 | 266.0833 | 1596.5 | 7.45 | 0.58 | 25.5 | 0.2 | 7.4 | 0.12 | 1.6216 | 7.5 | 1 | 6.5 | 29 | 8.8 | 9 | 480 | 120 | 66 | 37 | 3.6 | 226.6 | 4.6 | 36 | 17 | 1.4 | 7.4 | 16 | BMRL | 4.8 | 8.8 | 66.4 | 82.4 |  | C12-20 | Primary | 1998-02-21 | 10:30 | 359.0833 | 1077.25 | 7.55 | 0.52 | 22 | 0.2 | 4.4 | 0.0733 | 1.6659 | 5.5 | 1.03 | 4.47 | 29 | 8.9 | 9 | 220 | 36 | 40 | 40 | 10 | 126 | 2.9 | 12 | 4.2 | 1.2 | 8.9 | 11 | BMRL | 4 | 4.6 | 29.2 | 40.2
[9 empty] | D3 | Duplicate | 1998-02-21 | 10:30 | 359.0833 | 1077.25 | 2154.5 | 8 | 0.69 | 35 | 22.3 | 95 | 77 | 0.2 | 140 | 12 | 0.1908 | 1.59 | 13 | 1.04 | 11.96 | 29 | 9 | 9 | 910 | 340 | 75 | 21 | BMRL | 436 | 14 | 86 | 39 | 1.7 | 4.6 | 20 | BMRL | 4.3 | 12 | 145.3 | 165.3 | D6 | Duplicate | 1998-02-17 | 13:30 | 266.0833 | 1596.5 | 7.59 | 0.43 | 25.6 | 0.2 | 7.2 | 0.121 | 1.6806 | 7.5 | 0.78 | 6.72 | 29 | 8.9 | 9 | 450 | 130 | 71 | 36 | 3.5 | 240.5 | 5.3 | 35 | 13 | 1.3 | 7.4 | 16 | BMRL | 4.4 | 7.9 | 62 | 78 |  | D9 | Duplicate | 1998-02-21 | 10:30 | 359.0833 | 1077.25 | 7.55 | 0.49 | 22 | 0.2 | 4.6 | 0.073 | 1.587 | 5.5 | 1 | 4.5 | 29 | 8.9 | 9 | 210 | 36 | 42 | 40 | 10 | 128 | 2.6 | 12 | 4.3 | 1.1 | 8.8 | 11 | BMRL | 4 | 4.7 | 28.8 | 39.8
[10 empty] | Average | --- | --- | --- | --- | --- | 7.995 | 0.715 | 35 | 22.3 | 95 | 77 | 0.2 | 140 | 11.85 | 0.18995 | 1.6031 | 13 | 1.035 | 11.965 | 29 | 8.95 | 9 | 942.5 | 335 | 75.5 | 20.5 | 1 | 431.5 | 14.5 | 83 | 38.5 | 1.75 | 4.6 | 20 |  | 4.3 | 12 | 142.35 | 162.35 |  | Average | --- | --- | --- | --- | 7.52 | 0.505 | 25.55 | 0.2 | 7.3 | 0.1205 | 1.6511 | 7.5 | 0.89 | 6.61 | 29 | 8.85 | 9 | 465 | 125 | 68.5 | 36.5 | 3.55 | 233.55 | 4.95 | 35.5 | 15 | 1.35 | 7.4 | 16 |  | 4.6 | 8.35 | 64.2 | 80.2 |  |  | Average | --- | --- | --- | --- | 7.55 | 0.505 | 22 | 0.2 | 4.5 | 0.07315 | 1.6264 | 5.5 | 1.015 | 4.485 | 29 | 8.9 | 9 | 215 | 36 | 41 | 40 | 10 | 127 | 2.75 | 12 | 4.25 | 1.15 | 8.85 | 11 |  | 4 | 4.65 | 29 | 40
[10 empty] | RPD | --- | --- | --- | --- | --- | 0.12508 | 6.993 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5316 | 0.89497 | 1.6368 | 0 | 0.96618 | 0.083577 | 0 | 1.1173 | 0 | 6.8966 | 2.9851 | 1.3245 | 4.878 | #VALUE! | 2.0857 | 6.8966 | 7.2289 | 2.5974 | 5.7143 | 0 | 0 |  | 0 | 0 | 4.1447 | 3.6341 |  | RPD | --- | --- | --- | --- | 1.8617 | 29.703 | 0.39139 | 0 | 2.7397 | 0.82988 | 3.5694 | 0 | 24.7191 | 3.3283 | 0 | 1.1299 | 0 | 6.4516 | 8 | 7.2993 | 2.7397 | 2.8169 | 5.9516 | 14.1414 | 2.8169 | 26.6667 | 7.4074 | 0 | 0 |  | 8.6957 | 10.7784 | 6.8536 | 5.4863 |  |  | RPD | --- | --- | --- | --- | 0 | 5.9406 | 0 | 0 | 4.4444 | 0.41012 | 4.8543 | 0 | 2.9557 | 0.6689 | 0 | 0 | 0 | 4.6512 | 0 | 4.878 | 0 | 0 | 1.5748 | 10.9091 | 0 | 2.3529 | 8.6957 | 1.1299 | 0 |  | 0 | 2.1505 | 1.3793 | 1
[9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [19 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [19 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
Note on L6: Reviewer M.H. (1/24/00): Reviewer changed scale from "pilot" to "full" based on pretreatment diagram in summary report.
Note on AA14: M.H. (8/13/99): The dip observed in all influent curves (and the corresponding spike in ammonia) was explained by the consultant to be: "...a change in influent water quality due to a changing to the inner well field, which contains significantly better water quality than the ones used to supply the WTP."
Note on AA15: M.H. (8/13/99): The dip observed in all influent curves (and the corresponding spike in ammonia) was explained by the consultant to be: "...a change in influent water quality due to a changing to the inner well field, which contains significantly better water quality than the ones used to supply the WTP."
Note on AC14: M.H. (8/13/99): The dip observed in all influent curves (and the corresponding spike in ammonia) was explained by the consultant to be: "...a change in influent water quality due to a changing to the inner well field, which contains significantly better water quality than the ones used to supply the WTP."
Note on AC15: M.H. (8/13/99): The dip observed in all influent curves (and the corresponding spike in ammonia) was explained by the consultant to be: "...a change in influent water quality due to a changing to the inner well field, which contains significantly better water quality than the ones used to supply the WTP."
Note on AD14: M.H. (8/13/99): The dip observed in all influent curves (and the corresponding spike in ammonia) was explained by the consultant to be: "...a change in influent water quality due to a changing to the inner well field, which contains significantly better water quality than the ones used to supply the WTP."
Note on AD15: M.H. (8/13/99): The dip observed in all influent curves (and the corresponding spike in ammonia) was explained by the consultant to be: "...a change in influent water quality due to a changing to the inner well field, which contains significantly better water quality than the ones used to supply the WTP."
Note on AI5: warathbu: Temperatures for the SDS are target values, the first set of corrections said that it was measured, but it is a target temperature.
Note on AI39: warathbu: Temperatures for the SDS are target values, the first set of corrections said that it was measured, but it is a target temperature.
Note on AL14: M.H. (8/13/99): The dip observed in all influent curves (and the corresponding spike in ammonia) was explained by the consultant to be: "...a change in influent water quality due to a changing to the inner well field, which contains significantly better water quality than the ones used to supply the WTP."
Note on AL15: M.H. (8/13/99): The dip observed in all influent curves (and the corresponding spike in ammonia) was explained by the consultant to be: "...a change in influent water quality due to a changing to the inner well field, which contains significantly better water quality than the ones used to supply the WTP."
Note on AM14: M.H. (8/13/99): The dip observed in all influent curves (and the corresponding spike in ammonia) was explained by the consultant to be: "...a change in influent water quality due to a changing to the inner well field, which contains significantly better water quality than the ones used to supply the WTP."
Note on AM15: M.H. (8/13/99): The dip observed in all influent curves (and the corresponding spike in ammonia) was explained by the consultant to be: "...a change in influent water quality due to a changing to the inner well field, which contains significantly better water quality than the ones used to supply the WTP."
Note on AN14: M.H. (8/13/99): The dip observed in all influent curves (and the corresponding spike in ammonia) was explained by the consultant to be: "...a change in influent water quality due to a changing to the inner well field, which contains significantly better water quality than the ones used to supply the WTP."
Note on AN15: M.H. (8/13/99): The dip observed in all influent curves (and the corresponding spike in ammonia) was explained by the consultant to be: "...a change in influent water quality due to a changing to the inner well field, which contains significantly better water quality than the ones used to supply the WTP."
Note on AO14: M.H. (8/13/99): The dip observed in all influent curves (and the corresponding spike in ammonia) was explained by the consultant to be: "...a change in influent water quality due to a changing to the inner well field, which contains significantly better water quality than the ones used to supply the WTP."
Note on AO15: M.H. (8/13/99): The dip observed in all influent curves (and the corresponding spike in ammonia) was explained by the consultant to be: "...a change in influent water quality due to a changing to the inner well field, which contains significantly better water quality than the ones used to supply the WTP."
Note on AP14: M.H. (8/13/99): The dip observed in all influent curves (and the corresponding spike in ammonia) was explained by the consultant to be: "...a change in influent water quality due to a changing to the inner well field, which contains significantly better water quality than the ones used to supply the WTP."
Note on AP15: M.H. (8/13/99): The dip observed in all influent curves (and the corresponding spike in ammonia) was explained by the consultant to be: "...a change in influent water quality due to a changing to the inner well field, which contains significantly better water quality than the ones used to supply the WTP."
Note on AQ14: M.H. (8/13/99): The dip observed in all influent curves (and the corresponding spike in ammonia) was explained by the consultant to be: "...a change in influent water quality due to a changing to the inner well field, which contains significantly better water quality than the ones used to supply the WTP."
Note on AQ15: M.H. (8/13/99): The dip observed in all influent curves (and the corresponding spike in ammonia) was explained by the consultant to be: "...a change in influent water quality due to a changing to the inner well field, which contains significantly better water quality than the ones used to supply the WTP."
Note on AR14: M.H. (8/13/99): The dip observed in all influent curves (and the corresponding spike in ammonia) was explained by the consultant to be: "...a change in influent water quality due to a changing to the inner well field, which contains significantly better water quality than the ones used to supply the WTP."
Note on AR15: M.H. (8/13/99): The dip observed in all influent curves (and the corresponding spike in ammonia) was explained by the consultant to be: "...a change in influent water quality due to a changing to the inner well field, which contains significantly better water quality than the ones used to supply the WTP."
Note on AS14: M.H. (8/13/99): The dip observed in all influent curves (and the corresponding spike in ammonia) was explained by the consultant to be: "...a change in influent water quality due to a changing to the inner well field, which contains significantly better water quality than the ones used to supply the WTP."
Note on AS15: M.H. (8/13/99): The dip observed in all influent curves (and the corresponding spike in ammonia) was explained by the consultant to be: "...a change in influent water quality due to a changing to the inner well field, which contains significantly better water quality than the ones used to supply the WTP."
Note on AT14: M.H. (8/13/99): The dip observed in all influent curves (and the corresponding spike in ammonia) was explained by the consultant to be: "...a change in influent water quality due to a changing to the inner well field, which contains significantly better water quality than the ones used to supply the WTP."
Note on AT15: M.H. (8/13/99): The dip observed in all influent curves (and the corresponding spike in ammonia) was explained by the consultant to be: "...a change in influent water quality due to a changing to the inner well field, which contains significantly better water quality than the ones used to supply the WTP."
Note on AU14: M.H. (8/13/99): The dip observed in all influent curves (and the corresponding spike in ammonia) was explained by the consultant to be: "...a change in influent water quality due to a changing to the inner well field, which contains significantly better water quality than the ones used to supply the WTP."
Note on AU15: M.H. (8/13/99): The dip observed in all influent curves (and the corresponding spike in ammonia) was explained by the consultant to be: "...a change in influent water quality due to a changing to the inner well field, which contains significantly better water quality than the ones used to supply the WTP."
Note on AV14: M.H. (8/13/99): The dip observed in all influent curves (and the corresponding spike in ammonia) was explained by the consultant to be: "...a change in influent water quality due to a changing to the inner well field, which contains significantly better water quality than the ones used to supply the WTP."
Note on AV15: M.H. (8/13/99): The dip observed in all influent curves (and the corresponding spike in ammonia) was explained by the consultant to be: "...a change in influent water quality due to a changing to the inner well field, which contains significantly better water quality than the ones used to supply the WTP."
Note on AW14: M.H. (8/13/99): The dip observed in all influent curves (and the corresponding spike in ammonia) was explained by the consultant to be: "...a change in influent water quality due to a changing to the inner well field, which contains significantly better water quality than the ones used to supply the WTP."
Note on AW15: M.H. (8/13/99): The dip observed in all influent curves (and the corresponding spike in ammonia) was explained by the consultant to be: "...a change in influent water quality due to a changing to the inner well field, which contains significantly better water quality than the ones used to supply the WTP."
Note on AX14: M.H. (8/13/99): The dip observed in all influent curves (and the corresponding spike in ammonia) was explained by the consultant to be: "...a change in influent water quality due to a changing to the inner well field, which contains significantly better water quality than the ones used to supply the WTP."
Note on AX15: M.H. (8/13/99): The dip observed in all influent curves (and the corresponding spike in ammonia) was explained by the consultant to be: "...a change in influent water quality due to a changing to the inner well field, which contains significantly better water quality than the ones used to supply the WTP."
Note on AY14: M.H. (8/13/99): The dip observed in all influent curves (and the corresponding spike in ammonia) was explained by the consultant to be: "...a change in influent water quality due to a changing to the inner well field, which contains significantly better water quality than the ones used to supply the WTP."
Note on AY15: M.H. (8/13/99): The dip observed in all influent curves (and the corresponding spike in ammonia) was explained by the consultant to be: "...a change in influent water quality due to a changing to the inner well field, which contains significantly better water quality than the ones used to supply the WTP."
Note on AZ14: M.H. (8/13/99): The dip observed in all influent curves (and the corresponding spike in ammonia) was explained by the consultant to be: "...a change in influent water quality due to a changing to the inner well field, which contains significantly better water quality than the ones used to supply the WTP."
Note on AZ15: M.H. (8/13/99): The dip observed in all influent curves (and the corresponding spike in ammonia) was explained by the consultant to be: "...a change in influent water quality due to a changing to the inner well field, which contains significantly better water quality than the ones used to supply the WTP."
Note on BA14: M.H. (8/13/99): The dip observed in all influent curves (and the corresponding spike in ammonia) was explained by the consultant to be: "...a change in influent water quality due to a changing to the inner well field, which contains significantly better water quality than the ones used to supply the WTP."
Note on BA15: M.H. (8/13/99): The dip observed in all influent curves (and the corresponding spike in ammonia) was explained by the consultant to be: "...a change in influent water quality due to a changing to the inner well field, which contains significantly better water quality than the ones used to supply the WTP."
Note on BB14: M.H. (8/13/99): The dip observed in all influent curves (and the corresponding spike in ammonia) was explained by the consultant to be: "...a change in influent water quality due to a changing to the inner well field, which contains significantly better water quality than the ones used to supply the WTP."
Note on BB15: M.H. (8/13/99): The dip observed in all influent curves (and the corresponding spike in ammonia) was explained by the consultant to be: "...a change in influent water quality due to a changing to the inner well field, which contains significantly better water quality than the ones used to supply the WTP."
Note on BT5: warathbu: Temperatures for the SDS are target values, the first set of corrections said that it was measured, but it is a target temperature.
Note on BT39: warathbu: Temperatures for the SDS are target values, the first set of corrections said that it was measured, but it is a target temperature.
Note on CE46: warathbu: modified from 3..3 to 3.3
Note on DE5: warathbu: Temperatures for the SDS are target values, the first set of corrections said that it was measured, but it is a target temperature.
Note on DE39: warathbu: Temperatures for the SDS are target values, the first set of corrections said that it was measured, but it is a target temperature.