## Sheet1. 1st Quarter
FIELD-SET 1: 1st QUARTER RSSCT RESULTS (FILE: gacrssct.xls)
Field 1-1: PWS And Treatment Plant Data |  | Field 1-2: Full-Scale GAC Characteristics1 |  | Field 1-3: RSSCT Design Parameters |  |  |  | Field 1-4: Pretreatment Used Prior To GAC1 |  |  | Field 1-5: GAC Influent Water Quality For The 10-Minute EBCT Run | [6 empty] | Field 1-6: GAC Influent Water Quality For The 20-Minute EBCT Run1 | [6 empty] | Field 1-7: GAC Effluent Water Quality For The 10-Minute EBCT Run1 | [15 empty] | Field 1-7: GAC Effluent Water Quality For The 10-Minute EBCT Run (continued) | [17 empty] | Field 1-8: GAC Effluent Water Quality For The 20-Minute EBCT Run1 | [14 empty] | Field 1-8: GAC Effluent Water Quality For The 20-Minute EBCT Run (continued) | [18 empty] | Field 1-9: GAC Cost Parameters
|  |  |  | Input Design Parameters |  | US Standard Mesh Sizes | [18 empty] | Group C, 12 effluent samples per run | [33 empty] | Group C, 12 effluent samples per run
PWS Name | East Bay Municipal Utility District | Carbon manufacturer | Calgon | RSSCT influent TOC (mg/L) | 3 | US standard | Opening | Process | Description | Scale | 10-min. EBCT Start Date | 1998-04-08 | [5 empty] | 20-min. EBCT Start Date | 1998-04-08 | [5 empty] | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Cost Parameter | Parameter value
Public Water System Identification Number | CA0110005 | Carbon trade name | Filtrasorb 300 | Inner diameter of the RSSCT column, DSC (mm) | 15 | mesh size | (mm) | Coagulation | Alum (Al2(SO4)3.14H2O) 27.5 mg/L, Cationic Polymer 1 mg/L | Full-Scale | 10-min. EBCT Start Time | 13:05 | [5 empty] | 20-min. EBCT Start Time | 13:05 | [5 empty] | ID | duplicated? | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | Capital Recovery Interest Rate (%) | 5.5
Water Industry Data Base Number (optional) | NA | Carbon type | bituminous | Minimum RSSCT Reynolds number, ReSC, min | 0.5 | 4 | 4.75 | Flocculation | 4-stage, Detention Time = 53 minutes | Full-Scale | [15 empty] | Y/N | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | Capital Recovery Period (years) | 30
|  | Original GAC mesh size, upper (US standard mesh) | 8 | Full-scale operating temperature, ToC (oC) | 13.7 | 6 | 3.35 | Sedimentation | Conventional, Detention Time = 104 minutes | Full-Scale | Group A, 2 samples per batch | [6 empty] | Group A, 2 samples per batch | [6 empty] | C1-10 | N | 1998-04-08 | 14:05 | 1 | 78.9333 | 8.05 | 15 | 0.2 | BMRL | #VALUE! | 1.4 | 0.83 | 0.57 | 14.3 | 8.34 | 93 | NA | 0.29 | 1.1 | 1.3 | 0.34 | 3.03 | BMRL | BMRL | 0.44 | BMRL | 0.31 | 0.31 | NA | NA | NA | 0.75 | 1.06 | C1-20 | N | 1998-04-08 | 14:05 | 1 | 39.4667 | 8.92 | 15 | 0.1 | BMRL | #VALUE! | 1.8 | 1.5 | 0.3 | 14.4 | 8.3 | 93 | NR | 0.27 | 0.13 | 0.59 | 0.47 | 1.46 | BMRL | BMRL | BMRL | BMRL | 0.14 | 0.14 | NA | NA | NA | 0.14 | 0.28 | Overhead & Profit Factor (% of construction costs) | 15
Official ICR Contact Person |  | Original GAC mesh size, lower (US standard mesh) | 30 | Full-scale bed porosity, eLC | 0.45 | 8 | 2.36 | Ozonation | Dose = 1.2 mg/L | Full-Scale | Parameter | Units | Sample A1-10 | Sample A2-10 | Average | RPD |  | Parameter | Units | Sample A1-20 | Sample A2-20 | Average | RPD |  | C2-10 | N | 1998-04-09 | 6:00 | 16.9167 | 1335.2889 | 7.6 | 15.4 | 0.2 | BMRL | #VALUE! | 1.4 | 0.71 | 0.69 | 14.3 | 8.32 | 93 | 83 | 0.85 | 0.17 | 0.71 | 0.47 | 2.2 | BMRL | BMRL | 0.45 | BMRL | 0.42 | 0.45 | NA | NA | NA | 0.87 | 1.32 | C2-20 | N | 1998-04-09 | 17:00 | 27.9167 | 1101.7778 | 7.7 | 15.7 | 0.2 | BMRL | #VALUE! | 1.8 | 1.46 | 0.34 | 14.8 | 8.4 | 93 | NR | 0.33 | 0.24 | 0.7 | 0.28 | 1.55 | BMRL | BMRL | 0.51 | BMRL | 0.55 | 0.23 | NA | NA | NA | 1.06 | 1.29 | Special Sitework Factor (% of construction costs) | 20
Mailing Address |  | Original carbon particle diameter, dLC (mm) | 1.48 | Measured RSSCT dry bed density, rSC (g/cm3) | 0.5 | 10 | 2 | Filtration | GAC/Sand, GAC Depth = 18 inch, Sand Depth = 12 inch, Effective Size = 0.80-1.0 mm, UC = 1.8 , SG = 1.65, EBCT = 3.6 minutes (for GAC only), Length of GAC in Service = 9 years | Full-Scale | Sampling date | MM/DD/YY | 1998-04-08 | 1998-04-16 | --- | --- |  | Sampling date | MM/DD/YY | 1998-04-08 | 1998-04-16 | --- | --- |  | C3-10 | N | 1998-04-09 | 17:00 | 27.9167 | 2203.5556 | 7.6 | 15.6 | 0.2 | BMRL | #VALUE! | 1.4 | 0.8 | 0.6 | 14.3 | 8.32 | 93 | NA | 0.37 | 0.17 | 0.89 | 0.3 | 1.73 | BMRL | 0.15 | 0.7 | BMRL | 0.71 | 0.54 | NA | NA | NA | 1.56 | 2.1 | C3-20 | N | 1998-04-10 | 18:00 | 52.9167 | 2088.4444 | 7.5 | 16 | 0.1 | BMRL | #VALUE! | 1.8 | 1.51 | 0.29 | 14.8 | 8.5 | 93 | NR | 0.39 | 0.3 | 0.89 | 0.3 | 1.88 | BMRL | BMRL | 0.48 | BMRL | 0.59 | 0.29 | NA | NA | NA | 1.07 | 1.36 | Construction Contingencies (% of construction costs) | 15
|  | 1: These are the characteristics before the carbon is ground for RSSCT experiments. |  | RSSCT GAC mesh size, upper (US standard mesh) | 100 | 12 | 1.68 | Prefiltration | 1um - Polypropylene Cartridge Filter | Bench-Scale | Sampling time | hh:mm | 13:05 | 8:30 | --- | --- |  | Sampling time | hh:mm | 13:05 | 8:30 | --- | --- |  | C4-10 | Y | 1998-04-10 | 7:30 | 42.4167 | 3348.0889 | 7.6 | 15.2 | 0.2 | BMRL | #VALUE! | 1.1 | 0.455 | 0.645 | 14.55 | 8.405 | 93 | 6.2 | 0.285 | 0.34 | 1.3 | 0.84 | 1.525 | BMRL | 0.19 | 0.42 | BMRL | 0.19 | 0.57 | NA | NA | NA | 0.4 | 0.685 | C4-20 | N | 1998-04-11 | 18:00 | 76.9167 | 3035.6444 | 7.43 | 14.5 | BMRL | BMRL | #VALUE! | 1.2 | 0.77 | 0.43 | 14.4 | 8.4 | 93 | BMRL | 0.32 | 0.17 | 0.65 | 0.32 | 1.46 | BMRL | BMRL | BMRL | BMRL | BMRL | 0.12 | NA | NA | NA | 0 | 0.12 | Engineering Fee Factor (% of construction costs) | 15
Phone Number |  |  |  | RSSCT GAC mesh size, lower (US standard mesh) | 200 | 16 | 1.18 |  |  |  | Operation time | hh.hh | 0 | 187.4167 | --- | --- |  | Operation time | hh.hh | 0 | 187.4167 | --- | --- |  | C5-10 | N | 1998-04-10 | 18:00 | 52.9167 | 4176.8889 | 7.7 | 14.4 | 0.3 | 0.004 | 1.3333 | 1.4 | 0.76 | 0.64 | 14.4 | 8.45 | 93 | 59 | 0.53 | 1 | 3.4 | 2 | 6.93 | BMRL | 0.49 | 0.48 | BMRL | 1.4 | 1.1 | NA | NA | NA | 2.37 | 3.47 | C5-20 | N | 1998-04-12 | 19:00 | 101.9167 | 4022.3111 | 7.61 | 14.2 | 0.34 | BMRL | #VALUE! | 1.2 | 0.6 | 0.6 | 14.4 | 8.4 | 93 | BMRL | 0.24 | 0.2 | 1.2 | 0.79 | 2.43 | BMRL | BMRL | BMRL | BMRL | 0.67 | 0.27 | NA | NA | NA | 0.67 | 0.94 | 1998 ENR Construction Cost Index (CCI base year 1913) | 5921
FAX Number | [5 empty] | 20 | 0.85 |  |  |  | Bed volumes | (10 minutes) | 0 | 14793.4222 | --- | --- |  | Bed volumes | (20 minutes) | 0 | 7396.7111 | --- | --- |  | C6-10 | N | 1998-04-11 | 6:00 | 64.9167 | 5124.0889 | 7.6 | 14.5 | 0.5 | 0.004 | 0.8 | 1.15 | 0.46 | 0.69 | 14.7 | 8.26 | 93 | NA | 1 | 2.6 | 6.4 | 3.4 | 13.4 | BMRL | 0.91 | 0.92 | BMRL | 2 | 1.5 | NA | NA | NA | 3.83 | 5.33 | C6-20 | N | 1998-04-13 | 20:00 | 126.9167 | 5008.9778 | 7.35 | 15.2 | 0.4 | BMRL | #VALUE! | 2 | 1.48 | 0.52 | 15.3 | 8.6 | 116 | NA | 0.6 | 1.4 | 3.4 | 1.6 | 7 | BMRL | 0.23 | 0.24 | BMRL | 1 | 0.82 | NA | NA | NA | 1.47 | 2.29 | 1998 Producers Price Index (PPI base year 1967 = 100) | 366
E-Mail Address (optional) |  |  |  | Estimated Run Length |  | 30 | 0.6 |  |  |  | Alkalinity | mg/L as CaCO3 | 80 | 78 | 79 | 2.5316 |  | Alkalinity | mg/L as CaCO3 | 80 | 78 | 79 | 2.5316 |  | C7-10 | N | 1998-04-11 | 17:00 | 75.9167 | 5992.3556 | 7.42 | 14.3 | 0.8 | 0.009 | 1.125 | 1.3 | 0.59 | 0.71 | 14.3 | 8.56 | 93 | 63 | 3.2 | 6.1 | 9.4 | 2.8 | 21.5 | BMRL | 1.9 | 0.89 | BMRL | 2.5 | 2.3 | NA | NA | NA | 5.29 | 7.59 | C7-20 | N | 1998-04-14 | 21:30 | 152.4167 | 6015.3778 | 7.6 | 14.6 | 0.62 | 0.004 | 0.64516 | 1.8 | 1.09 | 0.71 | 14.7 | 8.4 | 106 | NR | 1.5 | 4.2 | 8.1 | 3.3 | 17.1 | BMRL | 1.4 | 0.47 | BMRL | 1.8 | 1.8 | NA | NA | NA | 3.67 | 5.47 | Labor Rate + Fringe ($/work-hour) | 38
|  |  |  | Bed volumes to 50% TOC breakthrough, BV50 | 5202.3804 | 40 | 0.425 |  |  |  | Total hardness | mg/L as CaCO3 | 110 | 120 | 115 | 8.6957 |  | Total hardness | mg/L as CaCO3 | 110 | 120 | 115 | 8.6957 |  | C8-10 | N | 1998-04-12 | 7:15 | 90.1667 | 7117.1556 | 7.8 | 14.3 | 1.1 | 0.012 | 1.0909 | 1.8 | 0.98 | 0.82 | 14.8 | 8.6 | 93 | NR | 8.8 | 9.8 | 11 | 2 | 31.6 | BMRL | 4.8 | 2.5 | BMRL | 3.4 | 4.1 | NA | NA | NA | 10.7 | 14.8 | C8-20 | N | 1998-04-15 | 7:30 | 162.4167 | 6410.0444 | 7.5 | 16.9 | 0.75 | 0.005 | 0.66667 | 2 | 1.19 | 0.81 | 14.6 | 8.3 | 97 | NR | 2.7 | 5.5 | 8.7 | 2.5 | 19.4 | BMRL | 2.1 | 1.1 | BMRL | 2.4 | 2.8 | NA | NA | NA | 5.6 | 8.4 | Labor Overhead Factor (% of labor) | 20
Technical ICR Contact Person |  |  |  | Estimated run length, BVT ( = 2 x BV50) | 10404.7608 | 50 | 0.3 |  |  |  | Calcium hardness | mg/L as CaCO3 | 70 | 69.2 | 69.6 | 1.1494 |  | Calcium hardness | mg/L as CaCO3 | 70 | 69.2 | 69.6 | 1.1494 |  | C9-10 | N | 1998-04-13 | 7:20 | 114.25 | 9018.1333 | 7.5 | 14.8 | 1.6 | 0.02 | 1.25 | 1.4 | 0.26 | 1.14 | 14.4 | 8.5 | 93 | NR | 12 | 9.1 | 7.9 | 1.4 | 30.4 | BMRL | 5.6 | 3.3 | BMRL | 2.8 | 4.2 | NA | NA | NA | 11.7 | 15.9 | C9-20 | Y | 1998-04-17 | 8:30 | 211.4167 | 8343.9111 | 7.3 | 14.6 | 1.2 | 0.0125 | 1.0417 | 2.1 | 1.25 | 0.85 | 15.55 | 8.4 | 101 | NR | 8.35 | 9.55 | 10.5 | 1.85 | 30.25 | BMRL | 3.9 | 2.5 | 0.16 | 2.5 | 3.45 | NA | NA | NA | 8.98 | 12.43 | Electric Rate ($/kW-h) | 0.065
Mailing Address |  |  |  | BVT + 30% safety factor, BVT+30% ( = 2.6 x BV50) | 13526.189 | 60 | 0.25 |  |  |  | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! |  | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! |  | C10-10 | Y | 1998-04-14 | 8:30 | 139.4167 | 11004.6222 | 7.75 | 14.6 | 1.75 | 0.028 | 1.5964 | 2.2 | 0.945 | 1.255 | 14.4 | 8.3 | 104 | NA | 19.5 | 13.5 | 8.85 | 0.84 | 42.69 | BMRL | 8.7 | 6.3 | BMRL | 1.6 | 4.6 | NA | NA | NA | 16.6 | 21.2 | C10-20 | N | 1998-04-19 | 8:30 | 259.4167 | 10238.3111 | 7.5 | 14.3 | 1.3 | 0.017 | 1.3077 | 2.2 | 1.15 | 1.05 | 15.5 | 8.7 | 97 | NR | 17 | 13 | 11 | 1.8 | 42.8 | BMRL | 5.5 | 2.8 | BMRL | 2.3 | 3.9 | NA | NA | NA | 10.6 | 14.5 | Fuel Oil Rate ($/gal) | 0.58
[6 empty] | 70 | 0.21 |  |  |  | Bromide | mg/L | NR | 45 | 45 | #VALUE! |  | Bromide | mg/L | NR | 45 | 45 | #VALUE! |  | C11-10 | N | 1998-04-15 | 7:30 | 162.4167 | 12820.0889 | 7.43 | 16.4 | 1.8 | 0.027 | 1.5 | 2 | 0.6 | 1.4 | 15.3 | 8.18 | 96 | NR | 18 | 13 | 8.7 | 0.8 | 40.5 | NR | 8.6 | NR | BMRL | 1.9 | 8.6 | NA | NA | NA | NR | NR | C11-20 | Y | 1998-04-21 | 8:30 | 307.4167 | 12132.7111 | 7.515 | 14.3 | 1.5 | 0.022 | 1.4667 | 1.9 | 0.82 | 1.08 | 15.5 | 8.5 | 98 | NR | 19 | 12 | 9.95 | 1.1 | 42.05 | 1.7 | 7.55 | 4.45 | 0.66 | 3 | 4.5 | NA | NA | NA | 16.51 | 21.01 | Natural Gas Rate ($/ft3) | 0.006
Phone Number |  |  |  | General RSSCT Design Parameters |  | 80 | 0.18 | [17 empty] | C12-10 | Y | 1998-04-16 | 8:30 | 187.4167 | 14793.4222 | 7.395 | 14.4 | 1.95 | 0.0305 | 1.5645 | 2 | 0.13 | 1.87 | 14.8 | 8.295 | 96 | NR | 18 | 11 | 8.3 | 0.775 | 38.075 | BMRL | 8.4 | 5.9 | BMRL | 2.35 | 5 | NA | NA | NA | 12.45 | 17.45 | C12-20 | Y | 1998-04-23 | 8:30 | 355.4167 | 14027.1111 | 7.44 | 14.85 | 1.6 | 0.02 | 1.25 | 2 | 0.755 | 1.245 | 15.55 | 8.5 | 97 | NR | 21 | 13 | 9.55 | 1.02 | 44.57 | 1.9 | 7.95 | 5 | 0.4 | 2.55 | 4.35 | NA | NA | NA | 16.85 | 21.2 | Current Process Water Rate ($/1000 gal) | 0.14
FAX Number |  |  |  | Kinematic viscosity at ToC, nLC (m2/s) | 1.2015e-06 | 100 | 0.15 |  |  |  | Group B, 3 samples per batch | [6 empty] | Group B, 3 samples per batch | [74 empty] | Modifications to Existing Plant (% of construction costs) | 25
E-Mail Address (optional) |  |  |  | RSSCT carbon particle diameter, dSC (mm) | 0.1125 | 120 | 0.125 |  |  |  | Parameter | Units | Sample B1-10 | Sample B2-10 | Sample B3-10 | Average | %SD | Parameter | Units | Sample B1-20 | Sample B2-20 | Sample B3-20 | Average | %SD
|  |  |  | Scaling factor, SF | 13.1556 | 140 | 0.106 | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | Sampling date | MM/DD/YY | 1998-04-08 | 1998-04-12 | 1998-04-16 | --- | --- | Sampling date | MM/DD/YY | 1998-04-08 | 1998-04-12 | 1998-04-27 | --- | ---
Plant Name | Upper San Leandro |  |  | RSSCT hydraulic loading rate, vSC (m/hr) | 8.6511 | 170 | 0.088 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | Sampling time | hh:mm | 14:05 | 8:15 | 10:30 | --- | --- | Sampling time | hh:mm | 14:05 | 8:15 | 9:45 | --- | ---
Treatment Plant Category | Conventional with Ozone |  |  | RSSCT flow rate, QSC (mL/min) | 25.4796 | 200 | 0.075 | is to list the pretreatment processes used in this particular RSSCT run. |  |  | Operation time | hh.hh | 1 | 91.1667 | 189.4167 | --- | --- | Operation time | hh.hh | 1 | 91.1667 | 452.6667 | --- | ---
Process Train Name | NA |  |  | Estimated total influent volume required, VSCT (L) | 785.9228 | 230 | 0.062 |  |  |  | Bed volumes | (10 minute) | 78.9333 | 7196.0889 | 14951.2889 | --- | --- | Bed volumes | (20 minute) | 39.4667 | 3598.0444 | 17865.2444 | --- | --- | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
ICR Treatment Plant Identification Number | 139 |  |  |  |  | 270 | 0.053 |  |  |  | pH | --- | 7.16 | 7.6 | 7.3 | 7.3533 | 3.0571 | pH | --- | 7.16 | 7.6 | 7.3 | 7.3533 | 3.0571 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
PWSID Number of Plant (if assigned) | CA0110005 |  |  | 10-Minute EBCT Run |  | 325 | 0.044 |  |  |  | Turbidity | ntu | 0.1 | 0.15 | 0.07 | 0.10667 | 37.8886 | Turbidity | ntu | 0.1 | 0.15 | 0.07 | 0.10667 | 37.8886 | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below. | [33 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below.
Historical Minimum Water Temperature (oC) | 8 |  |  | Full-scale empty bed contact time, EBCTLC (min) | 10 | 400 | 0.037 |  |  |  | Temperature | oC | 14.1 | 13.6 | 14.1 | 13.9333 | 2.0718 | Temperature | oC | 14.1 | 13.6 | 14.1 | 13.9333 | 2.0718
Historical Average Water Temperature (oC) | 14 |  |  | Estimated full-scale run time, tLCT (days) | 93.9319 | [5 empty] | Total organic carbon | mg/L | 3 | 3.1 | 3.7 | 3.2667 | 11.5896 | Total organic carbon | mg/L | 3 | 3.1 | 3.1 | 3.0667 | 1.8827 | Group D, 3 duplicate effluent samples per run (results from primary and duplicate analyses) | [33 empty] | Group D, 3 duplicate effluent samples per run (results from primary and duplicate analyses)
State Approved Plant Capacity (MGD) | 55 |  |  | RSSCT empty bed contact time, EBCTSC (min) | 0.76014 | [5 empty] | UV254 | cm-1 | 0.05 | 0.057 | 0.054 | 0.053667 | 6.5439 | UV254 | cm-1 | 0.05 | 0.057 | 0.059 | 0.055333 | 8.5406 | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS
|  |  |  | Estimated RSSCT run time, tSCT (days) | 7.1401 | [5 empty] | SUVA | L/(mg*m) | 1.6667 | 1.8387 | 1.4595 | 1.6549 | 11.4745 | SUVA | L/(mg*m) | 1.6667 | 1.8387 | 1.9032 | 1.8029 | 6.7828 | ID | Type | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6
|  |  |  | RSSCT bed length, lSC (cm) | 10.96 | [5 empty] | SDS-Cl2 dose | mg/L | 3 | 3 | 1.6 | 2.5333 | 31.9062 | SDS-Cl2 dose | mg/L | 3 | 3 | 3.3 | 3.1 | 5.5873 |  |  | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L
|  |  |  | Estimated volume required for 10-minute EBCT, VSC (L) | 261.9743 | [5 empty] | SDS-Free Cl2 residual | mg/L | 0.57 | 0.51 | 0.13 | 0.40333 | 59.1588 | SDS-Free Cl2 residual | mg/L | 0.57 | 0.51 | 0.76 | 0.61333 | 21.2791 | C4-10 | Primary | 1998-04-10 | 7:30 | 42.4167 | 3348.0889 | 7.6 | 15.2 | 0.2 | BMRL | #VALUE! | 1.4 | 0.81 | 0.59 | 14.4 | 8.41 | 93 | NA | 0.27 | 0.34 | 1.3 | 0.84 | 2.75 | BMRL | 0.19 | 0.42 | BMRL | 0.19 | 0.57 | NA | NA | NA | 0.8 | 1.37 | C9-20 | Primary | 1998-04-17 | 8:30 | 211.4167 | 8343.9111 | 7.3 | 14.6 | 1.2 | 0.013 | 1.0833 | 2 | 1 | 1 | 15.8 | 8.2 | 96 | NR | 7 | 9.2 | 10 | 1.7 | 27.9 | BMRL | 3.8 | 2.8 | BMRL | 3 | 3.6 | NA | NA | NA | 9.6 | 13.2
|  |  |  | Mass GAC required, mSC (g) | 9.684 | [5 empty] | SDS-Cl2 demand | mg/L | 2.43 | 2.49 | 1.47 | 2.13 | 26.8715 | SDS-Cl2 demand | mg/L | 2.43 | 2.49 | 2.54 | 2.4867 | 2.2148 | D4-10 | Duplicate | 1998-04-10 | 7:30 | 42.4167 | 3348.0889 | 7.6 | 15.2 | 0.2 | BMRL | #VALUE! | 0.8 | 0.1 | 0.7 | 14.7 | 8.4 | 93 | 6.2 | 0.3 | BMRL | BMRL | BMRL | 0.3 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | D9-20 | Duplicate | 1998-04-17 | 9:30 | 212.4167 | 8383.3778 | 7.3 | 14.6 | 1.2 | 0.012 | 1 | 2.2 | 1.5 | 0.7 | 15.3 | 8.6 | 106 | NR | 9.7 | 9.9 | 11 | 2 | 32.6 | BMRL | 4 | 2.2 | 0.16 | 2 | 3.3 | NA | NA | NA | 8.36 | 11.66
[11 empty] | SDS-Chlorination temp. | oC | 14.6 | 14.6 | 14.6 | 14.6 | 0 | SDS-Chlorination temp. | oC | 14.6 | 14.6 | 16.3 | 15.1667 | 6.4714 | Avg-C4-10 | Average | --- | --- | --- | --- | 7.6 | 15.2 | 0.2 | #DIV/0! | #VALUE! | 1.1 | 0.455 | 0.645 | 14.55 | 8.405 | 93 | 6.2 | 0.285 | 0.34 | 1.3 | 0.84 | 1.525 | #DIV/0! | 0.19 | 0.42 | #DIV/0! | 0.19 | 0.57 | #DIV/0! | #DIV/0! | #DIV/0! | 0.4 | 0.685 | Avg-C7-20 | Average | --- | --- | --- | --- | 7.3 | 14.6 | 1.2 | 0.0125 | 1.0417 | 2.1 | 1.25 | 0.85 | 15.55 | 8.4 | 101 | #DIV/0! | 8.35 | 9.55 | 10.5 | 1.85 | 30.25 | #DIV/0! | 3.9 | 2.5 | 0.16 | 2.5 | 3.45 | #DIV/0! | #DIV/0! | #DIV/0! | 8.98 | 12.43
|  |  |  | 20-Minute EBCT Run | [6 empty] | SDS-Chlorination pH | --- | 8.2 | 8.4 | NA | 8.3 | 1.7039 | SDS-Chlorination pH | --- | 8.2 | 8.4 | 8.42 | 8.34 | 1.4587 | RPD-C4-10 | RPD | --- | --- | --- | --- | 0 | 0 | 0 | #VALUE! | #VALUE! | 54.5455 | 156.044 | 17.0543 | 2.0619 | 0.11898 | 0 | #VALUE! | 10.5263 | #VALUE! | #VALUE! | #VALUE! | 160.6557 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 200 | 200 | RPD-C7-20 | RPD | --- | --- | --- | --- | 0 | 0 | 0 | 8 | 8 | 9.5238 | 40 | 35.2941 | 3.2154 | 4.7619 | 9.901 | #VALUE! | 32.3353 | 7.3298 | 9.5238 | 16.2162 | 15.5372 | #VALUE! | 5.1282 | 24 | #VALUE! | 40 | 8.6957 | #VALUE! | #VALUE! | #VALUE! | 13.8085 | 12.3894
|  |  |  | Full-scale empty bed contact time, EBCTLC (min) | 20 | [5 empty] | SDS-Incubation time | hours | 96 | 96 | NA | 96 | 0 | SDS-Incubation time | hours | 96 | 96 | 96 | 96 | 0 | C10-10 | Primary | 1998-04-14 | 8:30 | 139.4167 | 11004.6222 | 7.8 | 14.6 | 1.8 | 0.031 | 1.7222 | 2.2 | 0.95 | 1.25 | 14.4 | 8.3 | 104 | NA | 20 | 14 | 9.6 | 0.89 | 44.49 | BMRL | 8.3 | 5.9 | BMRL | 1.4 | 4.4 | NA | NA | NA | 15.6 | 20 | C11-20 | Primary | 1998-04-21 | 8:30 | 307.4167 | 12132.7111 | 7.5 | 14.3 | 1.5 | 0.022 | 1.4667 | 2 | 0.86 | 1.14 | 15.5 | 8.6 | 98 | NR | 21 | 12 | 10 | 1.2 | 44.2 | BMRL | 7.8 | 3.5 | 0.88 | 3.2 | 4.7 | NA | NA | NA | 15.38 | 20.08
|  |  |  | Estimated full-scale run time, tLCT (days) | 187.8637 | [5 empty] | SDS-TOX | mg Cl- /L | 270 | 270 | NA | 270 | 0 | SDS-TOX | mg Cl- /L | 270 | 270 | 180 | 240 | 21.6506 | D10-10 | Duplicate | 1998-04-14 | 9:30 | 140.4167 | 11083.5556 | 7.7 | 14.6 | 1.7 | 0.025 | 1.4706 | 2.2 | 0.94 | 1.26 | 14.4 | 8.3 | 104 | NA | 19 | 13 | 8.1 | 0.79 | 40.89 | BMRL | 9.1 | 6.7 | BMRL | 1.8 | 4.8 | NA | NA | NA | 17.6 | 22.4 | D11-20 | Duplicate | 1998-04-21 | 9:30 | 308.4167 | 12172.1778 | 7.53 | 14.3 | 1.5 | 0.022 | 1.4667 | 1.8 | 0.78 | 1.02 | 15.5 | 8.4 | 98 | NR | 17 | 12 | 9.9 | 1 | 39.9 | 1.7 | 7.3 | 5.4 | 0.44 | 2.8 | 4.3 | NA | NA | NA | 17.64 | 21.94
|  |  |  | RSSCT empty bed contact time, EBCTSC (min) | 1.5203 | [5 empty] | SDS-CHCl3 | mg/L | 54 | 58 | NA | 56 | 5.0508 | SDS-CHCl3 | mg/L | 54 | 58 | 58 | 56.6667 | 4.0754 | Avg-C10-10 | Average | --- | --- | --- | --- | 7.75 | 14.6 | 1.75 | 0.028 | 1.5964 | 2.2 | 0.945 | 1.255 | 14.4 | 8.3 | 104 | #DIV/0! | 19.5 | 13.5 | 8.85 | 0.84 | 42.69 | #DIV/0! | 8.7 | 6.3 | #DIV/0! | 1.6 | 4.6 | #DIV/0! | #DIV/0! | #DIV/0! | 16.6 | 21.2 | Avg-C11-20 | Average | --- | --- | --- | --- | 7.515 | 14.3 | 1.5 | 0.022 | 1.4667 | 1.9 | 0.82 | 1.08 | 15.5 | 8.5 | 98 | #DIV/0! | 19 | 12 | 9.95 | 1.1 | 42.05 | 1.7 | 7.55 | 4.45 | 0.66 | 3 | 4.5 | #DIV/0! | #DIV/0! | #DIV/0! | 16.51 | 21.01
|  |  |  | Estimated RSSCT run time, tSCT (days) | 14.2802 | [5 empty] | SDS-BDCM | mg/L | 17 | 18 | NA | 17.5 | 4.0406 | SDS-BDCM | mg/L | 17 | 18 | 6.5 | 13.8333 | 46.0518 | RPD-C10-10 | RPD | --- | --- | --- | --- | 1.2903 | 0 | 5.7143 | 21.4286 | 15.7625 | 0 | 1.0582 | 0.79681 | 0 | 0 | 0 | #VALUE! | 5.1282 | 7.4074 | 16.9492 | 11.9048 | 8.4329 | #VALUE! | 9.1954 | 12.6984 | #VALUE! | 25 | 8.6957 | #VALUE! | #VALUE! | #VALUE! | 12.0482 | 11.3208 | RPD-C11-20 | RPD | --- | --- | --- | --- | 0.3992 | 0 | 0 | 0 | 0 | 10.5263 | 9.7561 | 11.1111 | 0 | 2.3529 | 0 | #VALUE! | 21.0526 | 0 | 1.005 | 18.1818 | 10.2259 | #VALUE! | 6.6225 | 42.6966 | 66.6667 | 13.3333 | 8.8889 | #VALUE! | #VALUE! | #VALUE! | 13.6887 | 8.8529
|  |  |  | RSSCT bed length, lSC (cm) | 21.92 | [5 empty] | SDS-DBCM | mg/L | 7 | 6.7 | NA | 6.85 | 3.0968 | SDS-DBCM | mg/L | 7 | 6.7 | 18 | 10.5667 | 60.9388 | C12-10 | Primary | 1998-04-16 | 8:30 | 187.4167 | 14793.4222 | 7.4 | 14.3 | 1.9 | 0.03 | 1.5789 | 2 | 0.13 | 1.87 | 14.6 | 8.31 | 96 | NR | 19 | 12 | 8.3 | 0.86 | 40.16 | BMRL | 8.4 | 9 | BMRL | 2.9 | 5.6 | NA | NA | NA | 20.3 | 25.9 | C12-20 | Primary | 1998-04-23 | 8:30 | 355.4167 | 14027.1111 | 7.44 | 15 | 1.6 | 0.021 | 1.3125 | 2 | 0.75 | 1.25 | 15.5 | 8.5 | 97 | NR | 22 | 14 | 10 | 1.1 | 47.1 | 1.9 | 8 | 5.2 | 0.3 | 2.6 | 4.3 | NA | NA | NA | 18 | 22.3
|  |  |  | Estimated volume required for 20-minute EBCT, VSC (L) | 523.9485 | [5 empty] | SDS-CHBr3 | mg/L | 0.31 | 0.4 | NA | 0.355 | 17.9267 | SDS-CHBr3 | mg/L | 0.31 | 0.4 | 0.24 | 0.31667 | 25.3289 | D12-10 | Duplicate | 1998-04-16 | 10:30 | 189.4167 | 14951.2889 | 7.39 | 14.5 | 2 | 0.031 | 1.55 | 2 | 0.13 | 1.87 | 15 | 8.28 | 96 | NR | 17 | 10 | 8.3 | 0.69 | 35.99 | BMRL | BMRL | 2.8 | BMRL | 1.8 | 4.4 | NA | NA | NA | 4.6 | 9 | D12-20 | Duplicate | 1998-04-23 | 9:30 | 356.4167 | 14066.5778 | 7.44 | 14.7 | 1.6 | 0.019 | 1.1875 | 2 | 0.76 | 1.24 | 15.6 | 8.5 | 97 | NR | 20 | 12 | 9.1 | 0.94 | 42.04 | BMRL | 7.9 | 4.8 | 0.5 | 2.5 | 4.4 | NA | NA | NA | 15.7 | 20.1
|  |  |  | Mass GAC required, mSC (g) | 19.3679 | [5 empty] | SDS-THM4 | mg/L | 78.31 | 83.1 | NA | 80.705 | 4.1968 | SDS-THM4 | mg/L | 78.31 | 83.1 | 82.74 | 81.3833 | 3.2779 | Avg-C12-10 | Average | --- | --- | --- | --- | 7.395 | 14.4 | 1.95 | 0.0305 | 1.5645 | 2 | 0.13 | 1.87 | 14.8 | 8.295 | 96 | #DIV/0! | 18 | 11 | 8.3 | 0.775 | 38.075 | #DIV/0! | 8.4 | 5.9 | #DIV/0! | 2.35 | 5 | #DIV/0! | #DIV/0! | #DIV/0! | 12.45 | 17.45 | Avg-C12-20 | Average | --- | --- | --- | --- | 7.44 | 14.85 | 1.6 | 0.02 | 1.25 | 2 | 0.755 | 1.245 | 15.55 | 8.5 | 97 | #DIV/0! | 21 | 13 | 9.55 | 1.02 | 44.57 | 1.9 | 7.95 | 5 | 0.4 | 2.55 | 4.35 | #DIV/0! | #DIV/0! | #DIV/0! | 16.85 | 21.2
[11 empty] | SDS-MCAA* | mg/L | 3.1 | 0.34 | NA | 1.72 | 113.466 | SDS-MCAA* | mg/L | 3.1 | 0.34 | BMRL | 1.72 | 113.466 | RPD-C12-10 | RPD | --- | --- | --- | --- | 0.13523 | 1.3889 | 5.1282 | 3.2787 | 1.8503 | 0 | 0 | 0 | 2.7027 | 0.36166 | 0 | #VALUE! | 11.1111 | 18.1818 | 0 | 21.9355 | 10.9521 | #VALUE! | #VALUE! | 105.0847 | #VALUE! | 46.8085 | 24 | #VALUE! | #VALUE! | #VALUE! | 126.1044 | 96.8481 | RPD-C12-20 | RPD | --- | --- | --- | --- | 0 | 2.0202 | 0 | 10 | 10 | 0 | 1.3245 | 0.80321 | 0.64309 | 0 | 0 | #VALUE! | 9.5238 | 15.3846 | 9.4241 | 15.6863 | 11.3529 | #VALUE! | 1.2579 | 8 | 50 | 3.9216 | 2.2989 | #VALUE! | #VALUE! | #VALUE! | 13.6499 | 10.3774
[11 empty] | SDS-DCAA* | mg/L | 19 | 18 | NA | 18.5 | 3.8222 | SDS-DCAA* | mg/L | 19 | 18 | 19 | 18.6667 | 3.0929 | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[11 empty] | SDS-TCAA* | mg/L | 15 | 12 | NA | 13.5 | 15.7135 | SDS-TCAA* | mg/L | 15 | 12 | 8.9 | 11.9667 | 25.4886 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
[11 empty] | SDS-MBAA* | mg/L | 0.32 | 0.24 | NA | 0.28 | 20.2031 | SDS-MBAA* | mg/L | 0.32 | 0.24 | BMRL | 0.28 | 20.2031
[11 empty] | SDS-DBAA* | mg/L | 1.6 | 1.6 | NA | 1.6 | 0 | SDS-DBAA* | mg/L | 1.6 | 1.6 | 1 | 1.4 | 24.7436
[11 empty] | SDS-BCAA* | mg/L | 6.2 | 5.8 | NA | 6 | 4.714 | SDS-BCAA* | mg/L | 6.2 | 5.8 | 5 | 5.6667 | 10.7825
[11 empty] | SDS-TBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0!
[11 empty] | SDS-CDBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0!
[11 empty] | SDS-DCBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0!
[11 empty] | SDS-HAA5 | mg/L | 39.02 | 32.18 | NA | 35.6 | 13.586 | SDS-HAA5 | mg/L | 39.02 | 32.18 | 28.9 | 33.3667 | 15.4744
[11 empty] | SDS-HAA6 | mg/L | 45.22 | 37.98 | NA | 41.6 | 12.3064 | SDS-HAA6 | mg/L | 45.22 | 37.98 | 33.9 | 39.0333 | 14.6875
[11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [6 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [6 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
Note on N9: Reviewer M.H. (10/25/99): Per utility, "No samples were collected for THM, HAA, TOX."
Note on T32: Chlorine dose was corrected. This is the same dose as B2-20.
Note on AB32: Chlorine dose is the same as B2-10
Note on AC38: asheikho: Value of this sample has been verified
Note on AG29: Duplicate samples were collected in two different bottles, one right after another. They were not collected in the same bottle. This was done to reduce probability of contamination and loss of any VOCs such as chloroform.
Note on AG37: As our original data sheets indicate Cl2 dose, pH, and temp were not switched.
Note on AJ37: Duplicate samples were collected in two different bottles, one right after another. They were not collected in the same bottle. This was done to reduce probability of contamination and loss of any VOCs such as chloroform.
Note on AO5: This test was done based on the estimated breathrough run, so it was terminated before reaching 70% goal. On-site TOC monitoring was avaiable but it had calibration problem during this round of testing and could not been relied upon.
Note on AR36: asheikho: High variability of chlorine dose is verified
Note on AS36: asheikho: High variability of chlorine dose is verified
Note on AZ36: asheikho: High variability of these samples has been verified
Note on BA36: asheikho: High variability of these samples has been verified
Note on BB36: asheikho: High variability of these samples has been verified
Note on BC36: asheikho: High variability of these samples has been verified
Note on BD18: Outlier.
Note on BF18: Outlier.
Note on BF44: asheikho: High variability of this sample has been verified
Note on BH44: asheikho: High variability of these samples has been verified
Note on BI44: asheikho: High variability of this sample has been verified
Note on BM36: asheikho: High variability of these samples has been verified
Note on BM44: asheikho: High variability of this sample has been verified
Note on BN36: asheikho: High variability of these samples has been verified
Note on BN44: asheikho: High variability of this sample has been verified
Note on BP33: pH duplicate typo was corrected.
Note on BX5: This test was done based on the estimated breathrough run, so it was terminated before reaching 70% goal. On-site TOC monitoring was avaiable but it had calibration problem during this round of testing and could not been relied upon.
Note on CA17: Samples #10 & 11 were verfied and they were not switched.
Note on CB36: asheikho: Verfied
Note on CB40: asheikho: Verified.
Note on CC36: asheikho: Verified
Note on CF13: High incubation time is correct
Note on CF14: High incubation time is correct
Note on CH36: asheikho: Verified.
Note on CO36: asheikho: verified.
Note on CO40: asheikho: Verified.
Note on CP40: asheikho: Verified.
Note on CP44: asheikho: Verified.
Note on CQ36: asheikho: verified

## Sheet2. 2nd Quarter
FIELD-SET 2: 2nd QUARTER RSSCT RESULTS (FILE: gacrssct.xls)
Field 2-1: PWS And Treatment Plant Data |  | Field 2-2: Full-Scale GAC Characteristics1 |  | Field 2-3: RSSCT Design Parameters |  |  |  | Field 2-4: Pretreatment Used Prior To GAC1 |  |  | Field 2-5: GAC Influent Water Quality For The 10-Minute EBCT Run | [6 empty] | Field 2-6: GAC Influent Water Quality For The 20-Minute EBCT Run1 | [6 empty] | Field 2-7: GAC Effluent Water Quality For The 10-Minute EBCT Run1 | [15 empty] | Field 2-7: GAC Effluent Water Quality For The 10-Minute EBCT Run (continued) | [17 empty] | Field 2-8: GAC Effluent Water Quality For The 20-Minute EBCT Run1 | [14 empty] | Field 2-8: GAC Effluent Water Quality For The 20-Minute EBCT Run (continued) | [18 empty] | Field 2-9: GAC Cost Parameters
|  |  |  | Input Design Parameters |  | US Standard Mesh Sizes | [18 empty] | Group C, 12 effluent samples per run | [33 empty] | Group C, 12 effluent samples per run
PWS Name | East Bay Municipal Utility District | Carbon manufacturer | Calgon | RSSCT influent TOC (mg/L) | 2.8 | US standard | Opening | Process | Description | Scale | 10-min. EBCT Start Date | 1998-09-08 | [5 empty] | 20-min. EBCT Start Date | 1998-09-08 | [5 empty] | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Cost Parameter | Parameter value
Public Water System Identification Number | CA0110005 | Carbon trade name | Filtrasorb 300 | Inner diameter of the RSSCT column, DSC (mm) | 15 | mesh size | (mm) | Coagulation | Alum (Al2(SO4)3.14H2O) 27.5 mg/L, Cationic Polymer 1 mg/L | Full-Scale | 10-min. EBCT Start Time | 15:00 | [5 empty] | 20-min. EBCT Start Time | 15:00 | [5 empty] | ID | duplicated? | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | Capital Recovery Interest Rate (%) | 5.5
Water Industry Data Base Number (optional) | NA | Carbon type | bituminous | Minimum RSSCT Reynolds number, ReSC, min | 0.5 | 4 | 4.75 | Flocculation | 4-stage, Detention Time = 88 minutes | Full-Scale | [15 empty] | Y/N | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | Capital Recovery Period (years) | 30
|  | Original GAC mesh size, upper (US standard mesh) | 8 | Full-scale operating temperature, ToC (oC) | 18 | 6 | 3.35 | Sedimentation | Conventional, Detention Time = 173 minutes | Full-Scale | Group A, 2 samples per batch | [6 empty] | Group A, 2 samples per batch | [6 empty] | C1-10 | N | 1998-09-08 | 16:00 | 1 | 78.9333 | 8.3 | 20.1 | NR | BMRL | #VALUE! | 2 | 0.87 | 1.13 | 19.6 | 8.76 | 47 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | C1-20 | N | 1998-09-08 | 16:00 | 1 | 39.4667 | 7.8 | 18.9 | NR | BMRL | #VALUE! | 2 | 1.47 | 0.53 | 19.8 | 8.94 | 47.5 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | Overhead & Profit Factor (% of construction costs) | 15
Official ICR Contact Person |  | Original GAC mesh size, lower (US standard mesh) | 30 | Full-scale bed porosity, eLC | 0.45 | 8 | 2.36 | Ozonation | Dose = 3 mg/L | Full-Scale | Parameter | Units | Sample A1-10 | Sample A2-10 | Average | RPD |  | Parameter | Units | Sample A1-20 | Sample A2-20 | Average | RPD |  | C2-10 | N | 1998-09-09 | 7:00 | 16 | 1262.9333 | 7.9 | 20.2 | 0.36 | BMRL | #VALUE! | 2 | 0.98 | 1.02 | 19.5 | 8.91 | 47 | NR | 1.8 | 1.5 | 2.5 | 1.6 | 7.4 | BMRL | 0.6 | 0.26 | BMRL | 0.42 | 0.76 | NA | NA | NA | 1.28 | 2.04 | C2-20 | N | 1998-09-09 | 20:00 | 29 | 1144.5333 | 7.8 | 19.2 | 0.33 | BMRL | #VALUE! | 2 | 1.35 | 0.65 | 19.5 | 8.9 | 47.5 | NR | 1.6 | 0.96 | 1.9 | 0.77 | 5.23 | BMRL | 0.23 | 0.46 | BMRL | 0.59 | 0.48 | NA | NA | NA | 1.28 | 1.76 | Special Sitework Factor (% of construction costs) | 20
Mailing Address |  | Original carbon particle diameter, dLC (mm) | 1.48 | Measured RSSCT dry bed density, rSC (g/cm3) | 0.5 | 10 | 2 | Filtration | GAC/Sand, GAC Depth = 18 inch, Sand Depth = 12 inch, Effective Size = 0.80-1.0 mm, UC = 1.8 , SG = 1.65, EBCT = 3.6 minutes (for GAC only), Length of GAC in Service = 9 years | Full-Scale | Sampling date | MM/DD/YY | 1998-09-08 | 1998-09-18 | --- | --- |  | Sampling date | MM/DD/YY | 1998-09-08 | 1998-09-29 | --- | --- |  | C3-10 | Y | 1998-09-09 | 20:00 | 29 | 2289.0667 | 7.7 | 19.2 | 0.4 | 0.003 | #VALUE! | 2 | 1.2 | 0.8 | 19.75 | 8.93 | 46.5 | 49 | 1.75 | 1.85 | 3.85 | 2.15 | 9.6 | BMRL | 1.05 | 0.405 | BMRL | 1.25 | 1.27 | NA | NA | NA | 2.705 | 3.975 | C3-20 | Y | 1998-09-11 | 8:00 | 65 | 2565.3333 | 7.8 | 19.35 | 0.395 | 0.005 | 1.2758 | 2 | 1.415 | 0.585 | 19.75 | 9 | 48.25 | 36 | 1.45 | 2.2 | 4.55 | 2.25 | 10.45 | BMRL | 0.53 | 0.345 | BMRL | 1.085 | 0.9 | NA | NA | NA | 1.96 | 2.86 | Construction Contingencies (% of construction costs) | 15
|  | 1: These are the characteristics before the carbon is ground for RSSCT experiments. |  | RSSCT GAC mesh size, upper (US standard mesh) | 100 | 12 | 1.68 | Prefiltration | 1um - Polypropylene Cartridge Filter | Bench-Scale | Sampling time | hh:mm | 15:00 | 9:00 | --- | --- |  | Sampling time | hh:mm | 15:00 | 12:00 | --- | --- |  | C4-10 | N | 1998-09-10 | 11:00 | 44 | 3473.0667 | 7.9 | 19.7 | 0.39 | 0.011 | 2.8205 | 2 | 0.87 | 1.13 | 19.5 | 8.97 | 48 | 30 | 1.7 | 4 | 9.7 | 4.9 | 20.3 | BMRL | 0.81 | 0.2 | BMRL | 2.1 | 1.4 | NA | NA | NA | 3.11 | 4.51 | C4-20 | N | 1998-09-12 | 11:00 | 92 | 3630.9333 | 7.9 | 19.6 | 0.64 | BMRL | #VALUE! | 2 | 1.44 | 0.56 | 20 | 9.1 | 47.5 | 57 | 2.9 | 5.8 | 11 | 4.4 | 24.1 | BMRL | 1.1 | 0.71 | BMRL | 3.1 | 2.1 | NA | NA | NA | 4.91 | 7.01 | Engineering Fee Factor (% of construction costs) | 15
Phone Number |  |  |  | RSSCT GAC mesh size, lower (US standard mesh) | 200 | 16 | 1.18 |  |  |  | Operation time | hh.hh | 0 | 234 | --- | --- |  | Operation time | hh.hh | 0 | 501 | --- | --- |  | C5-10 | N | 1998-09-11 | 8:00 | 65 | 5130.6667 | 7.8 | 19.3 | 1.1 | 0.014 | 1.2727 | 2 | 0.91 | 1.09 | 19.6 | 8.96 | 48.5 | 61 | 10 | 10 | 13 | 2.2 | 35.2 | BMRL | 3.6 | 0.89 | BMRL | 2.9 | 3 | NA | NA | NA | 7.39 | 10.39 | C5-20 | N | 1998-09-13 | 18:30 | 123.5 | 4874.1333 | 7.9 | 20 | 1 | 0.01 | 1 | 2 | 1.25 | 0.75 | 20.4 | 8.99 | 47.5 | 54 | 8 | 9.8 | 13 | 2.8 | 33.6 | BMRL | 2.8 | 1 | BMRL | 2.9 | 2.7 | NA | NA | NA | 6.7 | 9.4 | 1998 ENR Construction Cost Index (CCI base year 1913) | 5921
FAX Number | [5 empty] | 20 | 0.85 |  |  |  | Bed volumes | (10 minutes) | 0 | 18470.4 | --- | --- |  | Bed volumes | (20 minutes) | 0 | 19772.8 | --- | --- |  | C6-10 | N | 1998-09-11 | 20:00 | 77 | 6077.8667 | 7.8 | 19.3 | 1.4 | 0.013 | 0.92857 | 2 | 0.97 | 1.03 | 20.4 | 8.9 | 47 | 80 | 16 | 12 | 12 | 1.6 | 41.6 | BMRL | 5.1 | 1.5 | BMRL | 3.2 | 3.8 | NA | NA | NA | 9.8 | 13.6 | C6-20 | N | 1998-09-14 | 19:00 | 148 | 5841.0667 | 8.05 | 20 | 1.2 | 0.011 | 0.91667 | 2 | 1 | 1 | 20.3 | 8.9 | 48 | 77 | 14 | 12 | 14 | 2.4 | 42.4 | BMRL | 4.5 | 1.5 | BMRL | 3.5 | 3.5 | NA | NA | NA | 9.5 | 13 | 1998 Producers Price Index (PPI base year 1967 = 100) | 366
E-Mail Address (optional) |  |  |  | Estimated Run Length |  | 30 | 0.6 |  |  |  | Alkalinity | mg/L as CaCO3 | 100 | 110 | 105 | 9.5238 |  | Alkalinity | mg/L as CaCO3 | 100 | 100 | 100 | 0 |  | C7-10 | Y | 1998-09-12 | 11:00 | 92 | 7261.8667 | 7.8 | 19.35 | 1.4 | 0.0125 | 0.89286 | 2.2 | 0.795 | 1.405 | 20 | 9 | 48 | 122.5 | 23 | 14 | 10.45 | 1.14 | 48.59 | BMRL | 8.2 | 2.35 | BMRL | 3.2 | 5.4 | NA | NA | NA | 13.75 | 19.15 | C7-20 | Y | 1998-09-16 | 9:00 | 186 | 7340.8 | 7.95 | 19.85 | 1.25 | 0.0135 | 1.0833 | 2 | 0.95 | 1.05 | 20.25 | 8.915 | 48 | 88 | 16 | 13 | 13 | 2 | 44 | BMRL | 5.65 | 2.35 | BMRL | 3.5 | 4.4 | NA | NA | NA | 11.5 | 15.9 | Labor Rate + Fringe ($/work-hour) | 38
|  |  |  | Bed volumes to 50% TOC breakthrough, BV50 | 5690.5506 | 40 | 0.425 |  |  |  | Total hardness | mg/L as CaCO3 | 140 | 130 | 135 | 7.4074 |  | Total hardness | mg/L as CaCO3 | 140 | 140 | 140 | 0 |  | C8-10 | N | 1998-09-13 | 8:00 | 113 | 8919.4667 | 7.8 | 19.5 | 1.8 | 0.019 | 1.0556 | 2.3 | 0.8 | 1.5 | 19.8 | 9.1 | 48 | 120 | 29 | 16 | 11 | 0.84 | 56.84 | BMRL | 10 | 3.4 | BMRL | 2.9 | 5.9 | NA | NA | NA | 16.3 | 22.2 | C8-20 | N | 1998-09-20 | 10:00 | 283 | 11169.0667 | 8.05 | 19.9 | 1.7 | 0.017 | 1 | 2 | 0.43 | 1.57 | 20.2 | 9.1 | 49 | 94 | 31 | 14 | 8.2 | 0.71 | 53.91 | BMRL | 8.8 | 3.4 | BMRL | 3.1 | 5.6 | NA | NA | NA | 15.3 | 20.9 | Labor Overhead Factor (% of labor) | 20
Technical ICR Contact Person |  |  |  | Estimated run length, BVT ( = 2 x BV50) | 11381.1013 | 50 | 0.3 |  |  |  | Calcium hardness | mg/L as CaCO3 | 75 | 75 | 75 | 0 |  | Calcium hardness | mg/L as CaCO3 | 74.5 | 76 | 75.25 | 1.9934 |  | C9-10 | N | 1998-09-14 | 12:00 | 141 | 11129.6 | 7.8 | 19.5 | 2.1 | 0.02 | 0.95238 | 2.3 | 0.62 | 1.68 | 20.3 | 8.95 | 49 | 130 | 37 | 18 | 12 | 0.84 | 67.84 | BMRL | 12 | 4 | BMRL | 3.8 | 6 | NA | NA | NA | 19.8 | 25.8 | C9-20 | N | 1998-09-23 | 9:00 | 354 | 13971.2 | 8.1 | 19.8 | 1.7 | 0.019 | 1.1176 | 2.3 | 0.78 | 1.52 | 19.8 | 9.04 | 48 | 110 | 48 | 1.2 | BMRL | BMRL | 49.2 | BMRL | 6.6 | 2.3 | BMRL | 2.1 | 3.6 | NA | NA | NA | 11 | 14.6 | Electric Rate ($/kW-h) | 0.065
Mailing Address |  |  |  | BVT + 30% safety factor, BVT+30% ( = 2.6 x BV50) | 14795.4317 | 60 | 0.25 |  |  |  | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! |  | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! |  | C10-10 | N | 1998-09-15 | 16:15 | 169.25 | 13359.4667 | 7.9 | 19.5 | 1.9 | 0.022 | 1.1579 | 2.5 | 0.93 | 1.57 | 20.5 | 9.05 | 47 | 130 | 39 | 17 | 11 | 0.75 | 67.75 | BMRL | 9.5 | 4 | BMRL | 1.4 | 4.5 | NA | NA | NA | 14.9 | 19.4 | C10-20 | N | 1998-09-25 | 10:00 | 403 | 15905.0667 | 8.1 | 19.6 | 1.9 | 0.022 | 1.1579 | 2.4 | 0.92 | 1.48 | 19 | 9.06 | 48 | 150 | 39 | 18 | 11 | 0.85 | 68.85 | BMRL | 7.2 | 2.8 | BMRL | 2.1 | 3.8 | NA | NA | NA | 12.1 | 15.9 | Fuel Oil Rate ($/gal) | 0.58
[6 empty] | 70 | 0.21 |  |  |  | Bromide | mg/L | 45 | 46 | 45.5 | 2.1978 |  | Bromide | mg/L | 45 | 46 | 45.5 | 2.1978 |  | C11-10 | Y | 1998-09-16 | 18:45 | 195.75 | 15451.2 | 7.9 | 20.1 | 1.95 | 0.025 | 1.2855 | 2.8 | 1.215 | 1.585 | 20.5 | 8.915 | 48 | 155 | 43 | 17.5 | 10.5 | 0.68 | 71.68 | BMRL | 14 | 6 | BMRL | 3.6 | 6.8 | NA | NA | NA | 23.6 | 30.4 | C11-20 | Y | 1998-09-27 | 11:00 | 452 | 17838.9333 | 8.05 | 19.85 | 1.85 | 0.0215 | 1.1623 | 2.4 | 0.965 | 1.435 | 19.25 | 9.15 | 48 | 140 | 36.5 | 16.5 | 10.5 | 0.885 | 64.385 | BMRL | 7.35 | 2.75 | BMRL | 2.2 | 3.95 | NA | NA | NA | 12.3 | 16.25 | Natural Gas Rate ($/ft3) | 0.006
Phone Number |  |  |  | General RSSCT Design Parameters |  | 80 | 0.18 | [17 empty] | C12-10 | N | 1998-09-18 | 11:30 | 236.5 | 18667.7333 | 7.9 | 19.6 | 2.1 | 0.024 | 1.1429 | 2.8 | 1 | 1.8 | 20 | 8.96 | 46 | 180 | 45 | 18 | 11 | 0.63 | 74.63 | BMRL | 16 | 6.6 | BMRL | 4.2 | 7.7 | NA | NA | NA | 26.8 | 34.5 | C12-20 | N | 1998-09-29 | 11:00 | 500 | 19733.3333 | 8.1 | 18.7 | 1.8 | 0.026 | 1.4444 | 2.4 | 0.85 | 1.55 | 19.2 | 9.1 | 48 | 130 | 37 | 17 | 11 | 0.89 | 65.89 | BMRL | 11 | 5.1 | BMRL | 2.4 | 4.8 | NA | NA | NA | 18.5 | 23.3 | Current Process Water Rate ($/1000 gal) | 0.14
FAX Number |  |  |  | Kinematic viscosity at ToC, nLC (m2/s) | 1.0784e-06 | 100 | 0.15 |  |  |  | Group B, 3 samples per batch | [6 empty] | Group B, 3 samples per batch | [74 empty] | Modifications to Existing Plant (% of construction costs) | 25
E-Mail Address (optional) |  |  |  | RSSCT carbon particle diameter, dSC (mm) | 0.1125 | 120 | 0.125 |  |  |  | Parameter | Units | Sample B1-10 | Sample B2-10 | Sample B3-10 | Average | %SD | Parameter | Units | Sample B1-20 | Sample B2-20 | Sample B3-20 | Average | %SD
|  |  |  | Scaling factor, SF | 13.1556 | 140 | 0.106 | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | Sampling date | MM/DD/YY | 1998-09-08 | 1998-09-13 | 1998-09-18 | --- | --- | Sampling date | MM/DD/YY | 1998-09-08 | 1998-09-18 | 1998-10-01 | --- | ---
Plant Name | Upper San Leandro |  |  | RSSCT hydraulic loading rate, vSC (m/hr) | 7.7645 | 170 | 0.088 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | Sampling time | hh:mm | 16:30 | 8:15 | 12:00 | --- | --- | Sampling time | hh:mm | 16:30 | 12:00 | 12:00 | --- | ---
Treatment Plant Category | Conventional with Ozone |  |  | RSSCT flow rate, QSC (mL/min) | 22.8684 | 200 | 0.075 | is to list the pretreatment processes used in this particular RSSCT run. |  |  | Operation time | hh.hh | 1.5 | 113.25 | 237 | --- | --- | Operation time | hh.hh | 1.5 | 237 | 549 | --- | ---
Process Train Name | NA |  |  | Estimated total influent volume required, VSCT (L) | 771.5695 | 230 | 0.062 |  |  |  | Bed volumes | (10 minute) | 118.4 | 8939.2 | 18707.2 | --- | --- | Bed volumes | (20 minute) | 59.2 | 9353.6 | 21667.2 | --- | --- | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
ICR Treatment Plant Identification Number | 139 |  |  |  |  | 270 | 0.053 |  |  |  | pH | --- | 7.8 | 7.8 | 7.8 | 7.8 | 0 | pH | --- | 7.8 | 7.8 | 8.04 | 7.88 | 1.7584 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
PWSID Number of Plant (if assigned) | CA0110005 |  |  | 10-Minute EBCT Run |  | 325 | 0.044 |  |  |  | Turbidity | ntu | 0.086 | 0.06 | 0.06 | 0.068667 | 21.8608 | Turbidity | ntu | 0.09 | 0.058 | 0.058 | 0.068667 | 26.9056 | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below. | [33 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below.
Historical Minimum Water Temperature (oC) | 8 |  |  | Full-scale empty bed contact time, EBCTLC (min) | 10 | 400 | 0.037 |  |  |  | Temperature | oC | 19.3 | 19.4 | 19.4 | 19.3667 | 0.29812 | Temperature | oC | 19.3 | 19.4 | 19.7 | 19.4667 | 1.0693
Historical Average Water Temperature (oC) | 14 |  |  | Estimated full-scale run time, tLCT (days) | 102.7461 | [5 empty] | Total organic carbon | mg/L | 2.9 | 3.1 | 3.1 | 3.0333 | 3.8067 | Total organic carbon | mg/L | 2.9 | 3.1 | 3 | 3 | 3.3333 | Group D, 3 duplicate effluent samples per run (results from primary and duplicate analyses) | [33 empty] | Group D, 3 duplicate effluent samples per run (results from primary and duplicate analyses)
State Approved Plant Capacity (MGD) | 55 |  |  | RSSCT empty bed contact time, EBCTSC (min) | 0.76014 | [5 empty] | UV254 | cm-1 | 0.042 | 0.04 | 0.042 | 0.041333 | 2.7936 | UV254 | cm-1 | 0.042 | 0.042 | 0.041 | 0.041667 | 1.3856 | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS
|  |  |  | Estimated RSSCT run time, tSCT (days) | 7.8101 | [5 empty] | SUVA | L/(mg*m) | 1.4483 | 1.2903 | 1.3548 | 1.3645 | 5.8203 | SUVA | L/(mg*m) | 1.4483 | 1.3548 | 1.3667 | 1.3899 | 3.6604 | ID | Type | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6
|  |  |  | RSSCT bed length, lSC (cm) | 9.8368 | [5 empty] | SDS-Cl2 dose | mg/L | 3.3 | 3.8 | 3.8 | 3.6333 | 7.9452 | SDS-Cl2 dose | mg/L | 3.3 | 3.8 | 3.8 | 3.6333 | 7.9452 |  |  | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L
|  |  |  | Estimated volume required for 10-minute EBCT, VSC (L) | 257.1898 | [5 empty] | SDS-Free Cl2 residual | mg/L | 0.3 | 0.63 | 1 | 0.64333 | 54.4337 | SDS-Free Cl2 residual | mg/L | 0.3 | 1 | 0.73 | 0.67667 | 52.1726 | C3-10 | Primary | 1998-09-09 | 20:00 | 29 | 2289.0667 | 7.7 | 19.2 | 0.41 | BMRL | #VALUE! | 2 | 0.98 | 1.02 | 19.5 | 8.9 | 47 | 44 | 1.9 | 2.1 | 3.8 | 1.5 | 9.3 | BMRL | 1.7 | 0.47 | BMRL | 1.5 | 1.8 | NA | NA | NA | 3.67 | 5.47 | C3-20 | Primary | 1998-09-11 | 8:00 | 65 | 2565.3333 | 7.8 | 19.5 | 0.36 | 0.005 | 1.3889 | 2 | 1.24 | 0.76 | 19.6 | 9 | 48.5 | 40 | 1.9 | 2.9 | 5.1 | 2.2 | 12.1 | BMRL | 0.42 | 0.3 | BMRL | 0.87 | 1.1 | NA | NA | NA | 1.59 | 2.69
|  |  |  | Mass GAC required, mSC (g) | 8.6915 | [5 empty] | SDS-Cl2 demand | mg/L | 3 | 3.17 | 2.8 | 2.99 | 6.1941 | SDS-Cl2 demand | mg/L | 3 | 2.8 | 3.07 | 2.9567 | 4.7391 | D3-10 | Duplicate | 1998-09-09 | 20:00 | 29 | 2289.0667 | 7.7 | 19.2 | 0.39 | 0.003 | 0.76923 | 2 | 1.42 | 0.58 | 20 | 8.96 | 46 | 54 | 1.6 | 1.6 | 3.9 | 2.8 | 9.9 | BMRL | 0.4 | 0.34 | BMRL | 1 | 0.74 | NA | NA | NA | 1.74 | 2.48 | D3-20 | Duplicate | 1998-09-11 | 9:00 | 66 | 2604.8 | 7.8 | 19.2 | 0.43 | 0.005 | 1.1628 | 2 | 1.59 | 0.41 | 19.9 | 9 | 48 | 32 | 1 | 1.5 | 4 | 2.3 | 8.8 | BMRL | 0.64 | 0.39 | BMRL | 1.3 | 0.7 | NA | NA | NA | 2.33 | 3.03
[11 empty] | SDS-Chlorination temp. | oC | 20.1 | 19.7 | 19.8 | 19.8667 | 1.0478 | SDS-Chlorination temp. | oC | 20.1 | 19.8 | 19.8 | 19.9 | 0.87038 | Avg-C3-10 | Average | --- | --- | --- | --- | 7.7 | 19.2 | 0.4 | 0.003 | #VALUE! | 2 | 1.2 | 0.8 | 19.75 | 8.93 | 46.5 | 49 | 1.75 | 1.85 | 3.85 | 2.15 | 9.6 | #DIV/0! | 1.05 | 0.405 | #DIV/0! | 1.25 | 1.27 | #DIV/0! | #DIV/0! | #DIV/0! | 2.705 | 3.975 | Avg-C3-20 | Average | --- | --- | --- | --- | 7.8 | 19.35 | 0.395 | 0.005 | 1.2758 | 2 | 1.415 | 0.585 | 19.75 | 9 | 48.25 | 36 | 1.45 | 2.2 | 4.55 | 2.25 | 10.45 | #DIV/0! | 0.53 | 0.345 | #DIV/0! | 1.085 | 0.9 | #DIV/0! | #DIV/0! | #DIV/0! | 1.96 | 2.86
|  |  |  | 20-Minute EBCT Run | [6 empty] | SDS-Chlorination pH | --- | 9 | 9.1 | 9 | 9.0333 | 0.63913 | SDS-Chlorination pH | --- | 9 | 9 | 9.1 | 9.0333 | 0.63913 | RPD-C3-10 | RPD | --- | --- | --- | --- | 0 | 0 | 5 | #VALUE! | #VALUE! | 0 | 36.6667 | 55 | 2.5316 | 0.67189 | 2.1505 | 20.4082 | 17.1429 | 27.027 | 2.5974 | 60.4651 | 6.25 | #VALUE! | 123.8095 | 32.0988 | #VALUE! | 40 | 83.4646 | #VALUE! | #VALUE! | #VALUE! | 71.3494 | 75.2201 | RPD-C3-20 | RPD | --- | --- | --- | --- | 0 | 1.5504 | 17.7215 | 0 | 17.7215 | 0 | 24.735 | 59.8291 | 1.519 | 0 | 1.0363 | 22.2222 | 62.069 | 63.6364 | 24.1758 | 4.4444 | 31.5789 | #VALUE! | 41.5094 | 26.087 | #VALUE! | 39.6313 | 44.4444 | #VALUE! | #VALUE! | #VALUE! | 37.7551 | 11.8881
|  |  |  | Full-scale empty bed contact time, EBCTLC (min) | 20 | [5 empty] | SDS-Incubation time | hours | 47 | 48 | 48 | 47.6667 | 1.2112 | SDS-Incubation time | hours | 47 | 48 | 48 | 47.6667 | 1.2112 | C7-10 | Primary | 1998-09-12 | 11:00 | 92 | 7261.8667 | 7.8 | 19.3 | 1.4 | 0.013 | 0.92857 | 2.2 | 0.99 | 1.21 | 19.9 | 9 | 48 | 95 | 22 | 14 | 11 | 1.5 | 48.5 | BMRL | 8 | 2.5 | BMRL | 3.8 | 5.7 | NA | NA | NA | 14.3 | 20 | C7-20 | Primary | 1998-09-16 | 9:00 | 186 | 7340.8 | 8 | 20 | 1.3 | 0.013 | 1 | 2 | 1 | 1 | 20.3 | 8.92 | 48 | 81 | 16 | 13 | 13 | 2 | 44 | BMRL | 5.6 | 2.3 | BMRL | 2.8 | 3.8 | NA | NA | NA | 10.7 | 14.5
|  |  |  | Estimated full-scale run time, tLCT (days) | 205.4921 | [5 empty] | SDS-TOX | mg Cl- /L | 300 | 310 | 300 | 303.3333 | 1.9034 | SDS-TOX | mg Cl- /L | 300 | 300 | 250 | 283.3333 | 10.1885 | D7-10 | Duplicate | 1998-09-12 | 11:00 | 92 | 7261.8667 | 7.8 | 19.4 | 1.4 | 0.012 | 0.85714 | 2.2 | 0.6 | 1.6 | 20.1 | 9 | 48 | 150 | 24 | 14 | 9.9 | 0.78 | 48.68 | BMRL | 8.4 | 2.2 | BMRL | 2.6 | 5.1 | NA | NA | NA | 13.2 | 18.3 | D7-20 | Duplicate | 1998-09-16 | 9:30 | 186.5 | 7360.5333 | 7.9 | 19.7 | 1.2 | 0.014 | 1.1667 | 2 | 0.9 | 1.1 | 20.2 | 8.91 | 48 | 95 | 16 | 13 | 13 | 2 | 44 | BMRL | 5.7 | 2.4 | BMRL | 4.2 | 5 | NA | NA | NA | 12.3 | 17.3
|  |  |  | RSSCT empty bed contact time, EBCTSC (min) | 1.5203 | [5 empty] | SDS-CHCl3 | mg/L | 79 | 89 | 87 | 85 | 6.2253 | SDS-CHCl3 | mg/L | 79 | 87 | 66 | 77.3333 | 13.7053 | Avg-C7-10 | Average | --- | --- | --- | --- | 7.8 | 19.35 | 1.4 | 0.0125 | 0.89286 | 2.2 | 0.795 | 1.405 | 20 | 9 | 48 | 122.5 | 23 | 14 | 10.45 | 1.14 | 48.59 | #DIV/0! | 8.2 | 2.35 | #DIV/0! | 3.2 | 5.4 | #DIV/0! | #DIV/0! | #DIV/0! | 13.75 | 19.15 | Avg-C7-20 | Average | --- | --- | --- | --- | 7.95 | 19.85 | 1.25 | 0.0135 | 1.0833 | 2 | 0.95 | 1.05 | 20.25 | 8.915 | 48 | 88 | 16 | 13 | 13 | 2 | 44 | #DIV/0! | 5.65 | 2.35 | #DIV/0! | 3.5 | 4.4 | #DIV/0! | #DIV/0! | #DIV/0! | 11.5 | 15.9
|  |  |  | Estimated RSSCT run time, tSCT (days) | 15.6202 | [5 empty] | SDS-BDCM | mg/L | 23 | 22 | 22 | 22.3333 | 2.5852 | SDS-BDCM | mg/L | 23 | 22 | 20 | 21.6667 | 7.0501 | RPD-C7-10 | RPD | --- | --- | --- | --- | 0 | 0.5168 | 0 | 8 | 8 | 0 | 49.0566 | 27.758 | 1 | 0 | 0 | 44.898 | 8.6957 | 0 | 10.5263 | 63.1579 | 0.37045 | #VALUE! | 4.878 | 12.766 | #VALUE! | 37.5 | 11.1111 | #VALUE! | #VALUE! | #VALUE! | 8 | 8.8773 | RPD-C7-20 | RPD | --- | --- | --- | --- | 1.2579 | 1.5113 | 8 | 7.4074 | 15.3846 | 0 | 10.5263 | 9.5238 | 0.49383 | 0.11217 | 0 | 15.9091 | 0 | 0 | 0 | 0 | 0 | #VALUE! | 1.7699 | 4.2553 | #VALUE! | 40 | 27.2727 | #VALUE! | #VALUE! | #VALUE! | 13.913 | 17.6101
|  |  |  | RSSCT bed length, lSC (cm) | 19.6736 | [5 empty] | SDS-DBCM | mg/L | 7.3 | 7.4 | 7.4 | 7.3667 | 0.78373 | SDS-DBCM | mg/L | 7.3 | 7.4 | 8 | 7.5667 | 5.0034 | C11-10 | Primary | 1998-09-16 | 18:45 | 195.75 | 15451.2 | 7.9 | 20.1 | 1.9 | 0.027 | 1.4211 | 2.8 | 1.19 | 1.61 | 20.5 | 8.91 | 48 | 160 | 43 | 18 | 11 | 0.7 | 72.7 | BMRL | 14 | 6.2 | BMRL | 4 | 6.9 | NA | NA | NA | 24.2 | 31.1 | C11-20 | Primary | 1998-09-27 | 11:00 | 452 | 17838.9333 | 8.1 | 19.8 | 1.8 | 0.021 | 1.1667 | 2.4 | 0.95 | 1.45 | 19.3 | 9.2 | 48 | 150 | 38 | 16 | 10 | 0.85 | 64.85 | BMRL | 6.7 | 2.4 | BMRL | 2 | 3.6 | NA | NA | NA | 11.1 | 14.7
|  |  |  | Estimated volume required for 20-minute EBCT, VSC (L) | 514.3797 | [5 empty] | SDS-CHBr3 | mg/L | 0.4 | 0.3 | 0.32 | 0.34 | 15.5632 | SDS-CHBr3 | mg/L | 0.4 | 0.32 | 0.45 | 0.39 | 16.8139 | D11-10 | Duplicate | 1998-09-16 | 18:45 | 195.75 | 15451.2 | 7.9 | 20.1 | 2 | 0.023 | 1.15 | 2.8 | 1.24 | 1.56 | 20.5 | 8.92 | 48 | 150 | 43 | 17 | 10 | 0.66 | 70.66 | BMRL | 14 | 5.8 | BMRL | 3.2 | 6.7 | NA | NA | NA | 23 | 29.7 | D11-20 | Duplicate | 1998-09-24 | 11:30 | 380.5 | 15017.0667 | 8 | 19.9 | 1.9 | 0.022 | 1.1579 | 2.4 | 0.98 | 1.42 | 19.2 | 9.1 | 48 | 130 | 35 | 17 | 11 | 0.92 | 63.92 | BMRL | 8 | 3.1 | BMRL | 2.4 | 4.3 | NA | NA | NA | 13.5 | 17.8
|  |  |  | Mass GAC required, mSC (g) | 17.3831 | [5 empty] | SDS-THM4 | mg/L | 109.7 | 118.7 | 116.72 | 115.04 | 4.1111 | SDS-THM4 | mg/L | 109.7 | 116.72 | 94.45 | 106.9567 | 10.6451 | Avg-C11-10 | Average | --- | --- | --- | --- | 7.9 | 20.1 | 1.95 | 0.025 | 1.2855 | 2.8 | 1.215 | 1.585 | 20.5 | 8.915 | 48 | 155 | 43 | 17.5 | 10.5 | 0.68 | 71.68 | #DIV/0! | 14 | 6 | #DIV/0! | 3.6 | 6.8 | #DIV/0! | #DIV/0! | #DIV/0! | 23.6 | 30.4 | Avg-C11-20 | Average | --- | --- | --- | --- | 8.05 | 19.85 | 1.85 | 0.0215 | 1.1623 | 2.4 | 0.965 | 1.435 | 19.25 | 9.15 | 48 | 140 | 36.5 | 16.5 | 10.5 | 0.885 | 64.385 | #DIV/0! | 7.35 | 2.75 | #DIV/0! | 2.2 | 3.95 | #DIV/0! | #DIV/0! | #DIV/0! | 12.3 | 16.25
[11 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | BMRL | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | BMRL | BMRL | #DIV/0! | #DIV/0! | RPD-C11-10 | RPD | --- | --- | --- | --- | 0 | 0 | 5.1282 | 16 | 21.085 | 0 | 4.1152 | 3.1546 | 0 | 0.11217 | 0 | 6.4516 | 0 | 5.7143 | 9.5238 | 5.8824 | 2.846 | #VALUE! | 0 | 6.6667 | #VALUE! | 22.2222 | 2.9412 | #VALUE! | #VALUE! | #VALUE! | 5.0847 | 4.6053 | RPD-C11-20 | RPD | --- | --- | --- | --- | 1.2422 | 0.50378 | 5.4054 | 4.6512 | 0.75472 | 0 | 3.1088 | 2.0906 | 0.51948 | 1.0929 | 0 | 14.2857 | 8.2192 | 6.0606 | 9.5238 | 7.9096 | 1.4444 | #VALUE! | 17.6871 | 25.4545 | #VALUE! | 18.1818 | 17.7215 | #VALUE! | #VALUE! | #VALUE! | 19.5122 | 19.0769
[11 empty] | SDS-DCAA* | mg/L | 23 | 28 | 29 | 26.6667 | 12.0546 | SDS-DCAA* | mg/L | 23 | 29 | 20 | 24 | 19.0941 | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[11 empty] | SDS-TCAA* | mg/L | 8.4 | 9.9 | 13 | 10.4333 | 22.4848 | SDS-TCAA* | mg/L | 8.4 | 13 | 8 | 9.8 | 28.3519 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
[11 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | BMRL | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | BMRL | BMRL | #DIV/0! | #DIV/0!
[11 empty] | SDS-DBAA* | mg/L | 1.6 | 2.4 | 1.9 | 1.9667 | 20.5498 | SDS-DBAA* | mg/L | 1.6 | 1.9 | 1.8 | 1.7667 | 8.6464
[11 empty] | SDS-BCAA* | mg/L | 7 | 10 | 8.6 | 8.5333 | 17.5911 | SDS-BCAA* | mg/L | 7 | 8.6 | 6.2 | 7.2667 | 16.8168
[11 empty] | SDS-TBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0!
[11 empty] | SDS-CDBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0!
[11 empty] | SDS-DCBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0!
[11 empty] | SDS-HAA5 | mg/L | 33 | 40.3 | 43.9 | 39.0667 | 14.2159 | SDS-HAA5 | mg/L | 33 | 43.9 | 29.8 | 35.5667 | 20.7838
[11 empty] | SDS-HAA6 | mg/L | 40 | 50.3 | 52.5 | 47.6 | 14.0191 | SDS-HAA6 | mg/L | 40 | 52.5 | 36 | 42.8333 | 20.0946
[11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [6 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [6 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
Note on N9: Reviewer M.H. (10/25/99): Per utility, "No samples were collected for THM, HAA, TOX."
Note on S21: Sample time and turbidity for B1-20 was corrected.
Note on AG29: Duplicate samples were collected in two different bottles, one right after another. They were not collected in the same bottle. This was done to reduce probability of contamination and loss of any VOCs such as chloroform.
Note on AO5: asheikho: Run terminated just before 70% breakthroug because the effluent TOC was decreasing.
Note on AX40: asheikho: Verified.
Note on BB40: asheikho: Data variability is verified.
Note on BH40: asheikho: Data variability is verified.
Note on BP29: Duplicate samples were collected in two different bottles, one right after another. They were not collected in the same bottle. This was done to reduce probability of contamination and loss of any VOCs such as chloroform.
Note on BX5: asheikho: Run terminated before 70% breakthroug because of high headloss and the effluent TOC was constant for 2-3 round of sampling.
Note on CH16: asheikho: Data is verified.
Note on CH37: Both results were identical as reported by lab.
Note on CI16: asheikho: Data is verified.
Note on CI37: Both results were identical as reported by lab.
Note on CJ37: Both results were identical as reported by lab.
Note on CK37: Both results were identical as reported by lab.

## Sheet3. 3rd Quarter
FIELD-SET 3: 3rd QUARTER RSSCT RESULTS (FILE: gacrssct.xls)
Field 3-1: PWS And Treatment Plant Data |  | Field 3-2: Full-Scale GAC Characteristics1 |  | Field 3-3: RSSCT Design Parameters |  |  |  | Field 3-4: Pretreatment Used Prior To GAC1 |  |  | Field 3-5: GAC Influent Water Quality For The 10-Minute EBCT Run | [6 empty] | Field 3-6: GAC Influent Water Quality For The 20-Minute EBCT Run1 | [6 empty] | Field 3-7: GAC Effluent Water Quality For The 10-Minute EBCT Run1 | [15 empty] | Field 3-7: GAC Effluent Water Quality For The 10-Minute EBCT Run (continued) | [17 empty] | Field 3-8: GAC Effluent Water Quality For The 20-Minute EBCT Run1 | [14 empty] | Field 3-8: GAC Effluent Water Quality For The 20-Minute EBCT Run (continued) | [18 empty] | Field 3-9: GAC Cost Parameters
|  |  |  | Input Design Parameters |  | US Standard Mesh Sizes | [18 empty] | Group C, 12 effluent samples per run | [33 empty] | Group C, 12 effluent samples per run
PWS Name | East Bay Municipal Utility District | Carbon manufacturer | Calgon | RSSCT influent TOC (mg/L) | 3.1 | US standard | Opening | Process | Description | Scale | 10-min. EBCT Start Date | 1998-12-10 | [5 empty] | 20-min. EBCT Start Date | 1998-12-10 | [5 empty] | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Cost Parameter | Parameter value
Public Water System Identification Number | CA0110005 | Carbon trade name | Filtrasorb 300 | Inner diameter of the RSSCT column, DSC (mm) | 15 | mesh size | (mm) | Coagulation | Alum (Al2(SO4)3.14H2O) 27.5 mg/L, Cationic Polymer 1 mg/L | Full-Scale | 10-min. EBCT Start Time | 15:10 | [5 empty] | 20-min. EBCT Start Time | 15:10 | [5 empty] | ID | duplicated? | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | Capital Recovery Interest Rate (%) | 5.5
Water Industry Data Base Number (optional) | NA | Carbon type | bituminous | Minimum RSSCT Reynolds number, ReSC, min | 0.5 | 4 | 4.75 | Flocculation | 4-stage, Detention Time = 132 minutes | Full-Scale | [15 empty] | Y/N | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | Capital Recovery Period (years) | 30
|  | Original GAC mesh size, upper (US standard mesh) | 8 | Full-scale operating temperature, ToC (oC) | 14 | 6 | 3.35 | Sedimentation | Conventional, Detention Time = 260 minutes | Full-Scale | Group A, 2 samples per batch | [6 empty] | Group A, 2 samples per batch | [6 empty] | C1-10 | N | 1998-12-10 | 16:10 | 1 | 78.9333 | 8.35 | 13 | 0.17 | BMRL | #VALUE! | 1.7 | 1.26 | 0.44 | 13.9 | 8.9 | 96 | 41 | 0.81 | 1.5 | 3.2 | 1.4 | 6.91 | 0.67 | 1.4 | 2.2 | BMRL | 0.59 | 0.46 | NA | NA | NA | 4.86 | 5.32 | C1-20 | N | 1998-12-10 | 16:10 | 1 | 39.4667 | 8.7 | 13.3 | 0.2 | BMRL | #VALUE! | 1.4 | 0.96 | 0.44 | 14.5 | 8.9 | 96 | 14 | 0.98 | 1.1 | 2.9 | 1.6 | 6.58 | BMRL | 0.61 | 1.5 | BMRL | 0.66 | 0.38 | NA | NA | NA | 2.77 | 3.15 | Overhead & Profit Factor (% of construction costs) | 15
Official ICR Contact Person |  | Original GAC mesh size, lower (US standard mesh) | 30 | Full-scale bed porosity, eLC | 0.45 | 8 | 2.36 | Ozonation | Dose = 2 mg/L | Full-Scale | Parameter | Units | Sample A1-10 | Sample A2-10 | Average | RPD |  | Parameter | Units | Sample A1-20 | Sample A2-20 | Average | RPD |  | C2-10 | N | 1998-12-11 | 11:15 | 20.0833 | 1585.2444 | 8.2 | 13.8 | 0.2 | BMRL | #VALUE! | 1.7 | 1.18 | 0.52 | 14.3 | 8.92 | 96 | 62 | 0.74 | 0.83 | 3 | 2.4 | 6.97 | BMRL | 0.82 | 1.6 | BMRL | 1.1 | 0.69 | NA | NA | NA | 3.52 | 4.21 | C2-20 | N | 1998-12-12 | 10:00 | 42.8333 | 1690.4889 | 8.25 | 13.1 | 0.23 | BMRL | #VALUE! | 1.4 | 0.88 | 0.52 | 15.3 | 8.82 | 95 | 8.4 | 0.59 | 0.4 | 1.8 | 1.8 | 4.59 | BMRL | 0.64 | 1.5 | 0.15 | 0.94 | 0.56 | NA | NA | NA | 3.23 | 3.79 | Special Sitework Factor (% of construction costs) | 20
Mailing Address |  | Original carbon particle diameter, dLC (mm) | 1.48 | Measured RSSCT dry bed density, rSC (g/cm3) | 0.5 | 10 | 2 | Filtration | GAC/Sand, GAC Depth = 18 inch, Sand Depth = 12 inch, Effective Size = 0.80-1.0 mm, UC = 1.8 , SG = 1.65, EBCT = 3.6 minutes (for GAC only), Length of GAC in Service = 9 years | Full-Scale | Sampling date | MM/DD/YY | 1998-12-10 | NA | --- | --- |  | Sampling date | MM/DD/YY | 1998-12-10 | 1998-12-27 | --- | --- |  | C3-10 | Y | 1998-12-12 | 10:00 | 42.8333 | 3380.9778 | 8.235 | 13.25 | 0.87 | 0.0078 | 0.89792 | 2.1 | 1.25 | 0.85 | 15.4 | 8.84 | 96 | 56 | 3.45 | 6.95 | 11.5 | 5.05 | 26.95 | 0.66 | 2.25 | 2.35 | 0.17 | 2.8 | 2.25 | NA | NA | NA | 7.9 | 10.15 | C3-20 | Y | 1998-12-13 | 9:30 | 66.3333 | 2617.9556 | 8.22 | 13.25 | 0.355 | 0.004 | 1.1268 | 1.5 | 0.75 | 0.75 | 15.2 | 8.89 | 96 | 11.3 | 0.965 | 1.2 | 3.85 | 2.8 | 8.815 | 0.745 | 1.03 | 1.95 | 0.14 | 1.5 | 1 | NA | NA | NA | 4.9225 | 5.9225 | Construction Contingencies (% of construction costs) | 15
|  | 1: These are the characteristics before the carbon is ground for RSSCT experiments. |  | RSSCT GAC mesh size, upper (US standard mesh) | 100 | 12 | 1.68 | Prefiltration | 1um - Polypropylene Cartridge Filter | Bench-Scale | Sampling time | hh:mm | 15:10 | NA | --- | --- |  | Sampling time | hh:mm | 15:10 | 10:00 | --- | --- |  | C4-10 | N | 1998-12-12 | 20:30 | 53.3333 | 4209.7778 | 8.27 | 13.3 | 1.1 | 0.015 | 1.3636 | 2.2 | 1.21 | 0.99 | 14.7 | 8.8 | 94.5 | 55 | 6.5 | 9 | 13 | 3.6 | 32.1 | 0.78 | 3.4 | 2.5 | 0.2 | 2.9 | 2.8 | NA | NA | NA | 9.78 | 12.58 | C4-20 | N | 1998-12-14 | 8:30 | 89.3333 | 3525.6889 | 7.97 | 16.3 | 0.69 | 0.009 | 1.3043 | 1.7 | 0.96 | 0.74 | 14.5 | 9 | 96 | 35 | 1.5 | 3.5 | 9.5 | 5.5 | 20 | 0.55 | 1.4 | 2 | 0.19 | 2.6 | 1.6 | NA | NA | NA | 6.74 | 8.34 | Engineering Fee Factor (% of construction costs) | 15
Phone Number |  |  |  | RSSCT GAC mesh size, lower (US standard mesh) | 200 | 16 | 1.18 |  |  |  | Operation time | hh.hh | 0 | #VALUE! | --- | --- |  | Operation time | hh.hh | 0 | 402.8333 | --- | --- |  | C5-10 | N | 1998-12-13 | 8:30 | 65.3333 | 5156.9778 | 8.27 | 13.1 | 1.3 | 0.016 | 1.2308 | 2.2 | 0.6 | 1.6 | 14.7 | 8.7 | 96 | 64 | 7.8 | 9.2 | 12 | 3.5 | 32.5 | 0.62 | 3.2 | 2.1 | 0.24 | 3.2 | 3 | NA | NA | NA | 9.36 | 12.36 | C5-20 | N | 1998-12-15 | 9:10 | 114 | 4499.2 | 8.01 | 13.1 | 1.2 | 0.011 | 0.91667 | 1.9 | 1.17 | 0.73 | 13 | 9.1 | 96 | 42 | 3.6 | 7 | 12 | 4.6 | 27.2 | 1.5 | 2.1 | 2.3 | 0.19 | 3.2 | 2.4 | NA | NA | NA | 9.29 | 11.69 | 1998 ENR Construction Cost Index (CCI base year 1913) | 5921
FAX Number | [5 empty] | 20 | 0.85 |  |  |  | Bed volumes | (10 minutes) | 0 | #VALUE! | --- | --- |  | Bed volumes | (20 minutes) | 0 | 15898.4889 | --- | --- |  | C6-10 | N | 1998-12-13 | 21:10 | 78 | 6156.8 | 8.3 | 13.2 | 1.5 | 0.017 | 1.1333 | 2.4 | 0.97 | 1.43 | 13.8 | 8.85 | 95 | 83 | 13 | 12 | 11 | 2 | 38 | 0.9 | 5.8 | 3.5 | 0.27 | 2.9 | 3.9 | NA | NA | NA | 13.37 | 17.27 | C6-20 | N | 1998-12-16 | 9:00 | 137.8333 | 5439.8222 | 7.93 | 14.2 | 1.7 | 0.013 | 0.76471 | 1.9 | 0.83 | 1.07 | 12.7 | 8.94 | 96 | 55 | 5.2 | 8.5 | 12 | 4.1 | 29.8 | BMRL | 3.2 | 2.6 | 0.49 | 3.4 | 3.2 | NA | NA | NA | 9.69 | 12.89 | 1998 Producers Price Index (PPI base year 1967 = 100) | 366
E-Mail Address (optional) |  |  |  | Estimated Run Length |  | 30 | 0.6 |  |  |  | Alkalinity | mg/L as CaCO3 | 110 | NA | 110 | #VALUE! |  | Alkalinity | mg/L as CaCO3 | 110 | 110 | 110 | 0 |  | C7-10 | Y | 1998-12-14 | 10:15 | 91.0833 | 7189.5111 | 8 | 13.2 | 1.8 | 0.0185 | 1.0325 | 2.4 | 1.15 | 1.25 | 14.05 | 8.76 | 95.5 | 86 | 13.5 | 11.5 | 11 | 2.15 | 38.15 | 1.095 | 5.7 | 3.65 | 0.25 | 3 | 3.6 | NA | NA | NA | 13.695 | 17.295 | C7-20 | Y | 1998-12-17 | 9:45 | 162.5833 | 6416.6222 | 7.85 | 13.9 | 1.6 | 0.0135 | 0.84375 | 1.9 | 1.1505 | 0.7495 | 11.75 | 8.97 | 96 | 62 | 9.65 | 10.5 | 12 | 3.25 | 35.4 | BMRL | 4.2 | 2.95 | 0.49 | 2.95 | 3.15 | NA | NA | NA | 10.59 | 13.74 | Labor Rate + Fringe ($/work-hour) | 38
|  |  |  | Bed volumes to 50% TOC breakthrough, BV50 | 4985.2797 | 40 | 0.425 |  |  |  | Total hardness | mg/L as CaCO3 | 120 | NA | 120 | #VALUE! |  | Total hardness | mg/L as CaCO3 | 120 | 130 | 125 | 8 |  | C8-10 | N | 1998-12-14 | 19:00 | 99.8333 | 7880.1778 | 8.2 | 13.2 | 2 | 0.019 | 0.95 | 2.3 | 0.88 | 1.42 | 14.4 | 8.96 | 96 | 90 | 16 | 12 | 12 | 2.2 | 42.2 | 1.4 | 5.5 | 3.1 | 0.28 | 3 | 3.6 | NA | NA | NA | 13.28 | 16.88 | C8-20 | N | 1998-12-18 | 9:30 | 186.3333 | 7353.9556 | 7.92 | 13.6 | 1.4 | 0.01 | 0.71429 | 1.9 | 1.06 | 0.84 | 11.6 | 8.88 | 96 | 66 | 7.3 | 8.8 | 11 | 2.8 | 29.9 | BMRL | 4.1 | 3.4 | 0.47 | 3.3 | 3.3 | NA | NA | NA | 11.27 | 14.57 | Labor Overhead Factor (% of labor) | 20
Technical ICR Contact Person |  |  |  | Estimated run length, BVT ( = 2 x BV50) | 9970.5595 | 50 | 0.3 |  |  |  | Calcium hardness | mg/L as CaCO3 | 84.5 | NA | 84.5 | #VALUE! |  | Calcium hardness | mg/L as CaCO3 | 84.5 | 77.2 | 80.85 | 9.0291 |  | C9-10 | N | 1998-12-15 | 18:05 | 122.9167 | 9702.2222 | 8 | 13.2 | NR | NR | #VALUE! | 2.5 | 1.4 | 1.1 | 13.1 | 9 | 96 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | C9-20 | N | 1998-12-19 | 9:30 | 210.3333 | 8301.1556 | 8.3 | 12.5 | 1.6 | 0.013 | 0.8125 | 1.9 | 0.28 | 1.62 | 11.9 | 8.89 | 95.5 | 57 | 6.4 | 9.1 | 11 | 2.2 | 28.7 | 0.92 | 3.9 | 2.8 | 0.49 | 4.3 | 4.2 | NA | NA | NA | 12.41 | 16.61 | Electric Rate ($/kW-h) | 0.065
Mailing Address |  |  |  | BVT + 30% safety factor, BVT+30% ( = 2.6 x BV50) | 12961.7273 | 60 | 0.25 |  |  |  | Ammonia | mg NH3-N / L | BMRL | NA | #DIV/0! | #VALUE! |  | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! |  | C10-10 | N | 1998-12-16 | 18:00 | 146.8333 | 11590.0444 | 8.2 | 13.5 | 2.2 | 0.022 | 1 | 2.2 | 0.86 | 1.34 | 12.4 | 8.89 | 96 | 120 | 21 | 13 | 9.9 | 1.8 | 45.7 | 1.9 | 7.1 | 3.9 | 0.33 | 2.7 | 4 | NA | NA | NA | 15.93 | 19.93 | C10-20 | N | 1998-12-21 | 9:20 | 258.1667 | 10188.9778 | 8.05 | 11.5 | 1.7 | 0.015 | 0.88235 | 2 | 0.94 | 1.06 | 11.6 | 8.8 | 96 | 74 | 12 | 12 | 11 | 2 | 37 | 0.54 | 5.4 | 3.2 | 0.24 | 2.6 | 3.3 | NA | NA | NA | 11.98 | 15.28 | Fuel Oil Rate ($/gal) | 0.58
[6 empty] | 70 | 0.21 |  |  |  | Bromide | mg/L | 54 | NA | 54 | #VALUE! |  | Bromide | mg/L | 54 | 45 | 49.5 | 18.1818 |  | C11-10 | Y | 1998-12-17 | 18:00 | 170.8333 | 13484.4444 | 8.035 | 13.75 | 2.2 | 0.0205 | 0.93182 | 2.1 | 0.985 | 1.115 | 12.8 | 8.93 | 96 | 115 | 25.5 | 13.5 | 11 | 1.35 | 51.35 | BMRL | 8.9 | 5.2 | 0.49 | 3.05 | 4.9 | NA | NA | NA | 17.64 | 22.54 | C11-20 | Y | 1998-12-23 | 9:10 | 306 | 12076.8 | 8.055 | 10.85 | 1.9 | 0.014 | 0.73684 | 2.1 | 1.055 | 1.045 | 11.75 | 9.48 | 96 | 83.5 | 14.5 | 13 | 12 | 2.05 | 41.55 | BMRL | 6.1 | 3.5 | 0.255 | 2.55 | 3.4 | NA | NA | NA | 12.405 | 15.805 | Natural Gas Rate ($/ft3) | 0.006
Phone Number |  |  |  | General RSSCT Design Parameters |  | 80 | 0.18 | [17 empty] | C12-10 | N | 1998-12-18 | 18:00 | 194.8333 | 15378.8444 | 8.07 | 13.8 | 2.3 | 0.023 | 1 | 2.3 | 1.09 | 1.21 | 11.9 | 8.85 | 96 | 120 | 25 | 14 | 10 | 1.1 | 50.1 | BMRL | 7.7 | 3.9 | BMRL | 2.2 | 3.8 | NA | NA | NA | 13.8 | 17.6 | C12-20 | N | 1998-12-27 | 10:00 | 402.8333 | 15898.4889 | 8.1 | 11.5 | 2 | 0.015 | 0.75 | 2 | 0.87 | 1.13 | 11.6 | 9 | 96 | 100 | 18 | 13 | 11 | 1.7 | 43.7 | 2.9 | 7.2 | 4 | 0.28 | 2.4 | 3.5 | NA | NA | NA | 16.78 | 20.28 | Current Process Water Rate ($/1000 gal) | 0.14
FAX Number |  |  |  | Kinematic viscosity at ToC, nLC (m2/s) | 1.1924e-06 | 100 | 0.15 |  |  |  | Group B, 3 samples per batch | [6 empty] | Group B, 3 samples per batch | [74 empty] | Modifications to Existing Plant (% of construction costs) | 25
E-Mail Address (optional) |  |  |  | RSSCT carbon particle diameter, dSC (mm) | 0.1125 | 120 | 0.125 |  |  |  | Parameter | Units | Sample B1-10 | Sample B2-10 | Sample B3-10 | Average | %SD | Parameter | Units | Sample B1-20 | Sample B2-20 | Sample B3-20 | Average | %SD
|  |  |  | Scaling factor, SF | 13.1556 | 140 | 0.106 | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | Sampling date | MM/DD/YY | 1998-12-10 | 1998-12-15 | 1998-12-18 | --- | --- | Sampling date | MM/DD/YY | 1998-12-10 | 1998-12-18 | 1998-12-27 | --- | ---
Plant Name | Upper San Leandro |  |  | RSSCT hydraulic loading rate, vSC (m/hr) | 8.5852 | 170 | 0.088 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | Sampling time | hh:mm | 16:10 | 18:05 | 18:00 | --- | --- | Sampling time | hh:mm | 16:10 | 18:00 | 10:00 | --- | ---
Treatment Plant Category | Conventional with Ozone |  |  | RSSCT flow rate, QSC (mL/min) | 25.2854 | 200 | 0.075 | is to list the pretreatment processes used in this particular RSSCT run. |  |  | Operation time | hh.hh | 1 | 122.9167 | 194.8333 | --- | --- | Operation time | hh.hh | 1 | 194.8333 | 402.8333 | --- | ---
Process Train Name | NA |  |  | Estimated total influent volume required, VSCT (L) | 747.3871 | 230 | 0.062 |  |  |  | Bed volumes | (10 minute) | 78.9333 | 9702.2222 | 15378.8444 | --- | --- | Bed volumes | (20 minute) | 39.4667 | 7689.4222 | 15898.4889 | --- | --- | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
ICR Treatment Plant Identification Number | 139 |  |  |  |  | 270 | 0.053 |  |  |  | pH | --- | 8.06 | 8.05 | 8.05 | 8.0533 | 0.071691 | pH | --- | 8.06 | 8.05 | 8.3 | 8.1367 | 1.7395 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
PWSID Number of Plant (if assigned) | CA0110005 |  |  | 10-Minute EBCT Run |  | 325 | 0.044 |  |  |  | Turbidity | ntu | 0.08 | 0.08 | 0.04 | 0.066667 | 34.641 | Turbidity | ntu | 0.08 | 0.04 | 0.08 | 0.066667 | 34.641 | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below. | [33 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below.
Historical Minimum Water Temperature (oC) | 8 |  |  | Full-scale empty bed contact time, EBCTLC (min) | 10 | 400 | 0.037 |  |  |  | Temperature | oC | 13.3 | 15.3 | 14.1 | 14.2333 | 7.0724 | Temperature | oC | 13.3 | 14.1 | 11.6 | 13 | 9.8209
Historical Average Water Temperature (oC) | 14 |  |  | Estimated full-scale run time, tLCT (days) | 90.012 | [5 empty] | Total organic carbon | mg/L | 3 | 3.2 | 3 | 3.0667 | 3.7653 | Total organic carbon | mg/L | 3 | 3 | 2.9 | 2.9667 | 1.9461 | Group D, 3 duplicate effluent samples per run (results from primary and duplicate analyses) | [33 empty] | Group D, 3 duplicate effluent samples per run (results from primary and duplicate analyses)
State Approved Plant Capacity (MGD) | 55 |  |  | RSSCT empty bed contact time, EBCTSC (min) | 0.76014 | [5 empty] | UV254 | cm-1 | 0.036 | 0.039 | 0.035 | 0.036667 | 5.6773 | UV254 | cm-1 | 0.036 | 0.035 | 0.031 | 0.034 | 7.7816 | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS
|  |  |  | Estimated RSSCT run time, tSCT (days) | 6.8421 | [5 empty] | SUVA | L/(mg*m) | 1.2 | 1.2188 | 1.1667 | 1.1951 | 2.2073 | SUVA | L/(mg*m) | 1.2 | 1.1667 | 1.069 | 1.1452 | 5.9466 | ID | Type | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6
|  |  |  | RSSCT bed length, lSC (cm) | 10.8765 | [5 empty] | SDS-Cl2 dose | mg/L | 3.7 | 3.6 | 3.7 | 3.6667 | 1.5746 | SDS-Cl2 dose | mg/L | 3.7 | 3.7 | 3 | 3.4667 | 11.658 |  |  | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L
|  |  |  | Estimated volume required for 10-minute EBCT, VSC (L) | 249.129 | [5 empty] | SDS-Free Cl2 residual | mg/L | 1.38 | 1.2 | 1.59 | 1.39 | 14.0426 | SDS-Free Cl2 residual | mg/L | 1.38 | 1.59 | 1.1 | 1.3567 | 18.1203 | C3-10 | Primary | 1998-12-12 | 10:00 | 42.8333 | 3380.9778 | 8.23 | 13.4 | 0.83 | 0.0077 | 0.92771 | 2.1 | 1.27 | 0.83 | 15.2 | 8.88 | 96 | 54 | 3.3 | 6.8 | 12 | 4.8 | 26.9 | BMRL | 2.1 | 2.4 | 0.18 | 2.9 | 2.2 | NA | NA | NA | 7.58 | 9.78 | C3-20 | Primary | 1998-12-13 | 9:30 | 66.3333 | 2617.9556 | 8.24 | 13.3 | 0.26 | 0.004 | 1.5385 | 1.5 | 0.64 | 0.86 | 14.6 | 8.81 | 96 | 13 | 1 | 1.2 | 4 | 3.4 | 9.6 | BMRL | 0.86 | 1.6 | BMRL | 1.6 | 1.1 | NA | NA | NA | 4.06 | 5.16
|  |  |  | Mass GAC required, mSC (g) | 9.6102 | [5 empty] | SDS-Cl2 demand | mg/L | 2.32 | 2.4 | 2.11 | 2.2767 | 6.5788 | SDS-Cl2 demand | mg/L | 2.32 | 2.11 | 1.9 | 2.11 | 9.9526 | D3-10 | Duplicate | 1998-12-12 | 10:00 | 42.8333 | 3380.9778 | 8.24 | 13.1 | 0.91 | 0.0079 | 0.86813 | 2.1 | 1.23 | 0.87 | 15.6 | 8.8 | 96 | 58 | 3.6 | 7.1 | 11 | 5.3 | 27 | 0.66 | 2.4 | 2.3 | 0.16 | 2.7 | 2.3 | NA | NA | NA | 8.22 | 10.52 | D3-20 | Duplicate | 1998-12-13 | 9:30 | 66.3333 | 2617.9556 | 8.2 | 13.2 | 0.45 | BMRL | #VALUE! | 1.5 | 0.86 | 0.64 | 15.8 | 8.97 | 96 | 9.6 | 0.93 | 1.2 | 3.7 | 2.2 | 8.03 | 0.745 | 1.2 | 2.3 | 0.14 | 1.4 | 0.9 | NA | NA | NA | 5.785 | 6.685
[11 empty] | SDS-Chlorination temp. | oC | 13.6 | 12.8 | 11.7 | 12.7 | 7.5113 | SDS-Chlorination temp. | oC | 13.6 | 11.7 | 11.4 | 12.2333 | 9.7523 | Avg-C3-10 | Average | --- | --- | --- | --- | 8.235 | 13.25 | 0.87 | 0.0078 | 0.89792 | 2.1 | 1.25 | 0.85 | 15.4 | 8.84 | 96 | 56 | 3.45 | 6.95 | 11.5 | 5.05 | 26.95 | 0.66 | 2.25 | 2.35 | 0.17 | 2.8 | 2.25 | #DIV/0! | #DIV/0! | #DIV/0! | 7.9 | 10.15 | Avg-C3-20 | Average | --- | --- | --- | --- | 8.22 | 13.25 | 0.355 | 0.004 | #VALUE! | 1.5 | 0.75 | 0.75 | 15.2 | 8.89 | 96 | 11.3 | 0.965 | 1.2 | 3.85 | 2.8 | 8.815 | 0.745 | 1.03 | 1.95 | 0.14 | 1.5 | 1 | #DIV/0! | #DIV/0! | #DIV/0! | 4.9225 | 5.9225
|  |  |  | 20-Minute EBCT Run | [6 empty] | SDS-Chlorination pH | --- | 8.9 | 8.92 | 8.81 | 8.8767 | 0.6601 | SDS-Chlorination pH | --- | 8.9 | 8.81 | 9.07 | 8.9267 | 1.4791 | RPD-C3-10 | RPD | --- | --- | --- | --- | 0.12143 | 2.2642 | 9.1954 | 2.5641 | 6.6352 | 0 | 3.2 | 4.7059 | 2.5974 | 0.90498 | 0 | 7.1429 | 8.6957 | 4.3165 | 8.6957 | 9.901 | 0.37106 | #VALUE! | 13.3333 | 4.2553 | 11.7647 | 7.1429 | 4.4444 | #VALUE! | #VALUE! | #VALUE! | 8.1013 | 7.2906 | RPD-C3-20 | RPD | --- | --- | --- | --- | 0.48662 | 0.75472 | 53.5211 | #VALUE! | #VALUE! | 0 | 29.3333 | 29.3333 | 7.8947 | 1.7998 | 0 | 30.0885 | 7.2539 | 0 | 7.7922 | 42.8571 | 17.8106 | #VALUE! | 33.0097 | 35.8974 | #VALUE! | 13.3333 | 20 | #VALUE! | #VALUE! | #VALUE! | 35.0432 | 25.7493
|  |  |  | Full-scale empty bed contact time, EBCTLC (min) | 20 | [5 empty] | SDS-Incubation time | hours | 96 | 96 | 96 | 96 | 0 | SDS-Incubation time | hours | 96 | 96 | 96 | 96 | 0 | C7-10 | Primary | 1998-12-14 | 10:15 | 91.0833 | 7189.5111 | 8 | 13.3 | 1.7 | 0.019 | 1.1176 | 2.4 | 1.18 | 1.22 | 14.1 | 8.76 | 95.5 | 88 | 14 | 12 | 11 | 2.2 | 39.2 | 0.99 | 5.7 | 3.6 | 0.25 | 3.1 | 3.6 | NA | NA | NA | 13.64 | 17.24 | C7-20 | Primary | 1998-12-17 | 9:45 | 162.5833 | 6416.6222 | 7.9 | 13.9 | 1.6 | 0.013 | 0.8125 | 1.9 | 1.321 | 0.579 | 11.9 | 9.08 | 96 | 57 | 11 | 11 | 12 | 3.1 | 37.1 | BMRL | 4.7 | 3.6 | 0.46 | 3.4 | 3.6 | NA | NA | NA | 12.16 | 15.76
|  |  |  | Estimated full-scale run time, tLCT (days) | 180.024 | [5 empty] | SDS-TOX | mg Cl- /L | 230 | 200 | 200 | 210 | 8.2479 | SDS-TOX | mg Cl- /L | 230 | 200 | 180 | 203.3333 | 12.3768 | D7-10 | Duplicate | 1998-12-14 | 10:15 | 91.0833 | 7189.5111 | 8 | 13.1 | 1.9 | 0.018 | 0.94737 | 2.4 | 1.12 | 1.28 | 14 | 8.76 | 95.5 | 84 | 13 | 11 | 11 | 2.1 | 37.1 | 1.2 | 5.7 | 3.7 | 0.25 | 2.9 | 3.6 | NA | NA | NA | 13.75 | 17.35 | D7-20 | Duplicate | 1998-12-17 | 9:45 | 162.5833 | 6416.6222 | 7.8 | 13.9 | 1.6 | 0.014 | 0.875 | 1.9 | 0.98 | 0.92 | 11.6 | 8.86 | 96 | 67 | 8.3 | 10 | 12 | 3.4 | 33.7 | BMRL | 3.7 | 2.3 | 0.52 | 2.5 | 2.7 | NA | NA | NA | 9.02 | 11.72
|  |  |  | RSSCT empty bed contact time, EBCTSC (min) | 1.5203 | [5 empty] | SDS-CHCl3 | mg/L | 47 | 53 | 46 | 48.6667 | 7.7793 | SDS-CHCl3 | mg/L | 47 | 46 | 41 | 44.6667 | 7.1968 | Avg-C7-10 | Average | --- | --- | --- | --- | 8 | 13.2 | 1.8 | 0.0185 | 1.0325 | 2.4 | 1.15 | 1.25 | 14.05 | 8.76 | 95.5 | 86 | 13.5 | 11.5 | 11 | 2.15 | 38.15 | 1.095 | 5.7 | 3.65 | 0.25 | 3 | 3.6 | #DIV/0! | #DIV/0! | #DIV/0! | 13.695 | 17.295 | Avg-C7-20 | Average | --- | --- | --- | --- | 7.85 | 13.9 | 1.6 | 0.0135 | 0.84375 | 1.9 | 1.1505 | 0.7495 | 11.75 | 8.97 | 96 | 62 | 9.65 | 10.5 | 12 | 3.25 | 35.4 | #DIV/0! | 4.2 | 2.95 | 0.49 | 2.95 | 3.15 | #DIV/0! | #DIV/0! | #DIV/0! | 10.59 | 13.74
|  |  |  | Estimated RSSCT run time, tSCT (days) | 13.6843 | [5 empty] | SDS-BDCM | mg/L | 17 | 20 | 17 | 18 | 9.6225 | SDS-BDCM | mg/L | 17 | 17 | 17 | 17 | 0 | RPD-C7-10 | RPD | --- | --- | --- | --- | 0 | 1.5152 | 11.1111 | 5.4054 | 16.4918 | 0 | 5.2174 | 4.8 | 0.71174 | 0 | 0 | 4.6512 | 7.4074 | 8.6957 | 0 | 4.6512 | 5.5046 | 19.1781 | 0 | 2.7397 | 0 | 6.6667 | 0 | #VALUE! | #VALUE! | #VALUE! | 0.80321 | 0.63602 | RPD-C7-20 | RPD | --- | --- | --- | --- | 1.2739 | 0 | 0 | 7.4074 | 7.4074 | 0 | 29.6393 | 45.497 | 2.5532 | 2.4526 | 0 | 16.129 | 27.9793 | 9.5238 | 0 | 9.2308 | 9.6045 | #VALUE! | 23.8095 | 44.0678 | 12.2449 | 30.5085 | 28.5714 | #VALUE! | #VALUE! | #VALUE! | 29.6506 | 29.4032
|  |  |  | RSSCT bed length, lSC (cm) | 21.753 | [5 empty] | SDS-DBCM | mg/L | 8.9 | 10 | 8.2 | 9.0333 | 10.0448 | SDS-DBCM | mg/L | 8.9 | 8.2 | 7.9 | 8.3333 | 6.1579 | C11-10 | Primary | 1998-12-17 | 18:00 | 170.8333 | 13484.4444 | 8.07 | 13.8 | 2.2 | 0.021 | 0.95455 | 2.1 | 0.96 | 1.14 | 12.2 | 9.05 | 96 | 120 | 28 | 14 | 11 | 1.5 | 54.5 | BMRL | 8.8 | 4.6 | 0.46 | 2.9 | 4.7 | NA | NA | NA | 16.76 | 21.46 | C11-20 | Primary | 1998-12-23 | 9:10 | 306 | 12076.8 | 8.05 | 10.8 | 1.9 | 0.014 | 0.73684 | 2.1 | 1.03 | 1.07 | 11.9 | 9.98 | 96 | 86 | 15 | 13 | 12 | 2 | 42 | BMRL | 6.1 | 3.4 | 0.26 | 2.5 | 3.4 | NA | NA | NA | 12.26 | 15.66
|  |  |  | Estimated volume required for 20-minute EBCT, VSC (L) | 498.2581 | [5 empty] | SDS-CHBr3 | mg/L | 0.73 | 0.68 | 0.53 | 0.64667 | 16.0954 | SDS-CHBr3 | mg/L | 0.73 | 0.53 | 0.51 | 0.59 | 20.6195 | D11-10 | Duplicate | 1998-12-17 | 18:00 | 170.8333 | 13484.4444 | 8 | 13.7 | 2.2 | 0.02 | 0.90909 | 2.1 | 1.01 | 1.09 | 13.4 | 8.81 | 96 | 110 | 23 | 13 | 11 | 1.2 | 48.2 | BMRL | 9 | 5.8 | 0.52 | 3.2 | 5.1 | NA | NA | NA | 18.52 | 23.62 | D11-20 | Duplicate | 1998-12-23 | 9:10 | 306 | 12076.8 | 8.06 | 10.9 | 1.9 | 0.014 | 0.73684 | 2.1 | 1.08 | 1.02 | 11.6 | 8.98 | 96 | 81 | 14 | 13 | 12 | 2.1 | 41.1 | BMRL | 6.1 | 3.6 | 0.25 | 2.6 | 3.4 | NA | NA | NA | 12.55 | 15.95
|  |  |  | Mass GAC required, mSC (g) | 19.2204 | [5 empty] | SDS-THM4 | mg/L | 73.63 | 83.68 | 71.73 | 76.3467 | 8.411 | SDS-THM4 | mg/L | 73.63 | 71.73 | 66.41 | 70.59 | 5.3018 | Avg-C11-10 | Average | --- | --- | --- | --- | 8.035 | 13.75 | 2.2 | 0.0205 | 0.93182 | 2.1 | 0.985 | 1.115 | 12.8 | 8.93 | 96 | 115 | 25.5 | 13.5 | 11 | 1.35 | 51.35 | #DIV/0! | 8.9 | 5.2 | 0.49 | 3.05 | 4.9 | #DIV/0! | #DIV/0! | #DIV/0! | 17.64 | 22.54 | Avg-C11-20 | Average | --- | --- | --- | --- | 8.055 | 10.85 | 1.9 | 0.014 | 0.73684 | 2.1 | 1.055 | 1.045 | 11.75 | 9.48 | 96 | 83.5 | 14.5 | 13 | 12 | 2.05 | 41.55 | #DIV/0! | 6.1 | 3.5 | 0.255 | 2.55 | 3.4 | #DIV/0! | #DIV/0! | #DIV/0! | 12.405 | 15.805
[11 empty] | SDS-MCAA* | mg/L | 4.8 | 4.4 | BMRL | 4.6 | 6.1488 | SDS-MCAA* | mg/L | 4.8 | BMRL | 4.8 | 4.8 | 0 | RPD-C11-10 | RPD | --- | --- | --- | --- | 0.87119 | 0.72727 | 0 | 4.878 | 4.878 | 0 | 5.0761 | 4.4843 | 9.375 | 2.6876 | 0 | 8.6957 | 19.6078 | 7.4074 | 0 | 22.2222 | 12.2687 | #VALUE! | 2.2472 | 23.0769 | 12.2449 | 9.8361 | 8.1633 | #VALUE! | #VALUE! | #VALUE! | 9.9773 | 9.583 | RPD-C11-20 | RPD | --- | --- | --- | --- | 0.12415 | 0.92166 | 0 | 0 | 0 | 0 | 4.7393 | 4.7847 | 2.5532 | 10.5485 | 0 | 5.988 | 6.8966 | 0 | 0 | 4.878 | 2.1661 | #VALUE! | 0 | 5.7143 | 3.9216 | 3.9216 | 0 | #VALUE! | #VALUE! | #VALUE! | 2.3378 | 1.8349
[11 empty] | SDS-DCAA* | mg/L | 17 | 16 | 16 | 16.3333 | 3.5348 | SDS-DCAA* | mg/L | 17 | 16 | 14 | 15.6667 | 9.7502 | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[11 empty] | SDS-TCAA* | mg/L | 8.5 | 9.1 | 11 | 9.5333 | 13.6901 | SDS-TCAA* | mg/L | 8.5 | 11 | 8 | 9.1667 | 17.5339 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
[11 empty] | SDS-MBAA* | mg/L | 0.26 | 0.43 | 0.62 | 0.43667 | 41.2426 | SDS-MBAA* | mg/L | 0.26 | 0.62 | 0.17 | 0.35 | 68.0336
[11 empty] | SDS-DBAA* | mg/L | 2.2 | 2 | 2.4 | 2.2 | 9.0909 | SDS-DBAA* | mg/L | 2.2 | 2.4 | 1.9 | 2.1667 | 11.6151
[11 empty] | SDS-BCAA* | mg/L | 5.4 | 5.4 | 6 | 5.6 | 6.1859 | SDS-BCAA* | mg/L | 5.4 | 6 | 5.1 | 5.5 | 8.332
[11 empty] | SDS-TBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0!
[11 empty] | SDS-CDBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0!
[11 empty] | SDS-DCBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0!
[11 empty] | SDS-HAA5 | mg/L | 32.76 | 31.93 | 30.02 | 31.57 | 4.4505 | SDS-HAA5 | mg/L | 32.76 | 30.02 | 28.87 | 30.55 | 6.5415
[11 empty] | SDS-HAA6 | mg/L | 38.16 | 37.33 | 36.02 | 37.17 | 2.9027 | SDS-HAA6 | mg/L | 38.16 | 36.02 | 33.97 | 36.05 | 5.8118
[11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [6 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [6 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
Note on N9: Reviewer M.H. (10/25/99): Per utility, "No samples were collected for THM, HAA, TOX."
Note on T10: Sample A2-10 was not collected. However, A2-20 was collected and analyzed.
Note on AG29: Duplicate samples were collected in two different bottles, one right after another. They were not collected in the same bottle. This was done to reduce probability of contamination and loss of any VOCs such as chloroform.
Note on BP29: Duplicate samples were collected in two different bottles, one right after another. They were not collected in the same bottle. This was done to reduce probability of contamination and loss of any VOCs such as chloroform.
Note on BP33: Duplicate samples were collected in two different bottles right after another. They were not collecyed in the same bottle. This was done to reduce probability of contamination and loss of any VOCs.
Note on BX5: asheikho: Run was terminated before 70% breakthrough because of high headloss across the RSSCT column.
Note on CH14: asheikho: Data verified.

## Sheet4. 4th Quarter
FIELD-SET 4: 4th QUARTER RSSCT RESULTS (FILE: gacrssct.xls)
Field 4-1: PWS And Treatment Plant Data |  | Field 4-2: Full-Scale GAC Characteristics1 |  | Field 4-3: RSSCT Design Parameters |  |  |  | Field 4-4: Pretreatment Used Prior To GAC1 |  |  | Field 4-5: GAC Influent Water Quality For The 10-Minute EBCT Run | [6 empty] | Field 4-6: GAC Influent Water Quality For The 20-Minute EBCT Run1 | [6 empty] | Field 4-7: GAC Effluent Water Quality For The 10-Minute EBCT Run1 | [15 empty] | Field 4-7: GAC Effluent Water Quality For The 10-Minute EBCT Run (continued) | [17 empty] | Field 4-8: GAC Effluent Water Quality For The 20-Minute EBCT Run1 | [14 empty] | Field 4-8: GAC Effluent Water Quality For The 20-Minute EBCT Run (continued) | [18 empty] | Field 4-9: GAC Cost Parameters
|  |  |  | Input Design Parameters |  | US Standard Mesh Sizes | [18 empty] | Group C, 12 effluent samples per run | [33 empty] | Group C, 12 effluent samples per run
PWS Name | East Bay Municipal Utility District | Carbon manufacturer | Calgon | RSSCT influent TOC (mg/L) | 2.6 | US standard | Opening | Process | Description | Scale | 10-min. EBCT Start Date | 1999-02-02 | [5 empty] | 20-min. EBCT Start Date | 1999-02-02 | [5 empty] | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Cost Parameter | Parameter value
Public Water System Identification Number | CA0110005 | Carbon trade name | Filtrasorb 300 | Inner diameter of the RSSCT column, DSC (mm) | 15 | mesh size | (mm) | Coagulation | Alum (Al2(SO4)3.14H2O) 27.5 mg/L, Cationic Polymer 1 mg/L | Full-Scale | 10-min. EBCT Start Time | 11:00 | [5 empty] | 20-min. EBCT Start Time | 11:00 | [5 empty] | ID | duplicated? | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | Capital Recovery Interest Rate (%) | 5.5
Water Industry Data Base Number (optional) | NA | Carbon type | bituminous | Minimum RSSCT Reynolds number, ReSC, min | 0.5 | 4 | 4.75 | Flocculation | 4-stage, Detention Time = 88 minutes | Full-Scale | [15 empty] | Y/N | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | Capital Recovery Period (years) | 30
|  | Original GAC mesh size, upper (US standard mesh) | 8 | Full-scale operating temperature, ToC (oC) | 10 | 6 | 3.35 | Sedimentation | Conventional, Detention Time = 173 minutes | Full-Scale | Group A, 2 samples per batch | [6 empty] | Group A, 2 samples per batch | [6 empty] | C1-10 | N | 1999-02-02 | 12:00 | 1 | 78.9333 | 8.1 | 11.5 | 0.29 | BMRL | #VALUE! | 1.2 | 0.8 | 0.4 | 12.5 | 8.9 | 95 | 40 | 0.46 | 0.11 | 0.4 | 0.17 | 1.14 | BMRL | BMRL | 0.19 | BMRL | 0.32 | 0.14 | NA | NA | NA | 0.51 | 0.65 | C1-20 | N | 1999-02-02 | 13:00 | 2 | 78.9333 | 8.53 | 11.7 | 0.31 | BMRL | #VALUE! | 1.2 | 0.8 | 0.4 | 12.5 | 9.1 | 95 | 5.3 | 0.31 | 0.19 | 0.58 | 0.25 | 1.33 | BMRL | BMRL | 0.2 | BMRL | 0.32 | 0.14 | NA | NA | NA | 0.52 | 0.66 | Overhead & Profit Factor (% of construction costs) | 15
Official ICR Contact Person |  | Original GAC mesh size, lower (US standard mesh) | 30 | Full-scale bed porosity, eLC | 0.45 | 8 | 2.36 | Ozonation | Dose = 3.3 mg/L | Full-Scale | Parameter | Units | Sample A1-10 | Sample A2-10 | Average | RPD |  | Parameter | Units | Sample A1-20 | Sample A2-20 | Average | RPD |  | C2-10 | N | 1999-02-03 | 9:25 | 22.4167 | 1769.4222 | 7.92 | 11.6 | 0.49 | BMRL | #VALUE! | 1.2 | 0.77 | 0.43 | 12.2 | 8.9 | 98 | 26 | 0.71 | 1.8 | 4.9 | 2.6 | 10.01 | BMRL | 0.13 | 0.24 | BMRL | 1.1 | 0.64 | NA | NA | NA | 1.47 | 2.11 | C2-20 | N | 1999-02-04 | 9:26 | 46.4333 | 1832.5689 | 7.91 | 12.5 | 0.44 | BMRL | #VALUE! | 1.2 | 0.76 | 0.44 | 13.1 | 8.92 | 97 | BMRL | 0.41 | 0.5 | 1.8 | 1 | 3.71 | BMRL | BMRL | 0.2 | BMRL | 0.67 | 0.37 | NA | NA | NA | 0.87 | 1.24 | Special Sitework Factor (% of construction costs) | 20
Mailing Address |  | Original carbon particle diameter, dLC (mm) | 1.48 | Measured RSSCT dry bed density, rSC (g/cm3) | 0.5 | 10 | 2 | Filtration | GAC/Sand, GAC Depth = 18 inch, Sand Depth = 12 inch, Effective Size = 0.80-1.0 mm, UC = 1.8 , SG = 1.65, EBCT = 3.6 minutes (for GAC only), Length of GAC in Service = 9 years | Full-Scale | Sampling date | MM/DD/YY | 1999-02-02 | 1999-02-15 | --- | --- |  | Sampling date | MM/DD/YY | 1999-02-02 | 1999-02-26 | --- | --- |  | C3-10 | Y | 1999-02-04 | 9:26 | 46.4333 | 3665.1378 | 7.84 | 12.05 | 1 | 0.006 | 0.6 | 1.2 | 0.53 | 0.67 | 13.25 | 8.945 | 97 | 34 | 5.65 | 6.35 | 7.7 | 1.75 | 21.45 | 0.37 | 2.6 | 1.09 | 0.22 | 1.8 | 1.75 | NA | NA | NA | 5.785 | 7.535 | C3-20 | Y | 1999-02-06 | 11:00 | 96 | 3788.8 | 8 | 12.05 | 0.845 | BMRL | #VALUE! | 1.3 | 0.745 | 0.555 | 12.05 | 8.84 | 96 | 32.5 | 1.85 | 4.6 | 8.2 | 3 | 17.65 | 0.38 | 0.96 | 0.465 | BMRL | 1.9 | 1.45 | NA | NA | NA | 3.515 | 4.965 | Construction Contingencies (% of construction costs) | 15
|  | 1: These are the characteristics before the carbon is ground for RSSCT experiments. |  | RSSCT GAC mesh size, upper (US standard mesh) | 100 | 12 | 1.68 | Prefiltration | 1um - Polypropylene Cartridge Filter | Bench-Scale | Sampling time | hh:mm | 11:00 | 8:30 | --- | --- |  | Sampling time | hh:mm | 11:00 | 9:45 | --- | --- |  | C4-10 | N | 1999-02-05 | 9:00 | 70 | 5525.3333 | 7.92 | 12.1 | 1.3 | 0.009 | 0.69231 | 1.3 | 0.46 | 0.84 | 13.1 | 8.96 | 96 | 39 | 11 | 8.3 | 7.5 | 0.99 | 27.79 | BMRL | 3.7 | 1.1 | 0.16 | 1.6 | 2.2 | NA | NA | NA | 6.56 | 8.76 | C4-20 | N | 1999-02-08 | 9:15 | 142.25 | 5614.1333 | 8.04 | 13.5 | 1.2 | 0.0092 | 0.76667 | 1.4 | 0.9 | 0.5 | 11.9 | 9 | 96 | 61 | 8.5 | 9 | 9.3 | 1.8 | 28.6 | 0.66 | 3.6 | 1.5 | BMRL | 2.5 | 2.8 | NA | NA | NA | 8.26 | 11.06 | Engineering Fee Factor (% of construction costs) | 15
Phone Number |  |  |  | RSSCT GAC mesh size, lower (US standard mesh) | 200 | 16 | 1.18 |  |  |  | Operation time | hh.hh | 0 | 309.5 | --- | --- |  | Operation time | hh.hh | 0 | 574.75 | --- | --- |  | C5-10 | N | 1999-02-06 | 11:00 | 96 | 7577.6 | 8.02 | 12.2 | 1.4 | 0.009 | 0.64286 | 1.5 | 0.55 | 0.95 | 11.9 | 8.87 | 96 | 70 | 14 | 9.3 | 7.6 | 0.8 | 31.7 | BMRL | 4.7 | 1.7 | 0.25 | 1.7 | 2.4 | NA | NA | NA | 8.35 | 10.75 | C5-20 | N | 1999-02-10 | 9:20 | 190.3333 | 7511.8222 | 8.07 | 12.2 | 1.3 | 0.01 | 0.76923 | 1.6 | 0.87 | 0.73 | 12.2 | 9.1 | 96 | 78 | 13 | 10 | 8.2 | 1.4 | 32.6 | 0.95 | 4.6 | 1.7 | 0.21 | 2.3 | 3.1 | NA | NA | NA | 9.76 | 12.86 | 1998 ENR Construction Cost Index (CCI base year 1913) | 5921
FAX Number | [5 empty] | 20 | 0.85 |  |  |  | Bed volumes | (10 minutes) | 0 | 24429.8667 | --- | --- |  | Bed volumes | (20 minutes) | 0 | 22683.4667 | --- | --- |  | C6-10 | N | 1999-02-07 | 12:00 | 121 | 9550.9333 | 8 | 12.2 | 1.6 | 0.011 | 0.6875 | 1.6 | 0.6 | 1 | 11.6 | 8.9 | 95 | 99 | 18 | 10 | 7.8 | 0.81 | 36.61 | BMRL | 6.9 | 2.9 | 0.21 | 2.1 | 3.4 | NA | NA | NA | 12.11 | 15.51 | C6-20 | N | 1999-02-11 | 9:00 | 214 | 8445.8667 | 8.11 | 11.8 | 1.3 | 0.009 | 0.69231 | 1.8 | 0.83 | 0.97 | 12 | 9 | 96 | 74 | 14 | 10 | 8.7 | 1.2 | 33.9 | 0.76 | 4.7 | 1.7 | 0.23 | 2.2 | 3 | NA | NA | NA | 9.59 | 12.59 | 1998 Producers Price Index (PPI base year 1967 = 100) | 366
E-Mail Address (optional) |  |  |  | Estimated Run Length |  | 30 | 0.6 |  |  |  | Alkalinity | mg/L as CaCO3 | 100 | 100 | 100 | 0 |  | Alkalinity | mg/L as CaCO3 | 100 | 100 | 100 | 0 |  | C7-10 | Y | 1999-02-08 | 9:15 | 142.25 | 11228.2667 | 8.035 | 12.7 | 1.65 | 0.0155 | 0.93934 | 1.6 | 0.61 | 0.99 | 11.8 | 9.15 | 96 | 105 | 24.5 | 12.5 | 7.55 | 0.5 | 45.05 | BMRL | 7 | 2.25 | 0.2 | 1.75 | 3.2 | NA | NA | NA | 11.1 | 14.3 | C7-20 | Y | 1999-02-13 | 9:00 | 262 | 10340.2667 | 8.175 | 13.6 | 1.55 | 0.0125 | 0.80645 | 1.8 | 0.805 | 0.995 | 13.7 | 9.035 | 96.5 | 125 | 18 | 11 | 8.15 | 0.825 | 37.975 | BMRL | 6 | 2.55 | 0.24 | 2.1 | 3.35 | NA | NA | NA | 10.77 | 14.12 | Labor Rate + Fringe ($/work-hour) | 38
|  |  |  | Bed volumes to 50% TOC breakthrough, BV50 | 6266.0576 | 40 | 0.425 |  |  |  | Total hardness | mg/L as CaCO3 | 120 | 120 | 120 | 0 |  | Total hardness | mg/L as CaCO3 | 120 | 110 | 115 | 8.6957 |  | C8-10 | N | 1999-02-09 | 9:15 | 166.25 | 13122.6667 | 8.14 | 14.1 | 2 | 0.016 | 0.8 | 1.9 | 0.9 | 1 | 13.4 | 8.96 | 96 | 120 | 25 | 11 | 7.6 | 0.56 | 44.16 | BMRL | 8.2 | 3.4 | 0.15 | 1.9 | 3.5 | NA | NA | NA | 13.65 | 17.15 | C8-20 | N | 1999-02-15 | 8:30 | 309.5 | 12214.9333 | 8.1 | 12.5 | 1.7 | 0.013 | 0.76471 | 1.8 | 0.59 | 1.21 | 13.7 | 8.87 | 96 | 99 | 15 | 10 | 8.3 | 0.79 | 34.09 | BMRL | 6.5 | 2.7 | 0.21 | 2.2 | 3.6 | NA | NA | NA | 11.61 | 15.21 | Labor Overhead Factor (% of labor) | 20
Technical ICR Contact Person |  |  |  | Estimated run length, BVT ( = 2 x BV50) | 12532.1152 | 50 | 0.3 |  |  |  | Calcium hardness | mg/L as CaCO3 | 74.8 | NA | 74.8 | #VALUE! |  | Calcium hardness | mg/L as CaCO3 | 74.8 | 74 | 74.4 | 1.0753 |  | C9-10 | N | 1999-02-10 | 9:20 | 190.3333 | 15023.6444 | 8.11 | 11.8 | 1.8 | 0.017 | 0.94444 | 2 | 0.86 | 1.14 | 12.7 | 9.1 | 96 | 140 | 30 | 13 | 7.4 | NR | NR | BMRL | 9.2 | 3.4 | 0.24 | 1.8 | 3.7 | NA | NA | NA | 14.64 | 18.34 | C9-20 | N | 1999-02-18 | 7:15 | 380.25 | 15007.2 | 8.13 | 12.5 | 1.7 | 0.016 | 0.94118 | 1.9 | 1.15 | 0.75 | 13.1 | 8.93 | 97.5 | 110 | 21 | 11 | 6.9 | 0.56 | 39.46 | BMRL | 8.2 | 3.8 | 0.28 | 1.8 | 3.7 | NA | NA | NA | 14.08 | 17.78 | Electric Rate ($/kW-h) | 0.065
Mailing Address |  |  |  | BVT + 30% safety factor, BVT+30% ( = 2.6 x BV50) | 16291.7497 | 60 | 0.25 |  |  |  | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! |  | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! |  | C10-10 | N | 1999-02-11 | 9:00 | 214 | 16891.7333 | 8.07 | 11.5 | 1.9 | 0.016 | 0.84211 | 2 | 0.93 | 1.07 | 12 | 8.7 | 96 | 110 | 28 | 12 | 7.3 | 0.42 | 47.72 | BMRL | 9.3 | 4.3 | 0.24 | 2 | 3.9 | NA | NA | NA | 15.84 | 19.74 | C10-20 | N | 1999-02-21 | 11:10 | 456.1667 | 18003.3778 | 8.2 | 12.8 | 1.8 | 0.018 | 1 | 2.1 | 0.78 | 1.32 | 12.9 | 8.93 | 94.5 | 100 | 22 | 11 | 7 | 0.66 | 40.66 | NR | NR | NR | 0.26 | 1 | 6.7 | NA | NA | NA | NR | NR | Fuel Oil Rate ($/gal) | 0.58
[6 empty] | 70 | 0.21 |  |  |  | Bromide | mg/L | 36 | 38 | 37 | 5.4054 |  | Bromide | mg/L | 36 | 41 | 38.5 | 12.987 |  | C11-10 | Y | 1999-02-13 | 9:00 | 262 | 20680.5333 | 8.15 | 12.8 | 1.95 | 0.0185 | 0.94868 | 2.1 | 0.77 | 1.33 | 12.6 | 9.045 | 96.5 | 135 | 30.5 | 12 | 6.5 | 0.435 | 49.435 | BMRL | 9.45 | 3.7 | 0.23 | 1.8 | 3.8 | NA | NA | NA | 15.18 | 18.98 | C11-20 | Y | 1999-02-24 | 10:00 | 527 | 20798.9333 | 8.11 | 12.95 | 1.95 | NR | #VALUE! | 2.1 | 1.13 | 0.97 | 13.35 | 8.955 | 96 | 145 | 26 | 12 | 7.9 | 0.62 | 46.52 | BMRL | 18 | 1.785 | 0.31 | 1.005 | 3.65 | NA | NA | NA | 18.58 | 20.08 | Natural Gas Rate ($/ft3) | 0.006
Phone Number |  |  |  | General RSSCT Design Parameters |  | 80 | 0.18 | [17 empty] | C12-10 | N | 1999-02-15 | 10:00 | 311 | 24548.2667 | 8.1 | 12.5 | 2.1 | 0.019 | 0.90476 | 2.1 | 0.74 | 1.36 | 12.1 | 8.92 | 96 | 130 | 30 | 12 | 6.8 | 0.4 | 49.2 | BMRL | 9.6 | 4.4 | 0.2 | 1.8 | 3.9 | NA | NA | NA | 16 | 19.9 | C12-20 | N | 1999-02-26 | 9:45 | 574.75 | 22683.4667 | 8.19 | 14.1 | 2 | 0.021 | 1.05 | 2.2 | 0.94 | 1.26 | 13.8 | 8.93 | 109 | 210 | 30 | 13 | 8 | 0.43 | 51.43 | BMRL | 9.7 | 4.4 | 0.2 | 1.9 | 4.1 | NA | NA | NA | 16.2 | 20.3 | Current Process Water Rate ($/1000 gal) | 0.14
FAX Number |  |  |  | Kinematic viscosity at ToC, nLC (m2/s) | 1.3222e-06 | 100 | 0.15 |  |  |  | Group B, 3 samples per batch | [6 empty] | Group B, 3 samples per batch | [74 empty] | Modifications to Existing Plant (% of construction costs) | 25
E-Mail Address (optional) |  |  |  | RSSCT carbon particle diameter, dSC (mm) | 0.1125 | 120 | 0.125 |  |  |  | Parameter | Units | Sample B1-10 | Sample B2-10 | Sample B3-10 | Average | %SD | Parameter | Units | Sample B1-20 | Sample B2-20 | Sample B3-20 | Average | %SD
|  |  |  | Scaling factor, SF | 13.1556 | 140 | 0.106 | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | Sampling date | MM/DD/YY | 1999-02-02 | 1999-02-09 | 1999-02-15 | --- | --- | Sampling date | MM/DD/YY | 1999-02-02 | 1999-02-15 | 1999-02-26 | --- | ---
Plant Name | Upper San Leandro |  |  | RSSCT hydraulic loading rate, vSC (m/hr) | 9.5196 | 170 | 0.088 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | Sampling time | hh:mm | 11:55 | 9:15 | 8:30 | --- | --- | Sampling time | hh:mm | 12:00 | 8:30 | 9:45 | --- | ---
Treatment Plant Category | Conventional with Ozone |  |  | RSSCT flow rate, QSC (mL/min) | 28.0375 | 200 | 0.075 | is to list the pretreatment processes used in this particular RSSCT run. |  |  | Operation time | hh.hh | 0.91667 | 166.25 | 309.5 | --- | --- | Operation time | hh.hh | 1 | 309.5 | 574.75 | --- | ---
Process Train Name | NA |  |  | Estimated total influent volume required, VSCT (L) | 1041.6423 | 230 | 0.062 |  |  |  | Bed volumes | (10 minute) | 72.3556 | 13122.6667 | 24429.8667 | --- | --- | Bed volumes | (20 minute) | 39.4667 | 12214.9333 | 22683.4667 | --- | --- | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
ICR Treatment Plant Identification Number | 139 |  |  |  |  | 270 | 0.053 |  |  |  | pH | --- | 7.98 | 8.07 | 8 | 8.0167 | 0.5895 | pH | --- | 7.98 | 8 | 8.18 | 8.0533 | 1.3678 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
PWSID Number of Plant (if assigned) | CA0110005 |  |  | 10-Minute EBCT Run |  | 325 | 0.044 |  |  |  | Turbidity | ntu | 0.1 | NA | 0.08 | 0.09 | 15.7135 | Turbidity | ntu | 0.1 | 0.08 | 0.067 | 0.082333 | 20.1902 | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below. | [33 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below.
Historical Minimum Water Temperature (oC) | 8 |  |  | Full-scale empty bed contact time, EBCTLC (min) | 10 | 400 | 0.037 |  |  |  | Temperature | oC | 11.5 | 14.7 | 11.6 | 12.6 | 14.4392 | Temperature | oC | 11.5 | 11.6 | 12.6 | 11.9 | 5.1116
Historical Average Water Temperature (oC) | 14 |  |  | Estimated full-scale run time, tLCT (days) | 113.1372 | [5 empty] | Total organic carbon | mg/L | 2.7 | 2.7 | 2.6 | 2.6667 | 2.1651 | Total organic carbon | mg/L | 2.7 | 2.6 | 2.5 | 2.6 | 3.8462 | Group D, 3 duplicate effluent samples per run (results from primary and duplicate analyses) | [33 empty] | Group D, 3 duplicate effluent samples per run (results from primary and duplicate analyses)
State Approved Plant Capacity (MGD) | 55 |  |  | RSSCT empty bed contact time, EBCTSC (min) | 0.76014 | [5 empty] | UV254 | cm-1 | 0.028 | 0.027 | 0.027 | 0.027333 | 2.1123 | UV254 | cm-1 | 0.028 | 0.027 | 0.028 | 0.027667 | 2.0868 | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS
|  |  |  | Estimated RSSCT run time, tSCT (days) | 8.6 | [5 empty] | SUVA | L/(mg*m) | 1.037 | 1 | 1.0385 | 1.0252 | 2.1271 | SUVA | L/(mg*m) | 1.037 | 1.0385 | 1.12 | 1.0652 | 4.4587 | ID | Type | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6
|  |  |  | RSSCT bed length, lSC (cm) | 12.0603 | [5 empty] | SDS-Cl2 dose | mg/L | 2.7 | 2.7 | 2.5 | 2.6333 | 4.3849 | SDS-Cl2 dose | mg/L | 2.7 | 2.5 | 2.5 | 2.5667 | 4.4988 |  |  | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L
|  |  |  | Estimated volume required for 10-minute EBCT, VSC (L) | 347.2141 | [5 empty] | SDS-Free Cl2 residual | mg/L | 0.47 | 1.04 | 0.81 | 0.77333 | 37.0815 | SDS-Free Cl2 residual | mg/L | 0.47 | 0.81 | 0.49 | 0.59 | 32.3369 | C3-10 | Primary | 1999-02-04 | 9:26 | 46.4333 | 3665.1378 | 7.85 | 12.1 | 1 | 0.006 | 0.6 | 1.2 | 0.52 | 0.68 | 14.1 | 8.91 | 97 | 36 | 5.2 | 6 | 7.6 | 1.7 | 20.5 | BMRL | 2 | 0.68 | 0.22 | 1.8 | 1.7 | NA | NA | NA | 4.7 | 6.4 | C3-20 | Primary | 1999-02-06 | 11:00 | 96 | 3788.8 | 8 | 12.1 | 0.87 | BMRL | #VALUE! | 1.3 | 0.69 | 0.61 | 11.8 | 8.84 | 96 | 27 | 1.8 | 4.5 | 8 | 3 | 17.3 | 0.38 | 0.95 | 0.47 | BMRL | 1.8 | 1.4 | NA | NA | NA | 3.6 | 5
|  |  |  | Mass GAC required, mSC (g) | 10.6561 | [5 empty] | SDS-Cl2 demand | mg/L | 2.23 | 1.66 | 1.69 | 1.86 | 17.2463 | SDS-Cl2 demand | mg/L | 2.23 | 1.69 | 2.01 | 1.9767 | 13.7372 | D3-10 | Duplicate | 1999-02-04 | 9:26 | 46.4333 | 3665.1378 | 7.83 | 12 | 1 | 0.006 | 0.6 | 1.2 | 0.54 | 0.66 | 12.4 | 8.98 | 97 | 32 | 6.1 | 6.7 | 7.8 | 1.8 | 22.4 | 0.37 | 3.2 | 1.5 | BMRL | 1.8 | 1.8 | NA | NA | NA | 6.87 | 8.67 | D3-20 | Duplicate | 1999-02-06 | 12:00 | 97 | 3828.2667 | 8 | 12 | 0.82 | BMRL | #VALUE! | 1.3 | 0.8 | 0.5 | 12.3 | 8.84 | 96 | 38 | 1.9 | 4.7 | 8.4 | 3 | 18 | BMRL | 0.97 | 0.46 | BMRL | 2 | 1.5 | NA | NA | NA | 3.43 | 4.93
[11 empty] | SDS-Chlorination temp. | oC | 12.5 | 13.7 | 12.3 | 12.8333 | 5.9002 | SDS-Chlorination temp. | oC | 12.5 | 12.3 | 13.45 | 12.75 | 4.8189 | Avg-C3-10 | Average | --- | --- | --- | --- | 7.84 | 12.05 | 1 | 0.006 | 0.6 | 1.2 | 0.53 | 0.67 | 13.25 | 8.945 | 97 | 34 | 5.65 | 6.35 | 7.7 | 1.75 | 21.45 | 0.37 | 2.6 | 1.09 | 0.22 | 1.8 | 1.75 | #DIV/0! | #DIV/0! | #DIV/0! | 5.785 | 7.535 | Avg-C3-20 | Average | --- | --- | --- | --- | 8 | 12.05 | 0.845 | #DIV/0! | #VALUE! | 1.3 | 0.745 | 0.555 | 12.05 | 8.84 | 96 | 32.5 | 1.85 | 4.6 | 8.2 | 3 | 17.65 | 0.38 | 0.96 | 0.465 | #DIV/0! | 1.9 | 1.45 | #DIV/0! | #DIV/0! | #DIV/0! | 3.515 | 4.965
|  |  |  | 20-Minute EBCT Run | [6 empty] | SDS-Chlorination pH | --- | 8.9 | 8.9 | 8.86 | 8.8867 | 0.25987 | SDS-Chlorination pH | --- | 8.9 | 8.86 | 9.07 | 8.9433 | 1.2468 | RPD-C3-10 | RPD | --- | --- | --- | --- | 0.2551 | 0.82988 | 0 | 0 | 0 | 0 | 3.7736 | 2.9851 | 12.8302 | 0.78256 | 0 | 11.7647 | 15.9292 | 11.0236 | 2.5974 | 5.7143 | 8.8578 | #VALUE! | 46.1538 | 75.2294 | #VALUE! | 0 | 5.7143 | #VALUE! | #VALUE! | #VALUE! | 37.5108 | 30.1261 | RPD-C3-20 | RPD | --- | --- | --- | --- | 0 | 0.82988 | 5.9172 | #VALUE! | #VALUE! | 0 | 14.7651 | 19.8198 | 4.1494 | 0 | 0 | 33.8462 | 5.4054 | 4.3478 | 4.878 | 0 | 3.966 | #VALUE! | 2.0833 | 2.1505 | #VALUE! | 10.5263 | 6.8966 | #VALUE! | #VALUE! | #VALUE! | 4.8364 | 1.4099
|  |  |  | Full-scale empty bed contact time, EBCTLC (min) | 20 | [5 empty] | SDS-Incubation time | hours | 95.5 | 96 | 98 | 96.5 | 1.3709 | SDS-Incubation time | hours | 95.5 | 98 | 98 | 97.1667 | 1.4855 | C7-10 | Primary | 1999-02-08 | 9:15 | 142.25 | 11228.2667 | 8.08 | 13.1 | 1.7 | 0.016 | 0.94118 | 1.6 | 0.58 | 1.02 | 11.7 | 9.2 | 96 | 110 | 26 | 13 | 7.7 | 0.57 | 47.27 | BMRL | 6.4 | 1.7 | BMRL | 1.7 | 3 | NA | NA | NA | 9.8 | 12.8 | C7-20 | Primary | 1999-02-13 | 9:00 | 262 | 10340.2667 | 8.15 | 14.7 | 1.5 | 0.012 | 0.8 | 1.8 | 0.76 | 1.04 | 13.3 | 9.07 | 96.5 | 110 | 18 | 11 | 8.2 | 0.83 | 38.03 | BMRL | 5.4 | 2.2 | BMRL | 1.8 | 2.9 | NA | NA | NA | 9.4 | 12.3
|  |  |  | Estimated full-scale run time, tLCT (days) | 226.2743 | [5 empty] | SDS-TOX | mg Cl- /L | 200 | 200 | 190 | 196.6667 | 2.9357 | SDS-TOX | mg Cl- /L | 200 | 190 | 240 | 210 | 12.5988 | D7-10 | Duplicate | 1999-02-08 | 10:30 | 143.5 | 11326.9333 | 7.99 | 12.3 | 1.6 | 0.015 | 0.9375 | 1.6 | 0.64 | 0.96 | 11.9 | 9.1 | 96 | 100 | 23 | 12 | 7.4 | 0.43 | 42.83 | BMRL | 7.6 | 2.8 | 0.2 | 1.8 | 3.4 | NA | NA | NA | 12.4 | 15.8 | D7-20 | Duplicate | 1999-02-13 | 10:00 | 263 | 10379.7333 | 8.2 | 12.5 | 1.6 | 0.013 | 0.8125 | 1.8 | 0.85 | 0.95 | 14.1 | 9 | 96.5 | 140 | 18 | 11 | 8.1 | 0.82 | 37.92 | BMRL | 6.6 | 2.9 | 0.24 | 2.4 | 3.8 | NA | NA | NA | 12.14 | 15.94
|  |  |  | RSSCT empty bed contact time, EBCTSC (min) | 1.5203 | [5 empty] | SDS-CHCl3 | mg/L | 43 | 49 | 41 | 44.3333 | 9.391 | SDS-CHCl3 | mg/L | 43 | 41 | 49 | 44.3333 | 9.391 | Avg-C7-10 | Average | --- | --- | --- | --- | 8.035 | 12.7 | 1.65 | 0.0155 | 0.93934 | 1.6 | 0.61 | 0.99 | 11.8 | 9.15 | 96 | 105 | 24.5 | 12.5 | 7.55 | 0.5 | 45.05 | #DIV/0! | 7 | 2.25 | 0.2 | 1.75 | 3.2 | #DIV/0! | #DIV/0! | #DIV/0! | 11.1 | 14.3 | Avg-C7-20 | Average | --- | --- | --- | --- | 8.175 | 13.6 | 1.55 | 0.0125 | 0.80625 | 1.8 | 0.805 | 0.995 | 13.7 | 9.035 | 96.5 | 125 | 18 | 11 | 8.15 | 0.825 | 37.975 | #DIV/0! | 6 | 2.55 | 0.24 | 2.1 | 3.35 | #DIV/0! | #DIV/0! | #DIV/0! | 10.77 | 14.12
|  |  |  | Estimated RSSCT run time, tSCT (days) | 17.1999 | [5 empty] | SDS-BDCM | mg/L | 15 | 15 | 13 | 14.3333 | 8.0561 | SDS-BDCM | mg/L | 15 | 13 | 15 | 14.3333 | 8.0561 | RPD-C7-10 | RPD | --- | --- | --- | --- | 1.1201 | 6.2992 | 6.0606 | 6.4516 | 0.39139 | 0 | 9.8361 | 6.0606 | 1.6949 | 1.0929 | 0 | 9.5238 | 12.2449 | 8 | 3.9735 | 28 | 9.8557 | #VALUE! | 17.1429 | 48.8889 | #VALUE! | 5.7143 | 12.5 | #VALUE! | #VALUE! | #VALUE! | 23.4234 | 20.979 | RPD-C7-20 | RPD | --- | --- | --- | --- | 0.61162 | 16.1765 | 6.4516 | 8 | 1.5504 | 0 | 11.1801 | 9.0452 | 5.8394 | 0.77476 | 0 | 24 | 0 | 0 | 1.227 | 1.2121 | 0.28966 | #VALUE! | 20 | 27.451 | #VALUE! | 28.5714 | 26.8657 | #VALUE! | #VALUE! | #VALUE! | 25.441 | 25.779
|  |  |  | RSSCT bed length, lSC (cm) | 24.1206 | [5 empty] | SDS-DBCM | mg/L | 6.8 | 5.3 | 6.2 | 6.1 | 12.3768 | SDS-DBCM | mg/L | 6.8 | 6.2 | 5.5 | 6.1667 | 10.5509 | C11-10 | Primary | 1999-02-13 | 9:00 | 262 | 20680.5333 | 8.15 | 13.2 | 1.9 | 0.018 | 0.94737 | 2.1 | 0.9 | 1.2 | 12.8 | 9.03 | 96.5 | 130 | 30 | 12 | 6.2 | 0.44 | 48.64 | BMRL | 9 | 3.5 | 0.27 | 1.8 | 3.7 | NA | NA | NA | 14.57 | 18.27 | C11-20 | Primary | 1999-02-24 | 10:00 | 527 | 20798.9333 | 8.09 | 13 | 2 | NR | #VALUE! | 2.1 | 1.11 | 0.99 | 13.5 | 8.99 | 96 | 140 | 27 | 12 | 7.6 | 0.58 | 47.18 | BMRL | NR | 3.3 | 0.31 | 1.7 | 5.8 | NA | NA | NA | NR | NR
|  |  |  | Estimated volume required for 20-minute EBCT, VSC (L) | 694.4282 | [5 empty] | SDS-CHBr3 | mg/L | 0.32 | 0.33 | 0.4 | 0.35 | 12.454 | SDS-CHBr3 | mg/L | 0.32 | 0.4 | BMRL | 0.36 | 15.7135 | D11-10 | Duplicate | 1999-02-13 | 10:00 | 263 | 20759.4667 | 8.15 | 12.4 | 2 | 0.019 | 0.95 | 2.1 | 0.64 | 1.46 | 12.4 | 9.06 | 96.5 | 140 | 31 | 12 | 6.8 | 0.43 | 50.23 | BMRL | 9.9 | 3.9 | 0.19 | 1.8 | 3.9 | NA | NA | NA | 15.79 | 19.69 | D11-20 | Duplicate | 1999-02-24 | 11:00 | 528 | 20838.4 | 8.13 | 12.9 | 1.9 | NR | #VALUE! | 2.1 | 1.15 | 0.95 | 13.2 | 8.92 | 96 | 150 | 25 | 12 | 8.2 | 0.66 | 45.86 | BMRL | 18 | 0.27 | BMRL | 0.31 | 1.5 | NA | NA | NA | 18.58 | 20.08
|  |  |  | Mass GAC required, mSC (g) | 21.3123 | [5 empty] | SDS-THM4 | mg/L | 65.12 | 69.63 | 60.6 | 65.1167 | 6.9337 | SDS-THM4 | mg/L | 65.12 | 60.6 | 69.5 | 65.0733 | 6.8387 | Avg-C11-10 | Average | --- | --- | --- | --- | 8.15 | 12.8 | 1.95 | 0.0185 | 0.94868 | 2.1 | 0.77 | 1.33 | 12.6 | 9.045 | 96.5 | 135 | 30.5 | 12 | 6.5 | 0.435 | 49.435 | #DIV/0! | 9.45 | 3.7 | 0.23 | 1.8 | 3.8 | #DIV/0! | #DIV/0! | #DIV/0! | 15.18 | 18.98 | Avg-C11-20 | Average | --- | --- | --- | --- | 8.11 | 12.95 | 1.95 | #DIV/0! | #VALUE! | 2.1 | 1.13 | 0.97 | 13.35 | 8.955 | 96 | 145 | 26 | 12 | 7.9 | 0.62 | 46.52 | #DIV/0! | 18 | 1.785 | 0.31 | 1.005 | 3.65 | #DIV/0! | #DIV/0! | #DIV/0! | 18.58 | 20.08
[11 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | BMRL | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | BMRL | BMRL | #DIV/0! | #DIV/0! | RPD-C11-10 | RPD | --- | --- | --- | --- | 0 | 6.25 | 5.1282 | 5.4054 | 0.27739 | 0 | 33.7662 | 19.5489 | 3.1746 | 0.33167 | 0 | 7.4074 | 3.2787 | 0 | 9.2308 | 2.2989 | 3.2163 | #VALUE! | 9.5238 | 10.8108 | 34.7826 | 0 | 5.2632 | #VALUE! | #VALUE! | #VALUE! | 8.0369 | 7.4816 | RPD-C11-20 | RPD | --- | --- | --- | --- | 0.49322 | 0.7722 | 5.1282 | #VALUE! | #VALUE! | 0 | 3.5398 | 4.1237 | 2.2472 | 0.78169 | 0 | 6.8966 | 7.6923 | 0 | 7.5949 | 12.9032 | 2.8375 | #VALUE! | #VALUE! | 169.7479 | #VALUE! | 138.3085 | 117.8082 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[11 empty] | SDS-DCAA* | mg/L | 11 | 15 | 14 | 13.3333 | 15.6125 | SDS-DCAA* | mg/L | 11 | 14 | 15 | 13.3333 | 15.6125 | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[11 empty] | SDS-TCAA* | mg/L | 4.8 | 7.5 | 7.2 | 6.5 | 22.7672 | SDS-TCAA* | mg/L | 4.8 | 7.2 | 5 | 5.6667 | 23.5 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
[11 empty] | SDS-MBAA* | mg/L | 0.27 | 0.28 | 0.36 | 0.30333 | 16.2623 | SDS-MBAA* | mg/L | 0.27 | 0.36 | 0.16 | 0.26333 | 38.0379
[11 empty] | SDS-DBAA* | mg/L | 1.2 | 1.4 | 1.4 | 1.3333 | 8.6603 | SDS-DBAA* | mg/L | 1.2 | 1.4 | 1.4 | 1.3333 | 8.6603
[11 empty] | SDS-BCAA* | mg/L | 3.2 | 4.5 | 4.1 | 3.9333 | 16.928 | SDS-BCAA* | mg/L | 3.2 | 4.1 | 4.8 | 4.0333 | 19.8863
[11 empty] | SDS-TBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0!
[11 empty] | SDS-CDBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0!
[11 empty] | SDS-DCBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0!
[11 empty] | SDS-HAA5 | mg/L | 17.27 | 24.18 | 22.96 | 21.47 | 17.1779 | SDS-HAA5 | mg/L | 17.27 | 22.96 | 21.56 | 20.5967 | 14.3946
[11 empty] | SDS-HAA6 | mg/L | 20.47 | 28.68 | 27.06 | 25.4033 | 17.1178 | SDS-HAA6 | mg/L | 20.47 | 27.06 | 26.36 | 24.63 | 14.696
[11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [6 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [6 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
Note on N9: Reviewer M.H. (10/25/99): Per utility, "No samples were collected for THM, HAA, TOX."
Note on AG29: Duplicate samples were collected in two different bottles, one right after another. They were not collected in the same bottle. This was done to reduce probability of contamination and loss of any VOCs such as chloroform.
Note on BB16: Oulier data.
Note on BC16: Oulier data.
Note on BP29: Duplicate samples were collected in two different bottles, one right after another. They were not collected in the same bottle. This was done to reduce probability of contamination and loss of any VOCs such as chloroform.
Note on BY18: Outlier.
Note on BY41: Outlier.
Note on BY42: Outlier.
Note on CG36: asheikho: High RPD verified.
Note on CG40: asheikho: High RPD verified.
Note on CM17: Outlier data.
Note on CN17: asheikho: Outlier data.
Note on CO17: Outlier data.
Note on CO44: asheikho: High RPD was verified.
Note on CQ44: asheikho: High RPD was verified.
Note on CR44: asheikho: High RPD was verified
Note on CV17: asheikho: oulier.
Note on CV41: asheikho: Outlier
Note on CW17: asheikho: outlier.
Note on CW41: asheikho: Outlier