## Sheet1. 1st Quarter
FIELD-SET 1: 1st QUARTER RSSCT RESULTS (FILE: gacrssct.xls)
Field 1-1: PWS And Treatment Plant Data |  | Field 1-2: Full-Scale GAC Characteristics1 |  | Field 1-3: RSSCT Design Parameters |  |  |  | Field 1-4: Pretreatment Used Prior To GAC1 |  |  | Field 1-5: GAC Influent Water Quality For The 10-Minute EBCT Run | [6 empty] | Field 1-6: GAC Influent Water Quality For The 20-Minute EBCT Run1 | [6 empty] | Field 1-7: GAC Effluent Water Quality For The 10-Minute EBCT Run1 | [15 empty] | Field 1-7: GAC Effluent Water Quality For The 10-Minute EBCT Run (continued) | [17 empty] | Field 1-8: GAC Effluent Water Quality For The 20-Minute EBCT Run1 | [14 empty] | Field 1-8: GAC Effluent Water Quality For The 20-Minute EBCT Run (continued) | [18 empty] | Field 1-9: GAC Cost Parameters
|  |  |  | Input Design Parameters |  | US Standard Mesh Sizes | [18 empty] | Group C, 12 effluent samples per run | [33 empty] | Group C, 12 effluent samples per run
PWS Name | Tarrant County Water Supply Project | Carbon manufacturer | General Carbon Corporation | RSSCT influent TOC (mg/L) | 3 | US standard | Opening | Process | Description | Scale | 10-min. EBCT Start Date | 1998-04-17 | [5 empty] | 20-min. EBCT Start Date | 1998-04-17 | [5 empty] | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Cost Parameter | Parameter value
Public Water System Identification Number | TX2200199 | Carbon trade name | GC 8X30 | Inner diameter of the RSSCT column, DSC (mm) | 8 | mesh size | (mm) | Coagulation | 47 mg/L alum, 13 mg/L Lime, 0.47 mg/L polymer | Full-Scale | 10-min. EBCT Start Time | 8:00 | [5 empty] | 20-min. EBCT Start Time | 8:00 | [5 empty] | ID | duplicated? | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | Capital Recovery Interest Rate (%) | 7
Water Industry Data Base Number (optional) | NA | Carbon type | Bituminous Coal | Minimum RSSCT Reynolds number, ReSC, min | 0.5 | 4 | 4.75 | Flocculation | Vertical Impeller-type | Full-Scale | [15 empty] | Y/N | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | Capital Recovery Period (years) | 20
|  | Original GAC mesh size, upper (US standard mesh) | 8 | Full-scale operating temperature, ToC (oC) | 20.6 | 6 | 3.35 | Sedimentation | Approximately 11-hour settling time | Full-Scale | Group A, 2 samples per batch | [6 empty] | Group A, 2 samples per batch | [6 empty] | C1-10 | N | 1998-04-17 | 9:00 | 1 | 85.8 | 7.45 | 23 | 0.123 | 0.0016 | 1.3008 | 1.5 | 0.719 | 0.781 | 17 | 7.61 | 119 | NR | BMRL | BMRL | 1.511 | 1.159 | 2.67 | BMRL | BMRL | BMRL | BMRL | 1.033 | BMRL | NA | NA | NA | 1.033 | 1.033 | C1-20 | N | 1998-04-17 | 9:00 | 1 | 42.9 | 7.45 | 23 | 0.051 | 0.0009 | 1.7647 | 1.5 | 0.712 | 0.788 | 17 | 7.78 | 119 | NR | BMRL | BMRL | 1.004 | BMRL | 1.004 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | Overhead & Profit Factor (% of construction costs) | 57.1
Official ICR Contact Person |  | Original GAC mesh size, lower (US standard mesh) | 30 | Full-scale bed porosity, eLC | 0.45 | 8 | 2.36 | Filtration | Sand, anthracite, garnet, Microfloc MS-186 | Full-Scale | Parameter | Units | Sample A1-10 | Sample A2-10 | Average | RPD |  | Parameter | Units | Sample A1-20 | Sample A2-20 | Average | RPD |  | C2-10 | N | 1998-04-17 | 20:00 | 12 | 1029.6 | 7.48 | 21 | 0.1067 | 0.0038 | 3.5614 | 1.5 | 0.708 | 0.792 | 17 | 7.68 | 119 | BMRL | BMRL | BMRL | 1.966 | 2.462 | 4.428 | BMRL | BMRL | BMRL | BMRL | 1.36 | 1.067 | NA | NA | NA | 1.36 | 2.427 | C2-20 | N | 1998-04-18 | 1:30 | 17.5 | 750.75 | 7.46 | 21 | 0.0457 | 0.0046 | 10.0656 | 1.5 | 0.708 | 0.792 | 17 | 7.8 | 119 | 28.43 | BMRL | BMRL | 1.899 | 1.29 | 3.189 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | Special Sitework Factor (% of construction costs) | NA
Mailing Address |  | Original carbon particle diameter, dLC (mm) | 1.6 | Measured RSSCT dry bed density, rSC (g/cm3) | 0.5 | 10 | 2 | Filtration | 1.0 um cartridge filter | Bench-scale | Sampling date | MM/DD/YY | 1998-04-17 | 1998-04-19 | --- | --- |  | Sampling date | MM/DD/YY | 1998-04-17 | 1998-04-23 | --- | --- |  | C3-10 | N | 1998-04-18 | 2:30 | 18.5 | 1587.3 | 7.38 | 21 | 0.14575 | 0.0058 | 3.9794 | 1.5 | 0.684 | 0.816 | 17 | 7.8 | 119 | BMRL | BMRL | BMRL | 2.618 | 3.603 | 6.221 | BMRL | BMRL | BMRL | BMRL | 1.371 | 1.079 | NA | NA | NA | 1.371 | 2.45 | AVG-C3-20 | Y | 1998-04-19 | 6:30 | 42.5 | 1823.25 | 7.75 | 23 | 0.12 | 0.004 | 3.3333 | 1.5 | 0.98 | 0.52 | 17 | 7.72 | 119.5 | 12.29 | BMRL | 1.86 | 3.05 | 1.79 | 6.7 | BMRL | 1.089 | BMRL | BMRL | 1.21 | 1.349 | NA | NA | NA | 2.299 | 3.648 | Construction Contingencies (% of construction costs) | 25
|  | 1: These are the characteristics before the carbon is ground for RSSCT experiments. |  | RSSCT GAC mesh size, upper (US standard mesh) | 100 | 12 | 1.68 | In-Line Filtration | 0.9 um exclusion size | Bench-scale | Sampling time | hh:mm | 8:00 | 14:00 | --- | --- |  | Sampling time | hh:mm | 8:00 | 8:00 | --- | --- |  | AVG-C4-10 | Y | 1998-04-18 | 11:30 | 27.5 | 2359.5 | 7.685 | 23 | 0.35433 | 0.0007 | 0.19804 | 1.5 | 0.879 | 0.621 | 17 | 7.66 | 119.5 | BMRL | 1.4275 | 3.638 | 6.396 | 3.538 | 14.9995 | BMRL | 1.416 | BMRL | BMRL | 2.3655 | 2.196 | NA | NA | NA | 3.7815 | 5.9775 | C4-20 | N | 1998-04-19 | 16:00 | 52 | 2230.8 | 7.87 | 23 | 0.17665 | 0.0021 | 1.1888 | 1.5 | 0.877 | 0.623 | 17 | 7.68 | 119.5 | 15.44 | BMRL | 2.071 | 3.467 | 1.901 | 7.439 | BMRL | 1.199 | BMRL | BMRL | 1.334 | 1.24 | NA | NA | NA | 2.533 | 3.773 | Engineering Fee Factor (% of construction costs) | 15
Phone Number |  |  |  | RSSCT GAC mesh size, lower (US standard mesh) | 200 | 16 | 1.18 |  |  |  | Operation time | hh.hh | 0 | 54 | --- | --- |  | Operation time | hh.hh | 0 | 139 | --- | --- |  | C5-10 | N | 1998-04-18 | 20:30 | 36.5 | 3131.7 | 7.61 | 24 | 0.71 | 0.0048 | 0.67606 | 1.5 | 0.692 | 0.808 | 17 | 7.69 | 119.5 | 45 | 2.953 | 7.458 | 11.76 | 4.81 | 26.981 | BMRL | 2.259 | BMRL | BMRL | 3.362 | 3.479 | NA | NA | NA | 5.621 | 9.1 | C5-20 | N | 1998-04-20 | 14:00 | 74 | 3174.6 | 7.71 | 22 | 0.5117 | 0.0008 | 0.15634 | 1.5 | 0.672 | 0.828 | 17 | 7.68 | 119 | 45 | 1.984 | 5.583 | 9.469 | 4.718 | 21.754 | BMRL | 1.688 | BMRL | BMRL | 2.772 | 2.45 | NA | NA | NA | 4.46 | 6.91 | 1998 ENR Construction Cost Index (CCI base year 1913) | 6095.24
FAX Number | [5 empty] | 20 | 0.85 |  |  |  | Bed volumes | (10 minutes) | 0 | 4633.2 | --- | --- |  | Bed volumes | (20 minutes) | 0 | 5963.1 | --- | --- |  | C6-10 | N | 1998-04-19 | 6:30 | 46.5 | 3989.7 | 7.85 | 24 | 1.1 | 0.0133 | 1.2091 | 1.98 | 0.826 | 1.154 | 17 | 7.62 | 119.5 | 45 | 8.211 | 14.238 | 15.427 | 3.756 | 41.632 | BMRL | 5.287 | 2.243 | BMRL | 3.857 | 5.691 | NA | NA | NA | 11.387 | 17.078 | C6-20 | N | 1998-04-21 | 4:30 | 88.5 | 3796.65 | 7.83 | 21 | 0.4951 | 0.0056 | 1.1311 | 1.5 | 0.747 | 0.753 | 17 | 7.72 | 119 | 45 | 4.206 | 10.034 | 14.83 | 5.268 | 34.338 | BMRL | 2.368 | BMRL | BMRL | 2.904 | 3.134 | NA | NA | NA | 5.272 | 8.406 | 1998 Producers Price Index (PPI base year 1967 = 100) | NA
E-Mail Address (optional) |  |  |  | Estimated Run Length |  | 30 | 0.6 |  |  |  | Alkalinity | mg/L as CaCO3 | 74.8 | 75.5 | 75.15 | 0.93147 |  | Alkalinity | mg/L as CaCO3 | 74.8 | 69.5 | 72.15 | 7.3458 |  | C7-10 | N | 1998-04-19 | 15:30 | 55.5 | 4761.9 | 7.85 | 22 | 1.3 | 0.0163 | 1.2538 | 7.42 | 3.34 | 4.08 | 17 | 7.64 | 119.5 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NA | NA | NA | NR | NR | AVG-C7-20 | Y | 1998-04-22 | 2:00 | 110 | 4719 | 7.69 | 23 | 1 | 0.0023 | 0.23 | 1.91 | 0.59 | 1.32 | 17 | 7.77 | 119.5 | 75.84 | 7.11 | 13.69 | 16.46 | 4.95 | 42.21 | BMRL | 3.43 | 1.58 | BMRL | 3.3 | 4.1 | NA | NA | NA | 8.31 | 12.41 | Labor Rate + Fringe ($/work-hour) | 27.2
|  |  |  | Bed volumes to 50% TOC breakthrough, BV50 | 5202.3804 | 40 | 0.425 |  |  |  | Total hardness | mg/L as CaCO3 | 100.1 | 104.2 | 102.15 | 4.0137 |  | Total hardness | mg/L as CaCO3 | 100.1 | 100.4 | 100.25 | 0.29925 |  | AVG-C8-10 | Y | 1998-04-20 | 3:45 | 64 | 5491.2 | 7.715 | 23 | 1.4 | 0.02005 | 1.4321 | 2.74 | 0.954 | 1.786 | 17 | 7.675 | 119 | 107.5 | 20.1045 | 20.2175 | 16.156 | 2.708 | 59.186 | BMRL | 8.8555 | 2.9125 | BMRL | 3.4165 | 6.564 | NA | NA | NA | 15.1845 | 21.7485 | C8-20 | N | 1998-04-22 | 17:30 | 125.5 | 5383.95 | 7.74 | 23 | 1.3 | 0.0151 | 1.1615 | 2.38 | 0.802 | 1.578 | 17 | 7.75 | 119.5 | 110 | 13.803 | 18.269 | 18.41 | 3.967 | 54.449 | BMRL | 6.907 | 3.074 | BMRL | 3.915 | 5.584 | NA | NA | NA | 13.896 | 19.48 | Labor Overhead Factor (% of labor) | 33
Technical ICR Contact Person |  |  |  | Estimated run length, BVT ( = 2 x BV50) | 10404.7608 | 50 | 0.3 |  |  |  | Calcium hardness | mg/L as CaCO3 | 83.9 | 88.1 | 86 | 4.8837 |  | Calcium hardness | mg/L as CaCO3 | 83.9 | 85.9 | 84.9 | 2.3557 |  | C9-10 | N | 1998-04-20 | 17:45 | 81.75 | 7014.15 | 7.7 | 21 | 1.7 | 0.0234 | 1.3765 | 3.04 | 0.936 | 2.104 | 17 | 7.7 | 119 | 105 | 25.982 | 23.57 | 17.364 | 2.511 | 69.427 | 2.818 | 11.183 | 6.102 | BMRL | 3.118 | 7.364 | NA | NA | NA | 23.221 | 30.585 | C9-20 | N | 1998-04-24 | 0:00 | 157 | 6735.3 | 7.63 | 23 | 1.7 | 0.0306 | 1.8 | 3 | 0.992 | 2.008 | 17 | 7.77 | 119.5 | 125 | 23.076 | 21.561 | 16.674 | 2.541 | 63.852 | BMRL | 11.32 | 4.798 | BMRL | 3.109 | 6.566 | NA | NA | NA | 19.227 | 25.793 | Electric Rate ($/kW-h) | 0.06
Mailing Address |  |  |  | BVT + 30% safety factor, BVT+30% ( = 2.6 x BV50) | 13526.189 | 60 | 0.25 |  |  |  | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! |  | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! |  | C10-10 | N | 1998-04-21 | 0:00 | 88 | 7550.4 | 7.9 | 21 | 1.8 | 0.0281 | 1.5611 | 3.2 | 0.948 | 2.252 | 17 | 7.63 | 119 | NR | 31.35 | 24.839 | 16.748 | 2.186 | 75.123 | BMRL | 13.447 | 5.713 | BMRL | 3.082 | 8.022 | NA | NA | NA | 22.242 | 30.264 | AVG-C10-20 | Y | 1998-04-25 | 2:00 | 183 | 7850.7 | 7.82 | 22 | 1.93 | 0.03 | 1.5544 | 3.46 | 1.12 | 2.34 | 17 | 7.79 | 119.5 | 170 | 29.41 | 24.48 | 16.63 | 2.01 | 72.53 | BMRL | 14.26 | 8.41 | BMRL | 3.06 | 7.23 | NA | NA | NA | 25.73 | 32.96 | Fuel Oil Rate ($/gal) | na
[6 empty] | 70 | 0.21 |  |  |  | Bromide | mg/L | 71 | 73 | 72 | 2.7778 |  | Bromide | mg/L | 71 | 78 | 74.5 | 9.396 |  | AVG-C11-10 | Y | 1998-04-21 | 14:00 | 102 | 8751.6 | 7.77 | 23 | 1.98 | 0.024 | 1.2121 | 3.28 | 1 | 2.28 | 17 | 7.71 | 119 | 162.5 | 34.52 | 24.72 | 14.8 | 1.62 | 75.66 | 2.117 | 14.61 | 4.63 | BMRL | 2.56 | 7.75 | NA | NA | NA | 23.917 | 31.667 | C11-20 | N | 1998-04-25 | 23:00 | 204 | 8751.6 | 7.95 | 23 | 2 | 0.032 | 1.6 | 2.42 | 0.853 | 1.567 | 17 | 7.8 | 120 | 175 | 30.684 | 23.037 | 14.954 | 1.888 | 70.563 | 2.697 | 16.708 | 7.189 | BMRL | 3.451 | 8.932 | NA | NA | NA | 30.045 | 38.977 | Natural Gas Rate ($/ft3) | 0.0053
Phone Number |  |  |  | General RSSCT Design Parameters |  | 80 | 0.18 | [17 empty] | C12-10 | N | 1998-04-22 | 0:00 | 112 | 9609.6 | 7.65 | 23 | 1.95 | 0.0286 | 1.4667 | 3.8 | 1.295 | 2.505 | 17 | 7.75 | 119.5 | 195 | 37.679 | 26.34 | 15.491 | 1.571 | 81.081 | BMRL | 17.379 | 8.196 | BMRL | 2.699 | 7.574 | NA | NA | NA | 28.274 | 35.848 | C12-20 | N | 1998-04-27 | 13:30 | 242.5 | 10403.25 | 7.98 | 22 | 2.2 | 0.0335 | 1.5227 | 2.52 | 0.668 | 1.852 | 17 | 7.67 | 120 | 195 | 35.612 | 24.532 | 15.048 | 1.697 | 76.889 | 2.417 | 20.643 | 12.368 | BMRL | 3.713 | 9.606 | NA | NA | NA | 39.141 | 48.747 | Current Process Water Rate ($/1000 gal) | 0.41
FAX Number |  |  |  | Kinematic viscosity at ToC, nLC (m2/s) | 1.0117e-06 | 100 | 0.15 |  |  |  | Group B, 3 samples per batch | [6 empty] | Group B, 3 samples per batch | [10 empty] | -861656 | -73930084.8 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -861656 | -36965042.4 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 | Modifications to Existing Plant (% of construction costs) | NA
E-Mail Address (optional) |  |  |  | RSSCT carbon particle diameter, dSC (mm) | 0.112 | 120 | 0.125 |  |  |  | Parameter | Units | Sample B1-10 | Sample B2-10 | Sample B3-10 | Average | %SD | Parameter | Units | Sample B1-20 | Sample B2-20 | Sample B3-20 | Average | %SD |  |  |  |  | -861656 | -73930084.8 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -861656 | -36965042.4 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
|  |  |  | Scaling factor, SF | 14.3 | 140 | 0.106 | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | Sampling date | MM/DD/YY | 1998-04-17 | 1998-04-19 | 1998-04-22 | --- | --- | Sampling date | MM/DD/YY | 1998-04-17 | 1998-04-23 | 1998-04-27 | --- | --- |  |  |  |  | -861656 | -73930084.8 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -861656 | -36965042.4 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
Plant Name | Tarrant County Water Supply Project |  |  | RSSCT hydraulic loading rate, vSC (m/hr) | 7.23 | 170 | 0.088 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | Sampling time | hh:mm | 8:00 | 14:00 | 10:00 | --- | --- | Sampling time | hh:mm | 8:00 | 8:00 | 9:00 | --- | --- |  |  |  |  | -861656 | -73930084.8 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -861656 | -36965042.4 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
Treatment Plant Category | CONV |  |  | RSSCT flow rate, QSC (mL/min) | 6.057 | 200 | 0.075 | is to list the pretreatment processes used in this particular RSSCT run. |  |  | Operation time | hh.hh | 0 | 54 | 122 | --- | --- | Operation time | hh.hh | 0 | 140 | 237 | --- | --- |  |  |  |  | -861656 | -73930084.8 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -861656 | -36965042.4 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
Process Train Name | Convential Filtration |  |  | Estimated total influent volume required, VSCT (L) | 171.8769 | 230 | 0.062 |  |  |  | Bed volumes | (10 minute) | 0 | 4633.2 | 10467.6 | --- | --- | Bed volumes | (20 minute) | 0 | 6006 | 10167.3 | --- | --- | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
ICR Treatment Plant Identification Number | 650 |  |  |  |  | 270 | 0.053 |  |  |  | pH | --- | 8.02 | 7.46 | 7.35 | 7.61 | 4.7215 | pH | --- | 8.02 | 7.49 | 7.83 | 7.78 | 3.4513 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
PWSID Number of Plant (if assigned) | TX2200199 |  |  | 10-Minute EBCT Run |  | 325 | 0.044 |  |  |  | Turbidity | ntu | 0.2 | 0.19 | 0.2 | 0.19667 | 2.9357 | Turbidity | ntu | 0.2 | 0.2 | 0.21 | 0.20333 | 2.8394 | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below. | [33 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below.
Historical Minimum Water Temperature (oC) | 12 |  |  | Full-scale empty bed contact time, EBCTLC (min) | 10 | 400 | 0.037 |  |  |  | Temperature | oC | 19 | 21 | 21 | 20.3333 | 5.6789 | Temperature | oC | 19 | 22 | 22 | 21 | 8.2479
Historical Average Water Temperature (oC) | 22.7 |  |  | Estimated full-scale run time, tLCT (days) | 93.9319 | [5 empty] | Total organic carbon | mg/L | 3.15 | 3 | 3 | 3.05 | 2.8394 | Total organic carbon | mg/L | 3.15 | 3.1 | 3 | 3.0833 | 2.4771 | Group D, 3 duplicate effluent samples per run (results from primary and duplicate analyses) | [33 empty] | Group D, 3 duplicate effluent samples per run (results from primary and duplicate analyses)
State Approved Plant Capacity (MGD) | 57 |  |  | RSSCT empty bed contact time, EBCTSC (min) | 0.6993 | [5 empty] | UV254 | cm-1 | 0.078 | 0.0658 | 0.0608 | 0.0682 | 12.973 | UV254 | cm-1 | 0.078 | 0.0631 | 0.0655 | 0.068867 | 11.617 | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS
|  |  |  | Estimated RSSCT run time, tSCT (days) | 6.5687 | [5 empty] | SUVA | L/(mg*m) | 2.4762 | 2.1933 | 2.0267 | 2.2321 | 10.1812 | SUVA | L/(mg*m) | 2.4762 | 2.0355 | 2.1833 | 2.2317 | 10.0505 | ID | Type | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6
|  |  |  | RSSCT bed length, lSC (cm) | 8.4266 | [5 empty] | SDS-Cl2 dose | mg/L | 6 | 4.5 | 5.4 | 5.3 | 14.245 | SDS-Cl2 dose | mg/L | 6 | 5.4 | 4.5 | 5.3 | 14.245 |  |  | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L
|  |  |  | Estimated volume required for 10-minute EBCT, VSC (L) | 57.2923 | [5 empty] | SDS-Free Cl2 residual | mg/L | 0.719 | 0.747 | 1.211 | 0.89233 | 30.9669 | SDS-Free Cl2 residual | mg/L | 0.719 | 1.259 | 1.407 | 1.1283 | 32.0946 | C4-10 | Primary | 1998-04-18 | 11:30 | 27.5 | 2359.5 | 7.69 | 23 | 0.34885 | 0.0008 | 0.22932 | 1.5 | 0.944 | 0.556 | 17 | 7.67 | 119.5 | BMRL | 1.548 | 3.696 | 6.354 | 3.322 | 14.92 | BMRL | 1.465 | BMRL | BMRL | 2.585 | 2.284 | NA | NA | NA | 4.05 | 6.334 | C3-20 | Primary | 1998-04-19 | 6:30 | 42.5 | 1823.25 | 7.76 | 23 | 0.1127 | 0.0037 | 3.2831 | 1.5 | 0.964 | 0.536 | 17 | 7.71 | 119.5 | 14.68 | BMRL | 2.001 | 3.226 | 1.855 | 7.082 | BMRL | 1.089 | BMRL | BMRL | 1.413 | 1.349 | NA | NA | NA | 2.502 | 3.851
|  |  |  | Mass GAC required, mSC (g) | 2.1178 | [5 empty] | SDS-Cl2 demand | mg/L | 5.281 | 3.753 | 4.189 | 4.4077 | 17.858 | SDS-Cl2 demand | mg/L | 5.281 | 4.141 | 3.093 | 4.1717 | 26.2323 | D-C4-10 | Duplicate | 1998-04-18 | 11:30 | 27.5 | 2359.5 | 7.68 | 23 | 0.3598 | 0.0006 | 0.16676 | 1.5 | 0.814 | 0.686 | 17 | 7.65 | 119.5 | BMRL | 1.307 | 3.58 | 6.438 | 3.754 | 15.079 | BMRL | 1.367 | BMRL | BMRL | 2.146 | 2.108 | NA | NA | NA | 3.513 | 5.621 | D-C3-20 | Duplicate | 1998-04-19 | 6:30 | 42.5 | 1823.25 | 7.74 | 23 | 0.11825 | BMRL | #VALUE! | 1.5 | 0.992 | 0.508 | 17 | 7.72 | 119.5 | 9.89 | BMRL | 1.727 | 2.871 | 1.716 | 6.314 | BMRL | BMRL | BMRL | BMRL | 1.009 | BMRL | NA | NA | NA | 1.009 | 1.009
[11 empty] | SDS-Chlorination temp. | oC | 17 | 17 | 17 | 17 | 0 | SDS-Chlorination temp. | oC | 17 | 17 | 17 | 17 | 0 | AVG-C4-10 | Average | --- | --- | --- | --- | 7.685 | 23 | 0.35433 | 0.0007 | 0.19804 | 1.5 | 0.879 | 0.621 | 17 | 7.66 | 119.5 | #DIV/0! | 1.4275 | 3.638 | 6.396 | 3.538 | 14.9995 | #DIV/0! | 1.416 | #DIV/0! | #DIV/0! | 2.3655 | 2.196 | #DIV/0! | #DIV/0! | #DIV/0! | 3.7815 | 5.9775 | AVG-C3-20 | Average | --- | --- | --- | --- | 7.75 | 23 | 0.11547 | 0.0037 | #VALUE! | 1.5 | 0.978 | 0.522 | 17 | 7.715 | 119.5 | 12.285 | #DIV/0! | 1.864 | 3.0485 | 1.7855 | 6.698 | #DIV/0! | 1.089 | #DIV/0! | #DIV/0! | 1.211 | 1.349 | #DIV/0! | #DIV/0! | #DIV/0! | 1.7555 | 2.43
|  |  |  | 20-Minute EBCT Run | [6 empty] | SDS-Chlorination pH | --- | 7.77 | 7.67 | 7.64 | 7.6933 | 0.88477 | SDS-Chlorination pH | --- | 7.77 | 7.79 | 7.7 | 7.7533 | 0.60952 | RPD-C4-10 | RPD | --- | --- | --- | --- | 0.13012 | 0 | 3.0904 | 28.5714 | 31.5921 | 0 | 14.7895 | 20.934 | 0 | 0.2611 | 0 | #VALUE! | 16.8827 | 3.1886 | 1.3133 | 12.2103 | 1.06 | #VALUE! | 6.9209 | #VALUE! | #VALUE! | 18.5584 | 8.0146 | #VALUE! | #VALUE! | #VALUE! | 14.2007 | 11.9281 | RPD-C3-20 | RPD | --- | --- | --- | --- | 0.25806 | 0 | 4.8062 | #VALUE! | #VALUE! | 0 | 2.863 | 5.364 | 0 | 0.12962 | 0 | 38.9906 | #VALUE! | 14.6996 | 11.6451 | 7.7849 | 11.4661 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 33.3609 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 85.047 | 116.9547
|  |  |  | Full-scale empty bed contact time, EBCTLC (min) | 20 | [5 empty] | SDS-Incubation time | hours | 119 | 119.5 | 119.5 | 119.3333 | 0.24191 | SDS-Incubation time | hours | 119 | 119.5 | 120 | 119.5 | 0.41841 | C8-10 | Primary | 1998-04-20 | 3:45 | 64 | 5491.2 | 7.7 | 23 | 1.4 | 0.0195 | 1.3929 | 2.74 | 0.92 | 1.82 | 17 | 7.63 | 119 | 105 | 20.435 | 21.359 | 17.608 | 3.08 | 62.482 | BMRL | 9.901 | 3.161 | BMRL | 3.921 | 7.548 | NA | NA | NA | 16.983 | 24.531 | C7-20 | Primary | 1998-04-22 | 2:00 | 110 | 4719 | 7.69 | 23 | 1 | 0.0023 | 0.23 | 1.91 | 0.594 | 1.316 | 17 | 7.77 | 119.5 | 77.18 | 7.104 | 13.554 | 16.133 | 4.735 | 41.526 | BMRL | 3.138 | 1.6 | BMRL | 3.038 | 4.14 | NA | NA | NA | 7.776 | 11.916
|  |  |  | Estimated full-scale run time, tLCT (days) | 187.8637 | [5 empty] | SDS-TOX | mg Cl- /L | 295 | 295 | 310 | 300 | 2.8868 | SDS-TOX | mg Cl- /L | 295 | 335 | 335 | 321.6667 | 7.1795 | D-C8-10 | Duplicate | 1998-04-20 | 3:45 | 64 | 5491.2 | 7.73 | 23 | 1.4 | 0.0206 | 1.4714 | 2.74 | 0.988 | 1.752 | 17 | 7.72 | 119 | 110 | 19.774 | 19.076 | 14.704 | 2.336 | 55.89 | BMRL | 7.81 | 2.664 | BMRL | 2.912 | 5.58 | NA | NA | NA | 13.386 | 18.966 | D-C7-20 | Duplicate | 1998-04-22 | 2:00 | 110 | 4719 | 7.68 | 23 | 1 | 0.0026 | 0.26 | 1.91 | 0.594 | 1.316 | 17 | 7.77 | 119.5 | 74.5 | 7.125 | 13.833 | 16.787 | 5.171 | 42.916 | BMRL | 3.716 | 1.55 | BMRL | 3.571 | 4.053 | NA | NA | NA | 8.837 | 12.89
|  |  |  | RSSCT empty bed contact time, EBCTSC (min) | 1.3986 | [5 empty] | SDS-CHCl3 | mg/L | 70.693 | 71.4 | 77.599 | 73.2307 | 5.1885 | SDS-CHCl3 | mg/L | 70.693 | 83.559 | 69.93 | 74.7273 | 10.2479 | AVG-C8-10 | Average | --- | --- | --- | --- | 7.715 | 23 | 1.4 | 0.02005 | 1.4321 | 2.74 | 0.954 | 1.786 | 17 | 7.675 | 119 | 107.5 | 20.1045 | 20.2175 | 16.156 | 2.708 | 59.186 | #DIV/0! | 8.8555 | 2.9125 | #DIV/0! | 3.4165 | 6.564 | #DIV/0! | #DIV/0! | #DIV/0! | 15.1845 | 21.7485 | AVG-C7-20 | Average | --- | --- | --- | --- | 7.685 | 23 | 1 | 0.00245 | 0.245 | 1.91 | 0.594 | 1.316 | 17 | 7.77 | 119.5 | 75.84 | 7.1145 | 13.6935 | 16.46 | 4.953 | 42.221 | #DIV/0! | 3.427 | 1.575 | #DIV/0! | 3.3045 | 4.0965 | #DIV/0! | #DIV/0! | #DIV/0! | 8.3065 | 12.403
|  |  |  | Estimated RSSCT run time, tSCT (days) | 13.1373 | [5 empty] | SDS-BDCM | mg/L | 28.495 | 27.983 | 32.272 | 29.5833 | 7.9183 | SDS-BDCM | mg/L | 28.495 | 33.302 | 29.972 | 30.5897 | 8.0495 | RPD-C8-10 | RPD | --- | --- | --- | --- | 0.38885 | 0 | 0 | 5.4863 | 5.4863 | 0 | 7.1279 | 3.8074 | 0 | 1.1726 | 0 | 4.6512 | 3.2878 | 11.2922 | 17.9747 | 27.4742 | 11.1378 | #VALUE! | 23.6124 | 17.0644 | #VALUE! | 29.5331 | 29.9817 | #VALUE! | #VALUE! | #VALUE! | 23.6886 | 25.588 | RPD-C7-20 | RPD | --- | --- | --- | --- | 0.13012 | 0 | 0 | 12.2449 | 12.2449 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5338 | 0.29517 | 2.0375 | 3.9733 | 8.8027 | 3.2922 | #VALUE! | 16.8661 | 3.1746 | #VALUE! | 16.1295 | 2.1238 | #VALUE! | #VALUE! | #VALUE! | 12.7731 | 7.8529
|  |  |  | RSSCT bed length, lSC (cm) | 16.8531 | [5 empty] | SDS-DBCM | mg/L | 9.242 | 8.472 | 10.328 | 9.3473 | 9.9758 | SDS-DBCM | mg/L | 9.242 | 10.585 | 10.079 | 9.9687 | 6.804 | C11-10 | Primary | 1998-04-21 | 14:00 | 102 | 8751.6 | 7.79 | 23 | 2 | 0.024 | 1.2 | 3.28 | 1.055 | 2.225 | 17 | 7.71 | 119 | 155 | 33.836 | 24.283 | 14.335 | 1.537 | 73.991 | BMRL | 12.723 | 3.683 | BMRL | 1.945 | 6.429 | NA | NA | NA | 18.351 | 24.78 | C10-20 | Primary | 1998-04-25 | 23:00 | 204 | 8751.6 | 7.85 | 22 | 1.95 | 0.03 | 1.5385 | 3.46 | 1.155 | 2.305 | 17 | 7.78 | 119.5 | 170 | 29.024 | 24.453 | 16.569 | 1.932 | 71.978 | BMRL | 14.135 | 8.796 | BMRL | 3.024 | 7.242 | NA | NA | NA | 25.955 | 33.197
|  |  |  | Estimated volume required for 20-minute EBCT, VSC (L) | 114.5846 | [5 empty] | SDS-CHBr3 | mg/L | BMRL | BMRL | BMRL | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | BMRL | BMRL | BMRL | #DIV/0! | #DIV/0! | D-C11-10 | Duplicate | 1998-04-21 | 14:00 | 102 | 8751.6 | 7.75 | 23 | 1.95 | 0.0239 | 1.2256 | 3.28 | 0.936 | 2.344 | 17 | 7.7 | 119 | 170 | 35.198 | 25.155 | 15.263 | 1.696 | 77.312 | 2.117 | 16.497 | 5.574 | BMRL | 3.176 | 9.068 | NA | NA | NA | 27.364 | 36.432 | D-C10-20 | Duplicate | 1998-04-25 | 23:00 | 204 | 8751.6 | 7.79 | 22 | 1.9 | 0.029 | 1.5263 | 3.46 | 1.075 | 2.385 | 17 | 7.8 | 119.5 | 170 | 29.797 | 24.507 | 16.685 | 2.081 | 73.07 | BMRL | 14.381 | 8.027 | BMRL | 3.102 | 7.218 | NA | NA | NA | 25.51 | 32.728
|  |  |  | Mass GAC required, mSC (g) | 4.2357 | [5 empty] | SDS-THM4 | mg/L | 108.43 | 107.855 | 120.199 | 112.1613 | 6.2114 | SDS-THM4 | mg/L | 108.43 | 127.446 | 109.981 | 115.2857 | 9.1596 | AVG-C11-10 | Average | --- | --- | --- | --- | 7.77 | 23 | 1.975 | 0.02395 | 1.2128 | 3.28 | 0.9955 | 2.2845 | 17 | 7.705 | 119 | 162.5 | 34.517 | 24.719 | 14.799 | 1.6165 | 75.6515 | 2.117 | 14.61 | 4.6285 | #DIV/0! | 2.5605 | 7.7485 | #DIV/0! | #DIV/0! | #DIV/0! | 22.8575 | 30.606 | AVG-C10-20 | Average | --- | --- | --- | --- | 7.82 | 22 | 1.925 | 0.0295 | 1.5324 | 3.46 | 1.115 | 2.345 | 17 | 7.79 | 119.5 | 170 | 29.4105 | 24.48 | 16.627 | 2.0065 | 72.524 | #DIV/0! | 14.258 | 8.4115 | #DIV/0! | 3.063 | 7.23 | #DIV/0! | #DIV/0! | #DIV/0! | 25.7325 | 32.9625
[11 empty] | SDS-MCAA* | mg/L | 4.307 | 4.363 | 3.93 | 4.2 | 5.6071 | SDS-MCAA* | mg/L | 4.307 | 4.032 | 3.413 | 3.9173 | 11.689 | RPD-C11-10 | RPD | --- | --- | --- | --- | 0.5148 | 0 | 2.5316 | 0.41754 | 2.1142 | 0 | 11.9538 | 5.209 | 0 | 0.12979 | 0 | 9.2308 | 3.9459 | 3.5277 | 6.2707 | 9.8361 | 4.3899 | #VALUE! | 25.8316 | 40.8556 | #VALUE! | 48.0765 | 34.0582 | #VALUE! | #VALUE! | #VALUE! | 39.4313 | 38.071 | RPD-C10-20 | RPD | --- | --- | --- | --- | 0.76726 | 0 | 2.5974 | 3.3898 | 0.7926 | 0 | 7.1749 | 3.4115 | 0 | 0.25674 | 0 | 0 | 2.6283 | 0.22059 | 0.69766 | 7.4259 | 1.5057 | #VALUE! | 1.7253 | 9.1422 | #VALUE! | 2.5465 | 0.33195 | #VALUE! | #VALUE! | #VALUE! | 1.7293 | 1.4228
[11 empty] | SDS-DCAA* | mg/L | 34.987 | 29.027 | 37.098 | 33.704 | 12.4189 | SDS-DCAA* | mg/L | 34.987 | 37.646 | 41.396 | 38.0097 | 8.4714 | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[11 empty] | SDS-TCAA* | mg/L | 22.335 | 13.988 | 26.982 | 21.1017 | 31.2023 | SDS-TCAA* | mg/L | 22.335 | 24.91 | 39.711 | 28.9853 | 32.3526 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
[11 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | BMRL | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | BMRL | BMRL | #DIV/0! | #DIV/0!
[11 empty] | SDS-DBAA* | mg/L | 2.252 | 1.656 | 2.027 | 1.9783 | 15.2131 | SDS-DBAA* | mg/L | 2.252 | 2.142 | 2.31 | 2.2347 | 3.8185
[11 empty] | SDS-BCAA* | mg/L | 11.163 | 9.738 | 10.321 | 10.4073 | 6.8837 | SDS-BCAA* | mg/L | 11.163 | 10.506 | 12.126 | 11.265 | 7.233
[11 empty] | SDS-TBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0!
[11 empty] | SDS-CDBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0!
[11 empty] | SDS-DCBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0!
[11 empty] | SDS-HAA5 | mg/L | 63.881 | 49.034 | 70.037 | 60.984 | 17.7047 | SDS-HAA5 | mg/L | 63.881 | 68.73 | 86.83 | 73.147 | 16.5356
[11 empty] | SDS-HAA6 | mg/L | 75.044 | 58.772 | 80.358 | 71.3913 | 15.754 | SDS-HAA6 | mg/L | 75.044 | 79.236 | 98.956 | 84.412 | 15.1266
[11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [6 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [6 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
Note on H7: Reviewer M.H. (12/13/99): Reviewer adjusted Reynolds number based on new full-scale temperatures.
Note on H8: Reviewer D.S. (10/13/99): Full-scale temperature is 20.6C, RSSCT designed for 20C.
Note on H10: Reviewer M.H. (12/14/99): The following comment applies to all quarers. Per Consultant: "The dry bed density was actually measured for all runs using an analytical balance. Only two significant figures were recorded".
Note on N6: Reviewer M.H. (12/14/99): This comment applies to all quarters. Regarding chlorine feeds, per consultant, "The goal was to turn off disinfectant application approximately three plant detention times prior to sampling. This was not always possible due to water demands and operational requirements. However, plant staff measured the chloramine residual prior to sampling to ensure a total chlorine resiudal of less than 0.1 mg/L. Instantaneous DBP analyses were not performed during sampling."
Note on AP5: Reviewer D.S. (10/21/99): Per Consultant: "In the DCSS, we reported UV254 down to 0.001 cm-1. Our lowest standard was 0.009 cm-1 for the study (The ICR low-level standard). This should be noted in the DCSS as reported between the MDL and MRL for the method."
Note on AX5: Reviewer M.H. (12/17/99): The following comment applies to TOX for all quarters: Per laboratory, "It appears that some random TOX contamination of the effluent water samples was present during most quarters. The source of this contamination was very elusive. The RSSCT apparatus was checked out with reagent water, and no evidence of increased TOC results were observed after passage through the apparatus. The wetted pump parts exposed to the sample were teflon and stainless steel; the RSSCT column was glass; the cartridge filter used to process the influent water was made of polypropylene and was checked for leaching organics; the filters used on the apparatus were nylon filters which also did not leach any organics. All dosing bottles and other glassware did not show evidence of contamination. The anlaysis for all TOX samples were performed on an automated Mitsubishi TOX analyzer using prepacked columns from COSA, Ind. In general, method blanks did not show evidence of contamination. However, some high RSDs resulted as some columns may have become contaminated or channelling may have occurred during sample preparation. See comments below on specific results affected. In some cases, only one contamination was suspected."
Note on BY5: Reviewer D.S. (10/21/99): Per Consultant: "In the DCSS, we reported UV254 down to 0.001 cm-1. Our lowest standard was 0.009 cm-1 for the study (The ICR low-level standard). This should be noted in the DCSS as reported between the MDL and MRL for the method."
Note on CG37: Reviewer D.S. (10/8/99): Per Consultant: "Only one replicate reported"

## Sheet2. 2nd Quarter
FIELD-SET 2: 2nd QUARTER RSSCT RESULTS (FILE: gacrssct.xls)
Field 2-1: PWS And Treatment Plant Data |  | Field 2-2: Full-Scale GAC Characteristics1 |  | Field 2-3: RSSCT Design Parameters |  |  |  | Field 2-4: Pretreatment Used Prior To GAC1 |  |  | Field 2-5: GAC Influent Water Quality For The 10-Minute EBCT Run | [6 empty] | Field 2-6: GAC Influent Water Quality For The 20-Minute EBCT Run1 | [6 empty] | Field 2-7: GAC Effluent Water Quality For The 10-Minute EBCT Run1 | [15 empty] | Field 2-7: GAC Effluent Water Quality For The 10-Minute EBCT Run (continued) | [17 empty] | Field 2-8: GAC Effluent Water Quality For The 20-Minute EBCT Run1 | [14 empty] | Field 2-8: GAC Effluent Water Quality For The 20-Minute EBCT Run (continued) | [18 empty] | Field 2-9: GAC Cost Parameters
|  |  |  | Input Design Parameters |  | US Standard Mesh Sizes | [18 empty] | Group C, 12 effluent samples per run | [33 empty] | Group C, 12 effluent samples per run
PWS Name | Tarrant County Water Supply Project | Carbon manufacturer | General Carbon Corporation | RSSCT influent TOC (mg/L) | 5 | US standard | Opening | Process | Description | Scale | 10-min. EBCT Start Date | 1998-08-11 | [5 empty] | 20-min. EBCT Start Date | 1998-08-17 | [5 empty] | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Cost Parameter | Parameter value
Public Water System Identification Number | TX2200199 | Carbon trade name | GC 8X30 | Inner diameter of the RSSCT column, DSC (mm) | 11 | mesh size | (mm) | Coagulation | 32mg/L alum, 14 ppm lime | Bench Scale | 10-min. EBCT Start Time | 8:00 | [5 empty] | 20-min. EBCT Start Time | 9:00 | [5 empty] | ID | duplicated? | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | Capital Recovery Interest Rate (%) | 7
Water Industry Data Base Number (optional) | NA | Carbon type | Bituminous Coal | Minimum RSSCT Reynolds number, ReSC, min | 0.63 | 4 | 4.75 | Flocculation | Polymer, 0.5 ppm | Bench Scale | [15 empty] | Y/N | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | Capital Recovery Period (years) | 20
|  | Original GAC mesh size, upper (US standard mesh) | 8 | Full-scale operating temperature, ToC (oC) | 29.8 | 6 | 3.35 | Sedimentation | Gravity settling for 24 hrs. | Bench Scale | Group A, 2 samples per batch | [6 empty] | Group A, 2 samples per batch | [6 empty] | C1-10 | N | 1998-08-11 | 11:00 | 3 | 257.4 | 8.19 | 23 | 0.492 | 0.0042 | 0.85366 | 1.5 | 0.563 | 0.937 | 27.6 | 6.93 | 120 | NR | 1.5 | 3.631 | 5.895 | 3.172 | 14.198 | BMRL | 1.0791 | BMRL | BMRL | 1.8603 | 1.7706 | NA | NA | NA | 2.9394 | 4.71 | C1-20 | N | 1998-08-17 | 12:00 | 3 | 128.7 | 8.11 | 24 | BMRL | 0.0037 | #VALUE! | 1.5 | 0.559 | 0.941 | 27.5 | 6.96 | 120 | NR | BMRL | 2.193 | 3.451 | 1.836 | 7.48 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | Overhead & Profit Factor (% of construction costs) | 57.1
Official ICR Contact Person |  | Original GAC mesh size, lower (US standard mesh) | 30 | Full-scale bed porosity, eLC | 0.45 | 8 | 2.36 | Filtration | 1.0um cartridge filter | Bench Scale | Parameter | Units | Sample A1-10 | Sample A2-10 | Average | RPD |  | Parameter | Units | Sample A1-20 | Sample A2-20 | Average | RPD |  | C2-10 | N | 1998-08-11 | 15:00 | 7 | 600.6 | 8.18 | 23 | 0.988 | 0.0077 | 0.77935 | 1.76 | 0.469 | 1.291 | 27.6 | 6.95 | 120 | 91 | 3.643 | 8.243 | 13.955 | 6.339 | 32.18 | BMRL | 2.4724 | 1.1875 | BMRL | 4.3502 | 3.7619 | NA | NA | NA | 8.0101 | 11.772 | C2-20 | N | 1998-08-17 | 18:00 | 9 | 386.1 | 8.12 | 23 | BMRL | 0.0106 | #VALUE! | 1.5 | 0.578 | 0.922 | 27.5 | 6.96 | 120 | NR | 2.182 | 4.933 | 7.122 | 3.493 | 17.73 | BMRL | 1.9519 | BMRL | BMRL | 2.1323 | 2.2856 | NA | NA | NA | 4.0842 | 6.3698 | Special Sitework Factor (% of construction costs) | NA
Mailing Address |  | Original carbon particle diameter, dLC (mm) | 1.6 | Measured RSSCT dry bed density, rSC (g/cm3) | 0.5 | 10 | 2 | In-Line Filtration | 0.9um exclusion filter | Bench Scale | Sampling date | MM/DD/YY | 1998-08-11 | 1998-08-13 | --- | --- |  | Sampling date | MM/DD/YY | 1998-08-17 | 1998-08-21 | --- | --- |  | C3-10 | N | 1998-08-11 | 19:00 | 11 | 943.8 | 8.2 | 23 | 1.3858 | 0.0141 | 1.0175 | 2.48 | 0.719 | 1.761 | 27.6 | 6.93 | 120 | 92 | 10.739 | 17.479 | 21.213 | 6.128 | 55.559 | BMRL | 7.8078 | 3.4462 | 1.6338 | 6.6283 | 8.565 | NA | NA | NA | 19.5161 | 28.0811 | C3-20 | N | 1998-08-18 | 2:00 | 17 | 729.3 | 8.17 | 24 | BMRL | 0.0073 | #VALUE! | 2 | 0.881 | 1.119 | 27.5 | 6.93 | 120 | 72 | 3.683 | 7.223 | 9.102 | 3.817 | 23.825 | BMRL | 3.6543 | 1.8113 | BMRL | 3.4977 | 4.0193 | NA | NA | NA | 8.9633 | 12.9826 | Construction Contingencies (% of construction costs) | 25
|  | 1: These are the characteristics before the carbon is ground for RSSCT experiments. |  | RSSCT GAC mesh size, upper (US standard mesh) | 100 | 12 | 1.68 |  |  |  | Sampling time | hh:mm | 8:45 | 17:20 | --- | --- |  | Sampling time | hh:mm | 14:00 | 10:50 | --- | --- |  | AVG-C4-10 | Y | 1998-08-12 | 1:00 | 17 | 1458.6 | 8.13 | 23 | 1.5868 | 0.0221 | 1.3927 | 2.84 | 0.67 | 2.17 | 27.6 | 6.95 | 120 | 148 | 15.53 | 22.91 | 23.06 | 5.2 | 66.7 | BMRL | 11.16 | 5.57 | 1.43 | 6.74 | 10.3 | NA | NA | NA | 24.9 | 35.2 | AVG-C4-20 | Y | 1998-08-18 | 14:30 | 29.5 | 1265.55 | 8.12 | 21 | 0.9 | 0.014 | 1.5556 | 1.73 | 0.25 | 1.48 | 27.5 | 6.93 | 120 | 68 | 4.91 | 10.16 | 16.77 | 7.52 | 39.36 | BMRL | 3.46 | 2.03 | 1.35 | 5.46 | 5.16 | NA | NA | NA | 12.3 | 17.46 | Engineering Fee Factor (% of construction costs) | 15
Phone Number |  |  |  | RSSCT GAC mesh size, lower (US standard mesh) | 200 | 16 | 1.18 |  |  |  | Operation time | hh.hh | 0.75 | 57.3333 | --- | --- |  | Operation time | hh.hh | 5 | 97.8333 | --- | --- |  | C5-10 | N | 1998-08-12 | 7:00 | 23 | 1973.4 | 8.16 | 21 | 2.001 | 0.0275 | 1.3743 | 3.6 | 0.956 | 2.644 | 27.6 | 6.95 | 120 | 170 | 24.324 | 27.618 | 23.282 | 3.864 | 79.088 | 2.268 | 15.8315 | 9.5537 | 1.7692 | 6.3698 | 12.8269 | NA | NA | NA | 35.7922 | 48.6191 | C5-20 | N | 1998-08-18 | 21:30 | 36.5 | 1565.85 | 8.14 | 21 | 1.4 | 0.0155 | 1.1071 | 2.29 | 0.606 | 1.684 | 27.5 | 6.93 | 120 | 91 | 6.865 | 15.649 | 20.551 | 5.846 | 48.911 | BMRL | 5.0634 | 2.2289 | 1.3004 | 5.7379 | 6.9558 | NA | NA | NA | 14.3306 | 21.2864 | 1998 ENR Construction Cost Index (CCI base year 1913) | 6095.24
FAX Number | [5 empty] | 20 | 0.85 |  |  |  | Bed volumes | (10 minutes) | 64.35 | 4919.2 | --- | --- |  | Bed volumes | (20 minutes) | 214.5 | 4197.05 | --- | --- |  | C6-10 | N | 1998-08-12 | 11:00 | 27 | 2316.6 | 8.18 | 23 | 2.2926 | 0.0323 | 1.4089 | 3.21 | 0.411 | 2.799 | 27.6 | 6.94 | 120 | 225 | 26.752 | 29.02 | 23.685 | 3.864 | 83.321 | BMRL | 14.2838 | 8.9538 | 1.6609 | 5.7363 | 11.717 | NA | NA | NA | 30.6348 | 42.3518 | C6-20 | N | 1998-08-19 | 6:30 | 45.5 | 1951.95 | 8.19 | 23 | 1.5 | 0.0217 | 1.4467 | 2.88 | 0.7 | 2.18 | 27.5 | 6.95 | 120 | 115 | 13.712 | 20.643 | 21.303 | 4.636 | 60.294 | BMRL | 10.4433 | 5.4321 | 1.8648 | 7.1595 | 10.9671 | NA | NA | NA | 24.8997 | 35.8668 | 1998 Producers Price Index (PPI base year 1967 = 100) | NA
E-Mail Address (optional) |  |  |  | Estimated Run Length |  | 30 | 0.6 |  |  |  | Alkalinity | mg/L as CaCO3 | 97.5 | 100 | 98.75 | 2.5316 |  | Alkalinity | mg/L as CaCO3 | 102.5 | 98 | 100.25 | 4.4888 |  | C7-10 | N | 1998-08-12 | 15:00 | 31 | 2659.8 | 8.15 | 21 | 2.4895 | 0.0363 | 1.4581 | 3.47 | 0.407 | 3.063 | 27.6 | 6.97 | 120 | 305 | 36.798 | 31.732 | 21.897 | 2.689 | 93.116 | 3.6754 | 22.5498 | 13.2792 | 1.7619 | 4.8126 | 11.5097 | NA | NA | NA | 46.0789 | 57.5886 | C7-20 | N | 1998-08-19 | 18:00 | 57 | 2445.3 | 8.16 | 22 | 2.1 | 0.0293 | 1.3952 | 3.07 | 0.383 | 2.687 | 27.5 | 6.93 | 120 | 180 | 21.721 | 27.485 | 23.063 | 3.925 | 76.194 | 2.5799 | 13.2296 | 8.2346 | 1.7379 | 6.4973 | 12.1209 | NA | NA | NA | 32.2793 | 44.4002 | Labor Rate + Fringe ($/work-hour) | 27.2
|  |  |  | Bed volumes to 50% TOC breakthrough, BV50 | 2677.927 | 40 | 0.425 |  |  |  | Total hardness | mg/L as CaCO3 | 116.5 | 113.1 | 114.8 | 2.9617 |  | Total hardness | mg/L as CaCO3 | 113.9 | 119.8 | 116.85 | 5.0492 |  | AVG-C8-10 | Y | 1998-08-12 | 21:00 | 37 | 3174.6 | 8.22 | 22.5 | 2.76 | 0.042 | 1.5217 | 3.78 | 0.53 | 3.25 | 27.6 | 6.97 | 120 | 285 | 40.9 | 33.14 | 21.26 | 2.48 | 97.78 | 3.65 | 22.01 | 15.96 | 1.58 | 5.39 | 13.98 | NA | NA | NA | 48.59 | 62.57 | AVG-C8-20 | Y | 1998-08-20 | 5:00 | 68 | 2917.2 | 8.17 | 23 | 2 | 0.03 | 1.5 | 3.26 | 0.563 | 2.697 | 27.4 | 6.94 | 120 | 163 | 24.3 | 28.94 | 23.59 | 3.61 | 80.44 | 2.13 | 19.36 | 11.84 | 1.79 | 8.59 | 16.48 | NA | NA | NA | 43.71 | 60.19 | Labor Overhead Factor (% of labor) | 33
Technical ICR Contact Person |  |  |  | Estimated run length, BVT ( = 2 x BV50) | 5355.8539 | 50 | 0.3 |  |  |  | Calcium hardness | mg/L as CaCO3 | 90.1 | 89.6 | 89.85 | 0.55648 |  | Calcium hardness | mg/L as CaCO3 | 89.6 | 95.6 | 92.6 | 6.4795 |  | C9-10 | N | 1998-08-13 | 3:00 | 43 | 3689.4 | 8.05 | 22 | 2.9774 | 0.0448 | 1.5047 | 4.16 | 0.563 | 3.597 | 27.6 | 6.94 | 120 | 255 | 45.313 | 33.745 | 20.395 | 2.134 | 101.587 | 3.1915 | 21.2668 | 14.5719 | 1.5319 | 4.6045 | 12.9092 | NA | NA | NA | 45.1666 | 58.0758 | C9-20 | N | 1998-08-20 | 12:00 | 75 | 3217.5 | 8.21 | 24 | 2.1 | 0.0343 | 1.6333 | 3.66 | 0.664 | 2.996 | 27.4 | 6.91 | 120 | 180 | 29.484 | 31.199 | 23.276 | 3.375 | 87.334 | 2.2244 | 21.6406 | 15.2747 | 1.874 | 7.6206 | 16.9652 | NA | NA | NA | 48.6343 | 65.5995 | Electric Rate ($/kW-h) | 0.06
Mailing Address |  |  |  | BVT + 30% safety factor, BVT+30% ( = 2.6 x BV50) | 6962.6101 | 60 | 0.25 |  |  |  | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! |  | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! |  | C10-10 | N | 1998-08-13 | 7:00 | 47 | 4032.6 | 8.21 | 23 | 3.1298 | 0.0481 | 1.5368 | 4.37 | 0.52 | 3.85 | 27.6 | 6.92 | 120 | 295 | 49.905 | 34.559 | 19.902 | 1.894 | 106.26 | 2.9158 | 27.7638 | 20.3164 | 1.5062 | 4.5177 | 13.9572 | NA | NA | NA | 57.0199 | 70.9771 | C10-20 | N | 1998-08-20 | 20:00 | 83 | 3560.7 | 8.21 | 22 | 2.2 | 0.0336 | 1.5273 | 3.9 | 0.806 | 3.094 | 27.4 | 6.94 | 120 | 205 | 33.748 | 31.027 | 22.513 | 2.86 | 90.148 | 2.4653 | 20.8705 | 14.2135 | 1.4819 | 6.3783 | 14.6637 | NA | NA | NA | 45.4095 | 60.0732 | Fuel Oil Rate ($/gal) | na
[6 empty] | 70 | 0.21 |  |  |  | Bromide | mg/L | 150 | 100 | 125 | 40 |  | Bromide | mg/L | 88.132 | 81 | 84.566 | 8.4336 |  | AVG-C11-10 | Y | 1998-08-13 | 13:00 | 53 | 4547.4 | 8.06 | 23 | 3.2575 | 0.05 | 1.5349 | 4.55 | 0.5 | 4.05 | 27.6 | 6.93 | 120 | 285 | 56.96 | 37.63 | 19.88 | 1.81 | 116.28 | 5.64 | 34.55 | 25.04 | 1.97 | 4.38 | 14.44 | NA | NA | NA | 71.58 | 86.02 | AVG-C11-20 | Y | 1998-08-21 | 5:00 | 92 | 3946.8 | 8.23 | 23 | 2.5 | 0.0393 | 1.572 | 4.36 | 0.75 | 3.61 | 27.4 | 6.93 | 120 | 235 | 42.6 | 33.78 | 21.6 | 2.473 | 100.453 | 2.67 | 28.28 | 19.99 | 1.72 | 6.67 | 17.76 | NA | NA | NA | 59.33 | 77.09 | Natural Gas Rate ($/ft3) | 0.0053
Phone Number |  |  |  | General RSSCT Design Parameters |  | 80 | 0.18 | [17 empty] | C12-10 | N | 1998-08-16 | 20:00 | 132 | 11325.6 | 8.19 | 23 | 3.6525 | 0.0609 | 1.6674 | 5.11 | 0.418 | 4.692 | 27.6 | 6.97 | 120 | 220 | 67.348 | 39.264 | 19.315 | 2.001 | 127.928 | 4.1518 | 34.2928 | 23.2186 | 1.7484 | 2.9623 | 12.0984 | NA | NA | NA | 66.3739 | 78.4723 | C12-20 | N | 1998-08-27 | 17:30 | 248.5 | 10660.65 | 8.09 | 23 | 3.6 | 0.0543 | 1.5083 | 5.19 | 0.208 | 4.982 | 27.5 | 6.93 | 120 | 210 | 68.299 | 39.624 | 18.848 | 1.756 | 128.527 | 4.0169 | 29.5279 | 25.3637 | BMRL | 4.0523 | 14.5216 | NA | NA | NA | 62.9608 | 77.4824 | Current Process Water Rate ($/1000 gal) | 0.41
FAX Number |  |  |  | Kinematic viscosity at ToC, nLC (m2/s) | 8.1427e-07 | 100 | 0.15 |  |  |  | Group B, 3 samples per batch | [6 empty] | Group B, 3 samples per batch | [10 empty] | -864440 | -74168952 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -864585 | -37090696.5 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 | Modifications to Existing Plant (% of construction costs) | NA
E-Mail Address (optional) |  |  |  | RSSCT carbon particle diameter, dSC (mm) | 0.1125 | 120 | 0.125 |  |  |  | Parameter | Units | Sample B1-10 | Sample B2-10 | Sample B3-10 | Average | %SD | Parameter | Units | Sample B1-20 | Sample B2-20 | Sample B3-20 | Average | %SD |  |  |  |  | -864440 | -74168952 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -864585 | -37090696.5 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
|  |  |  | Scaling factor, SF | 14.3 | 140 | 0.106 | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | Sampling date | MM/DD/YY | 1998-08-11 | 1998-08-12 | 1998-08-13 | --- | --- | Sampling date | MM/DD/YY | 1998-08-17 | 1998-08-20 | 1998-08-21 | --- | --- |  |  |  |  | -864440 | -74168952 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -864585 | -37090696.5 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
Plant Name | Tarrant County Water Supply Project |  |  | RSSCT hydraulic loading rate, vSC (m/hr) | 7.3871 | 170 | 0.088 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | Sampling time | hh:mm | 8:45 | 13:30 | 17:20 | --- | --- | Sampling time | hh:mm | 14:00 | 9:15 | 10:50 | --- | --- |  |  |  |  | -864440 | -74168952 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -864585 | -37090696.5 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
Treatment Plant Category | CONV |  |  | RSSCT flow rate, QSC (mL/min) | 11.7003 | 200 | 0.075 | is to list the pretreatment processes used in this particular RSSCT run. |  |  | Operation time | hh.hh | 0.75 | 29.5 | 57.3333 | --- | --- | Operation time | hh.hh | 5 | 72.25 | 97.8333 | --- | --- |  |  |  |  | -864440 | -74168952 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -864585 | -37090696.5 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
Process Train Name | Convential Filtration |  |  | Estimated total influent volume required, VSCT (L) | 170.9052 | 230 | 0.062 |  |  |  | Bed volumes | (10 minute) | 64.35 | 2531.1 | 4919.2 | --- | --- | Bed volumes | (20 minute) | 214.5 | 3099.525 | 4197.05 | --- | --- | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
ICR Treatment Plant Identification Number | 650 |  |  |  |  | 270 | 0.053 |  |  |  | pH | --- | 8.25 | 8.23 | 8.11 | 8.1967 | 0.92378 | pH | --- | 8.08 | 8.12 | 8.19 | 8.13 | 0.68484 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
PWSID Number of Plant (if assigned) | TX2200199 |  |  | 10-Minute EBCT Run |  | 325 | 0.044 |  |  |  | Turbidity | ntu | 0.48 | 0.48 | 0.77 | 0.57667 | 29.0344 | Turbidity | ntu | 0.65 | 0.88 | 0.9 | 0.81 | 17.1512 | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below. | [33 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below.
Historical Minimum Water Temperature (oC) | 12 |  |  | Full-scale empty bed contact time, EBCTLC (min) | 10 | 400 | 0.037 |  |  |  | Temperature | oC | 19 | 21 | 21 | 20.3333 | 5.6789 | Temperature | oC | 23 | 23 | 23 | 23 | 0
Historical Average Water Temperature (oC) | 22.7 |  |  | Estimated full-scale run time, tLCT (days) | 48.3515 | [5 empty] | Total organic carbon | mg/L | 4.8 | 4.95 | 4.9 | 4.8833 | 1.564 | Total organic carbon | mg/L | 5.1 | 4.7 | 4.7 | 4.8333 | 4.7781 | Group D, 3 duplicate effluent samples per run (results from primary and duplicate analyses) | [33 empty] | Group D, 3 duplicate effluent samples per run (results from primary and duplicate analyses)
State Approved Plant Capacity (MGD) | 57 |  |  | RSSCT empty bed contact time, EBCTSC (min) | 0.6993 | [5 empty] | UV254 | cm-1 | 0.0872 | 0.092 | 0.0887 | 0.0893 | 2.7498 | UV254 | cm-1 | 0.0917 | 0.089 | 0.0896 | 0.0901 | 1.5735 | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS
|  |  |  | Estimated RSSCT run time, tSCT (days) | 3.3812 | [5 empty] | SUVA | L/(mg*m) | 1.8167 | 1.8586 | 1.8102 | 1.8285 | 1.4366 | SUVA | L/(mg*m) | 1.798 | 1.8936 | 1.9064 | 1.866 | 3.1732 | ID | Type | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6
|  |  |  | RSSCT bed length, lSC (cm) | 8.6097 | [5 empty] | SDS-Cl2 dose | mg/L | 7 | 7 | 7 | 7 | 0 | SDS-Cl2 dose | mg/L | 7 | 7 | 8 | 7.3333 | 7.873 |  |  | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L
|  |  |  | Estimated volume required for 10-minute EBCT, VSC (L) | 56.9684 | [5 empty] | SDS-Free Cl2 residual | mg/L | 0.559 | 0.438 | 0.411 | 0.46933 | 16.7937 | SDS-Free Cl2 residual | mg/L | 0.469 | 0.434 | 0.857 | 0.58667 | 40.0174 | C4-10 | Primary | 1998-08-12 | 1:00 | 17 | 1458.6 | 8.13 | 23 | 1.5868 | 0.0221 | 1.3927 | 2.84 | 0.547 | 2.293 | 27.6 | 6.96 | 120 | 140 | 15.571 | 22.858 | 23.348 | 5.193 | 66.97 | BMRL | 10.9432 | 5.7403 | 1.5295 | 6.4127 | 10.1691 | NA | NA | NA | 24.6257 | 34.7948 | C4-20 | Primary | 1998-08-18 | 14:30 | 29.5 | 1265.55 | 8.12 | 21 | 0.9 | 0.015 | 1.6667 | 1.73 | 0.259 | 1.471 | 27.5 | 6.92 | 120 | 76 | 4.789 | 10.106 | 16.762 | 7.395 | 39.052 | BMRL | 3.2479 | 1.7258 | 1.302 | 5.2559 | 4.9509 | NA | NA | NA | 11.5316 | 16.4825
|  |  |  | Mass GAC required, mSC (g) | 4.091 | [5 empty] | SDS-Cl2 demand | mg/L | 6.441 | 6.562 | 6.589 | 6.5307 | 1.2069 | SDS-Cl2 demand | mg/L | 6.531 | 6.566 | 7.143 | 6.7467 | 5.0941 | D1-10 | Duplicate | 1998-08-12 | 1:00 | 17 | 1458.6 | 8.12 | 23 | 1.5868 | 0.022 | 1.3864 | 2.84 | 0.786 | 2.054 | 27.6 | 6.93 | 120 | 155 | 15.486 | 22.956 | 22.777 | 5.209 | 66.428 | BMRL | 11.3729 | 5.4041 | 1.3288 | 7.0598 | 10.4237 | NA | NA | NA | 25.1656 | 35.5893 | D1-20 | Duplicate | 1998-08-18 | 14:30 | 29.5 | 1265.55 | 8.12 | 21 | 0.9 | 0.0138 | 1.5333 | 1.73 | 0.248 | 1.482 | 27.5 | 6.93 | 120 | 59 | 5.039 | 10.21 | 16.785 | 7.639 | 39.673 | BMRL | 3.677 | 2.3294 | 1.4031 | 5.6557 | 5.3752 | NA | NA | NA | 13.0652 | 18.4404
[11 empty] | SDS-Chlorination temp. | oC | 27.6 | 27.6 | 27.6 | 27.6 | 0 | SDS-Chlorination temp. | oC | 27.5 | 27.5 | 27.4 | 27.4667 | 0.2102 | AVG-C4-10 | Average | --- | --- | --- | --- | 8.125 | 23 | 1.5868 | 0.02205 | 1.3896 | 2.84 | 0.6665 | 2.1735 | 27.6 | 6.945 | 120 | 147.5 | 15.5285 | 22.907 | 23.0625 | 5.201 | 66.699 | #DIV/0! | 11.158 | 5.5722 | 1.4291 | 6.7363 | 10.2964 | #DIV/0! | #DIV/0! | #DIV/0! | 24.8956 | 35.1921 | AVG-C4-20 | Average | --- | --- | --- | --- | 8.12 | 21 | 0.9 | 0.0144 | 1.6 | 1.73 | 0.2535 | 1.4765 | 27.5 | 6.925 | 120 | 67.5 | 4.914 | 10.158 | 16.7735 | 7.517 | 39.3625 | #DIV/0! | 3.4625 | 2.0276 | 1.3525 | 5.4558 | 5.1631 | #DIV/0! | #DIV/0! | #DIV/0! | 12.2984 | 17.4614
|  |  |  | 20-Minute EBCT Run | [6 empty] | SDS-Chlorination pH | --- | 6.95 | 6.92 | 6.97 | 6.9467 | 0.36228 | SDS-Chlorination pH | --- | 6.96 | 6.94 | 6.97 | 6.9567 | 0.21958 | RPD-C4-10 | RPD | --- | --- | --- | --- | 0.12308 | 0 | 0 | 0.45351 | 0.45351 | 0 | 35.859 | 10.9961 | 0 | 0.43197 | 0 | 10.1695 | 0.54738 | 0.42782 | 2.4759 | 0.30763 | 0.81261 | #VALUE! | 3.851 | 6.0335 | 14.0433 | 9.6062 | 2.4727 | #VALUE! | #VALUE! | #VALUE! | 2.1687 | 2.2576 | RPD-C4-20 | RPD | --- | --- | --- | --- | 0 | 0 | 0 | 8.3333 | 8.3333 | 0 | 4.3393 | 0.74501 | 0 | 0.1444 | 0 | 25.1852 | 5.0875 | 1.0238 | 0.13712 | 3.246 | 1.5776 | #VALUE! | 12.393 | 29.7692 | 7.4748 | 7.328 | 8.218 | #VALUE! | #VALUE! | #VALUE! | 12.4699 | 11.2127
|  |  |  | Full-scale empty bed contact time, EBCTLC (min) | 20 | [5 empty] | SDS-Incubation time | hours | 120 | 120 | 120 | 120 | 0 | SDS-Incubation time | hours | 120 | 120 | 120 | 120 | 0 | C8-10 | Primary | 1998-08-12 | 21:00 | 37 | 3174.6 | 8.22 | 23 | 2.7499 | 0.042 | 1.5273 | 3.78 | 0.508 | 3.272 | 27.6 | 6.97 | 120 | 300 | 41.621 | 33.267 | 21.354 | 2.509 | 98.751 | 3.2845 | 20.4382 | 14.2913 | 1.4909 | 4.8661 | 12.8134 | NA | NA | NA | 44.371 | 57.1844 | C8-20 | Primary | 1998-08-20 | 5:00 | 68 | 2917.2 | 8.17 | 23 | 2 | 0.0291 | 1.455 | 3.26 | 0.547 | 2.713 | 27.4 | 6.95 | 120 | 155 | 24.92 | 29.48 | 24.301 | 3.797 | 82.498 | 2.2109 | 20.2342 | 12.1179 | 1.9292 | 8.8853 | 16.833 | NA | NA | NA | 45.3775 | 62.2105
|  |  |  | Estimated full-scale run time, tLCT (days) | 96.7029 | [5 empty] | SDS-TOX | mg Cl- /L | 320 | 490 | 345 | 385 | 23.841 | SDS-TOX | mg Cl- /L | 500 | 585 | 450 | 511.6667 | 13.3391 | D2-10 | Duplicate | 1998-08-12 | 21:00 | 37 | 3174.6 | 8.22 | 22 | 2.7608 | 0.0415 | 1.5032 | 3.78 | 0.551 | 3.229 | 27.6 | 6.96 | 120 | 270 | 40.175 | 33.019 | 21.159 | 2.456 | 96.809 | 4.0118 | 23.59 | 17.6209 | 1.6747 | 5.9235 | 15.1367 | NA | NA | NA | 52.8209 | 67.9576 | D2-20 | Duplicate | 1998-08-20 | 5:00 | 68 | 2917.2 | 8.14 | 23 | 2 | 0.03 | 1.5 | 3.26 | 0.563 | 2.697 | 27.4 | 6.93 | 120 | 170 | 23.677 | 28.406 | 22.883 | 3.432 | 78.398 | 2.0515 | 18.4808 | 11.5663 | 1.6421 | 8.3024 | 16.1358 | NA | NA | NA | 42.0431 | 58.1789
|  |  |  | RSSCT empty bed contact time, EBCTSC (min) | 1.3986 | [5 empty] | SDS-CHCl3 | mg/L | 115.136 | 120.915 | 124.466 | 120.1723 | 3.9186 | SDS-CHCl3 | mg/L | 117.177 | 113.495 | 130.052 | 120.2413 | 7.23 | AVG-C8-10 | Average | --- | --- | --- | --- | 8.22 | 22.5 | 2.7553 | 0.04175 | 1.5153 | 3.78 | 0.5295 | 3.2505 | 27.6 | 6.965 | 120 | 285 | 40.898 | 33.143 | 21.2565 | 2.4825 | 97.78 | 3.6481 | 22.0141 | 15.9561 | 1.5828 | 5.3948 | 13.975 | #DIV/0! | #DIV/0! | #DIV/0! | 48.596 | 62.571 | AVG-C8-20 | Average | --- | --- | --- | --- | 8.155 | 23 | 2 | 0.02955 | 1.4775 | 3.26 | 0.555 | 2.705 | 27.4 | 6.94 | 120 | 162.5 | 24.2985 | 28.943 | 23.592 | 3.6145 | 80.448 | 2.1312 | 19.3575 | 11.8421 | 1.7856 | 8.5938 | 16.4844 | #DIV/0! | #DIV/0! | #DIV/0! | 43.7103 | 60.1947
|  |  |  | Estimated RSSCT run time, tSCT (days) | 6.7624 | [5 empty] | SDS-BDCM | mg/L | 45.173 | 45.674 | 47.581 | 46.1427 | 2.7536 | SDS-BDCM | mg/L | 45.983 | 45.138 | 47.61 | 46.2437 | 2.717 | RPD-C8-10 | RPD | --- | --- | --- | --- | 0 | 4.4444 | 0.39559 | 1.1976 | 1.5932 | 0 | 8.1209 | 1.3229 | 0 | 0.14358 | 0 | 10.5263 | 3.5356 | 0.74827 | 0.91737 | 2.1349 | 1.9861 | 19.9361 | 14.3172 | 20.8673 | 11.6123 | 19.6004 | 16.6246 | #VALUE! | #VALUE! | #VALUE! | 17.3881 | 17.2176 | RPD-C8-20 | RPD | --- | --- | --- | --- | 0.36787 | 0 | 0 | 3.0457 | 3.0457 | 0 | 2.8829 | 0.5915 | 0 | 0.28818 | 0 | 9.2308 | 5.1155 | 3.7107 | 6.0105 | 10.0982 | 5.0965 | 7.4794 | 9.058 | 4.658 | 16.0782 | 6.7828 | 4.2295 | #VALUE! | #VALUE! | #VALUE! | 7.6284 | 6.6976
|  |  |  | RSSCT bed length, lSC (cm) | 17.2194 | [5 empty] | SDS-DBCM | mg/L | 13.703 | 13.868 | 14.482 | 14.0177 | 2.9284 | SDS-DBCM | mg/L | 13.829 | 13.581 | 13.43 | 13.6133 | 1.4798 | C11-10 | Primary | 1998-08-13 | 13:00 | 53 | 4547.4 | 8.09 | 23 | 3.2575 | 0.048 | 1.4735 | 4.55 | 0.488 | 4.062 | 27.6 | 6.95 | 120 | 280 | 57.687 | 37.951 | 20.63 | 1.926 | 118.194 | 5.4105 | 35.4153 | 26.7872 | 1.9155 | 4.7373 | 14.7387 | NA | NA | NA | 74.2658 | 89.0045 | C-11-20 | Primary | 1998-08-21 | 5:00 | 92 | 3946.8 | 8.23 | 23 | 2.5 | 0.0393 | 1.572 | 4.36 | 0.684 | 3.676 | 27.4 | 6.96 | 120 | 210 | 43.704 | 34.324 | 21.926 | 2.473 | 102.427 | 2.9469 | 32.9428 | 22.5302 | 1.8629 | 7.7738 | 20.8819 | NA | NA | NA | 68.0566 | 88.9385
|  |  |  | Estimated volume required for 20-minute EBCT, VSC (L) | 113.9368 | [5 empty] | SDS-CHBr3 | mg/L | 0.736 | 0.797 | BMRL | 0.7665 | 5.6273 | SDS-CHBr3 | mg/L | BMRL | BMRL | BMRL | #DIV/0! | #DIV/0! | D3-10 | Duplicate | 1998-08-13 | 13:00 | 53 | 4547.4 | 8.02 | 23 | 3.2575 | 0.051 | 1.5656 | 4.55 | 0.504 | 4.046 | 27.6 | 6.91 | 120 | 290 | 56.238 | 37.299 | 19.138 | 1.693 | 114.368 | 5.8642 | 33.6937 | 23.2832 | 2.0222 | 4.029 | 14.1334 | NA | NA | NA | 68.8923 | 83.0257 | D3-20 | Duplicate | 1998-08-21 | 5:00 | 92 | 3946.8 | 8.22 | 23 | 2.5 | 0.0381 | 1.524 | 4.36 | 0.818 | 3.542 | 27.4 | 6.9 | 120 | 260 | 41.488 | 33.236 | 21.269 | 2.462 | 98.455 | 2.39 | 23.6104 | 17.4469 | 1.5783 | 5.5619 | 14.6359 | NA | NA | NA | 50.5875 | 65.2234
|  |  |  | Mass GAC required, mSC (g) | 8.182 | [5 empty] | SDS-THM4 | mg/L | 174.748 | 181.254 | 186.529 | 180.8437 | 3.2632 | SDS-THM4 | mg/L | 176.989 | 172.214 | 191.092 | 180.0983 | 5.4501 | AVG-C11-10 | Average | --- | --- | --- |  | 8.055 | 23 | 3.2575 | 0.0495 | 1.5196 | 4.55 | 0.496 | 4.054 | 27.6 | 6.93 | 120 | 285 | 56.9625 | 37.625 | 19.884 | 1.8095 | 116.281 | 5.6373 | 34.5545 | 25.0352 | 1.9688 | 4.3831 | 14.436 | #DIV/0! | #DIV/0! | #DIV/0! | 71.579 | 86.0151 | AVG-C11-20 | Average | --- | --- | --- | --- | 8.225 | 23 | 2.5 | 0.0387 | 1.548 | 4.36 | 0.751 | 3.609 | 27.4 | 6.93 | 120 | 235 | 42.596 | 33.78 | 21.5975 | 2.4675 | 100.441 | 2.6684 | 28.2766 | 19.9886 | 1.7206 | 6.6678 | 17.7589 | #DIV/0! | #DIV/0! | #DIV/0! | 59.322 | 77.081
[11 empty] | SDS-MCAA* | mg/L | 6.1107 | 6.5387 | 7.922 | 6.8571 | 13.8061 | SDS-MCAA* | mg/L | 6.0753 | 10.1981 | 3.1906 | 6.488 | 54.2838 | RPD-C11-10 | RPD | --- | --- | --- | --- | 0.86903 | 0 | 0 | 6.0606 | 6.0606 | 0 | 3.2258 | 0.39467 | 0 | 0.5772 | 0 | 3.5088 | 2.5438 | 1.7329 | 7.5035 | 12.8765 | 3.2903 | 8.0481 | 4.9823 | 13.9963 | 5.4194 | 16.1596 | 4.193 | #VALUE! | #VALUE! | #VALUE! | 7.5071 | 6.9509 | RPD-C11-20 | RPD | --- | --- | --- | --- | 0.12158 | 0 | 0 | 3.1008 | 3.1008 | 0 | 17.8429 | 3.7129 | 0 | 0.8658 | 0 | 21.2766 | 5.2024 | 3.2208 | 3.042 | 0.4458 | 3.9546 | 20.8698 | 33.004 | 25.4311 | 16.5407 | 33.1726 | 35.1711 | #VALUE! | #VALUE! | #VALUE! | 29.4479 | 30.7665
[11 empty] | SDS-DCAA* | mg/L | 51.1147 | 53.3507 | 56.4089 | 53.6248 | 4.9561 | SDS-DCAA* | mg/L | 56.7011 | 62.9714 | 62.6552 | 60.7759 | 5.8122 | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[11 empty] | SDS-TCAA* | mg/L | 43.3526 | 56.801 | 48.9061 | 49.6866 | 13.6014 | SDS-TCAA* | mg/L | 48.4505 | 58.8867 | 49.1188 | 52.152 | 11.2018 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
[11 empty] | SDS-MBAA* | mg/L | 1.5699 | 1.8507 | 1.4921 | 1.6376 | 11.5191 | SDS-MBAA* | mg/L | 1.3862 | 1.7734 | 1.4526 | 1.5374 | 13.4683
[11 empty] | SDS-DBAA* | mg/L | 2.783 | 3.5554 | 2.7228 | 3.0204 | 15.3721 | SDS-DBAA* | mg/L | 3.0224 | 3.8497 | 2.9648 | 3.279 | 15.0995
[11 empty] | SDS-BCAA* | mg/L | 16.1316 | 20.0475 | 15.0805 | 17.0865 | 15.3195 | SDS-BCAA* | mg/L | 17.5261 | 21.4826 | 17.6364 | 18.8817 | 11.9328
[11 empty] | SDS-TBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0!
[11 empty] | SDS-CDBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0!
[11 empty] | SDS-DCBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0!
[11 empty] | SDS-HAA5 | mg/L | 104.9309 | 122.0965 | 117.4519 | 114.8264 | 7.7324 | SDS-HAA5 | mg/L | 115.6355 | 137.6793 | 119.382 | 124.2323 | 9.4945
[11 empty] | SDS-HAA6 | mg/L | 121.0625 | 142.144 | 132.5324 | 131.913 | 8.001 | SDS-HAA6 | mg/L | 133.1616 | 159.1619 | 137.0184 | 143.114 | 9.8041
[11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [6 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [6 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
Note on H7: Reviewer M.H. (12/13/99): Reviewer adjusted Reynolds number based on new full-scale temperatures.
Note on H8: Reviewer D.S. (10/13/99): Full-scale temperature is 29.8C, RSSCT designed for 20C.
Note on N5: Reviewer M.H. (12/17/99): Per consultant, "The pretreatment for the influent water was done all at once....The unfortunate circumstance in this quarter was that we could not collect at the exact same sampling point as the other 3 quarters due to the extreme drought conditions in Texas during Q2. We had to attempt pretreatement in the lab as close to PWS conditions as we could."
Note on Q18: Reviewer D.S. (10/8/99): Per Consultant: "The Bromide results were verified. RPD's were high for unknown reasons. QC samples for Bromide in all runs was acceptable based on ICR criteria".
Note on Q38: Reviewer D.S. (10/8/99): Per Consultant: "TOX results for all influent samples verified".
Note on Y18: Reviewer D.S. (10/8/99): Per Consultant: "The Bromide results were verified. RPD's were high for unknown reasons. QC samples for Bromide in all runs was acceptable based on ICR criteria".
Note on Y38: Reviewer D.S. (10/8/99): Per Consultant: "TOX results for all influent samples verified".
Note on AK5: Reviewer M.H. (12/17/99): Per consultant, "It is interesting that there is a long gap in both columns between samples 11 and 12. At EBCT 20, we did have some "down time" for repacking the column/stirring the column in order to minimize headloss buildup. This time was taken into account in operation time. At EBCT 10, we had less trouble with headloss and virtually no 'down time'."
Note on AP5: Reviewer D.S. (10/21/99): Per Consultant: "In the DCSS, we reported UV254 down to 0.001 cm-1. Our lowest standard was 0.009 cm-1 for the study (The ICR low-level standard). This should be noted in the DCSS as reported between the MDL and MRL for the method."
Note on BT5: Reviewer M.H. (12/17/99): Per consultant, "It is interesting that there is a long gap in both columns between samples 11 and 12. At EBCT 20, we did have some "down time" for repacking the column/stirring the column in order to minimize headloss buildup. This time was taken into account in operation time. At EBCT 10, we had less trouble with headloss and virtually no 'down time'."
Note on BY5: Reviewer D.S. (10/21/99): Per Consultant: "In the DCSS, we reported UV254 down to 0.001 cm-1. Our lowest standard was 0.009 cm-1 for the study (The ICR low-level standard). This should be noted in the DCSS as reported between the MDL and MRL for the method."
Note on CG10: Reviewer D.S. (10/8/99): Per Consultant: "Only one replicate reported"
Note on CG42: Reviewer D.S. (10/8/99): Per Consultant: "Only one replicate reported"
Note on CM44: Reviewer D.S. (10/8/99): Per Consultant: "HAA results verified. All QC for the analytical runs met ICR criteria".
Note on CN44: Reviewer D.S. (10/8/99): Per Consultant: "HAA results verified. All QC for the analytical runs met ICR criteria".
Note on CO44: Reviewer D.S. (10/8/99): Per Consultant: "HAA results verified. All QC for the analytical runs met ICR criteria".
Note on CQ44: Reviewer D.S. (10/8/99): Per Consultant: "HAA results verified. All QC for the analytical runs met ICR criteria".
Note on CR44: Reviewer D.S. (10/8/99): Per Consultant: "HAA results verified. All QC for the analytical runs met ICR criteria".

## Sheet3. 3rd Quarter
FIELD-SET 3: 3rd QUARTER RSSCT RESULTS (FILE: gacrssct.xls)
Field 3-1: PWS And Treatment Plant Data |  | Field 3-2: Full-Scale GAC Characteristics1 |  | Field 3-3: RSSCT Design Parameters |  |  |  | Field 3-4: Pretreatment Used Prior To GAC1 |  |  | Field 3-5: GAC Influent Water Quality For The 10-Minute EBCT Run | [6 empty] | Field 3-6: GAC Influent Water Quality For The 20-Minute EBCT Run1 | [6 empty] | Field 3-7: GAC Effluent Water Quality For The 10-Minute EBCT Run1 | [15 empty] | Field 3-7: GAC Effluent Water Quality For The 10-Minute EBCT Run (continued) | [17 empty] | Field 3-8: GAC Effluent Water Quality For The 20-Minute EBCT Run1 | [14 empty] | Field 3-8: GAC Effluent Water Quality For The 20-Minute EBCT Run (continued) | [18 empty] | Field 3-9: GAC Cost Parameters
|  |  |  | Input Design Parameters |  | US Standard Mesh Sizes | [18 empty] | Group C, 12 effluent samples per run | [33 empty] | Group C, 12 effluent samples per run
PWS Name | Tarrant County Water Supply Project | Carbon manufacturer | General Carbon Corporation | RSSCT influent TOC (mg/L) | 3.7 | US standard | Opening | Process | Description | Scale | 10-min. EBCT Start Date | 1998-10-19 | [5 empty] | 20-min. EBCT Start Date | 1998-10-05 | [5 empty] | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Cost Parameter | Parameter value
Public Water System Identification Number | TX2200199 | Carbon trade name | GC 8X30 | Inner diameter of the RSSCT column, DSC (mm) | 11 | mesh size | (mm) | Coagulation | 30 mg/L alum, 27.8 mg/L lime, 0.43 mg/L polymer | Full Scale | 10-min. EBCT Start Time | 9:00 | [5 empty] | 20-min. EBCT Start Time | 8:00 | [5 empty] | ID | duplicated? | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | Capital Recovery Interest Rate (%) | 7
Water Industry Data Base Number (optional) | NA | Carbon type | Bituminous | Minimum RSSCT Reynolds number, ReSC, min | 0.561 | 4 | 4.75 | Flocculation | Vertical impeller-type | Full Scale | [15 empty] | Y/N | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | Capital Recovery Period (years) | 20
|  | Original GAC mesh size, upper (US standard mesh) | 8 | Full-scale operating temperature, ToC (oC) | 24.8 | 6 | 3.35 | Sedimentation | Approximately 9.5-hour settling time | Full Scale | Group A, 2 samples per batch | [6 empty] | Group A, 2 samples per batch | [6 empty] | C1-10 | N | 1998-10-19 | 12:00 | 3 | 257.4 | 8.22 | 23 | BMRL | 0.0081 | #VALUE! | 2.7 | 0.968 | 1.732 | 27.4 | 8 | 120 | NR | BMRL | 2.42 | 4.021 | 2.888 | 9.329 | BMRL | BMRL | BMRL | BMRL | 1.1813 | 1.2544 | NA | NA | NA | 1.1813 | 2.4357 | C1-20 | N | 1998-10-05 | 11:00 | 3 | 128.7 | 8.51 | 23 | BMRL | 0.0044 | #VALUE! | 2 | 0.329 | 1.671 | 27.1 | 7.99 | 120 | 26.7 | BMRL | BMRL | 1.911 | 2.664 | 4.575 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | Overhead & Profit Factor (% of construction costs) | 57.1
Official ICR Contact Person |  | Original GAC mesh size, lower (US standard mesh) | 30 | Full-scale bed porosity, eLC | 0.45 | 8 | 2.36 | Filtration | Sand, anthracite, garnet, Microfloc MS-186 | Full Scale | Parameter | Units | Sample A1-10 | Sample A2-10 | Average | RPD |  | Parameter | Units | Sample A1-20 | Sample A2-20 | Average | RPD |  | C2-10 | N | 1998-10-19 | 16:00 | 7 | 600.6 | 7.96 | 23 | BMRL | 0.0035 | #VALUE! | 2.7 | 0.818 | 1.882 | 27.4 | 8.01 | 120 | NR | 1.068 | 2.948 | 5.723 | 3.324 | 13.063 | BMRL | 1.2543 | BMRL | BMRL | 1.729 | 1.7403 | NA | NA | NA | 2.9833 | 4.7236 | C2-20 | N | 1998-10-05 | 19:00 | 11 | 471.9 | 7.99 | 23 | BMRL | 0.007 | #VALUE! | 2 | 0.337 | 1.663 | 27.1 | 8.02 | 120 | 70.5 | BMRL | BMRL | 2.591 | 3.392 | 5.983 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | Special Sitework Factor (% of construction costs) | NA
Mailing Address |  | Original carbon particle diameter, dLC (mm) | 1.6 | Measured RSSCT dry bed density, rSC (g/cm3) | 0.5 | 10 | 2 | Filtration | 1.0 um cartridge filter | Bench Scale | Sampling date | MM/DD/YY | 1998-10-19 | 1998-10-22 | --- | --- |  | Sampling date | MM/DD/YY | 1998-10-05 | 1998-10-12 | --- | --- |  | C3--10 | N | 1998-10-19 | 22:45 | 13.75 | 1179.75 | 8.04 | 21 | BMRL | 0.0035 | #VALUE! | 2.7 | 0.798 | 1.902 | 27.4 | 8 | 120 | 33 | 1.06 | 3.423 | 7.512 | 5.288 | 17.283 | BMRL | 1.2492 | BMRL | BMRL | 1.9735 | 1.8697 | NA | NA | NA | 3.2227 | 5.0924 | C3-20 | N | 1998-10-06 | 6:00 | 22 | 943.8 | 8.13 | 24 | BMRL | 0.0067 | #VALUE! | 2 | 0.263 | 1.737 | 27.1 | 8.03 | 120 | BMRL | BMRL | 1.012 | 3.278 | 4.487 | 8.777 | BMRL | BMRL | BMRL | BMRL | 1.7661 | 1.0457 | NA | NA | NA | 1.7661 | 2.8118 | Construction Contingencies (% of construction costs) | 25
|  | 1: These are the characteristics before the carbon is ground for RSSCT experiments. |  | RSSCT GAC mesh size, upper (US standard mesh) | 100 | 12 | 1.68 | In-Line Filtration | 0.9 um exclusion size | Bench Scale | Sampling time | hh:mm | 10:00 | 14:00 | --- | --- |  | Sampling time | hh:mm | 8:30 | 8:00 | --- | --- |  | AVG-C4-10 | Y | 1998-10-20 | 6:00 | 21 | 1801.8 | 8.04 | 23 | 0.9 | 0.009 | 1 | 3.2 | 0.65 | 2.55 | 27.4 | 8.03 | 120 | 60.5 | 6 | 15.33 | 21.78 | 10.13 | 53.24 | BMRL | 5.27 | 1.14 | BMRL | 5.24 | 5.73 | NA | NA | NA | 11.65 | 17.38 | AVG-C4-20 | Y | 1998-10-07 | 1:00 | 41 | 1758.9 | 8.09 | 23 | BMRL | 0.006 | #VALUE! | 2 | 0.2 | 1.8 | 27.1 | 8.01 | 120 | 29.5 | BMRL | 2.54 | 8.51 | 10.78 | 21.83 | BMRL | 2.13 | BMRL | BMRL | 3.86 | 2.02 | NA | NA | NA | 5.99 | 8.01 | Engineering Fee Factor (% of construction costs) | 15
Phone Number |  |  |  | RSSCT GAC mesh size, lower (US standard mesh) | 200 | 16 | 1.18 |  |  |  | Operation time | hh.hh | 1 | 77 | --- | --- |  | Operation time | hh.hh | 0.5 | 168 | --- | --- |  | C5-10 | N | 1998-10-20 | 12:00 | 27 | 2316.6 | 8.03 | 23 | 1.6 | 0.018 | 1.125 | 4.18 | 0.798 | 3.382 | 27.4 | 8.02 | 120 | 130 | 19.864 | 25.704 | 23.292 | 6.24 | 75.1 | BMRL | 11.9953 | 2.569 | 1.4756 | 5.3453 | 9.3795 | NA | NA | NA | 21.3852 | 30.7647 | C5-20 | N | 1998-10-07 | 12:00 | 52 | 2230.8 | 7.99 | 22 | 1 | 0.0103 | 1.03 | 1.93 | 0.047 | 1.883 | 27.1 | 8.02 | 120 | NR | NR | NR | NR | NR | 0 | NR | NR | NR | NR | NR | NR | NA | NA | NA | 0 | 0 | 1998 ENR Construction Cost Index (CCI base year 1913) | 6095.24
FAX Number | [5 empty] | 20 | 0.85 |  |  |  | Bed volumes | (10 minutes) | 85.8 | 6606.6 | --- | --- |  | Bed volumes | (20 minutes) | 21.45 | 7207.2 | --- | --- |  | C6-10 | N | 1998-10-20 | 17:00 | 32 | 2745.6 | 8.02 | 22 | 1.8 | 0.0218 | 1.2111 | 4.54 | 0.81 | 3.73 | 27.4 | 8.04 | 120 | 175 | 30.949 | 30.178 | 22.849 | 5.119 | 89.095 | BMRL | 16.5862 | 3.7405 | 1.2528 | 5.8493 | 11.722 | NA | NA | NA | 27.4288 | 39.1508 | C6-20 | N | 1998-10-08 | 2:00 | 66 | 2831.4 | 8.06 | 22 | 1.6 | 0.0181 | 1.1313 | 3.06 | 0.097 | 2.963 | 27.1 | 7.92 | 120 | NR | NR | NR | NR | NR | 0 | NR | NR | NR | NR | NR | NR | NA | NA | NA | 0 | 0 | 1998 Producers Price Index (PPI base year 1967 = 100) | NA
E-Mail Address (optional) |  |  |  | Estimated Run Length |  | 30 | 0.6 |  |  |  | Alkalinity | mg/L as CaCO3 | 86 | 81.1 | 83.55 | 5.8648 |  | Alkalinity | mg/L as CaCO3 | 89.5 | 82.4 | 85.95 | 8.2606 |  | C7-10 | N | 1998-10-20 | 22:00 | 37 | 3174.6 | 8.11 | 22 | 2.05 | 0.0256 | 1.2488 | 4.83 | 0.759 | 4.071 | 27.3 | 8.02 | 120 | 215 | 35.714 | 32.01 | 21.7 | 3.866 | 93.29 | BMRL | 17.1608 | 4.4737 | 1.2589 | 4.8771 | 10.7317 | NA | NA | NA | 27.7705 | 38.5022 | C7-20 | N | 1998-10-08 | 14:00 | 78 | 3346.2 | 7.97 | 22 | 1.9 | 0.0221 | 1.1632 | 4.26 | 0.767 | 3.493 | 27 | 8 | 120 | 130 | 24.924 | 24.5 | 24.332 | 9.296 | 83.052 | 2.1789 | 14.3794 | 3.1316 | BMRL | 7.508 | 9.4729 | NA | NA | NA | 27.1979 | 36.6708 | Labor Rate + Fringe ($/work-hour) | 27.2
|  |  |  | Bed volumes to 50% TOC breakthrough, BV50 | 3960.933 | 40 | 0.425 |  |  |  | Total hardness | mg/L as CaCO3 | 94.7 | 88.4 | 91.55 | 6.8815 |  | Total hardness | mg/L as CaCO3 | 94.1 | 78.1 | 86.1 | 18.583 |  | AVG-C8-10 | Y | 1998-10-21 | 7:00 | 46 | 3946.8 | 8.05 | 22.5 | 2.23 | 0.029 | 1.3004 | 5.34 | 0.88 | 4.46 | 27.3 | 8.01 | 120 | 197.5 | 42.79 | 33.46 | 21.1 | 3.33 | 100.68 | 2.13 | 18.77 | 5.34 | 1.19 | 4.36 | 10.77 | NA | NA | NA | 31.79 | 42.56 | AVG-C8-20 | Y | 1998-10-09 | 6:00 | 94 | 4032.6 | 8.04 | 23 | 2.2 | 0.023 | 1.0455 | 4.71 | 0.86 | 3.85 | 27 | 8.02 | 120 | 130 | 33.24 | 27.71 | 23.06 | 6.93 | 90.94 | 3.34 | 16.91 | 4.1 | 1.02 | 6.98 | 9.87 | NA | NA | NA | 32.35 | 42.22 | Labor Overhead Factor (% of labor) | 33
Technical ICR Contact Person |  |  |  | Estimated run length, BVT ( = 2 x BV50) | 7921.8659 | 50 | 0.3 |  |  |  | Calcium hardness | mg/L as CaCO3 | 76.9 | 71.9 | 74.4 | 6.7204 |  | Calcium hardness | mg/L as CaCO3 | 74.4 | 62.4 | 68.4 | 17.5439 |  | C9-10 | N | 1998-10-21 | 13:00 | 52 | 4461.6 | 8.12 | 23 | 2.4 | 0.03 | 1.25 | 5.58 | 0.909 | 4.671 | 27.3 | 8.01 | 120 | 200 | 45.817 | 33.04 | 19.773 | 3.024 | 101.654 | 2.7676 | 22.1108 | 6.5133 | 1.2834 | 4.7446 | 12.2146 | NA | NA | NA | 37.4197 | 49.6343 | C9-20 | N | 1998-10-09 | 23:00 | 111 | 4761.9 | 7.8 | 21 | 2.3 | 0.026 | 1.1304 | 4.92 | 0.865 | 4.055 | 27 | 7.99 | 120 | 180 | 38.102 | 30.459 | 23.103 | 5.863 | 97.527 | 4.5365 | 17.6954 | 4.7668 | 1.0892 | 6.3918 | 10.1749 | NA | NA | NA | 34.4797 | 44.6546 | Electric Rate ($/kW-h) | 0.06
Mailing Address |  |  |  | BVT + 30% safety factor, BVT+30% ( = 2.6 x BV50) | 10298.4257 | 60 | 0.25 |  |  |  | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! |  | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! |  | C10-10 | N | 1998-10-21 | 17:00 | 56 | 4804.8 | 8 | 21 | 2.45 | 0.0334 | 1.3633 | 5.71 | 0.893 | 4.817 | 27.3 | 8.02 | 120 | 200 | 49.969 | 34.133 | 20.517 | 3.072 | 107.691 | 2.4012 | 22.7642 | 7.5123 | 1.1243 | 4.6352 | 12.4195 | NA | NA | NA | 38.4372 | 50.8567 | C10-20 | N | 1998-10-10 | 19:00 | 131 | 5619.9 | 8.06 | 21 | 2.5 | 0.0305 | 1.22 | 5.2 | 0.873 | 4.327 | 27 | 8.04 | 120 | 180 | 46.462 | 31.985 | 22.541 | 5.125 | 106.113 | 4.1431 | 19.9717 | 5.352 | 1.1752 | 5.8484 | 10.2433 | NA | NA | NA | 36.4904 | 46.7337 | Fuel Oil Rate ($/gal) | na
[6 empty] | 70 | 0.21 |  |  |  | Bromide | mg/L | 100.4 | 99.9 | 100.15 | 0.49925 |  | Bromide | mg/L | 102 | 102.1 | 102.05 | 0.097991 |  | AVG-C11-10 | Y | 1998-10-22 | 10:00 | 73 | 6263.4 | 8.08 | 23.5 | 2.5 | 0.038 | 1.52 | 6.02 | 0.91 | 5.11 | 27.3 | 8.01 | 120 | 202.5 | 61.84 | 35.6 | 20.03 | 2.85 | 120.32 | 5.43 | 32.14 | 10.3 | 2.01 | 5.36 | 13.77 | NA | NA | NA | 55.24 | 69.01 | AVG-C11-20 | Y | 1998-10-11 | 16:00 | 152 | 6520.8 | 8.13 | 21 | 2.63 | 0.035 | 1.3308 | 5.48 | 1.07 | 4.41 | 27 | 8.02 | 120 | 230 | 59.67 | 34.16 | 22.2 | 4.62 | 120.65 | 6.03 | 26.45 | 7.89 | 1.19 | 7.21 | 13.77 | NA | NA | NA | 48.77 | 62.54 | Natural Gas Rate ($/ft3) | 0.0053
Phone Number |  |  |  | General RSSCT Design Parameters |  | 80 | 0.18 | [17 empty] | C12-10 | N | 1998-10-23 | 16:00 | 103 | 8837.4 | 8.16 | 24 | 2.8 | 0.0475 | 1.6964 | 6.18 | 1.031 | 5.149 | 27 | 8.01 | 120 | 245 | 66.933 | 35.268 | 19.44 | 2.872 | 124.513 | 5.3269 | 34.6732 | 11.3002 | 2.1371 | 5.9137 | 15.9286 | NA | NA | NA | 59.3511 | 75.2797 | C12-20 | N | 1998-10-13 | 22:00 | 206 | 8837.4 | 8.3 | 21 | 2.85 | 0.0339 | 1.1895 | 5.52 | 0.837 | 4.683 | 27.1 | 8.02 | 120 | 205 | 58.864 | 35.065 | 20.907 | 3.27 | 118.106 | 4.1969 | 41.2498 | 15.4149 | 1.609 | 8.2367 | 20.7227 | NA | NA | NA | 70.7073 | 91.43 | Current Process Water Rate ($/1000 gal) | 0.41
FAX Number |  |  |  | Kinematic viscosity at ToC, nLC (m2/s) | 9.1473e-07 | 100 | 0.15 |  |  |  | Group B, 3 samples per batch | [6 empty] | Group B, 3 samples per batch | [10 empty] | -866097 | -74311122.6 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -865760 | -37141104 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 | Modifications to Existing Plant (% of construction costs) | NA
E-Mail Address (optional) |  |  |  | RSSCT carbon particle diameter, dSC (mm) | 0.1125 | 120 | 0.125 |  |  |  | Parameter | Units | Sample B1-10 | Sample B2-10 | Sample B3-10 | Average | %SD | Parameter | Units | Sample B1-20 | Sample B2-20 | Sample B3-20 | Average | %SD |  |  |  |  | -866097 | -74311122.6 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -865760 | -37141104 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
|  |  |  | Scaling factor, SF | 14.3 | 140 | 0.106 | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | Sampling date | MM/DD/YY | 1998-10-19 | 1998-10-21 | 1998-10-22 | --- | --- | Sampling date | MM/DD/YY | 1998-10-05 | 1998-10-08 | 1998-10-12 | --- | --- |  |  |  |  | -866097 | -74311122.6 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -865760 | -37141104 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
Plant Name | Tarrant County Water Supply Project |  |  | RSSCT hydraulic loading rate, vSC (m/hr) | 7.3895 | 170 | 0.088 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | Sampling time | hh:mm | 10:00 | 6:00 | 14:00 | --- | --- | Sampling time | hh:mm | 8:30 | 8:30 | 8:00 | --- | --- |  |  |  |  | -866097 | -74311122.6 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -865760 | -37141104 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
Treatment Plant Category | CONV |  |  | RSSCT flow rate, QSC (mL/min) | 11.7042 | 200 | 0.075 | is to list the pretreatment processes used in this particular RSSCT run. |  |  | Operation time | hh.hh | 1 | 45 | 77 | --- | --- | Operation time | hh.hh | 0.5 | 72.5 | 168 | --- | --- |  |  |  |  | -866097 | -74311122.6 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -865760 | -37141104 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
Process Train Name | Convential Filtration |  |  | Estimated total influent volume required, VSCT (L) | 189.9903 | 230 | 0.062 |  |  |  | Bed volumes | (10 minute) | 85.8 | 3861 | 6606.6 | --- | --- | Bed volumes | (20 minute) | 21.45 | 3110.25 | 7207.2 | --- | --- | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
ICR Treatment Plant Identification Number | 650 |  |  |  |  | 270 | 0.053 |  |  |  | pH | --- | 8.03 | 8.12 | 8.06 | 8.07 | 0.56785 | pH | --- | 8.18 | 8.11 | 8.16 | 8.15 | 0.4424 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
PWSID Number of Plant (if assigned) | TX2200199 |  |  | 10-Minute EBCT Run |  | 325 | 0.044 |  |  |  | Turbidity | ntu | 0.38 | 0.26 | 0.22 | 0.28667 | 29.0465 | Turbidity | ntu | 0.2 | 0.22 | 0.35 | 0.25667 | 31.7319 | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below. | [33 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below.
Historical Minimum Water Temperature (oC) | 12 |  |  | Full-scale empty bed contact time, EBCTLC (min) | 10 | 400 | 0.037 |  |  |  | Temperature | oC | 21 | 21 | 21 | 21 | 0 | Temperature | oC | 19 | 21 | 21 | 20.3333 | 5.6789
Historical Average Water Temperature (oC) | 22.7 |  |  | Estimated full-scale run time, tLCT (days) | 51.2 | [5 empty] | Total organic carbon | mg/L | 3.8 | 3.7 | 3.5 | 3.6667 | 4.166 | Total organic carbon | mg/L | 3.8 | 3.8 | 3.7 | 3.7667 | 1.5328 | Group D, 3 duplicate effluent samples per run (results from primary and duplicate analyses) | [33 empty] | Group D, 3 duplicate effluent samples per run (results from primary and duplicate analyses)
State Approved Plant Capacity (MGD) | 57 |  |  | RSSCT empty bed contact time, EBCTSC (min) | 0.6993 | [5 empty] | UV254 | cm-1 | 0.0644 | 0.0599 | NR | 0.06215 | 5.1198 | UV254 | cm-1 | 0.0544 | 0.0564 | 0.0648 | 0.058533 | 9.4279 | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS
|  |  |  | Estimated RSSCT run time, tSCT (days) | 3.5804 | [5 empty] | SUVA | L/(mg*m) | 1.6947 | 1.6189 | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | 1.4316 | 1.4842 | 1.7514 | 1.5557 | 11.0212 | ID | Type | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6
|  |  |  | RSSCT bed length, lSC (cm) | 8.6125 | [5 empty] | SDS-Cl2 dose | mg/L | 7.62 | 7.62 | 7.62 | 7.62 | 0 | SDS-Cl2 dose | mg/L | 6.84 | 6.84 | 7.78 | 7.1533 | 7.5868 |  |  | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L
|  |  |  | Estimated volume required for 10-minute EBCT, VSC (L) | 60.3443 | [5 empty] | SDS-Free Cl2 residual | mg/L | 0.649 | 0.715 | 0.617 | 0.66033 | 7.5679 | SDS-Free Cl2 residual | mg/L | 0.602 | 0.403 | 0.984 | 0.663 | 44.5346 | C4-10 | Primary | 1998-10-20 | 6:00 | 21 | 1801.8 | 8.05 | 23 | 0.9 | 0.0089 | 0.98889 | 3.2 | 0.637 | 2.563 | 27.4 | 8.03 | 120 | 57.5 | 5.85 | 14.98 | 21.667 | 10.136 | 52.633 | BMRL | 5.1795 | 1.1538 | BMRL | 5.2036 | 5.7294 | NA | NA | NA | 11.5369 | 17.2663 | C4-20 | Primary | 1998-10-07 | 1:00 | 41 | 1758.9 | 8.07 | 23 | BMRL | 0.0059 | #VALUE! | 2 | 0.209 | 1.791 | 27 | 8 | 120 | 29.5 | BMRL | 2.613 | 8.655 | 10.739 | 22.007 | BMRL | 2.329 | BMRL | BMRL | 4.3725 | 2.335 | NA | NA | NA | 6.7015 | 9.0365
|  |  |  | Mass GAC required, mSC (g) | 4.0924 | [5 empty] | SDS-Cl2 demand | mg/L | 6.971 | 6.905 | 7.003 | 6.9597 | 0.71804 | SDS-Cl2 demand | mg/L | 6.238 | 6.437 | 6.796 | 6.4903 | 4.3572 | D1-10 | Duplicate | 1998-10-20 | 6:00 | 21 | 1801.8 | 8.03 | 23 | 0.9 | 0.0094 | 1.0444 | 3.2 | 0.657 | 2.543 | 27.4 | 8.02 | 120 | 63.5 | 6.144 | 15.688 | 21.9 | 10.128 | 53.86 | BMRL | 5.3693 | 1.1237 | BMRL | 5.2701 | 5.7315 | NA | NA | NA | 11.7631 | 17.4946 | D1-20 | Duplicate | 1998-10-07 | 1:00 | 41 | 1758.9 | 8.1 | 23 | BMRL | 0.006 | #VALUE! | 2 | 0.194 | 1.806 | 27 | 8.01 | 120 | BMRL | BMRL | 2.471 | 8.366 | 10.826 | 21.663 | BMRL | 1.938 | BMRL | BMRL | 3.3467 | 1.7144 | NA | NA | NA | 5.2847 | 6.9991
[11 empty] | SDS-Chlorination temp. | oC | 27.4 | 27.4 | 27.3 | 27.3667 | 0.21097 | SDS-Chlorination temp. | oC | 27.1 | 27.1 | 27 | 27.0667 | 0.21331 | AVG-C4-10 | Average | --- | --- | --- | --- | 8.04 | 23 | 0.9 | 0.00915 | 1.0167 | 3.2 | 0.647 | 2.553 | 27.4 | 8.025 | 120 | 60.5 | 5.997 | 15.334 | 21.7835 | 10.132 | 53.2465 | #DIV/0! | 5.2744 | 1.1387 | #DIV/0! | 5.2368 | 5.7305 | #DIV/0! | #DIV/0! | #DIV/0! | 11.65 | 17.3804 | AVG-C4-20 | Average | --- | --- | --- | --- | 8.085 | 23 | #DIV/0! | 0.00595 | #VALUE! | 2 | 0.2015 | 1.7985 | 27 | 8.005 | 120 | 29.5 | #DIV/0! | 2.542 | 8.5105 | 10.7825 | 21.835 | #DIV/0! | 2.1335 | #DIV/0! | #DIV/0! | 3.8596 | 2.0247 | #DIV/0! | #DIV/0! | #DIV/0! | 5.9931 | 8.0178
|  |  |  | 20-Minute EBCT Run | [6 empty] | SDS-Chlorination pH | --- | 8.02 | 8.02 | 8.01 | 8.0167 | 0.072019 | SDS-Chlorination pH | --- | 8.01 | 8.02 | 8.04 | 8.0233 | 0.19039 | RPD-C4-10 | RPD | --- | --- | --- | --- | 0.24876 | 0 | 0 | 5.4645 | 5.4645 | 0 | 3.0912 | 0.78339 | 0 | 0.12461 | 0 | 9.9174 | 4.9025 | 4.6172 | 1.0696 | 0.078958 | 2.3044 | #VALUE! | 3.5985 | 2.6432 | #VALUE! | 1.2698 | 0.036646 | #VALUE! | #VALUE! | #VALUE! | 1.9416 | 1.3135 | RPD-C4-20 | RPD | --- | --- | --- | --- | 0.37106 | 0 | #VALUE! | 1.6807 | #VALUE! | 0 | 7.4442 | 0.83403 | 0 | 0.12492 | 0 | #VALUE! | #VALUE! | 5.5862 | 3.3958 | 0.80686 | 1.5755 | #VALUE! | 18.3267 | #VALUE! | #VALUE! | 26.5779 | 30.6515 | #VALUE! | #VALUE! | #VALUE! | 23.6405 | 25.411
|  |  |  | Full-scale empty bed contact time, EBCTLC (min) | 20 | [5 empty] | SDS-Incubation time | hours | 120 | 120 | 120 | 120 | 0 | SDS-Incubation time | hours | 120 | 120 | 120 | 120 | 0 | C8-10 | Primary | 1998-10-21 | 7:00 | 46 | 3946.8 | 8.05 | 23 | 2.2 | 0.029 | 1.3182 | 5.34 | 0.889 | 4.451 | 27.3 | 8.01 | 120 | 200 | 42.437 | 33.454 | 21.265 | 3.367 | 100.523 | BMRL | 18.1361 | 5.3262 | 1.1024 | 4.3917 | 10.6277 | NA | NA | NA | 28.9564 | 39.5841 | C8-20 | Primary | 1998-10-09 | 6:00 | 94 | 4032.6 | 8.01 | 23 | 2.2 | 0.0225 | 1.0227 | 4.71 | 0.747 | 3.963 | 27 | 8.02 | 120 | 110 | 32.27 | 26.176 | 23.102 | 7.292 | 88.84 | 3.4331 | 16.4199 | 3.7531 | 1.0228 | 6.983 | 9.7339 | NA | NA | NA | 31.6119 | 41.3458
|  |  |  | Estimated full-scale run time, tLCT (days) | 110 | [5 empty] | SDS-TOX | mg Cl- /L | 365 | 370 | 350 | 361.6667 | 2.8779 | SDS-TOX | mg Cl- /L | 330 | 415 | 365 | 370 | 11.546 | D2-10 | Duplicate | 1998-10-21 | 7:00 | 46 | 3946.8 | 8.05 | 22 | 2.25 | 0.0283 | 1.2578 | 5.34 | 0.869 | 4.471 | 27.3 | 8.01 | 120 | 195 | 43.149 | 33.463 | 20.94 | 3.284 | 100.836 | 2.1289 | 19.3947 | 5.3481 | 1.274 | 4.3353 | 10.9126 | NA | NA | NA | 32.481 | 43.3936 | D2-20 | Duplicate | 1998-10-09 | 6:00 | 94 | 4032.6 | 8.06 | 23 | 2.2 | 0.0228 | 1.0364 | 4.71 | 0.976 | 3.734 | 27 | 8.02 | 120 | 150 | 34.202 | 29.242 | 23.02 | 6.571 | 93.035 | 3.2485 | 17.4057 | 4.4519 | BMRL | 6.9784 | 10.0129 | NA | NA | NA | 32.0845 | 42.0974
|  |  |  | RSSCT empty bed contact time, EBCTSC (min) | 1.3986 | [5 empty] | SDS-CHCl3 | mg/L | 108.019 | 113.569 | 110.61 | 110.7327 | 2.5079 | SDS-CHCl3 | mg/L | 76.609 | 85.906 | 118.868 | 93.7943 | 23.6757 | AVG-C8-10 | Average | --- | --- | --- | --- | 8.05 | 22.5 | 2.225 | 0.02865 | 1.288 | 5.34 | 0.879 | 4.461 | 27.3 | 8.01 | 120 | 197.5 | 42.793 | 33.4585 | 21.1025 | 3.3255 | 100.6795 | 2.1289 | 18.7654 | 5.3372 | 1.1882 | 4.3635 | 10.7701 | #DIV/0! | #DIV/0! | #DIV/0! | 30.7187 | 41.4888 | AVG-C8-20 | Average | --- | --- | --- | --- | 8.035 | 23 | 2.2 | 0.02265 | 1.0295 | 4.71 | 0.8615 | 3.8485 | 27 | 8.02 | 120 | 130 | 33.236 | 27.709 | 23.061 | 6.9315 | 90.9375 | 3.3408 | 16.9128 | 4.1025 | 1.0228 | 6.9807 | 9.8734 | #DIV/0! | #DIV/0! | #DIV/0! | 31.8482 | 41.7216
|  |  |  | Estimated RSSCT run time, tSCT (days) | 7.6923 | [5 empty] | SDS-BDCM | mg/L | 39.48 | 39.999 | 39.022 | 39.5003 | 1.2375 | SDS-BDCM | mg/L | 30.968 | 33.3 | 41.488 | 35.252 | 15.6728 | RPD-C8-10 | RPD | --- | --- | --- | --- | 0 | 4.4444 | 2.2472 | 2.4433 | 4.6898 | 0 | 2.2753 | 0.44833 | 0 | 0 | 0 | 2.5316 | 1.6638 | 0.026899 | 1.5401 | 2.4959 | 0.31089 | #VALUE! | 6.707 | 0.41033 | 14.442 | 1.2925 | 2.6453 | #VALUE! | #VALUE! | #VALUE! | 11.4738 | 9.182 | RPD-C8-20 | RPD | --- | --- | --- | --- | 0.62228 | 0 | 0 | 1.3245 | 1.3245 | 0 | 26.5815 | 5.9504 | 0 | 0 | 0 | 30.7692 | 5.813 | 11.065 | 0.35558 | 10.4018 | 4.6131 | 5.5256 | 5.8287 | 17.0335 | #VALUE! | 0.065896 | 2.8258 | #VALUE! | #VALUE! | #VALUE! | 1.4839 | 1.8015
|  |  |  | RSSCT bed length, lSC (cm) | 17.225 | [5 empty] | SDS-DBCM | mg/L | 16.836 | 16.936 | 16.431 | 16.7343 | 1.598 | SDS-DBCM | mg/L | 13.682 | 14.38 | 17.91 | 15.324 | 14.791 | C11-10 | Primary | 1998-10-22 | 10:00 | 73 | 6263.4 | 8.09 | 23 | 2.5 | 0.0382 | 1.528 | 6.02 | 0.889 | 5.131 | 27.3 | 8 | 120 | 220 | 61.093 | 36.19 | 19.971 | 2.909 | 120.163 | 6.044 | 33.4207 | 10.7676 | 2.0487 | 5.5902 | 13.8103 | NA | NA | NA | 57.8712 | 71.6815 | C11-20 | Primary | 1998-10-11 | 16:00 | 152 | 6520.8 | 8.16 | 21 | 2.65 | 0.0345 | 1.3019 | 5.48 | 1.031 | 4.449 | 27 | 8 | 120 | 230 | 59.517 | 34.134 | 22.069 | 4.547 | 120.267 | BMRL | 26.0757 | 8.0375 | 1.2301 | 6.8103 | 13.5098 | NA | NA | NA | 42.1536 | 55.6634
|  |  |  | Estimated volume required for 20-minute EBCT, VSC (L) | 129.646 | [5 empty] | SDS-CHBr3 | mg/L | 1.929 | 1.977 | 1.661 | 1.8557 | 9.1765 | SDS-CHBr3 | mg/L | 1.567 | 1.645 | 2.403 | 1.8717 | 24.6731 | D3-10 | Duplicate | 1998-10-22 | 10:00 | 73 | 6263.4 | 8.07 | 24 | 2.5 | 0.0387 | 1.548 | 6.02 | 0.928 | 5.092 | 27.3 | 8.02 | 120 | 185 | 62.593 | 35.008 | 20.08 | 2.792 | 120.473 | 4.8149 | 30.8654 | 9.8292 | 1.9759 | 5.1282 | 13.7317 | NA | NA | NA | 52.6136 | 66.3453 | D3-20 | Duplicate | 1998-10-11 | 16:00 | 152 | 6520.8 | 8.1 | 21 | 2.6 | 0.0361 | 1.3885 | 5.48 | 1.103 | 4.377 | 27 | 8.04 | 120 | NR | 59.823 | 34.185 | 22.336 | 4.702 | 121.046 | 6.0279 | 26.8196 | 7.7485 | 1.1413 | 7.6014 | 14.0362 | NA | NA | NA | 49.3387 | 63.3749
|  |  |  | Mass GAC required, mSC (g) | 8.1847 | [5 empty] | SDS-THM4 | mg/L | 166.264 | 172.481 | 167.724 | 168.823 | 1.9257 | SDS-THM4 | mg/L | 122.826 | 135.231 | 180.669 | 146.242 | 20.8237 | AVG-C11-10 | Average | --- | --- | --- | --- | 8.08 | 23.5 | 2.5 | 0.03845 | 1.538 | 6.02 | 0.9085 | 5.1115 | 27.3 | 8.01 | 120 | 202.5 | 61.843 | 35.599 | 20.0255 | 2.8505 | 120.318 | 5.4295 | 32.1431 | 10.2984 | 2.0123 | 5.3592 | 13.771 | #DIV/0! | #DIV/0! | #DIV/0! | 55.2424 | 69.0134 | AVG-C11-20 | Average | --- | --- | --- | --- | 8.13 | 21 | 2.625 | 0.0353 | 1.3452 | 5.48 | 1.067 | 4.413 | 27 | 8.02 | 120 | 230 | 59.67 | 34.1595 | 22.2025 | 4.6245 | 120.6565 | 6.0279 | 26.4476 | 7.893 | 1.1857 | 7.2058 | 13.773 | #DIV/0! | #DIV/0! | #DIV/0! | 45.7462 | 59.5192
[11 empty] | SDS-MCAA* | mg/L | 7.2154 | 7.5965 | 8.5089 | 7.7736 | 8.5506 | SDS-MCAA* | mg/L | 2.3181 | 7.8778 | 8.9263 | 6.3741 | 55.7176 | RPD-C11-10 | RPD | --- | --- | --- | --- | 0.24752 | 4.2553 | 0 | 1.3004 | 1.3004 | 0 | 4.2928 | 0.76299 | 0 | 0.24969 | 0 | 17.284 | 2.4255 | 3.3203 | 0.54431 | 4.1045 | 0.25765 | 22.6377 | 7.9498 | 9.1121 | 3.6178 | 8.6207 | 0.57076 | #VALUE! | #VALUE! | #VALUE! | 9.5173 | 7.7321 | RPD-C11-20 | RPD | --- | --- | --- | --- | 0.73801 | 0 | 1.9048 | 4.5326 | 6.436 | 0 | 6.7479 | 1.6315 | 0 | 0.49875 | 0 | #VALUE! | 0.51282 | 0.1493 | 1.2026 | 3.3517 | 0.64563 | #VALUE! | 2.8127 | 3.6615 | 7.4892 | 10.9786 | 3.822 | #VALUE! | #VALUE! | #VALUE! | 15.7065 | 12.9563
[11 empty] | SDS-DCAA* | mg/L | 43.7995 | 45.3908 | 49.7579 | 46.3161 | 6.6609 | SDS-DCAA* | mg/L | 39.1064 | 37.6477 | 40.7318 | 39.162 | 3.9395 | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[11 empty] | SDS-TCAA* | mg/L | 15.5972 | 15.9618 | 20.7056 | 17.4215 | 16.3586 | SDS-TCAA* | mg/L | 14.1631 | 14.2353 | 15.4866 | 14.6283 | 5.0871 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
[11 empty] | SDS-MBAA* | mg/L | 1.6781 | 1.5205 | 2.1321 | 1.7769 | 17.8707 | SDS-MBAA* | mg/L | BMRL | 1.7665 | 1.2615 | 1.514 | 23.5858
[11 empty] | SDS-DBAA* | mg/L | 3.4929 | 3.4457 | 4.5182 | 3.8189 | 15.8694 | SDS-DBAA* | mg/L | 4.6612 | 4.5525 | 4.4164 | 4.5434 | 2.6997
[11 empty] | SDS-BCAA* | mg/L | 15.4992 | 15.4209 | 18.1599 | 16.36 | 9.5309 | SDS-BCAA* | mg/L | 15.658 | 15.4388 | 15.4136 | 15.5035 | 0.86704
[11 empty] | SDS-TBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0!
[11 empty] | SDS-CDBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0!
[11 empty] | SDS-DCBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0!
[11 empty] | SDS-HAA5 | mg/L | 71.7831 | 73.9153 | 85.6227 | 77.107 | 9.6638 | SDS-HAA5 | mg/L | 60.2488 | 66.0798 | 70.8226 | 65.7171 | 8.0591
[11 empty] | SDS-HAA6 | mg/L | 87.2823 | 89.3362 | 103.7826 | 93.467 | 9.6209 | SDS-HAA6 | mg/L | 75.9068 | 81.5186 | 86.2362 | 81.2205 | 6.3668
[11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [6 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [6 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
Note on H7: Reviewer M.H. (12/13/99): Reviewer adjusted Reynolds number based on new full-scale temperatures.
Note on H8: Reviewer D.S. (10/13/99): Full-scale temperature is 24.8C, RSSCT designed for 20C.
Note on AP5: Reviewer D.S. (10/21/99): Per Consultant: "In the DCSS, we reported UV254 down to 0.001 cm-1. Our lowest standard was 0.009 cm-1 for the study (The ICR low-level standard). This should be noted in the DCSS as reported between the MDL and MRL for the method."
Note on BY5: Reviewer D.S. (10/21/99): Per Consultant: "In the DCSS, we reported UV254 down to 0.001 cm-1. Our lowest standard was 0.009 cm-1 for the study (The ICR low-level standard). This should be noted in the DCSS as reported between the MDL and MRL for the method."
Note on CG16: Reviewer D.S. (10/8/99): Per Consultant: "Only one replicate reported"
Note on CG37: Reviewer D.S. (10/8/99): Per Consultant: "Only one replicate reported"

## Sheet4. 4th Quarter
FIELD-SET 4: 4th QUARTER RSSCT RESULTS (FILE: gacrssct.xls)
Field 4-1: PWS And Treatment Plant Data |  | Field 4-2: Full-Scale GAC Characteristics1 |  | Field 4-3: RSSCT Design Parameters |  |  |  | Field 4-4: Pretreatment Used Prior To GAC1 |  |  | Field 4-5: GAC Influent Water Quality For The 10-Minute EBCT Run | [6 empty] | Field 4-6: GAC Influent Water Quality For The 20-Minute EBCT Run1 | [6 empty] | Field 4-7: GAC Effluent Water Quality For The 10-Minute EBCT Run1 | [15 empty] | Field 4-7: GAC Effluent Water Quality For The 10-Minute EBCT Run (continued) | [17 empty] | Field 4-8: GAC Effluent Water Quality For The 20-Minute EBCT Run1 | [14 empty] | Field 4-8: GAC Effluent Water Quality For The 20-Minute EBCT Run (continued) | [18 empty] | Field 4-9: GAC Cost Parameters
|  |  |  | Input Design Parameters |  | US Standard Mesh Sizes | [18 empty] | Group C, 12 effluent samples per run | [33 empty] | Group C, 12 effluent samples per run
PWS Name | Tarrant County Water Supply Project | Carbon manufacturer | General Carbon Corporation | RSSCT influent TOC (mg/L) | 3.3 | US standard | Opening | Process | Description | Scale | 10-min. EBCT Start Date | 1999-01-14 | [5 empty] | 20-min. EBCT Start Date | 1999-01-11 | [5 empty] | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Cost Parameter | Parameter value
Public Water System Identification Number | TX2200199 | Carbon trade name | GC 8X30 | Inner diameter of the RSSCT column, DSC (mm) | 11 | mesh size | (mm) | Coagulation | 29.5 mg/L alum, 7 mg/L lime, 0.44 mg/L polymer | Full Scale | 10-min. EBCT Start Time | 8:00 | [5 empty] | 20-min. EBCT Start Time | 7:00 | [5 empty] | ID | duplicated? | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | Capital Recovery Interest Rate (%) | 7
Water Industry Data Base Number (optional) | NA | Carbon type | Bituminous | Minimum RSSCT Reynolds number, ReSC, min | 0.432 | 4 | 4.75 | Flocculation | Vertical impeller-type | Full Scale | [15 empty] | Y/N | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | Capital Recovery Period (years) | 20
|  | Original GAC mesh size, upper (US standard mesh) | 8 | Full-scale operating temperature, ToC (oC) | 14.2 | 6 | 3.35 | Sedimentation | Approximately 13.9-hour settling time | Full Scale | Group A, 2 samples per batch | [6 empty] | Group A, 2 samples per batch | [6 empty] | C1-10 | N | 1999-01-14 | 11:00 | 3 | 257.4 | 8.41 | 26 | BMRL | 0.0039 | #VALUE! | 2 | 1.103 | 0.897 | 18.8 | 7.96 | 120 | NR | BMRL | 1.14 | 2.288 | 1.618 | 5.046 | BMRL | BMRL | BMRL | BMRL | 1.0961 | 1.0774 | NA | NA | NA | 1.0961 | 2.1735 | C1-20 | N | 1999-01-11 | 10:00 | 3 | 128.7 | 8.47 | 22 | BMRL | 0.002 | #VALUE! | 2 | 1.343 | 0.657 | 18.9 | 7.97 | 120 | 63 | BMRL | BMRL | 1.087 | BMRL | 1.087 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | Overhead & Profit Factor (% of construction costs) | 57.1
Official ICR Contact Person |  | Original GAC mesh size, lower (US standard mesh) | 30 | Full-scale bed porosity, eLC | 0.45 | 8 | 2.36 | Filtration | Sand, anthracite, garnet, Microfloc MS-186 | Full Scale | Parameter | Units | Sample A1-10 | Sample A2-10 | Average | RPD |  | Parameter | Units | Sample A1-20 | Sample A2-20 | Average | RPD |  | C2-10 | N | 1999-01-14 | 16:00 | 8 | 686.4 | 8.59 | 25 | BMRL | 0.0015 | #VALUE! | 2 | 1.139 | 0.861 | 18.8 | 7.96 | 120 | NR | BMRL | 1.457 | 2.856 | 1.891 | 6.204 | BMRL | BMRL | BMRL | BMRL | 1.2689 | 1.2604 | NA | NA | NA | 1.2689 | 2.5293 | C2-20 | N | 1999-01-11 | 20:00 | 13 | 557.7 | 8.19 | 23 | BMRL | 0.0022 | #VALUE! | 2 | 1.123 | 0.877 | 18.9 | 7.95 | 120 | 62 | BMRL | 1.091 | 2.068 | 1.47 | 4.629 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | Special Sitework Factor (% of construction costs) | NA
Mailing Address |  | Original carbon particle diameter, dLC (mm) | 1.6 | Measured RSSCT dry bed density, rSC (g/cm3) | 0.5 | 10 | 2 | Filtration | 1.0 um cartridge filter | Bench Scale | Sampling date | MM/DD/YY | 1999-01-14 | 1999-01-18 | --- | --- |  | Sampling date | MM/DD/YY | 1999-01-11 | 1999-01-19 | --- | --- |  | C3-10 | N | 1999-01-14 | 23:00 | 15 | 1287 | 8.31 | 24 | BMRL | 0.002 | #VALUE! | 2 | 1.015 | 0.985 | 18.8 | 7.95 | 120 | BMRL | BMRL | 2.487 | 5.052 | 3.258 | 10.797 | BMRL | 1.4861 | BMRL | BMRL | 2.1565 | 1.9743 | NA | NA | NA | 3.6426 | 5.6169 | C3-20 | N | 1999-01-12 | 11:00 | 28 | 1201.2 | 8.22 | 25 | BMRL | 0.0022 | #VALUE! | 2 | 1.223 | 0.777 | 18.9 | 7.96 | 120 | 63.5 | BMRL | 1.866 | 4.08 | 2.347 | 8.293 | BMRL | BMRL | BMRL | BMRL | 1.3897 | 1.2781 | NA | NA | NA | 1.3897 | 2.6678 | Construction Contingencies (% of construction costs) | 25
|  | 1: These are the characteristics before the carbon is ground for RSSCT experiments. |  | RSSCT GAC mesh size, upper (US standard mesh) | 100 | 12 | 1.68 | In-Line Filtration | 0.9 um exclusion size | Bench Scale | Sampling time | hh:mm | 8:00 | 10:30 | --- | --- |  | Sampling time | hh:mm | 8:00 | 7:33 | --- | --- |  | AVG-C4-10 | Y | 1999-01-15 | 9:00 | 25 | 2145 | 8.3 | 25 | 1.1 | 0.011 | 1 | 2.5 | 0.87 | 1.63 | 18.8 | 7.96 | 120 | 32.42 | 6.3 | 13.46 | 15.86 | 5.26 | 40.88 | BMRL | 5.66 | 2.06 | 1.25 | 5.48 | 6.21 | NA | NA | NA | 14.45 | 20.66 | AVG-C4-20 | Y | 1999-01-13 | 6:00 | 47 | 2016.3 | 8.08 | 25 | 0.8 | 0.009 | 1.125 | 2 | 0.7 | 1.3 | 18.9 | 7.97 | 120 | 71.25 | 2.59 | 8.31 | 13.9 | 6.57 | 31.37 | BMRL | 3.01 | BMRL | 1 | 3.86 | 3.76 | NA | NA | NA | 7.87 | 11.63 | Engineering Fee Factor (% of construction costs) | 15
Phone Number |  |  |  | RSSCT GAC mesh size, lower (US standard mesh) | 200 | 16 | 1.18 |  |  |  | Operation time | hh.hh | 0 | 98.5 | --- | --- |  | Operation time | hh.hh | 1 | 192.55 | --- | --- |  | C5-10 | N | 1999-01-15 | 15:00 | 31 | 2659.8 | 7.84 | 25 | 1.5 | 0.017 | 1.1333 | 3.03 | 0.952 | 2.078 | 18.8 | 7.95 | 120 | 58.5 | 12.777 | 18.528 | 16.624 | 4.275 | 52.204 | BMRL | 7.2898 | 2.7352 | 1.3147 | 4.6182 | 6.9803 | NA | NA | NA | 15.9579 | 22.9382 | C5-20 | N | 1999-01-13 | 19:00 | 60 | 2574 | 8.35 | 23 | 1.2 | 0.0127 | 1.0583 | 2.64 | 1.075 | 1.565 | 18.9 | 7.97 | 120 | 78 | 7.192 | 14.491 | 16.095 | 4.729 | 42.507 | BMRL | 5.0355 | 1.8105 | 1.1832 | 4.0249 | 5.65 | NA | NA | NA | 12.0541 | 17.7041 | 1998 ENR Construction Cost Index (CCI base year 1913) | 6095.24
FAX Number | [5 empty] | 20 | 0.85 |  |  |  | Bed volumes | (10 minutes) | 0 | 8451.3 | --- | --- |  | Bed volumes | (20 minutes) | 42.9 | 8260.395 | --- | --- |  | C6-10 | N | 1999-01-15 | 21:00 | 37 | 3174.6 | 7.85 | 25 | 1.95 | 0.021 | 1.0769 | 3.39 | 0.996 | 2.394 | 18.8 | 7.96 | 120 | NR | 18.99 | 20.91 | 16.09 | 3.336 | 59.326 | BMRL | 10.8418 | 4.7206 | 1.3836 | 4.7101 | 8.3413 | NA | NA | NA | 21.6561 | 29.9974 | C6-20 | N | 1999-01-14 | 10:00 | 75 | 3217.5 | 8.34 | 24 | 1.3 | 0.0141 | 1.0846 | 2.79 | 1.079 | 1.711 | 18.8 | 7.95 | 120 | 51 | 10.187 | 17.038 | 15.794 | 4.331 | 47.35 | BMRL | 6.7543 | 2.506 | 1.397 | 5.3497 | 7.0656 | NA | NA | NA | 16.007 | 23.0726 | 1998 Producers Price Index (PPI base year 1967 = 100) | NA
E-Mail Address (optional) |  |  |  | Estimated Run Length |  | 30 | 0.6 |  |  |  | Alkalinity | mg/L as CaCO3 | 91.5 | 95 | 93.25 | 3.7534 |  | Alkalinity | mg/L as CaCO3 | 97.5 | 95 | 96.25 | 2.5974 |  | C7-10 | N | 1999-01-16 | 4:00 | 44 | 3775.2 | 7.88 | 26 | 1.95 | 0.025 | 1.2821 | 3.66 | 1.071 | 2.589 | 18.8 | 7.95 | 120 | 114 | 24.512 | 22.239 | 15.148 | 2.59 | 64.489 | BMRL | 12.445 | 5.9277 | 1.4144 | 4.4161 | 8.7862 | NA | NA | NA | 24.2032 | 32.9894 | C7-20 | N | 1999-01-15 | 1:00 | 90 | 3861 | 8.3 | 24 | 1.4 | 0.0143 | 1.0214 | 2.86 | 1.119 | 1.741 | 18.8 | 7.95 | 120 | 85.5 | 10.604 | 17.337 | 16.006 | 4.36 | 48.307 | BMRL | 7.5557 | 2.6772 | 1.2198 | 5.7555 | 7.6439 | NA | NA | NA | 17.2082 | 24.8521 | Labor Rate + Fringe ($/work-hour) | 27.2
|  |  |  | Bed volumes to 50% TOC breakthrough, BV50 | 4596.1227 | 40 | 0.425 |  |  |  | Total hardness | mg/L as CaCO3 | 106.1 | 113.1 | 109.6 | 6.3869 |  | Total hardness | mg/L as CaCO3 | 110.9 | 111.5 | 111.2 | 0.53957 |  | AVG-C8-10 | Y | 1999-01-16 | 13:00 | 53 | 4547.4 | 8.23 | 22 | 2.1 | 0.027 | 1.2857 | 3.85 | 1.18 | 2.67 | 18.8 | 7.95 | 120 | 162.5 | 29.98 | 23.51 | 14.61 | 2.43 | 70.53 | 2.01 | 14.35 | 8.01 | 1.49 | 4.3 | 9.27 | NA | NA | NA | 30.16 | 39.43 | AVG-C8-20 | Y | 1999-01-15 | 18:00 | 107 | 4590.3 | 7.84 | 25 | 1.7 | 0.017 | 1 | 3.25 | 1.13 | 2.12 | 18.8 | 7.96 | 120 | 94.25 | 15.27 | 18.63 | 15.31 | 3.49 | 52.7 | BMRL | 8.51 | 3.49 | 1.45 | 5.07 | 8.14 | NA | NA | NA | 18.52 | 26.66 | Labor Overhead Factor (% of labor) | 33
Technical ICR Contact Person |  |  |  | Estimated run length, BVT ( = 2 x BV50) | 9192.2454 | 50 | 0.3 |  |  |  | Calcium hardness | mg/L as CaCO3 | 92.4 | 98.1 | 95.25 | 5.9843 |  | Calcium hardness | mg/L as CaCO3 | 97.6 | 98.4 | 98 | 0.81633 |  | C9-10 | N | 1999-01-16 | 19:00 | 59 | 5062.2 | 8.28 | 22 | 2.2 | 0.028 | 1.2727 | 3.95 | 1.095 | 2.855 | 18.8 | 7.94 | 120 | 150 | 30.942 | 23.784 | 13.942 | 2.162 | 70.83 | BMRL | 15.3688 | 9.7454 | 1.5384 | 4.3789 | 9.9728 | NA | NA | NA | 31.0315 | 41.0043 | C9-20 | N | 1999-01-16 | 14:00 | 127 | 5448.3 | 8.23 | 23 | 1.9 | 0.0214 | 1.1263 | 3.62 | 1.243 | 2.377 | 18.8 | 7.95 | 120 | 110 | 20.55 | 20.129 | 15.037 | 2.89 | 58.606 | BMRL | 9.3037 | 4.5367 | 1.4162 | 4.0882 | 7.5356 | NA | NA | NA | 19.3448 | 26.8804 | Electric Rate ($/kW-h) | 0.06
Mailing Address |  |  |  | BVT + 30% safety factor, BVT+30% ( = 2.6 x BV50) | 11949.919 | 60 | 0.25 |  |  |  | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! |  | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! |  | C10-10 | N | 1999-01-17 | 2:00 | 66 | 5662.8 | 8.22 | 23 | 2.3 | 0.0297 | 1.2913 | 3.64 | 0.901 | 2.739 | 18.7 | 7.95 | 120 | 140 | 30.365 | 23.695 | 13.98 | 2.201 | 70.241 | BMRL | 18.277 | 8.4914 | BMRL | 4.018 | 10.2625 | NA | NA | NA | 30.7864 | 41.0489 | C10-20 | N | 1999-01-17 | 12:00 | 149 | 6392.1 | 8.2 | 21 | 2.2 | 0.028 | 1.2727 | 3.64 | 0.972 | 2.668 | 18.7 | 7.97 | 120 | 70 | 30.202 | 22.767 | 14.789 | 2.547 | 70.305 | BMRL | 14.4646 | 6.0518 | BMRL | 3.3977 | 7.816 | NA | NA | NA | 23.9141 | 31.7301 | Fuel Oil Rate ($/gal) | na
[6 empty] | 70 | 0.21 |  |  |  | Bromide | mg/L | 73 | 77 | 75 | 5.3333 |  | Bromide | mg/L | 72 | 57 | 64.5 | 23.2558 |  | AVG-C11-10 | Y | 1999-01-17 | 17:00 | 81 | 6949.8 | 8.19 | 21 | 2.43 | 0.034 | 1.3992 | 3.88 | 0.82 | 3.06 | 18.7 | 7.97 | 120 | 192.25 | 41.18 | 25.69 | 13.81 | 2.09 | 82.77 | 2.6 | 21.64 | 8.86 | 1.05 | 3.51 | 10.07 | NA | NA | NA | 37.66 | 47.73 | AVG-C11-20 | Y | 1999-01-18 | 12:00 | 173 | 7421.7 | 8.2 | 22 | 2.38 | 0.033 | 1.3866 | 3.88 | 1.03 | 2.85 | 18.7 | 7.97 | 120 | 147.5 | 35.85 | 25.07 | 14.14 | 2.32 | 77.38 | 2.75 | 21.19 | 9.82 | 1.21 | 3.84 | 10.53 | NA | NA | NA | 38.81 | 49.34 | Natural Gas Rate ($/ft3) | 0.0053
Phone Number |  |  |  | General RSSCT Design Parameters |  | 80 | 0.18 | [17 empty] | C12-10 | N | 1999-01-18 | 23:00 | 111 | 9523.8 | 8.22 | 22 | 2.6 | 0.0377 | 1.45 | 4 | 0.794 | 3.206 | 18.7 | 7.96 | 120 | 170 | 42.663 | 26.038 | 13.728 | 1.847 | 84.276 | 4.1397 | 26.9583 | 12.9228 | 1.1231 | 3.7249 | 12.0744 | NA | NA | NA | 48.8688 | 60.9432 | C12-20 | N | 1999-01-19 | 18:00 | 203 | 8708.7 | 8.19 | 22 | 2.6 | 0.0349 | 1.3423 | 4 | 1.039 | 2.961 | 18.7 | 7.97 | 120 | 185 | 40.16 | 25.497 | 14.362 | 1.88 | 81.899 | 2.6951 | 21.037 | 10.8733 | 1.0995 | 3.438 | 10.2424 | NA | NA | NA | 39.1429 | 49.3853 | Current Process Water Rate ($/1000 gal) | 0.41
FAX Number |  |  |  | Kinematic viscosity at ToC, nLC (m2/s) | 1.1863e-06 | 100 | 0.15 |  |  |  | Group B, 3 samples per batch | [6 empty] | Group B, 3 samples per batch | [10 empty] | -868184 | -74490187.2 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -868111 | -37241961.9 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 | Modifications to Existing Plant (% of construction costs) | NA
E-Mail Address (optional) |  |  |  | RSSCT carbon particle diameter, dSC (mm) | 0.1125 | 120 | 0.125 |  |  |  | Parameter | Units | Sample B1-10 | Sample B2-10 | Sample B3-10 | Average | %SD | Parameter | Units | Sample B1-20 | Sample B2-20 | Sample B3-20 | Average | %SD |  |  |  |  | -868184 | -74490187.2 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -868111 | -37241961.9 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
|  |  |  | Scaling factor, SF | 14.3 | 140 | 0.106 | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | Sampling date | MM/DD/YY | 1999-01-14 | 1999-01-16 | 1999-01-18 | --- | --- | Sampling date | MM/DD/YY | 1999-01-11 | 1999-01-14 | 1999-01-19 | --- | --- |  |  |  |  | -868184 | -74490187.2 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -868111 | -37241961.9 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
Plant Name | Tarrant County Water Supply Project |  |  | RSSCT hydraulic loading rate, vSC (m/hr) | 7.3799 | 170 | 0.088 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | Sampling time | hh:mm | 8:00 | 23:30 | 10:30 | --- | --- | Sampling time | hh:mm | 8:00 | 12:00 | 7:33 | --- | --- |  |  |  |  | -868184 | -74490187.2 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -868111 | -37241961.9 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
Treatment Plant Category | CONV |  |  | RSSCT flow rate, QSC (mL/min) | 11.689 | 200 | 0.075 | is to list the pretreatment processes used in this particular RSSCT run. |  |  | Operation time | hh.hh | 0 | 63.5 | 98.5 | --- | --- | Operation time | hh.hh | 1 | 77 | 192.55 | --- | --- |  |  |  |  | -868184 | -74490187.2 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -868111 | -37241961.9 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
Process Train Name | Conventional Filtration |  |  | Estimated total influent volume required, VSCT (L) | 293.0399 | 230 | 0.062 |  |  |  | Bed volumes | (10 minute) | 0 | 5448.3 | 8451.3 | --- | --- | Bed volumes | (20 minute) | 42.9 | 3303.3 | 8260.395 | --- | --- | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
ICR Treatment Plant Identification Number | 650 |  |  |  |  | 270 | 0.053 |  |  |  | pH | --- | 8.29 | 8.28 | 8.22 | 8.2633 | 0.45816 | pH | --- | 8.24 | 8.27 | 8.31 | 8.2733 | 0.42448 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
PWSID Number of Plant (if assigned) | TX2200199 |  |  | 10-Minute EBCT Run |  | 325 | 0.044 |  |  |  | Turbidity | ntu | 0.39 | 0.44 | 0.29 | 0.37333 | 20.4579 | Turbidity | ntu | 0.35 | 0.36 | 0.14 | 0.28333 | 43.8462 | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below. | [33 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below.
Historical Minimum Water Temperature (oC) | 12 |  |  | Full-scale empty bed contact time, EBCTLC (min) | 10 | 400 | 0.037 |  |  |  | Temperature | oC | 23 | 24 | 22 | 23 | 4.3478 | Temperature | oC | 20 | 24 | 20 | 21.3333 | 10.8253
Historical Average Water Temperature (oC) | 22.7 |  |  | Estimated full-scale run time, tLCT (days) | 82.9855 | [5 empty] | Total organic carbon | mg/L | 3.35 | 3.3 | 3.45 | 3.3667 | 2.2686 | Total organic carbon | mg/L | 3.5 | 3.4 | 3.3 | 3.4 | 2.9412 | Group D, 3 duplicate effluent samples per run (results from primary and duplicate analyses) | [33 empty] | Group D, 3 duplicate effluent samples per run (results from primary and duplicate analyses)
State Approved Plant Capacity (MGD) | 57 |  |  | RSSCT empty bed contact time, EBCTSC (min) | 0.6993 | [5 empty] | UV254 | cm-1 | 0.0616 | 0.063 | 0.062 | 0.0622 | 1.1593 | UV254 | cm-1 | 0.059 | 0.0619 | 0.059 | 0.059967 | 2.7921 | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS
|  |  |  | Estimated RSSCT run time, tSCT (days) | 5.8032 | [5 empty] | SUVA | L/(mg*m) | 1.8388 | 1.9091 | 1.7971 | 1.8483 | 3.0622 | SUVA | L/(mg*m) | 1.6857 | 1.8206 | 1.7879 | 1.7647 | 3.9867 | ID | Type | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6
|  |  |  | RSSCT bed length, lSC (cm) | 8.6013 | [5 empty] | SDS-Cl2 dose | mg/L | 5.7 | 6.28 | 5.62 | 5.8667 | 6.1395 | SDS-Cl2 dose | mg/L | 5.7 | 5.7 | 5.62 | 5.6733 | 0.81412 |  |  | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L
|  |  |  | Estimated volume required for 10-minute EBCT, VSC (L) | 97.68 | [5 empty] | SDS-Free Cl2 residual | mg/L | 1.319 | 1.115 | 0.936 | 1.1233 | 17.0596 | SDS-Free Cl2 residual | mg/L | 1.299 | 1.359 | 1.059 | 1.239 | 12.8124 | C4-10 | Primary | 1999-01-15 | 9:00 | 25 | 2145 | 8.29 | 25 | 1.1 | 0.0107 | 0.97273 | 2.5 | 0.865 | 1.635 | 18.8 | 7.94 | 120 | 31.77 | 6.322 | 13.412 | 15.997 | 5.085 | 40.816 | BMRL | 5.6971 | 1.9934 | 1.2466 | 5.3958 | 6.0459 | NA | NA | NA | 14.3329 | 20.3788 | C4-20 | Primary | 1999-01-13 | 6:00 | 47 | 2016.3 | 8.05 | 25 | 0.8 | 0.0088 | 1.1 | 2 | 0.712 | 1.288 | 18.9 | 7.97 | 120 | 56.5 | 2.512 | 8.126 | 13.742 | 6.496 | 30.876 | BMRL | 3.0028 | BMRL | BMRL | 3.8624 | 3.761 | NA | NA | NA | 6.8652 | 10.6262
|  |  |  | Mass GAC required, mSC (g) | 4.0871 | [5 empty] | SDS-Cl2 demand | mg/L | 4.381 | 5.165 | 4.684 | 4.7433 | 8.3349 | SDS-Cl2 demand | mg/L | 4.401 | 4.341 | 4.561 | 4.4343 | 2.5646 | D1-10 | Duplicate | 1999-01-15 | 9:00 | 25 | 2145 | 8.3 | 25 | 1.1 | 0.0107 | 0.97273 | 2.5 | 0.873 | 1.627 | 18.8 | 7.97 | 120 | 33.07 | 6.286 | 13.515 | 15.721 | 5.437 | 40.959 | BMRL | 5.6249 | 2.1315 | BMRL | 5.5605 | 6.3654 | NA | NA | NA | 13.3169 | 19.6823 | D1-20 | Duplicate | 1999-01-13 | 6:00 | 47 | 2016.3 | 8.11 | 25 | 0.8 | 0.0083 | 1.0375 | 2 | 0.684 | 1.316 | 18.9 | 7.96 | 120 | 86 | 2.664 | 8.502 | 14.067 | 6.637 | 31.87 | BMRL | 3.0121 | BMRL | 1.0001 | 3.8675 | 3.7633 | NA | NA | NA | 7.8797 | 11.643
[11 empty] | SDS-Chlorination temp. | oC | 18.9 | 18.7 | 18.7 | 18.7667 | 0.61529 | SDS-Chlorination temp. | oC | 18.9 | 18.8 | 18.7 | 18.8 | 0.53191 | AVG-C4-10 | Average | --- | --- | --- | --- | 8.295 | 25 | 1.1 | 0.0107 | 0.97273 | 2.5 | 0.869 | 1.631 | 18.8 | 7.955 | 120 | 32.42 | 6.304 | 13.4635 | 15.859 | 5.261 | 40.8875 | #DIV/0! | 5.661 | 2.0625 | 1.2466 | 5.4782 | 6.2057 | #DIV/0! | #DIV/0! | #DIV/0! | 13.8249 | 20.0306 | AVG-C4-20 | Average | --- | --- | --- | --- | 8.08 | 25 | 0.8 | 0.00855 | 1.0688 | 2 | 0.698 | 1.302 | 18.9 | 7.965 | 120 | 71.25 | 2.588 | 8.314 | 13.9045 | 6.5665 | 31.373 | #DIV/0! | 3.0074 | #DIV/0! | 1.0001 | 3.8649 | 3.7622 | #DIV/0! | #DIV/0! | #DIV/0! | 7.3724 | 11.1346
|  |  |  | 20-Minute EBCT Run | [6 empty] | SDS-Chlorination pH | --- | 7.96 | 7.96 | 7.98 | 7.9667 | 0.14494 | SDS-Chlorination pH | --- | 7.94 | 7.94 | 7.95 | 7.9433 | 0.072684 | RPD-C4-10 | RPD | --- | --- | --- | --- | 0.12055 | 0 | 0 | 0 | 0 | 0 | 0.9206 | 0.4905 | 0 | 0.37712 | 0 | 4.0099 | 0.57107 | 0.76503 | 1.7403 | 6.6907 | 0.34974 | #VALUE! | 1.2754 | 6.6959 | #VALUE! | 3.0065 | 5.1485 | #VALUE! | #VALUE! | #VALUE! | 7.3491 | 3.4772 | RPD-C4-20 | RPD | --- | --- | --- | --- | 0.74257 | 0 | 0 | 5.848 | 5.848 | 0 | 4.0115 | 2.1505 | 0 | 0.12555 | 0 | 41.4035 | 5.8733 | 4.5225 | 2.3374 | 2.1473 | 3.1683 | #VALUE! | 0.30923 | #VALUE! | #VALUE! | 0.13196 | 0.061135 | #VALUE! | #VALUE! | #VALUE! | 13.7607 | 9.1319
|  |  |  | Full-scale empty bed contact time, EBCTLC (min) | 20 | [5 empty] | SDS-Incubation time | hours | 120 | 120 | 120 | 120 | 0 | SDS-Incubation time | hours | 120 | 120 | 120 | 120 | 0 | C8-10 | Primary | 1999-01-16 | 13:00 | 53 | 4547.4 | 8.21 | 22 | 2.1 | 0.0268 | 1.2762 | 3.85 | 1.171 | 2.679 | 18.8 | 7.95 | 120 | 175 | 29.438 | 23.051 | 14.842 | 2.439 | 69.77 | 2.0054 | 13.7708 | 7.1389 | 1.4385 | 4.1009 | 8.8636 | NA | NA | NA | 28.4545 | 37.3181 | C8-20 | Primary | 1999-01-15 | 18:00 | 107 | 4590.3 | 7.85 | 25 | 1.7 | 0.018 | 1.0588 | 3.25 | 1.111 | 2.139 | 18.8 | 7.96 | 120 | 96.5 | 15.319 | 19.082 | 15.626 | 3.599 | 53.626 | BMRL | 7.9744 | 3.2644 | 1.3657 | 4.876 | 7.6239 | NA | NA | NA | 17.4805 | 25.1044
|  |  |  | Estimated full-scale run time, tLCT (days) | 165.9711 | [5 empty] | SDS-TOX | mg Cl- /L | 290 | 305 | 280 | 291.6667 | 4.3142 | SDS-TOX | mg Cl- /L | 285 | 285 | 230 | 266.6667 | 11.9078 | D2-10 | Duplicate | 1999-01-16 | 13:00 | 53 | 4547.4 | 8.24 | 22 | 2.1 | 0.0268 | 1.2762 | 3.85 | 1.187 | 2.663 | 18.8 | 7.94 | 120 | 150 | 30.524 | 23.974 | 14.372 | 2.424 | 71.294 | BMRL | 14.9347 | 8.8736 | 1.5441 | 4.4945 | 9.6841 | NA | NA | NA | 29.8469 | 39.531 | D2-20 | Duplicate | 1999-01-15 | 18:00 | 107 | 4590.3 | 7.83 | 25 | 1.7 | 0.016 | 0.94118 | 3.25 | 1.143 | 2.107 | 18.8 | 7.96 | 120 | 92 | 15.214 | 18.185 | 14.985 | 3.376 | 51.76 | BMRL | 9.0389 | 3.7209 | 1.5289 | 5.2689 | 8.6463 | NA | NA | NA | 19.5576 | 28.2039
|  |  |  | RSSCT empty bed contact time, EBCTSC (min) | 1.3986 | [5 empty] | SDS-CHCl3 | mg/L | 86.86 | 86.912 | 77.624 | 83.7987 | 6.3813 | SDS-CHCl3 | mg/L | 105.182 | 84.436 | 79.369 | 89.6623 | 15.254 | AVG-C8-10 | Average | --- | --- | --- | --- | 8.225 | 22 | 2.1 | 0.0268 | 1.2762 | 3.85 | 1.179 | 2.671 | 18.8 | 7.945 | 120 | 162.5 | 29.981 | 23.5125 | 14.607 | 2.4315 | 70.532 | 2.0054 | 14.3528 | 8.0062 | 1.4913 | 4.2977 | 9.2738 | #DIV/0! | #DIV/0! | #DIV/0! | 29.1507 | 38.4246 | AVG-C8-20 | Average | --- | --- | --- | --- | 7.84 | 25 | 1.7 | 0.017 | 1 | 3.25 | 1.127 | 2.123 | 18.8 | 7.96 | 120 | 94.25 | 15.2665 | 18.6335 | 15.3055 | 3.4875 | 52.693 | #DIV/0! | 8.5067 | 3.4926 | 1.4473 | 5.0724 | 8.1351 | #DIV/0! | #DIV/0! | #DIV/0! | 18.5191 | 26.6542
|  |  |  | Estimated RSSCT run time, tSCT (days) | 11.6064 | [5 empty] | SDS-BDCM | mg/L | 30.836 | 30.041 | 28.253 | 29.71 | 4.4528 | SDS-BDCM | mg/L | 36.483 | 30.704 | 30.091 | 32.426 | 10.8765 | RPD-C8-10 | RPD | --- | --- | --- | --- | 0.36474 | 0 | 0 | 0 | 0 | 0 | 1.3571 | 0.59903 | 0 | 0.12587 | 0 | 15.3846 | 3.6223 | 3.9256 | 3.2176 | 0.6169 | 2.1607 | #VALUE! | 8.1092 | 21.6668 | 7.0811 | 9.1584 | 8.8475 | #VALUE! | #VALUE! | #VALUE! | 4.7766 | 5.7591 | RPD-C8-20 | RPD | --- | --- | --- | --- | 0.2551 | 0 | 0 | 11.7647 | 11.7647 | 0 | 2.8394 | 1.5073 | 0 | 0 | 0 | 4.7745 | 0.68778 | 4.8139 | 4.188 | 6.3943 | 3.5413 | #VALUE! | 12.5137 | 13.0703 | 11.2762 | 7.7458 | 12.5678 | #VALUE! | #VALUE! | #VALUE! | 11.216 | 11.6286
|  |  |  | RSSCT bed length, lSC (cm) | 17.2026 | [5 empty] | SDS-DBCM | mg/L | 11.458 | 10.879 | 10.883 | 11.0733 | 3.0085 | SDS-DBCM | mg/L | 10.377 | 11.715 | 11.347 | 11.1463 | 6.2012 | C11-10 | Primary | 1999-01-17 | 17:00 | 81 | 6949.8 | 8.21 | 21 | 2.45 | 0.0337 | 1.3755 | 3.88 | 0.743 | 3.137 | 18.7 | 7.94 | 120 | 255 | 42.114 | 26.253 | 14.135 | 2.229 | 84.731 | 2.5986 | 22.0908 | 7.7221 | 1.0454 | 3.5188 | 10.0207 | NA | NA | NA | 36.9757 | 46.9964 | C11-20 | Primary | 1999-01-18 | 12:00 | 173 | 7421.7 | 8.2 | 23 | 2.35 | 0.0326 | 1.3872 | 3.88 | 0.964 | 2.916 | 18.7 | 7.97 | 120 | 145 | 36.927 | 25.274 | 14.382 | 2.305 | 78.888 | BMRL | 19.1327 | 9.874 | 1.0848 | 3.4879 | 9.523 | NA | NA | NA | 33.5794 | 43.1024
|  |  |  | Estimated volume required for 20-minute EBCT, VSC (L) | 195.36 | [5 empty] | SDS-CHBr3 | mg/L | 1.024 | BMRL | 1.004 | 1.014 | 1.3947 | SDS-CHBr3 | mg/L | BMRL | BMRL | BMRL | #DIV/0! | #DIV/0! | D3-10 | Duplicate | 1999-01-17 | 17:00 | 81 | 6949.8 | 8.16 | 21 | 2.4 | 0.0337 | 1.4042 | 3.88 | 0.893 | 2.987 | 18.7 | 7.99 | 120 | 129.5 | 40.254 | 25.136 | 13.477 | 1.944 | 80.811 | BMRL | 21.1817 | 9.9984 | BMRL | 3.5006 | 10.1104 | NA | NA | NA | 34.6807 | 44.7911 | D3-20 | Duplicate | 2000-01-18 | 12:00 | 8933 | 383225.7 | 8.19 | 21 | 2.4 | 0.0336 | 1.4 | 3.88 | 1.087 | 2.793 | 18.7 | 7.97 | 120 | 150 | 34.771 | 24.861 | 13.894 | 2.339 | 75.865 | 2.7519 | 23.2527 | 9.7634 | 1.3343 | 4.2005 | 11.5377 | NA | NA | NA | 41.3028 | 52.8405
|  |  |  | Mass GAC required, mSC (g) | 8.1741 | [5 empty] | SDS-THM4 | mg/L | 130.178 | 127.832 | 117.764 | 125.258 | 5.2652 | SDS-THM4 | mg/L | 152.042 | 126.855 | 120.807 | 133.2347 | 12.4337 | AVG-C11-10 | Average | --- | --- | --- | --- | 8.185 | 21 | 2.425 | 0.0337 | 1.3898 | 3.88 | 0.818 | 3.062 | 18.7 | 7.965 | 120 | 192.25 | 41.184 | 25.6945 | 13.806 | 2.0865 | 82.771 | 2.5986 | 21.6363 | 8.8603 | 1.0454 | 3.5097 | 10.0655 | #DIV/0! | #DIV/0! | #DIV/0! | 35.8282 | 45.8937 | AVG-C11-20 | Average | --- | --- | --- | --- | 8.195 | 22 | 2.375 | 0.0331 | 1.3936 | 3.88 | 1.0255 | 2.8545 | 18.7 | 7.97 | 120 | 147.5 | 35.849 | 25.0675 | 14.138 | 2.322 | 77.3765 | 2.7519 | 21.1927 | 9.8187 | 1.2095 | 3.8442 | 10.5304 | #DIV/0! | #DIV/0! | #DIV/0! | 37.4411 | 47.9714
[11 empty] | SDS-MCAA* | mg/L | 4.8926 | 3.3329 | BMRL | 4.1128 | 26.816 | SDS-MCAA* | mg/L | 2.8786 | 6.1697 | 2.7041 | 3.9175 | 49.8394 | RPD-C11-10 | RPD | --- | --- | --- | --- | 0.61087 | 0 | 2.0619 | 0 | 2.0619 | 0 | 18.3374 | 4.8988 | 0 | 0.62775 | 0 | 65.2796 | 4.5163 | 4.3472 | 4.766 | 13.6592 | 4.736 | #VALUE! | 4.2017 | 25.6911 | #VALUE! | 0.51856 | 0.89116 | #VALUE! | #VALUE! | #VALUE! | 6.4056 | 4.8052 | RPD-C11-20 | RPD | --- | --- | --- | --- | 0.12203 | 9.0909 | 2.1053 | 3.0211 | 0.91603 | 0 | 11.9941 | 4.309 | 0 | 0 | 0 | 3.3898 | 6.0141 | 1.6476 | 3.4517 | 1.4643 | 3.9069 | #VALUE! | 19.4407 | 1.1264 | 20.6275 | 18.537 | 19.1323 | #VALUE! | #VALUE! | #VALUE! | 20.6281 | 20.2998
[11 empty] | SDS-DCAA* | mg/L | 42.4704 | 38.8262 | 48.1383 | 43.145 | 10.8763 | SDS-DCAA* | mg/L | 43.5493 | 46.3771 | 43.645 | 44.5238 | 3.6064 | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[11 empty] | SDS-TCAA* | mg/L | 23.085 | 24.5281 | 23.3645 | 23.6592 | 3.2349 | SDS-TCAA* | mg/L | 30.2059 | 29.6163 | 24.9579 | 28.26 | 10.173 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
[11 empty] | SDS-MBAA* | mg/L | 1.7551 | 1.3504 | 1.0531 | 1.3862 | 25.4196 | SDS-MBAA* | mg/L | 1.4303 | 1.8233 | BMRL | 1.6268 | 17.0822
[11 empty] | SDS-DBAA* | mg/L | 4.0627 | 3.5681 | 2.6607 | 3.4305 | 20.7275 | SDS-DBAA* | mg/L | 3.2662 | 4.1163 | 2.6691 | 3.3505 | 21.7063
[11 empty] | SDS-BCAA* | mg/L | 15.0142 | 14.0629 | 14.4373 | 14.5048 | 3.3039 | SDS-BCAA* | mg/L | 15.3105 | 15.7359 | 13.8037 | 14.95 | 6.7912
[11 empty] | SDS-TBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0!
[11 empty] | SDS-CDBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0!
[11 empty] | SDS-DCBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0!
[11 empty] | SDS-HAA5 | mg/L | 76.2658 | 71.6057 | 75.2166 | 74.3627 | 3.2874 | SDS-HAA5 | mg/L | 81.3303 | 88.1027 | 73.9761 | 81.1364 | 8.7079
[11 empty] | SDS-HAA6 | mg/L | 91.28 | 85.6686 | 89.6539 | 88.8675 | 3.2489 | SDS-HAA6 | mg/L | 96.6408 | 103.8386 | 87.7798 | 96.0864 | 8.3714
[11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [6 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [6 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
Note on H7: Reviewer M.H. (12/13/99): Reviewer adjusted Reynolds number based on new full-scale temperatures.
Note on H8: Reviewer D.S. (10/13/99): Full-scale temperature is 14.2C, RSSCT designed for 20C.
Note on AB18: Reviewer D.S. (10/8/99): Per Consultant: "The Bromide results were verified".
Note on AP5: Reviewer D.S. (10/21/99): Per Consultant: "In the DCSS, we reported UV254 down to 0.001 cm-1. Our lowest standard was 0.009 cm-1 for the study (The ICR low-level standard). This should be noted in the DCSS as reported between the MDL and MRL for the method."
Note on AX17: Reviewer D.S. (10/8/99): Per Consultant: "Only one replicate reported"
Note on AX43: Reviewer D.S. (10/8/99): Per Consultant: "TOX results verified".
Note on BY5: Reviewer D.S. (10/21/99): Per Consultant: "In the DCSS, we reported UV254 down to 0.001 cm-1. Our lowest standard was 0.009 cm-1 for the study (The ICR low-level standard). This should be noted in the DCSS as reported between the MDL and MRL for the method."
Note on CG35: Reviewer D.S. (10/8/99): Per Consultant: "TOX results verified".
Note on CG38: Reviewer D.S. (10/8/99): Per Consultant: "Only one replicate reported"