## Readme
Self-monitoring data for Edwardsport IGCC Station
This Excel spreadsheet contains self-monitoring data submitted by Duke Energy as part of its request for a fundamentally different factors (FDF) variance providing alternative effluent limitations for certain parameters in discharges of gasification wastewater. The data are associated with a grey water treatment system that includes thermal evaporation followed by reverse osmosis filtration of the condensate from the evaporation stage. The data included here are a subset of the data submitted by Duke Energy. This spreadsheet includes data for only the treatment system influent and effluent monitoring locations; Duke Energy also provided data for other monitoring locations. In addition, this spreadsheet includes data for only arsenic, mercury, selenium and total dissolved solids (TDS); Duke Energy also provided data for other parameters. EPA's evaluated summary statistics and potential effluent limitations using unadjusted data, and also using certain adjustments to measurement values (i.e., "baseline substitution") for detected and non-detected values that are below a baseline value. The column named Final_concentration presents the values that were used for limitations that take into account baseline substitution; the column named Final_NBA_Concentration presents the values that were used for limitations that do not factor in baseline substitution. See "Statistical Support Document: Effluent Limitations for FGD Wastewater, Gasification Wastewater, and Combustion Residual Leachate for the Final Effluent Limitations Guidelines and Standards" for more information about baseline substitution and which limitations factor in (or do not factor in) baseline substitution. For more details about the available data, excluded data and rationale for exclusion, baseline values, and the procedures for setting the limitations based on these data, see the memo titled "Alternative effluent limitations for gasification wastewater at the Edwardsport IGCC Station."
Below are the column names for the data tab ("Edwardsport_20170602") and a brief explanation of the information contained in each column.
Column Name | Description
Plant_Name | Name of the plant
Data_Source | The source of the sampling data. For this dataset, all data are from plant self-monitoring.
Analyte | Name of the pollutant.
Date_Collected | Date the sample was collected or analyzed.
Sampling_Location | Location where the samples were collected.
Included_in_Limits | Indicator of whether the data point was included in the limit calculations: Yes = samples were collected for a combination of sampling location and analyte used for limit calculation and the data point was included in limit calculation, No = samples were collected for a combination of sampling location and analyte used for limit calculation, but data points were excluded from the limit calculations due to some reasons listed in the Inclusion_Comment column, or NA = samples were collected for a combination of sampling location and analyte not used in the limit calculations, including those subject to exclusion due to some reasons listed in the Inclusion_Comment column.
Inclusion_Comment | For data used for limit calculations, the information shown is the location where the sample was collected. For data that was excluded or would be excluded if that combination of sampling location were used for the limit calculations, inclusion_comment states the reason for exclusion. For data collected for a combination of sampling location and analyte not used in the limit calculations, but for which the data was not excluded for any other reason, inclusion_comment is “Sampling Location Not Used for Limit”.
Units | Unit of concentration.
Original_Indicator | Original Indicator for the Original_Concentration: D (i.e., detected) or ND (i.e., non-detected).
Original_Concentration | Original concentration.
Final_NBA_Indicator | Final non-baseline-adjusted indicator: D (i.e., detected) or ND (i.e., non-detected). Indicates whether the measurement is detected or nondetected before accounting for baseline adjustment, and after accounting for exclusions, and aggregation of duplicate and overlapping samples (if any). If the cell is blank, this means that the data points were excluded and therefore there is no indicator for that data point. Statistical analyses were performed using unadjusted data (i.e., Final_NBA_Concentration) and baseline-adjusted data (i.e., Final_Adj_Concentration). EPA evaluated both the baseline-unadjusted and adjusted limits and used the higher result for the alternative effluent limits, if there was a difference.
Final_NBA_Concentration | The measurement before accounting for baseline adjustment, and after accounting for exclusions, and aggregation of duplicates and overlapping samples (if any). If the cell is blank, this means that the data points were excluded. Statistical analyses were performed using unadjusted data (i.e., Final_NBA_Concentration) and baseline-adjusted data (i.e., Final_Adj_Concentration). EPA evaluated both the baseline-unadjusted and adjusted limits and used the higher result for the alternative effluent limits, if there was a difference.
Baseline | Baseline value for each pollutant.
Baseline_adjusted | Yes if Baseline value was used in place of Original Concentration; otherwise, No if Original Concentration was retained (i.e., not replaced with baseline value).
Final__Adj_Indicator | Final indicator for the measurement in the baseline-adjusted dataset: D (i.e., detected) or ND (i.e., non-detected). Indicates whether the measurement is detected or nondetected after accounting for baseline adjustment, and after accounting for exclusions, baseline adjustment and aggregation of duplicate and overlapping samples (if any). If the cell is blank, this means that the data points were excluded and therefore there is no indicator for that data point. Statistical analyses were performed using unadjusted data (i.e., Final_NBA_Concentration) and baseline-adjusted data (i.e., Final_Adj_Concentration). EPA evaluated both the baseline-unadjusted and adjusted limits and used the higher result for the alternative effluent limits, if there was a difference.
Final_Adj_Concentration | The measurement after accounting for baseline adjustment, and after accounting for exclusions, baseline adjustments, and aggregation of duplicates and overlapping samples (if any). If the cell is blank, this means that the data points were excluded.Statistical analyses were performed using unadjusted data (i.e., Final_NBA_Concentration) and baseline-adjusted data (i.e., Final_Adj_Concentration). EPA evaluated both the baseline-unadjusted and adjusted limits and used the higher result for the alternative effluent limits, if there was a difference.

## Edwardsport_20170602
Plant_name | Data_source | Analyte | Date_Collected | Sampling_Location | Included_in_Limits | Inclusion_Comment | Units | Original_Indicator | Original_Concentration | Final_NBA_Indicator | Final_NBA_Concentration | Baseline | Baseline_Adjusted | Final_Adj_Indicator | Final_Adj_Concentration
EdwardSport | Plant Self-Monitoring | Arsenic | 2013-05-09 | Outfall 501-Cyanide Destruct Pumps Effluent | NA | Does not represent typical operation of the gasification process | µg/L | ND | 1 | ND | 1 | 2 | Yes | ND | 2
EdwardSport | Plant Self-Monitoring | Arsenic | 2013-05-23 | Outfall 501-Cyanide Destruct Pumps Effluent | NA | Does not represent typical operation of the gasification process | µg/L | ND | 2 | ND | 2 | 2 | No | ND | 2
EdwardSport | Plant Self-Monitoring | Arsenic | 2013-06-06 | Outfall 501-Cyanide Destruct Pumps Effluent | NA | Does not represent typical operation of the gasification process | µg/L | ND | 2 | ND | 2 | 2 | No | ND | 2
EdwardSport | Plant Self-Monitoring | Arsenic | 2013-06-13 | Outfall 501-Cyanide Destruct Pumps Effluent | NA | Does not represent typical operation of the gasification process | µg/L | ND | 2 | ND | 2 | 2 | No | ND | 2
EdwardSport | Plant Self-Monitoring | Arsenic | 2013-07-24 | Outfall 501-Cyanide Destruct Pumps Effluent | NA | Does not represent typical operation of the gasification process | µg/L | D | 2 | D | 2 | 2 | No | D | 2
EdwardSport | Plant Self-Monitoring | Arsenic | 2013-07-31 | Outfall 501-Cyanide Destruct Pumps Effluent | NA | Does not represent typical operation of the gasification process | µg/L | ND | 1 | ND | 1 | 2 | Yes | ND | 2
EdwardSport | Plant Self-Monitoring | Arsenic | 2013-08-02 | Outfall 501-Cyanide Destruct Pumps Effluent | NA | Does not represent typical operation of the gasification process | µg/L | ND | 1 | ND | 1 | 2 | Yes | ND | 2
EdwardSport | Plant Self-Monitoring | Arsenic | 2013-08-21 | Outfall 501-Cyanide Destruct Pumps Effluent | NA | Does not represent typical operation of the gasification process | µg/L | D | 15 | D | 15 | 2 | No | D | 15
EdwardSport | Plant Self-Monitoring | Arsenic | 2013-09-05 | Outfall 501-Cyanide Destruct Pumps Effluent | NA | Does not represent typical operation of the gasification process | µg/L | ND | 10 | ND | 10 | 2 | No | ND | 10
EdwardSport | Plant Self-Monitoring | Arsenic | 2013-09-25 | Outfall 501-Cyanide Destruct Pumps Effluent | NA | Does not represent typical operation of the gasification process | µg/L | ND | 10 | ND | 10 | 2 | No | ND | 10
EdwardSport | Plant Self-Monitoring | Arsenic | 2013-10-08 | Outfall 501-Cyanide Destruct Pumps Effluent | NA | Does not represent typical operation of the gasification process | µg/L | ND | 10 | ND | 10 | 2 | No | ND | 10
EdwardSport | Plant Self-Monitoring | Arsenic | 2013-10-17 | Outfall 501-Cyanide Destruct Pumps Effluent | NA | Does not represent typical operation of the gasification process | µg/L | ND | 1 | ND | 1 | 2 | Yes | ND | 2
EdwardSport | Plant Self-Monitoring | Arsenic | 2015-09-08 | LP Grey Water Feed Pumps Influent | NA | Sampling Location Not Used for Limit | µg/L | D | 1100 | D | 1100 | 2 | No | D | 1100
EdwardSport | Plant Self-Monitoring | Arsenic | 2015-09-08 | RO Permeate Pumps Effluent | NA | Sampling Location Not Used for Limit | µg/L | ND | 1 | ND | 1 | 2 | Yes | ND | 2
EdwardSport | Plant Self-Monitoring | Arsenic | 2015-09-10 | LP Grey Water Feed Pumps Influent | NA | Sampling Location Not Used for Limit | µg/L | D | 120 | D | 120 | 2 | No | D | 120
EdwardSport | Plant Self-Monitoring | Arsenic | 2015-09-10 | RO Permeate Pumps Effluent | NA | Sampling Location Not Used for Limit | µg/L | ND | 1 | ND | 1 | 2 | Yes | ND | 2
EdwardSport | Plant Self-Monitoring | Arsenic | 2015-09-15 | LP Grey Water Feed Pumps Influent | NA | Sampling Location Not Used for Limit | µg/L | D | 120 | D | 120 | 2 | No | D | 120
EdwardSport | Plant Self-Monitoring | Arsenic | 2015-09-15 | RO Permeate Pumps Effluent | NA | Sampling Location Not Used for Limit | µg/L | ND | 2 | ND | 2 | 2 | No | ND | 2
EdwardSport | Plant Self-Monitoring | Arsenic | 2015-09-17 | LP Grey Water Feed Pumps Influent | NA | Sampling Location Not Used for Limit | µg/L | D | 130 | D | 130 | 2 | No | D | 130
EdwardSport | Plant Self-Monitoring | Arsenic | 2015-09-17 | RO Permeate Pumps Effluent | NA | Sampling Location Not Used for Limit | µg/L | ND | 2 | ND | 2 | 2 | No | ND | 2
EdwardSport | Plant Self-Monitoring | Arsenic | 2015-09-22 | LP Grey Water Feed Pumps Influent | NA | Sampling Location Not Used for Limit | µg/L | D | 31 | D | 31 | 2 | No | D | 31
EdwardSport | Plant Self-Monitoring | Arsenic | 2015-09-22 | RO Permeate Pumps Effluent | NA | Sampling Location Not Used for Limit | µg/L | ND | 1 | ND | 1 | 2 | Yes | ND | 2
EdwardSport | Plant Self-Monitoring | Arsenic | 2015-09-24 | LP Grey Water Feed Pumps Influent | NA | Sampling Location Not Used for Limit | µg/L | D | 63 | D | 63 | 2 | No | D | 63
EdwardSport | Plant Self-Monitoring | Arsenic | 2015-09-24 | RO Permeate Pumps Effluent | NA | Sampling Location Not Used for Limit | µg/L | ND | 1 | ND | 1 | 2 | Yes | ND | 2
EdwardSport | Plant Self-Monitoring | Arsenic | 2015-09-29 | LP Grey Water Feed Pumps Influent | NA | Sampling Location Not Used for Limit | µg/L | D | 67 | D | 67 | 2 | No | D | 67
EdwardSport | Plant Self-Monitoring | Arsenic | 2015-09-29 | RO Permeate Pumps Effluent | NA | Sampling Location Not Used for Limit | µg/L | ND | 1 | ND | 1 | 2 | Yes | ND | 2
EdwardSport | Plant Self-Monitoring | Arsenic | 2015-10-01 | LP Grey Water Feed Pumps Influent | NA | Sampling Location Not Used for Limit | µg/L | D | 42 | D | 42 | 2 | No | D | 42
EdwardSport | Plant Self-Monitoring | Arsenic | 2015-10-01 | RO Permeate Pumps Effluent | NA | Sampling Location Not Used for Limit | µg/L | ND | 1 | ND | 1 | 2 | Yes | ND | 2
EdwardSport | Plant Self-Monitoring | Arsenic | 2015-10-06 | LP Grey Water Feed Pumps Influent | NA | Sampling Location Not Used for Limit | µg/L | D | 33 | D | 33 | 2 | No | D | 33
EdwardSport | Plant Self-Monitoring | Arsenic | 2015-10-06 | RO Permeate Pumps Effluent | NA | Sampling Location Not Used for Limit | µg/L | ND | 1 | ND | 1 | 2 | Yes | ND | 2
EdwardSport | Plant Self-Monitoring | Arsenic | 2015-10-08 | LP Grey Water Feed Pumps Influent | NA | Sampling Location Not Used for Limit | µg/L | D | 38 | D | 38 | 2 | No | D | 38
EdwardSport | Plant Self-Monitoring | Arsenic | 2015-10-08 | RO Permeate Pumps Effluent | NA | Sampling Location Not Used for Limit | µg/L | ND | 1 | ND | 1 | 2 | Yes | ND | 2
EdwardSport | Plant Self-Monitoring | Arsenic | 2015-10-13 | LP Grey Water Feed Pumps Influent | NA | Possible system upset, contamination of sample, or lab error | µg/L | D | 210 | D | 210 | 2 | No | D | 210
EdwardSport | Plant Self-Monitoring | Arsenic | 2015-10-13 | RO Permeate Pumps Effluent | NA | Possible system upset, contamination of sample, or lab error | µg/L | ND | 1 | ND | 1 | 2 | Yes | ND | 2
EdwardSport | Plant Self-Monitoring | Arsenic | 2015-10-15 | LP Grey Water Feed Pumps Influent | NA | Sampling Location Not Used for Limit | µg/L | D | 230 | D | 230 | 2 | No | D | 230
EdwardSport | Plant Self-Monitoring | Arsenic | 2015-10-15 | RO Permeate Pumps Effluent | NA | Sampling Location Not Used for Limit | µg/L | ND | 1 | ND | 1 | 2 | Yes | ND | 2
EdwardSport | Plant Self-Monitoring | Arsenic | 2016-04-05 | Grey Water Feed Pumps Influent | NA | Sampling Location Not Used for Limit | µg/L | D | 210 | D | 210 | 2 | No | D | 210
EdwardSport | Plant Self-Monitoring | Arsenic | 2016-04-05 | Outfall 501-Cyanide Destruct Pumps Effluent | NA | Sampling Location Not Used for Limit | µg/L | ND | 1 | ND | 1 | 2 | Yes | ND | 2
EdwardSport | Plant Self-Monitoring | Arsenic | 2016-04-06 | Grey Water Feed Pumps Influent | NA | Sampling Location Not Used for Limit | µg/L | D | 330 | D | 330 | 2 | No | D | 330
EdwardSport | Plant Self-Monitoring | Arsenic | 2016-04-06 | Outfall 501-Cyanide Destruct Pumps Effluent | NA | Sampling Location Not Used for Limit | µg/L | ND | 1 | ND | 1 | 2 | Yes | ND | 2
EdwardSport | Plant Self-Monitoring | Arsenic | 2016-04-08 | Grey Water Feed Pumps Influent | NA | Sampling Location Not Used for Limit | µg/L | D | 260 | D | 260 | 2 | No | D | 260
EdwardSport | Plant Self-Monitoring | Arsenic | 2016-04-08 | Outfall 501-Cyanide Destruct Pumps Effluent | NA | Sampling Location Not Used for Limit | µg/L | ND | 1 | ND | 1 | 2 | Yes | ND | 2
EdwardSport | Plant Self-Monitoring | Arsenic | 2016-05-27 | Outfall 501-Cyanide Destruct Pumps Effluent | NA | Sampling Location Not Used for Limit | µg/L | ND | 1 | ND | 1 | 2 | Yes | ND | 2
EdwardSport | Plant Self-Monitoring | Arsenic | 2016-05-31 | Outfall 501-Cyanide Destruct Pumps Effluent | NA | Sampling Location Not Used for Limit | µg/L | ND | 1 | ND | 1 | 2 | Yes | ND | 2
EdwardSport | Plant Self-Monitoring | Arsenic | 2016-06-07 | Outfall 501-Cyanide Destruct Pumps Effluent | NA | Sampling Location Not Used for Limit | µg/L | ND | 1 | ND | 1 | 2 | Yes | ND | 2
EdwardSport | Plant Self-Monitoring | Arsenic | 2016-06-15 | Outfall 501-Cyanide Destruct Pumps Effluent | NA | Sampling Location Not Used for Limit | µg/L | ND | 1 | ND | 1 | 2 | Yes | ND | 2
EdwardSport | Plant Self-Monitoring | Arsenic | 2016-07-06 | Outfall 501-Cyanide Destruct Pumps Effluent | NA | Sampling Location Not Used for Limit | µg/L | ND | 1 | ND | 1 | 2 | Yes | ND | 2
EdwardSport | Plant Self-Monitoring | Arsenic | 2016-07-13 | Outfall 501-Cyanide Destruct Pumps Effluent | NA | Sampling Location Not Used for Limit | µg/L | ND | 1 | ND | 1 | 2 | Yes | ND | 2
EdwardSport | Plant Self-Monitoring | Arsenic | 2016-08-03 | Outfall 501-Cyanide Destruct Pumps Effluent | NA | Sampling Location Not Used for Limit | µg/L | ND | 1 | ND | 1 | 2 | Yes | ND | 2
EdwardSport | Plant Self-Monitoring | Arsenic | 2016-08-10 | Outfall 501-Cyanide Destruct Pumps Effluent | NA | Sampling Location Not Used for Limit | µg/L | ND | 1 | ND | 1 | 2 | Yes | ND | 2
EdwardSport | Plant Self-Monitoring | Arsenic | 2016-09-07 | Grey Water Feed Pumps Influent | NA | Sampling Location Not Used for Limit | µg/L | D | 361 |  |  | 2 | No
EdwardSport | Plant Self-Monitoring | Arsenic | 2016-09-07 | LP Grey Water Feed Pumps Influent | NA | Sampling Location Not Used for Limit | µg/L | D | 160 | D | 260.5 | 2 | No | D | 260.5
EdwardSport | Plant Self-Monitoring | Arsenic | 2016-09-07 | Outfall 501-Cyanide Destruct Pumps Effluent | NA | Sampling Location Not Used for Limit | µg/L | ND | 1 |  |  | 2 | Yes
EdwardSport | Plant Self-Monitoring | Arsenic | 2016-09-07 | RO Permeate Pumps Effluent | NA | Sampling Location Not Used for Limit | µg/L | ND | 1 | ND | 1 | 2 | Yes | ND | 2
EdwardSport | Plant Self-Monitoring | Arsenic | 2016-09-14 | Grey Water Feed Pumps Influent | NA | Sampling Location Not Used for Limit | µg/L | D | 594 |  |  | 2 | No
EdwardSport | Plant Self-Monitoring | Arsenic | 2016-09-14 | LP Grey Water Feed Pumps Influent | NA | Sampling Location Not Used for Limit | µg/L | D | 106 | D | 350 | 2 | No | D | 350
EdwardSport | Plant Self-Monitoring | Arsenic | 2016-09-14 | Outfall 501-Cyanide Destruct Pumps Effluent | NA | Sampling Location Not Used for Limit | µg/L | ND | 1 |  |  | 2 | Yes
EdwardSport | Plant Self-Monitoring | Arsenic | 2016-09-14 | RO Permeate Pumps Effluent | NA | Sampling Location Not Used for Limit | µg/L | ND | 1 | ND | 1 | 2 | Yes | ND | 2
EdwardSport | Plant Self-Monitoring | Arsenic | 2016-10-01 | Outfall 501-Cyanide Destruct Pumps Effluent | NA | Sampling Location Not Used for Limit | µg/L | ND | 1 | ND | 1 | 2 | Yes | ND | 2
EdwardSport | Plant Self-Monitoring | Mercury | 2013-07-22 | Outfall 501-Cyanide Destruct Pumps Effluent | No | Does not represent typical operation of the gasification process | ng/L | D | 2.08 | D | 2.08 | 0.5 | No | D | 2.08
EdwardSport | Plant Self-Monitoring | Mercury | 2013-08-08 | Outfall 501-Cyanide Destruct Pumps Effluent | No | Does not represent typical operation of the gasification process | ng/L | D | 9.58 | D | 9.58 | 0.5 | No | D | 9.58
EdwardSport | Plant Self-Monitoring | Mercury | 2013-10-03 | Outfall 501-Cyanide Destruct Pumps Effluent | No | Does not represent typical operation of the gasification process | ng/L | D | 2.53 | D | 2.53 | 0.5 | No | D | 2.53
EdwardSport | Plant Self-Monitoring | Mercury | 2015-09-08 | LP Grey Water Feed Pumps Influent | NA | LP Grey Water Feed Pumps Influent | ng/L | D | 6.55 | D | 6.55 | 0.5 | No | D | 6.55
EdwardSport | Plant Self-Monitoring | Mercury | 2015-09-08 | RO Permeate Pumps Effluent | Yes | RO Permeate Pumps Effluent | ng/L | D | 12.8 | D | 12.8 | 0.5 | No | D | 12.8
EdwardSport | Plant Self-Monitoring | Mercury | 2015-09-10 | LP Grey Water Feed Pumps Influent | NA | LP Grey Water Feed Pumps Influent | ng/L | D | 15.8 | D | 15.8 | 0.5 | No | D | 15.8
EdwardSport | Plant Self-Monitoring | Mercury | 2015-09-10 | RO Permeate Pumps Effluent | Yes | RO Permeate Pumps Effluent | ng/L | D | 5.25 | D | 5.25 | 0.5 | No | D | 5.25
EdwardSport | Plant Self-Monitoring | Mercury | 2015-09-15 | LP Grey Water Feed Pumps Influent | NA | LP Grey Water Feed Pumps Influent | ng/L | D | 10.8 | D | 10.8 | 0.5 | No | D | 10.8
EdwardSport | Plant Self-Monitoring | Mercury | 2015-09-15 | RO Permeate Pumps Effluent | Yes | RO Permeate Pumps Effluent | ng/L | D | 10.3 | D | 10.3 | 0.5 | No | D | 10.3
EdwardSport | Plant Self-Monitoring | Mercury | 2015-09-17 | LP Grey Water Feed Pumps Influent | NA | LP Grey Water Feed Pumps Influent | ng/L | D | 21.2 | D | 21.2 | 0.5 | No | D | 21.2
EdwardSport | Plant Self-Monitoring | Mercury | 2015-09-17 | RO Permeate Pumps Effluent | Yes | RO Permeate Pumps Effluent | ng/L | D | 6.55 | D | 6.55 | 0.5 | No | D | 6.55
EdwardSport | Plant Self-Monitoring | Mercury | 2015-09-22 | LP Grey Water Feed Pumps Influent | NA | LP Grey Water Feed Pumps Influent | ng/L | D | 22 | D | 22 | 0.5 | No | D | 22
EdwardSport | Plant Self-Monitoring | Mercury | 2015-09-22 | RO Permeate Pumps Effluent | Yes | RO Permeate Pumps Effluent | ng/L | D | 10.8 | D | 10.8 | 0.5 | No | D | 10.8
EdwardSport | Plant Self-Monitoring | Mercury | 2015-09-24 | LP Grey Water Feed Pumps Influent | NA | LP Grey Water Feed Pumps Influent | ng/L | D | 23.4 | D | 23.4 | 0.5 | No | D | 23.4
EdwardSport | Plant Self-Monitoring | Mercury | 2015-09-24 | RO Permeate Pumps Effluent | Yes | RO Permeate Pumps Effluent | ng/L | D | 11.5 | D | 11.5 | 0.5 | No | D | 11.5
EdwardSport | Plant Self-Monitoring | Mercury | 2015-09-29 | LP Grey Water Feed Pumps Influent | NA | LP Grey Water Feed Pumps Influent | ng/L | D | 44.4 | D | 44.4 | 0.5 | No | D | 44.4
EdwardSport | Plant Self-Monitoring | Mercury | 2015-09-29 | RO Permeate Pumps Effluent | Yes | RO Permeate Pumps Effluent | ng/L | D | 6.4 | D | 6.4 | 0.5 | No | D | 6.4
EdwardSport | Plant Self-Monitoring | Mercury | 2015-10-01 | LP Grey Water Feed Pumps Influent | NA | LP Grey Water Feed Pumps Influent | ng/L | D | 7.35 | D | 7.35 | 0.5 | No | D | 7.35
EdwardSport | Plant Self-Monitoring | Mercury | 2015-10-01 | RO Permeate Pumps Effluent | Yes | RO Permeate Pumps Effluent | ng/L | D | 3.92 | D | 3.92 | 0.5 | No | D | 3.92
EdwardSport | Plant Self-Monitoring | Mercury | 2015-10-06 | LP Grey Water Feed Pumps Influent | NA | LP Grey Water Feed Pumps Influent | ng/L | D | 15.6 | D | 15.6 | 0.5 | No | D | 15.6
EdwardSport | Plant Self-Monitoring | Mercury | 2015-10-06 | RO Permeate Pumps Effluent | Yes | RO Permeate Pumps Effluent | ng/L | D | 2.4 | D | 2.4 | 0.5 | No | D | 2.4
EdwardSport | Plant Self-Monitoring | Mercury | 2015-10-08 | LP Grey Water Feed Pumps Influent | NA | LP Grey Water Feed Pumps Influent | ng/L | D | 11.8 | D | 11.8 | 0.5 | No | D | 11.8
EdwardSport | Plant Self-Monitoring | Mercury | 2015-10-08 | RO Permeate Pumps Effluent | Yes | RO Permeate Pumps Effluent | ng/L | D | 5.79 | D | 5.79 | 0.5 | No | D | 5.79
EdwardSport | Plant Self-Monitoring | Mercury | 2015-10-13 | LP Grey Water Feed Pumps Influent | NA | Possible system upset, contamination of sample, or lab error | ng/L | D | 30.4 | D | 30.4 | 0.5 | No | D | 30.4
EdwardSport | Plant Self-Monitoring | Mercury | 2015-10-13 | RO Permeate Pumps Effluent | No | Possible system upset, contamination of sample, or lab error | ng/L | D | 3.05 | D | 3.05 | 0.5 | No | D | 3.05
EdwardSport | Plant Self-Monitoring | Mercury | 2015-10-15 | LP Grey Water Feed Pumps Influent | NA | LP Grey Water Feed Pumps Influent | ng/L | D | 59.5 | D | 59.5 | 0.5 | No | D | 59.5
EdwardSport | Plant Self-Monitoring | Mercury | 2015-10-15 | RO Permeate Pumps Effluent | Yes | RO Permeate Pumps Effluent | ng/L | D | 0.877 | D | 0.877 | 0.5 | No | D | 0.877
EdwardSport | Plant Self-Monitoring | Mercury | 2016-04-05 | Grey Water Feed Pumps Influent | NA | Grey Water Feed Pumps Influent | ng/L | D | 938 | D | 938 | 0.5 | No | D | 938
EdwardSport | Plant Self-Monitoring | Mercury | 2016-04-05 | Outfall 501-Cyanide Destruct Pumps Effluent | Yes | Outfall 501-Cyanide Destruct Pumps Effluent | ng/L | D | 4.74 |  |  | 0.5 | No
EdwardSport | Plant Self-Monitoring | Mercury | 2016-04-05 | RO Permeate Pumps Effluent | Yes | RO Permeate Pumps Effluent | ng/L | D | 4 | D | 4.37 | 0.5 | No | D | 4.37
EdwardSport | Plant Self-Monitoring | Mercury | 2016-04-06 | Grey Water Feed Pumps Influent | NA | Grey Water Feed Pumps Influent | ng/L | D | 6200 | D | 6200 | 0.5 | No | D | 6200
EdwardSport | Plant Self-Monitoring | Mercury | 2016-04-06 | Outfall 501-Cyanide Destruct Pumps Effluent | Yes | Outfall 501-Cyanide Destruct Pumps Effluent | ng/L | D | 8.39 |  |  | 0.5 | No
EdwardSport | Plant Self-Monitoring | Mercury | 2016-04-06 | RO Permeate Pumps Effluent | Yes | RO Permeate Pumps Effluent | ng/L | D | 6.47 | D | 7.43 | 0.5 | No | D | 7.43
EdwardSport | Plant Self-Monitoring | Mercury | 2016-04-08 | Grey Water Feed Pumps Influent | NA | Grey Water Feed Pumps Influent | ng/L | D | 1000 | D | 1000 | 0.5 | No | D | 1000
EdwardSport | Plant Self-Monitoring | Mercury | 2016-04-08 | Outfall 501-Cyanide Destruct Pumps Effluent | Yes | Outfall 501-Cyanide Destruct Pumps Effluent | ng/L | D | 3.09 |  |  | 0.5 | No
EdwardSport | Plant Self-Monitoring | Mercury | 2016-04-08 | RO Permeate Pumps Effluent | Yes | RO Permeate Pumps Effluent | ng/L | D | 5.2 | D | 4.145 | 0.5 | No | D | 4.145
EdwardSport | Plant Self-Monitoring | Mercury | 2016-05-27 | Outfall 501-Cyanide Destruct Pumps Effluent | Yes | Outfall 501-Cyanide Destruct Pumps Effluent | ng/L | D | 17.8 | D | 17.8 | 0.5 | No | D | 17.8
EdwardSport | Plant Self-Monitoring | Mercury | 2016-05-31 | Outfall 501-Cyanide Destruct Pumps Effluent | Yes | Outfall 501-Cyanide Destruct Pumps Effluent | ng/L | D | 4.46 | D | 4.46 | 0.5 | No | D | 4.46
EdwardSport | Plant Self-Monitoring | Mercury | 2016-06-07 | Outfall 501-Cyanide Destruct Pumps Effluent | Yes | Outfall 501-Cyanide Destruct Pumps Effluent | ng/L | D | 1.51 | D | 1.51 | 0.5 | No | D | 1.51
EdwardSport | Plant Self-Monitoring | Mercury | 2016-06-15 | Outfall 501-Cyanide Destruct Pumps Effluent | Yes | Outfall 501-Cyanide Destruct Pumps Effluent | ng/L | ND | 0.5 | ND | 0.5 | 0.5 | No | ND | 0.5
EdwardSport | Plant Self-Monitoring | Mercury | 2016-07-06 | Outfall 501-Cyanide Destruct Pumps Effluent | Yes | Outfall 501-Cyanide Destruct Pumps Effluent | ng/L | D | 3.53 | D | 3.53 | 0.5 | No | D | 3.53
EdwardSport | Plant Self-Monitoring | Mercury | 2016-07-13 | Outfall 501-Cyanide Destruct Pumps Effluent | Yes | Outfall 501-Cyanide Destruct Pumps Effluent | ng/L | D | 1.44 | D | 1.44 | 0.5 | No | D | 1.44
EdwardSport | Plant Self-Monitoring | Mercury | 2016-08-03 | Outfall 501-Cyanide Destruct Pumps Effluent | Yes | Outfall 501-Cyanide Destruct Pumps Effluent | ng/L | ND | 0.5 | ND | 0.5 | 0.5 | No | ND | 0.5
EdwardSport | Plant Self-Monitoring | Mercury | 2016-08-10 | Outfall 501-Cyanide Destruct Pumps Effluent | Yes | Outfall 501-Cyanide Destruct Pumps Effluent | ng/L | D | 4.07 | D | 4.07 | 0.5 | No | D | 4.07
EdwardSport | Plant Self-Monitoring | Mercury | 2016-09-07 | Grey Water Feed Pumps Influent | NA | Grey Water Feed Pumps Influent | ng/L | D | 39 |  |  | 0.5 | No
EdwardSport | Plant Self-Monitoring | Mercury | 2016-09-07 | LP Grey Water Feed Pumps Influent | NA | LP Grey Water Feed Pumps Influent | ng/L | D | 13.8 | D | 26.4 | 0.5 | No | D | 26.4
EdwardSport | Plant Self-Monitoring | Mercury | 2016-09-07 | Outfall 501-Cyanide Destruct Pumps Effluent | Yes | Outfall 501-Cyanide Destruct Pumps Effluent | ng/L | D | 2.05 |  |  | 0.5 | No
EdwardSport | Plant Self-Monitoring | Mercury | 2016-09-07 | RO Permeate Pumps Effluent | Yes | RO Permeate Pumps Effluent | ng/L | D | 4.73 | D | 3.39 | 0.5 | No | D | 3.39
EdwardSport | Plant Self-Monitoring | Mercury | 2016-09-14 | Grey Water Feed Pumps Influent | NA | Grey Water Feed Pumps Influent | ng/L | D | 21.8 |  |  | 0.5 | No
EdwardSport | Plant Self-Monitoring | Mercury | 2016-09-14 | LP Grey Water Feed Pumps Influent | NA | LP Grey Water Feed Pumps Influent | ng/L | D | 9.24 | D | 15.52 | 0.5 | No | D | 15.52
EdwardSport | Plant Self-Monitoring | Mercury | 2016-09-14 | Outfall 501-Cyanide Destruct Pumps Effluent | Yes | Outfall 501-Cyanide Destruct Pumps Effluent | ng/L | D | 0.78 |  |  | 0.5 | No
EdwardSport | Plant Self-Monitoring | Mercury | 2016-09-14 | RO Permeate Pumps Effluent | Yes | RO Permeate Pumps Effluent | ng/L | D | 1.79 | D | 1.285 | 0.5 | No | D | 1.285
EdwardSport | Plant Self-Monitoring | Mercury | 2016-10-01 | Outfall 501-Cyanide Destruct Pumps Effluent | Yes | Outfall 501-Cyanide Destruct Pumps Effluent | ng/L | D | 1.79 | D | 1.79 | 0.5 | No | D | 1.79
EdwardSport | Plant Self-Monitoring | Selenium | 2013-05-09 | Outfall 501-Cyanide Destruct Pumps Effluent | NA | Does not represent typical operation of the gasification process | µg/L | D | 7 | D | 7 | 5 | No | D | 7
EdwardSport | Plant Self-Monitoring | Selenium | 2013-05-23 | Outfall 501-Cyanide Destruct Pumps Effluent | NA | Does not represent typical operation of the gasification process | µg/L | ND | 2 | ND | 2 | 5 | Yes | ND | 5
EdwardSport | Plant Self-Monitoring | Selenium | 2013-06-06 | Outfall 501-Cyanide Destruct Pumps Effluent | NA | Does not represent typical operation of the gasification process | µg/L | ND | 2 | ND | 2 | 5 | Yes | ND | 5
EdwardSport | Plant Self-Monitoring | Selenium | 2013-06-13 | Outfall 501-Cyanide Destruct Pumps Effluent | NA | Does not represent typical operation of the gasification process | µg/L | ND | 2 | ND | 2 | 5 | Yes | ND | 5
EdwardSport | Plant Self-Monitoring | Selenium | 2013-07-24 | Outfall 501-Cyanide Destruct Pumps Effluent | NA | Does not represent typical operation of the gasification process | µg/L | D | 4 | D | 4 | 5 | Yes | ND | 5
EdwardSport | Plant Self-Monitoring | Selenium | 2013-07-31 | Outfall 501-Cyanide Destruct Pumps Effluent | NA | Does not represent typical operation of the gasification process | µg/L | ND | 1 | ND | 1 | 5 | Yes | ND | 5
EdwardSport | Plant Self-Monitoring | Selenium | 2013-08-02 | Outfall 501-Cyanide Destruct Pumps Effluent | NA | Does not represent typical operation of the gasification process | µg/L | ND | 1 | ND | 1 | 5 | Yes | ND | 5
EdwardSport | Plant Self-Monitoring | Selenium | 2013-08-21 | Outfall 501-Cyanide Destruct Pumps Effluent | NA | Does not represent typical operation of the gasification process | µg/L | ND | 10 | ND | 10 | 5 | No | ND | 10
EdwardSport | Plant Self-Monitoring | Selenium | 2013-09-05 | Outfall 501-Cyanide Destruct Pumps Effluent | NA | Does not represent typical operation of the gasification process | µg/L | ND | 10 | ND | 10 | 5 | No | ND | 10
EdwardSport | Plant Self-Monitoring | Selenium | 2013-09-25 | Outfall 501-Cyanide Destruct Pumps Effluent | NA | Does not represent typical operation of the gasification process | µg/L | ND | 10 | ND | 10 | 5 | No | ND | 10
EdwardSport | Plant Self-Monitoring | Selenium | 2013-10-08 | Outfall 501-Cyanide Destruct Pumps Effluent | NA | Does not represent typical operation of the gasification process | µg/L | ND | 10 | ND | 10 | 5 | No | ND | 10
EdwardSport | Plant Self-Monitoring | Selenium | 2013-10-17 | Outfall 501-Cyanide Destruct Pumps Effluent | NA | Does not represent typical operation of the gasification process | µg/L | ND | 10 | ND | 10 | 5 | No | ND | 10
EdwardSport | Plant Self-Monitoring | Selenium | 2015-09-08 | LP Grey Water Feed Pumps Influent | NA | Sampling Location Not Used for Limit | µg/L | D | 260 | D | 260 | 5 | No | D | 260
EdwardSport | Plant Self-Monitoring | Selenium | 2015-09-08 | RO Permeate Pumps Effluent | NA | Sampling Location Not Used for Limit | µg/L | ND | 1 | ND | 1 | 5 | Yes | ND | 5
EdwardSport | Plant Self-Monitoring | Selenium | 2015-09-10 | LP Grey Water Feed Pumps Influent | NA | Sampling Location Not Used for Limit | µg/L | D | 160 | D | 160 | 5 | No | D | 160
EdwardSport | Plant Self-Monitoring | Selenium | 2015-09-10 | RO Permeate Pumps Effluent | NA | Sampling Location Not Used for Limit | µg/L | ND | 1 | ND | 1 | 5 | Yes | ND | 5
EdwardSport | Plant Self-Monitoring | Selenium | 2015-09-15 | LP Grey Water Feed Pumps Influent | NA | Sampling Location Not Used for Limit | µg/L | D | 320 | D | 320 | 5 | No | D | 320
EdwardSport | Plant Self-Monitoring | Selenium | 2015-09-15 | RO Permeate Pumps Effluent | NA | Sampling Location Not Used for Limit | µg/L | ND | 2 | ND | 2 | 5 | Yes | ND | 5
EdwardSport | Plant Self-Monitoring | Selenium | 2015-09-17 | LP Grey Water Feed Pumps Influent | NA | Sampling Location Not Used for Limit | µg/L | D | 130 | D | 130 | 5 | No | D | 130
EdwardSport | Plant Self-Monitoring | Selenium | 2015-09-17 | RO Permeate Pumps Effluent | NA | Sampling Location Not Used for Limit | µg/L | ND | 2 | ND | 2 | 5 | Yes | ND | 5
EdwardSport | Plant Self-Monitoring | Selenium | 2015-09-22 | LP Grey Water Feed Pumps Influent | NA | Sampling Location Not Used for Limit | µg/L | D | 78 | D | 78 | 5 | No | D | 78
EdwardSport | Plant Self-Monitoring | Selenium | 2015-09-22 | RO Permeate Pumps Effluent | NA | Sampling Location Not Used for Limit | µg/L | ND | 1 | ND | 1 | 5 | Yes | ND | 5
EdwardSport | Plant Self-Monitoring | Selenium | 2015-09-24 | LP Grey Water Feed Pumps Influent | NA | Sampling Location Not Used for Limit | µg/L | D | 87 | D | 87 | 5 | No | D | 87
EdwardSport | Plant Self-Monitoring | Selenium | 2015-09-24 | RO Permeate Pumps Effluent | NA | Sampling Location Not Used for Limit | µg/L | ND | 1 | ND | 1 | 5 | Yes | ND | 5
EdwardSport | Plant Self-Monitoring | Selenium | 2015-09-29 | LP Grey Water Feed Pumps Influent | NA | Sampling Location Not Used for Limit | µg/L | D | 66 | D | 66 | 5 | No | D | 66
EdwardSport | Plant Self-Monitoring | Selenium | 2015-09-29 | RO Permeate Pumps Effluent | NA | Sampling Location Not Used for Limit | µg/L | ND | 1 | ND | 1 | 5 | Yes | ND | 5
EdwardSport | Plant Self-Monitoring | Selenium | 2015-10-01 | LP Grey Water Feed Pumps Influent | NA | Sampling Location Not Used for Limit | µg/L | D | 80 | D | 80 | 5 | No | D | 80
EdwardSport | Plant Self-Monitoring | Selenium | 2015-10-01 | RO Permeate Pumps Effluent | NA | Sampling Location Not Used for Limit | µg/L | ND | 1 | ND | 1 | 5 | Yes | ND | 5
EdwardSport | Plant Self-Monitoring | Selenium | 2015-10-06 | LP Grey Water Feed Pumps Influent | NA | Sampling Location Not Used for Limit | µg/L | D | 140 | D | 140 | 5 | No | D | 140
EdwardSport | Plant Self-Monitoring | Selenium | 2015-10-06 | RO Permeate Pumps Effluent | NA | Sampling Location Not Used for Limit | µg/L | ND | 1 | ND | 1 | 5 | Yes | ND | 5
EdwardSport | Plant Self-Monitoring | Selenium | 2015-10-08 | LP Grey Water Feed Pumps Influent | NA | Sampling Location Not Used for Limit | µg/L | D | 160 | D | 160 | 5 | No | D | 160
EdwardSport | Plant Self-Monitoring | Selenium | 2015-10-08 | RO Permeate Pumps Effluent | NA | Sampling Location Not Used for Limit | µg/L | D | 10 | D | 10 | 5 | No | D | 10
EdwardSport | Plant Self-Monitoring | Selenium | 2015-10-13 | LP Grey Water Feed Pumps Influent | NA | Possible system upset, contamination of sample, or lab error | µg/L | D | 140 | D | 140 | 5 | No | D | 140
EdwardSport | Plant Self-Monitoring | Selenium | 2015-10-13 | RO Permeate Pumps Effluent | NA | Possible system upset, contamination of sample, or lab error | µg/L | ND | 1 | ND | 1 | 5 | Yes | ND | 5
EdwardSport | Plant Self-Monitoring | Selenium | 2015-10-15 | LP Grey Water Feed Pumps Influent | NA | Sampling Location Not Used for Limit | µg/L | D | 110 | D | 110 | 5 | No | D | 110
EdwardSport | Plant Self-Monitoring | Selenium | 2015-10-15 | RO Permeate Pumps Effluent | NA | Sampling Location Not Used for Limit | µg/L | ND | 1 | ND | 1 | 5 | Yes | ND | 5
EdwardSport | Plant Self-Monitoring | Selenium | 2016-04-05 | Grey Water Feed Pumps Influent | NA | Sampling Location Not Used for Limit | µg/L | D | 130 | D | 130 | 5 | No | D | 130
EdwardSport | Plant Self-Monitoring | Selenium | 2016-04-05 | Outfall 501-Cyanide Destruct Pumps Effluent | NA | Sampling Location Not Used for Limit | µg/L | D | 2.9 | D | 2.9 | 5 | Yes | ND | 5
EdwardSport | Plant Self-Monitoring | Selenium | 2016-04-06 | Grey Water Feed Pumps Influent | NA | Sampling Location Not Used for Limit | µg/L | D | 250 | D | 250 | 5 | No | D | 250
EdwardSport | Plant Self-Monitoring | Selenium | 2016-04-06 | Outfall 501-Cyanide Destruct Pumps Effluent | NA | Sampling Location Not Used for Limit | µg/L | D | 4.1 | D | 4.1 | 5 | Yes | ND | 5
EdwardSport | Plant Self-Monitoring | Selenium | 2016-04-08 | Grey Water Feed Pumps Influent | NA | Sampling Location Not Used for Limit | µg/L | D | 120 | D | 120 | 5 | No | D | 120
EdwardSport | Plant Self-Monitoring | Selenium | 2016-04-08 | Outfall 501-Cyanide Destruct Pumps Effluent | NA | Sampling Location Not Used for Limit | µg/L | D | 3.8 | D | 3.8 | 5 | Yes | ND | 5
EdwardSport | Plant Self-Monitoring | Selenium | 2016-05-27 | Outfall 501-Cyanide Destruct Pumps Effluent | NA | Sampling Location Not Used for Limit | µg/L | D | 14.2 | D | 14.2 | 5 | No | D | 14.2
EdwardSport | Plant Self-Monitoring | Selenium | 2016-05-31 | Outfall 501-Cyanide Destruct Pumps Effluent | NA | Sampling Location Not Used for Limit | µg/L | ND | 1 | ND | 1 | 5 | Yes | ND | 5
EdwardSport | Plant Self-Monitoring | Selenium | 2016-06-07 | Outfall 501-Cyanide Destruct Pumps Effluent | NA | Sampling Location Not Used for Limit | µg/L | ND | 1 | ND | 1 | 5 | Yes | ND | 5
EdwardSport | Plant Self-Monitoring | Selenium | 2016-06-15 | Outfall 501-Cyanide Destruct Pumps Effluent | NA | Sampling Location Not Used for Limit | µg/L | ND | 1 | ND | 1 | 5 | Yes | ND | 5
EdwardSport | Plant Self-Monitoring | Selenium | 2016-07-06 | Outfall 501-Cyanide Destruct Pumps Effluent | NA | Sampling Location Not Used for Limit | µg/L | D | 1.1 | D | 1.1 | 5 | Yes | ND | 5
EdwardSport | Plant Self-Monitoring | Selenium | 2016-07-13 | Outfall 501-Cyanide Destruct Pumps Effluent | NA | Sampling Location Not Used for Limit | µg/L | D | 1.3 | D | 1.3 | 5 | Yes | ND | 5
EdwardSport | Plant Self-Monitoring | Selenium | 2016-08-03 | Outfall 501-Cyanide Destruct Pumps Effluent | NA | Sampling Location Not Used for Limit | µg/L | ND | 1 | ND | 1 | 5 | Yes | ND | 5
EdwardSport | Plant Self-Monitoring | Selenium | 2016-08-10 | Outfall 501-Cyanide Destruct Pumps Effluent | NA | Sampling Location Not Used for Limit | µg/L | D | 7.2 | D | 7.2 | 5 | No | D | 7.2
EdwardSport | Plant Self-Monitoring | Selenium | 2016-09-07 | Grey Water Feed Pumps Influent | NA | Sampling Location Not Used for Limit | µg/L | D | 82.6 |  |  | 5 | No
EdwardSport | Plant Self-Monitoring | Selenium | 2016-09-07 | LP Grey Water Feed Pumps Influent | NA | Sampling Location Not Used for Limit | µg/L | D | 95.9 | D | 89.25 | 5 | No | D | 89.25
EdwardSport | Plant Self-Monitoring | Selenium | 2016-09-07 | Outfall 501-Cyanide Destruct Pumps Effluent | NA | Sampling Location Not Used for Limit | µg/L | D | 1.5 |  |  | 5 | Yes
EdwardSport | Plant Self-Monitoring | Selenium | 2016-09-07 | RO Permeate Pumps Effluent | NA | Sampling Location Not Used for Limit | µg/L | ND | 1 | D | 1.25 | 5 | Yes | ND | 5
EdwardSport | Plant Self-Monitoring | Selenium | 2016-09-14 | Grey Water Feed Pumps Influent | NA | Sampling Location Not Used for Limit | µg/L | D | 33.2 |  |  | 5 | No
EdwardSport | Plant Self-Monitoring | Selenium | 2016-09-14 | LP Grey Water Feed Pumps Influent | NA | Sampling Location Not Used for Limit | µg/L | D | 108 | D | 70.6 | 5 | No | D | 70.6
EdwardSport | Plant Self-Monitoring | Selenium | 2016-09-14 | Outfall 501-Cyanide Destruct Pumps Effluent | NA | Sampling Location Not Used for Limit | µg/L | ND | 1 |  |  | 5 | Yes
EdwardSport | Plant Self-Monitoring | Selenium | 2016-09-14 | RO Permeate Pumps Effluent | NA | Sampling Location Not Used for Limit | µg/L | ND | 1 | ND | 1 | 5 | Yes | ND | 5
EdwardSport | Plant Self-Monitoring | Selenium | 2016-10-01 | Outfall 501-Cyanide Destruct Pumps Effluent | NA | Sampling Location Not Used for Limit | µg/L | D | 1 | D | 1 | 5 | Yes | ND | 5
EdwardSport | Plant Self-Monitoring | Total Dissolved Solid | 2015-09-08 | LP Grey Water Feed Pumps Influent | NA | LP Grey Water Feed Pumps Influent | mg/L | D | 2540 | D | 2540 | 10 | No | D | 2540
EdwardSport | Plant Self-Monitoring | Total Dissolved Solid | 2015-09-08 | RO Permeate Pumps Effluent | Yes | RO Permeate Pumps Effluent | mg/L | D | 20 | D | 20 | 10 | No | D | 20
EdwardSport | Plant Self-Monitoring | Total Dissolved Solid | 2015-09-10 | LP Grey Water Feed Pumps Influent | NA | LP Grey Water Feed Pumps Influent | mg/L | D | 3020 | D | 3020 | 10 | No | D | 3020
EdwardSport | Plant Self-Monitoring | Total Dissolved Solid | 2015-09-10 | RO Permeate Pumps Effluent | Yes | RO Permeate Pumps Effluent | mg/L | D | 40 | D | 40 | 10 | No | D | 40
EdwardSport | Plant Self-Monitoring | Total Dissolved Solid | 2015-09-15 | LP Grey Water Feed Pumps Influent | NA | LP Grey Water Feed Pumps Influent | mg/L | D | 2560 | D | 2560 | 10 | No | D | 2560
EdwardSport | Plant Self-Monitoring | Total Dissolved Solid | 2015-09-15 | RO Permeate Pumps Effluent | Yes | RO Permeate Pumps Effluent | mg/L | ND | 10 | ND | 10 | 10 | No | ND | 10
EdwardSport | Plant Self-Monitoring | Total Dissolved Solid | 2015-09-17 | LP Grey Water Feed Pumps Influent | NA | LP Grey Water Feed Pumps Influent | mg/L | D | 2090 | D | 2090 | 10 | No | D | 2090
EdwardSport | Plant Self-Monitoring | Total Dissolved Solid | 2015-09-17 | RO Permeate Pumps Effluent | Yes | RO Permeate Pumps Effluent | mg/L | D | 20 | D | 20 | 10 | No | D | 20
EdwardSport | Plant Self-Monitoring | Total Dissolved Solid | 2015-09-22 | LP Grey Water Feed Pumps Influent | NA | LP Grey Water Feed Pumps Influent | mg/L | D | 2200 | D | 2200 | 10 | No | D | 2200
EdwardSport | Plant Self-Monitoring | Total Dissolved Solid | 2015-09-22 | RO Permeate Pumps Effluent | Yes | RO Permeate Pumps Effluent | mg/L | D | 10 | D | 10 | 10 | No | D | 10
EdwardSport | Plant Self-Monitoring | Total Dissolved Solid | 2015-09-24 | LP Grey Water Feed Pumps Influent | NA | LP Grey Water Feed Pumps Influent | mg/L | D | 2140 | D | 2140 | 10 | No | D | 2140
EdwardSport | Plant Self-Monitoring | Total Dissolved Solid | 2015-09-24 | RO Permeate Pumps Effluent | Yes | RO Permeate Pumps Effluent | mg/L | ND | 10 | ND | 10 | 10 | No | ND | 10
EdwardSport | Plant Self-Monitoring | Total Dissolved Solid | 2015-09-29 | LP Grey Water Feed Pumps Influent | NA | LP Grey Water Feed Pumps Influent | mg/L | D | 2700 | D | 2700 | 10 | No | D | 2700
EdwardSport | Plant Self-Monitoring | Total Dissolved Solid | 2015-09-29 | RO Permeate Pumps Effluent | Yes | RO Permeate Pumps Effluent | mg/L | D | 32 | D | 32 | 10 | No | D | 32
EdwardSport | Plant Self-Monitoring | Total Dissolved Solid | 2015-10-01 | LP Grey Water Feed Pumps Influent | NA | LP Grey Water Feed Pumps Influent | mg/L | D | 2980 | D | 2980 | 10 | No | D | 2980
EdwardSport | Plant Self-Monitoring | Total Dissolved Solid | 2015-10-01 | RO Permeate Pumps Effluent | Yes | RO Permeate Pumps Effluent | mg/L | D | 20 | D | 20 | 10 | No | D | 20
EdwardSport | Plant Self-Monitoring | Total Dissolved Solid | 2015-10-06 | LP Grey Water Feed Pumps Influent | NA | LP Grey Water Feed Pumps Influent | mg/L | D | 2680 | D | 2680 | 10 | No | D | 2680
EdwardSport | Plant Self-Monitoring | Total Dissolved Solid | 2015-10-06 | RO Permeate Pumps Effluent | Yes | RO Permeate Pumps Effluent | mg/L | D | 20 | D | 20 | 10 | No | D | 20
EdwardSport | Plant Self-Monitoring | Total Dissolved Solid | 2015-10-08 | LP Grey Water Feed Pumps Influent | NA | LP Grey Water Feed Pumps Influent | mg/L | D | 1660 | D | 1660 | 10 | No | D | 1660
EdwardSport | Plant Self-Monitoring | Total Dissolved Solid | 2015-10-08 | RO Permeate Pumps Effluent | Yes | RO Permeate Pumps Effluent | mg/L | D | 14 | D | 14 | 10 | No | D | 14
EdwardSport | Plant Self-Monitoring | Total Dissolved Solid | 2015-10-13 | LP Grey Water Feed Pumps Influent | NA | Possible system upset, contamination of sample, or lab error | mg/L | D | 2230 | D | 2230 | 10 | No | D | 2230
EdwardSport | Plant Self-Monitoring | Total Dissolved Solid | 2015-10-13 | RO Permeate Pumps Effluent | No | Possible system upset, contamination of sample, or lab error | mg/L | D | 222 | D | 222 | 10 | No | D | 222
EdwardSport | Plant Self-Monitoring | Total Dissolved Solid | 2015-10-15 | LP Grey Water Feed Pumps Influent | NA | LP Grey Water Feed Pumps Influent | mg/L | D | 2120 | D | 2120 | 10 | No | D | 2120
EdwardSport | Plant Self-Monitoring | Total Dissolved Solid | 2015-10-15 | RO Permeate Pumps Effluent | Yes | RO Permeate Pumps Effluent | mg/L | D | 60 | D | 60 | 10 | No | D | 60
EdwardSport | Plant Self-Monitoring | Total Dissolved Solid | 2016-04-05 | Grey Water Feed Pumps Influent | NA | Grey Water Feed Pumps Influent | mg/L | D | 1410 | D | 1410 | 10 | No | D | 1410
EdwardSport | Plant Self-Monitoring | Total Dissolved Solid | 2016-04-05 | Outfall 501-Cyanide Destruct Pumps Effluent | Yes | Outfall 501-Cyanide Destruct Pumps Effluent | mg/L | D | 34 | D | 34 | 10 | No | D | 34
EdwardSport | Plant Self-Monitoring | Total Dissolved Solid | 2016-04-06 | Grey Water Feed Pumps Influent | NA | Grey Water Feed Pumps Influent | mg/L | D | 1360 | D | 1360 | 10 | No | D | 1360
EdwardSport | Plant Self-Monitoring | Total Dissolved Solid | 2016-04-06 | Outfall 501-Cyanide Destruct Pumps Effluent | Yes | Outfall 501-Cyanide Destruct Pumps Effluent | mg/L | D | 72 | D | 72 | 10 | No | D | 72
EdwardSport | Plant Self-Monitoring | Total Dissolved Solid | 2016-04-08 | Grey Water Feed Pumps Influent | NA | Grey Water Feed Pumps Influent | mg/L | D | 870 | D | 870 | 10 | No | D | 870
EdwardSport | Plant Self-Monitoring | Total Dissolved Solid | 2016-04-08 | Outfall 501-Cyanide Destruct Pumps Effluent | Yes | Outfall 501-Cyanide Destruct Pumps Effluent | mg/L | D | 42 | D | 42 | 10 | No | D | 42
EdwardSport | Plant Self-Monitoring | Total Dissolved Solid | 2016-04-14 | Grey Water Feed Pumps Influent | NA | Grey Water Feed Pumps Influent | mg/L | D | 586 |  |  | 10 | No
EdwardSport | Plant Self-Monitoring | Total Dissolved Solid | 2016-04-14 | LP Grey Water Feed Pumps Influent | NA | LP Grey Water Feed Pumps Influent | mg/L | D | 790 | D | 688 | 10 | No | D | 688
EdwardSport | Plant Self-Monitoring | Total Dissolved Solid | 2016-04-14 | RO Permeate Pumps Effluent | Yes | RO Permeate Pumps Effluent | mg/L | D | 19 | D | 19 | 10 | No | D | 19
EdwardSport | Plant Self-Monitoring | Total Dissolved Solid | 2016-05-27 | Outfall 501-Cyanide Destruct Pumps Effluent | Yes | Outfall 501-Cyanide Destruct Pumps Effluent | mg/L | ND | 10 | ND | 10 | 10 | No | ND | 10
EdwardSport | Plant Self-Monitoring | Total Dissolved Solid | 2016-05-31 | Outfall 501-Cyanide Destruct Pumps Effluent | Yes | Outfall 501-Cyanide Destruct Pumps Effluent | mg/L | ND | 10 | ND | 10 | 10 | No | ND | 10
EdwardSport | Plant Self-Monitoring | Total Dissolved Solid | 2016-06-07 | Outfall 501-Cyanide Destruct Pumps Effluent | Yes | Outfall 501-Cyanide Destruct Pumps Effluent | mg/L | D | 24 | D | 24 | 10 | No | D | 24
EdwardSport | Plant Self-Monitoring | Total Dissolved Solid | 2016-06-15 | Outfall 501-Cyanide Destruct Pumps Effluent | Yes | Outfall 501-Cyanide Destruct Pumps Effluent | mg/L | ND | 10 | ND | 10 | 10 | No | ND | 10
EdwardSport | Plant Self-Monitoring | Total Dissolved Solid | 2016-07-06 | Outfall 501-Cyanide Destruct Pumps Effluent | Yes | Outfall 501-Cyanide Destruct Pumps Effluent | mg/L | ND | 10 | ND | 10 | 10 | No | ND | 10
EdwardSport | Plant Self-Monitoring | Total Dissolved Solid | 2016-07-13 | Outfall 501-Cyanide Destruct Pumps Effluent | Yes | Outfall 501-Cyanide Destruct Pumps Effluent | mg/L | ND | 10 | ND | 10 | 10 | No | ND | 10
EdwardSport | Plant Self-Monitoring | Total Dissolved Solid | 2016-08-03 | Outfall 501-Cyanide Destruct Pumps Effluent | Yes | Outfall 501-Cyanide Destruct Pumps Effluent | mg/L | ND | 10 | ND | 10 | 10 | No | ND | 10
EdwardSport | Plant Self-Monitoring | Total Dissolved Solid | 2016-08-10 | Outfall 501-Cyanide Destruct Pumps Effluent | Yes | Outfall 501-Cyanide Destruct Pumps Effluent | mg/L | ND | 10 | ND | 10 | 10 | No | ND | 10
EdwardSport | Plant Self-Monitoring | Total Dissolved Solid | 2016-09-07 | Grey Water Feed Pumps Influent | NA | Grey Water Feed Pumps Influent | mg/L | D | 2600 |  |  | 10 | No
EdwardSport | Plant Self-Monitoring | Total Dissolved Solid | 2016-09-07 | LP Grey Water Feed Pumps Influent | NA | LP Grey Water Feed Pumps Influent | mg/L | D | 570 | D | 1585 | 10 | No | D | 1585
EdwardSport | Plant Self-Monitoring | Total Dissolved Solid | 2016-09-07 | Outfall 501-Cyanide Destruct Pumps Effluent | Yes | Outfall 501-Cyanide Destruct Pumps Effluent | mg/L | ND | 10 |  |  | 10 | No
EdwardSport | Plant Self-Monitoring | Total Dissolved Solid | 2016-09-07 | RO Permeate Pumps Effluent | Yes | RO Permeate Pumps Effluent | mg/L | ND | 25 | ND | 17.5 | 10 | No | ND | 17.5
EdwardSport | Plant Self-Monitoring | Total Dissolved Solid | 2016-09-14 | Grey Water Feed Pumps Influent | NA | Grey Water Feed Pumps Influent | mg/L | D | 4200 |  |  | 10 | No
EdwardSport | Plant Self-Monitoring | Total Dissolved Solid | 2016-09-14 | LP Grey Water Feed Pumps Influent | NA | LP Grey Water Feed Pumps Influent | mg/L | D | 830 | D | 2515 | 10 | No | D | 2515
EdwardSport | Plant Self-Monitoring | Total Dissolved Solid | 2016-09-14 | Outfall 501-Cyanide Destruct Pumps Effluent | Yes | Outfall 501-Cyanide Destruct Pumps Effluent | mg/L | ND | 10 |  |  | 10 | No
EdwardSport | Plant Self-Monitoring | Total Dissolved Solid | 2016-09-14 | RO Permeate Pumps Effluent | Yes | RO Permeate Pumps Effluent | mg/L | ND | 25 | ND | 17.5 | 10 | No | ND | 17.5
EdwardSport | Plant Self-Monitoring | Total Dissolved Solid | 2016-10-01 | Outfall 501-Cyanide Destruct Pumps Effluent | Yes | Outfall 501-Cyanide Destruct Pumps Effluent | mg/L | D | 30 | D | 30 | 10 | No | D | 30