## List
Available Online Water Quality Monitoring Instruments for Source Water and Distribution System Monitoring
-Some online water quality monitoring instruments utilize analytical methods that have been approved by EPA for regulatory compliance. Click on the following link for a list of approved
methods: | https://www.epa.gov/dwanalyticalmethods/approved-drinking-water-analytical-methods
-While efforts have been made to include all viable OWQM instruments, there may be omissions or errors. If you note an omission or error, or if you have questions about this list, please contact EPA staff.
Shaded rows indicate instruments that generate multiple parameter measurements.
Monitoring Application | Parameter Measured | Measuring Principle | Instrument Vendor | Instrument Model | Range | Reagent Required | Link to website
DSM | Alkalinity | Colorimetry | Hach | APA6000 Alkalinity Analyzer | 1-1,000 mg/L total alkalinity as CaCO3; 5-1,000 mg/L CaCO3 phenolphthalein alkalinity | Yes | http://www.hach.com/apa6000-alkalinity-analyzer/product-details?id=7640280829
DSM | Alkalinity | Infrared sensor | Teledyne Analytical Instruments | 6800 Process Alkalinity Analyzer | 1-1,000 mg/L CaCO3 | No | http://www.teledyne-ai.com/pdf/6800.pdf
DSM | Alkalinity | Potentiometric titration | Liquid Analysis Systems, Inc. | L450 OH Online Alkalinity Analyzer | 20-10,00 mg/L CaCO3 | Yes | https://www.liquidanalysis.com/online_chemical_process_analyzer_products_and_services.html
DSM and SWM | Ammonia | Amperometric | ATI Analytical Technology, Inc. | Q45 Dissolved Ammonia Monitor | 0-2.000 mg/L NH4 (minimum); 0-20.00 mg/L NH4 (maximum) | Yes | http://www.analyticaltechnology.com/analyticaltechnology/gas-water-monitors/product.aspx?ProductID=1048
DSM | Ammonia | Ion selective electrode | Hach | AMTAX Ammonium Analyzer | 0.05-20.0 mg/L NH4-N | Yes | http://www.hach.com/amtax-sc-ammonium-analyzer-0-05-20mg-l-nh4-n-one-channel-continuous-sample-115-230v/product?id=7640092928
DSM | Ammonia | Colorimetry | Hach | 5500sc Ammonia Monochloramine Analyzer | 0.01-2 mg/L N | No | http://www.hach.com/5500-sc-ammonia-monochloramine-analyzer-1-channel/product?id=20731982901
DSM | Ammonia | Ion selective electrode | Intellitect | Intellisonde | 0-20.0 mg/L NH4-N | No | http://www.intellitect-water.co.uk/our-product
DSM and SWM | Ammonia | Ion selective electrode | s::can | ammo::lyser™ eco | 0.02-2 mg/L NH4-N (drinking water); 0.1-20 mg/L NH4-N (surface water) | No | http://www.s-can.at/text.php?kat=5&id=26&langcode=
SWM | Ammonia | Ion selective electrode | s::can | ammo::lyser™ pro | 0.1-2 mg/L NH4-N (surface water) | No | http://www.s-can.at/text.php?kat=5&id=26&langcode=
DSM | Ammonia | Ion selective electrode | SWAN Analytical Instruments | Swansensor Ammonium | 0.1-1,000 mg/L NH4-N | Yes | http://www.swan-analytical-usa.com/Catalog/en/ProductDetail.aspx?subchapter=Chapter_potablewater&prdtGroup=Grp_Ammonium_Potable&prdtSubGroup=SingleComp_AMI_ISE_Ammonium&prdtName=A-87.710.010
SWM | Ammonia | Ion selective electrode | YSI Environmental | EXO Ammonium Smart Sensor | 0-200 mg/L NH4 | Yes | https://www.ysi.com/Product/id-599710/EXO-Ammonium-Smart-Sensor
DSM and SWM | Bacteria | Fluorometry | MicroLan | BACTcontrol | 1-5 cfu/100 mL | Yes | http://www.microlan.nl/producten.php
DSM | Bacteria | Absorption spectroscopy | ZAPS Technologies | LiquID Station 1000-200 (Finished Drinking Water) | 0.1 to 2.3×107 MPN/100 mls | No | http://www.zapstechnologies.com/drinking-water-finished/
SWM | Bacteria | Absorption spectroscopy | ZAPS Technologies | LiquID Station 1500-100 (Environmental/Source Water) | 0.1 to 2.3×107 MPN/100 mls | No | http://www.zapstechnologies.com/industries/environmental/
DSM | Chlorine residual | Absorption spectroscopy | ZAPS Technologies | LiquID Station 1000-200 (Finished Drinking Water) | 0.01-11.0 mg/L Cl2 | No | http://www.zapstechnologies.com/drinking-water-finished/
DSM | Chlorine residual | Amperometric | ATI Analytical Technology, Inc. | Q46H/62-63 Residual Chlorine Monitor | 0-200.0 mg/L Cl2 | No | http://www.analyticaltechnology.com/analyticaltechnology/gas-water-monitors/product.aspx?ProductID=1037
DSM | Chlorine residual | Amperometric | ATI Analytical Technology, Inc. | Q45 Dissolved Ammonia Monitor | 0-10.00 mg/L NH2Cl | Yes | http://www.analyticaltechnology.com/analyticaltechnology/gas-water-monitors/product.aspx?ProductID=1048
DSM | Chlorine residual | Amperometric | Emerson-Rosemount | Rosemount™ 499ACL Free Chlorine Sensor | 0-10 mg/L Cl2 | No | http://www.emerson.com/catalog/en-us/automation-solutions/measurement-instrumentation/liquid-analysis-sensors/rosemount-499acl-sensor
DSM | Chlorine residual | Amperometric | Emerson-Rosemount | Rosemount™ FCL Free Chlorine Measuring System | 0-10 mg/L Cl2 | No | http://www.emerson.com/catalog/en-us/rosemount-fcl-measuring-system
DSM | Chlorine residual | Amperometric | Intellitect | Intellisonde | 0-5 mg/L Cl2 | No | http://www.intellitect-water.co.uk/our-product
DSM | Chlorine residual | Amperometric | s::can | chlori::lyser™ | 0-20 mg/L Cl2 | No | http://www.s-can.at/text.php?kat=5&id=41&langcode=
DSM | Chlorine residual | Amperometric | SWAN Analytical Instruments | Monitor AMI Trides | 0.00-5.00 mg/L Cl2 | No | http://www.swan-analytical-usa.com/Catalog/en/ProductDetail.aspx?subchapter=Chapter_potablewater&prdtGroup=Group_Chlor_Potable&prdtSubGroup=&prdtName=A-26.111.000
DSM | Chlorine residual | Amperometric | SWAN Analytical Instruments | Monitor AMI Trides; compact | 0.00-5.00 mg/L Cl2 | No | http://www.swan-analytical-usa.com/Catalog/en/ProductDetail.aspx?subchapter=Chapter_potablewater&prdtGroup=Group_Chlor_Potable&prdtSubGroup=&prdtName=A-26.111.100
DSM | Chlorine residual | Colorimetry | Hach | CL17 Total Chlorine Analyzer | 0-5 mg/L Cl2 | Yes | http://www.hach.com/cl17-with-reagents-for-total-chlorine/product?id=7640295862&callback=qs
DSM | Chlorine residual | Colorimetry | Hach | 5500sc Ammonia Monochloramine Analyzer | 0.1 to 10.0 mg/L Cl2 | No | http://www.hach.com/5500-sc-ammonia-monochloramine-analyzer-1-channel/product-details?id=20731982901&callback=qs
DSM | Chlorine residual | Colorimetry | SWAN Analytical Instruments | Analyzer AMI Codes-II | 0.00-5.00 mg/L Cl2 | Yes | http://www.swan-analytical-usa.com/Catalog/en/ProductDetail.aspx?subchapter=Chapter_potablewater&prdtGroup=Group_Chlor_Potable&prdtSubGroup=&prdtName=A-25.441.100.0
DSM | Chlorine residual | Colorimetry | SWAN Analytical Instruments | Analyzer AMI Codes-II TC | 0.00-5.00 mg/L Total Cl2 | Yes | http://www.swan-analytical-usa.com/Catalog/en/ProductDetail.aspx?subchapter=Chapter_potablewater&prdtGroup=Group_Chlor_Potable&prdtSubGroup=&prdtName=A-25.441.600.0
DSM | Chlorine residual | Colorimetry | SWAN Analytical Instruments | Analyzer AMI Codes-II CC | 0.00-5.00 mg/L Combined Cl2 | Yes | http://www.swan-analytical-usa.com/Catalog/en/ProductDetail.aspx?subchapter=Chapter_potablewater&prdtGroup=Group_Chlor_Potable&prdtSubGroup=&prdtName=A-25.441.700.0
DSM | Chlorine residual | Colorimetry | WTW | Drinking Water Analyzer Chlorine 3000 | 0-10 mg/L Cl2 | Yes | http://www.wtw.com/en/products/product-categories/analyzer/drinking-water-analyzer/chlorine-3000.html
DSM and SWM | Dissolved oxygen | Amperometric | ATI Analytical Technology, Inc. | Q46D Dissolved Oxygen Monitor-Clark Sensor | 0-40 mg/L O2 | No | http://www.analyticaltechnology.com/analyticaltechnology/gas-water-monitors/product.aspx?ProductID=1068
DSM and SWM | Dissolved oxygen | Amperometric | Hach | 550 Clark DO Sensor | 0-40 mg/L O2 | No | http://www.hach.com/dissolved-oxygen-sensors/5500-clark-do-sensors/family?productCategoryId=35546331648
DSM | Dissolved oxygen | Amperometric | Intellitect | Intellisonde | 0-100% Saturation | No | http://www.intellitect-water.co.uk/our-product
DSM and SWM | Dissolved oxygen | Amperometric | OTT-Hydromet | Hydrolab MS5- Multiparameter Mini Sonde | 0-50 mg/L O2 | No | http://www.ott.com/en-us/products/water-quality-2/hydrolab-ms5-mulitparameter-mini-sonde-57/
DSM | Dissolved oxygen | Amperometric | SWAN Analytical Instruments | Swansensor Oxysafe 1000 | 0-20 mg/L O2 | No | http://www.swan-analytical-usa.com/Catalog/en/ProductDetail.aspx?subchapter=Chapter_potablewater&prdtGroup=Group_Oxygen_PotableAndWaste&prdtSubGroup=Grp_Components_Oxygen_Potable-Waste&prdtName=A-87.232.011
DSM and SWM | Dissolved oxygen | Amperometric | WTW | TirOxmatic 700 IQ | 0-20 mg/L O2 | No | http://www.wtw.com/en/products/product-categories/sensor-technology/digital-iq-sensors-online/iq-electro-chemical-oxygen-sensors.html?mobile=1
DSM and SWM | Dissolved oxygen | Fluorometry | ATI Analytical Technology, Inc. | Q46D Dissolved Oxygen Monitor-Optical Sensor | 0-40 mg/L O2 | No | http://www.analyticaltechnology.com/analyticaltechnology/gas-water-monitors/product.aspx?ProductID=1068
DSM and SWM | Dissolved oxygen | Fluorometry | s::can | oxi::lyser™ | 0-25 mg/L O2 | No | http://www.s-can.at/text.php?kat=5&id=36&langcode=
DSM and SWM | Dissolved oxygen | Fluorometry | WTW | FDO 700 IQ | 0-20 mg/L O2 | No | http://www.wtw.com/en/products/product-categories/sensor-technology/digital-iq-sensors-online/iq-optical-dissolved-oxygen-sensors.html
DSM and SWM | Dissolved oxygen | Luminescence | Hach | LDO sc Luminescent DO Sensor | 0-20.0 mg/L O2 | No | http://www.hach.com/dissolved-oxygen-sensors/ldo-sc-luminescent-dissolved-oxygen-sensors/family?productCategoryId=35546331647
SWM | Dissolved oxygen | Luminescence | YSI Environmental | EXO Optical Dissolved Oxygen Smart Sensor | 0-50 mg/L O2 | No | https://www.ysi.com/Product/id-599100-01/EXO-Optical-Dissolved-Oxygen-Smart-Sensor
SWM | Dissolved oxygen | Luminescence | YSI Environmental | 600OMS V2 Optical Monitoring Sonde | 0-50 mg/L O2 | No | https://www.ysi.com/600OMS-V2
SWM | Dissolved oxygen | Luminescence | YSI Environmental | 6150 ROX Dissolved Oxygen Sensor | 0-50 mg/L O2 | No | https://www.ysi.com/rox
DSM and SWM | Hydrocarbons | Fluorometry | Advanced Sensors | EX-100P and EX-1000P | 0-20,000 mg/L | No | http://www.advancedsensors.co.uk/products/in-line-probe/ex-100p/
DSM and SWM | Hydrocarbons | Fluorometry | Modern Water, Inc. | PetroChek™ PAH | 0.05-200 μg/L Carbazole | No | http://www.modernwater.com/assets/downloads/Factsheets/MW_Factsheet_petrochek_PAH.pdf
DSM and SWM | Hydrocarbons | Fluorometry | Modern Water, Inc. | PetroChek™ BTEX | 0.003-50 mg/L BTEX | No | http://www.modernwater.com/assets/downloads/Factsheets/MW_Factsheet_petrochek_BTEX.pdf
DSM and SWM | Hydrocarbons | Fluorometry | Turner Designs | Cyclops-7™ | 0-1.5 mg/L PTSA; 7 mg/L 1,5 Napthalene Disulfonic Disodium Salt; >100 mg/L BTEX | No | http://www.turnerdesigns.com/products/submersible-fluorometer/cyclops-7-submersible-fluorescence-and-turbidity-sensors
DSM and SWM | Hydrocarbons | Absorption Spectroscopy | s::can | spectro::lyser™ | 0-500 Abs/m | No | http://www.s-can.at/text.php?kat=5&id=21&langcode=
DSM and SWM | Hydrocarbons | Absorption spectroscopy | Teledyne Analytical Instruments | Model 6600 Oil-in-Water Analyzer System | 0-200 mg/L oil in water | No | http://www.teledyne-ai.com/products/6600.asp
SWM | Hydrocarbons | Absorption spectroscopy | ZAPS Technologies | LiquID Station 1500-100 (Environmental/Source Water) | 0.5->100 DFU | No | http://www.zapstechnologies.com/industries/environmental/
DSM | Nitrate/nitrite | Absorption spectroscopy | ABB Inc | AV400 Series Nitrate Monitor | 0-100 mg/L NO3-N | No | http://new.abb.com/products/measurement-products/analytical/continuous-liquid-analyzer/av450-single-channel-nitrate-monitor
DSM | Nitrate/nitrite | Absorption spectroscopy | Real Tech Inc. | Real Nitrate Sensor GL2010.Nitrate | 0-80 mg/L NO3-N | No | http://realtechwater.com/nitrate-sensor/
DSM | Nitrate/nitrite | Absorption spectroscopy | Real Tech Inc. | Real Nitrate Sensor GL2020.Nitrate | 0-40 mg/L NO3-N | No | http://realtechwater.com/nitrate-sensor/
DSM | Nitrate/nitrite | Absorption spectroscopy | Real Tech Inc. | Real Nitrate Sensor GL2040.Nitrate | 0-20 mg/L NO3-N | No | http://realtechwater.com/nitrate-sensor/
DSM | Nitrate/nitrite | Absorption spectroscopy | Real Tech Inc. | Real Nitrate Sensor GL2080.Nitrate | 0-10 mg/L NO3-N | No | http://realtechwater.com/nitrate-sensor/
DSM | Nitrate/nitrite | Absorption spectroscopy | Real Tech Inc. | Real Nitrate Sensor GL3500.Nitrate | 0-1.3 mg/L NO3-N | No | http://realtechwater.com/nitrate-sensor/
DSM | Nitrate/nitrite | Absorption spectroscopy | Real Tech Inc. | Real Nitrate Sensor GL4000.Nitrate | 0-0.2 mg/L NO3-N | No | http://realtechwater.com/nitrate-sensor/
DSM and SWM | Nitrate/nitrite | Absorption spectroscopy | s::can | spectro::lyser™ | 0-7 mg/L NO3-N, 0-2 mg/L NO2-N (drinking water); 0-100 mg/L NO3-N, 0-40 mg/L NO2-N (surface water); 0-20 mg/L NO3-N, 0-5 mg/L NO2-N (ground water) | No | http://www.s-can.at/text.php?kat=5&id=21&langcode=
DSM and SWM | Nitrate/nitrite | Absorption spectroscopy | s::can | nitro::lyser™ | 0-20 mg/L NO3-N (drinking water); 0-100 mg NO3-N (surface water) | No | http://www.s-can.at/text.php?kat=5&id=24&langcode=
DSM and SWM | Nitrate/nitrite | Absorption spectroscopy | s::can | multi::lyser™ | 0-20 mg/L NO3-N (drinking water); 0-100 mg NO3-N (surface water) | No | http://www.s-can.at/text.php?kat=5&id=23&langcode=
SWM | Nitrate/nitrite | Absorption spectroscopy | YSI Environmental | NitraVis | 0-60 mg/L NO3/N (influent); 0-150 mg/L NO3-N (effluent) | No | https://www.ysi.com/nitravis
DSM | Nitrate/nitrite | Absorption spectroscopy | ZAPS Technologies | LiquID Station 1000-200 (Finished Drinking Water) | 0.03-50 mg/L NO3-N | No | http://www.zapstechnologies.com/drinking-water-finished/
SWM | Nitrate/nitrite | Absorption spectroscopy | ZAPS Technologies | LiquID Station 1500-100 (Environmental/Source Water) | 0.03-50 mg/L NO3-N | No | http://www.zapstechnologies.com/industries/environmental/
DSM | Nitrate/nitrite | Ion selective electrode | Hach | NISE sc ISE Nitrate Probe | 0-1,000 mg/L NO3-N | No | http://www.hach.com/nise-sc-ise-nitrate-probe/product?id=14667082654&callback=qs
DSM | Nitrate/nitrite | Ion selective electrode | Intellitect | Intellisonde | 0.1-20 mg/L NO3-N | No | http://www.intellitect-water.co.uk/our-product
DSM and SWM | Nitrate/nitrite | Ion selective electrode | s::can | ammo::lyser™ eco | 0.1-200 mg NO3-N (drinking water and surface water) | No | http://www.s-can.at/text.php?kat=5&id=26&langcode=
SWM | Nitrate/nitrite | Ion selective electrode | s::can | ammo::lyser™ pro | 0-200 mg/L NO3/N (surface water) | No | http://www.s-can.at/text.php?kat=5&id=26&langcode=
DSM | Nitrate/nitrite | Ion selective electrode | SWAN Analytical Instruments | Swansensor Nitrate | 0.1-1,000 mg/L NO3-N | Yes | http://www.swan-analytical-usa.com/Catalog/en/ProductDetail.aspx?subchapter=Chapter_potablewater&prdtGroup=Group_Nitrat&prdtSubGroup=SingleComp_AMI_ISE_Nitrat&prdtName=A-87.730.010
SWM | Nitrate/nitrite | Ion selective electrode | YSI Environmental | NitraLyt® Plus | 1-1,000 mg/L NO3-N | No | https://www.ysi.com/nitralyt
SWM | Nitrate/nitrite | Ion selective electrode | YSI Environmental | EXO Nitrate Smart Sensor | 0-200 mg NO3-N | Yes | https://www.ysi.com/Product/id-599709/EXO-Nitrate-Smart-Sensor
DSM and SWM | Ortho-phosphate | Colorimetry | ABB Inc | Aztec 600 Phosphate Analyzer AW636 | 0-50 mg/L PO4 | Yes | http://www.abb.com/product/seitp330/212e86a06925317bc1257d97004d1ebe.aspx
DSM and SWM | Ortho-phosphate | Colorimetry | Hach | 5500sc Phosphate Analyzer | 0.004-5 mg/L PO4 (low range); 0.2-50 mg/L PO4 (high range) | Yes | http://www.hach.com/phosphate-analyzers/5500-sc-phosphate-analyzer/family?productCategoryId=35546907032
DSM and SWM | Ortho-phosphate | Colorimetry | Hach | PHOSPHAX sc Phosphate Analyzer | 0.05-15 mg/L PO4 (low range); 1-50 mg/L PO4 (high range) | Yes | http://www.hach.com/phosphate-analyzers/phosphax-sc-phosphate-analyzer/family?productCategoryId=35546907029
DSM | Ortho-phosphate | Colorimetry | SWAN Analytical Instruments | Analyzer AMI Phosphate- II | 0.01-10 mg/L PO4 | Yes | http://www.swan-analytical-usa.com/Catalog/en/ProductDetail.aspx?subchapter=Chapter_potablewater&prdtGroup=Grp_Phosphate_Potable-Pool-Cooling-Waste&prdtSubGroup=&prdtName=A-25.421.100.0
DSM and SWM | Oxidation-reduction potential | Ion selective electrode | ATI Analytical Technology, Inc. | Q46P/R pH/ORP Monitor | -1,000-+2,000 mV | Yes | http://www.analyticaltechnology.com/sys/docs/1867/ATI_Q46PR.pdf
DSM | Oxidation-reduction potential | Ion selective electrode | Hach | Combination pH/ORP Sensor | -2,000-+2,000 mV | Yes | http://www.hach.com/ph-orp-sensors/3-4-in-combination-ph-orp-sensors/family?productCategoryId=35546331631
DSM | Oxidation-reduction potential | Ion selective electrode | Hach | Differential ORP Sensor | -1,500 -+1,500 mV | Yes | http://www.hach.com/ph-orp-sensors/differential-orp-sensors/family?productCategoryId=35546331625
DSM | Oxidation-reduction potential | Ion selective electrode | Hach | sensION+ Probe | -2,000-2,000 mV | Yes | http://www.hach.com/sension-meters-and-probes/sension-probes/family?productCategoryId=35547408096
DSM | Oxidation-reduction potential | Ion selective electrode | Intellitect | Intellisonde | -1,000-+1,000 mV | No | http://www.intellitect-water.co.uk/our-product
DSM and SWM | Oxidation-reduction potential | Ion selective electrode | s::can | redo::lyser™ | -500-+500 mV (drinking water); -1,000-+1,000 mV (surface water) | No | http://www.s-can.at/text.php?kat=5&id=38&langcode=
DSM | Oxidation-reduction potential | Ion selective electrode | SWAN Analytical Instruments | Swansensor Redox | -400-+1,200 mV | Yes | http://www.swan-analytical-usa.com/Catalog/en/ProductDetail.aspx?subchapter=Chapter_potablewater&prdtGroup=Grp_Redox_Potable&prdtSubGroup=Sub_Grp_Redox_Potable_CompSysIntegration&prdtName=A-87.420.200
SWM | Oxidation-reduction potential | Ion selective electrode | YSI Environmental | SensoLyt® Sensor | -2,000-+2,000 mV | No | https://www.ysi.com/sensolyt
SWM | Oxidation-reduction potential | Ion selective electrode | YSI Environmental | EXO pH & ORP Smart Sensor | -999-+999 mV | Yes | https://www.ysi.com/Product/id-599705/EXO-pH--ORP-Smart-Sensor
SWM | Oxidation-reduction potential | Ion selective electrode | YSI Environmental | 6565 pH/ORP Sensor | -999-+999 mV | Yes | https://www.ysi.com/Accessory/id-6565/6565-pHORP-Sensor
DSM and SWM | pH | Ion selective electrode | ATI Analytical Technology, Inc. | Q22PX pH Universal Sensor | 0-14.00 pH | Yes | http://www.analyticaltechnology.com/analyticaltechnology/gas-water-monitors/product.aspx?ProductID=1031
DSM | pH | Ion selective electrode | Hach | Analog Differential pH sensor | -2-14.0 pH | Yes | http://www.hach.com/ph-orp-sensors/analog-differential-ph-sensors/family?productCategoryId=35546331632
DSM | pH | Ion selective electrode | Hach | Combination pH/ORP Sensor | 0-14 pH | Yes | http://www.hach.com/ph-orp-sensors/3-4-in-combination-ph-orp-sensors/family?productCategoryId=35546331631
DSM | pH | Ion selective electrode | Hach | Digital Differential pH Sensor | -2-14.0 pH | Yes | http://www.hach.com/ph-orp-sensors/digital-differential-ph-sensors/family?productCategoryId=35546331624
DSM | pH | Ion selective electrode | Intellitect | Intellisonde | 2-12 pH | No | http://www.intellitect-water.co.uk/our-product
DSM and SWM | pH | Ion selective electrode | s::can | pH::lyser ™ | 5-9 pH (drinking water); 4-10 pH (surface water) | No | http://www.s-can.at/text.php?kat=5&id=37&langcode=
DSM and SWM | pH | Ion selective electrode | s::can | ammo::lyser™ eco | 4-10 pH | No | http://www.s-can.at/text.php?kat=5&id=26&langcode=
SWM | pH | Ion selective electrode | s::can | ammo::lyser™ pro | 4-10 pH | No | http://www.s-can.at/text.php?kat=5&id=26&langcode=
DSM | pH | Ion selective electrode | SWAN Analytical Instruments | Swansensor pH | 1-13 pH | Yes | http://www.swan-analytical-usa.com/Catalog/en/ProductDetail.aspx?subchapter=Chapter_potablewater&prdtGroup=Group_pH_Potable&prdtSubGroup=Subgroup_pH_Potable-Pool-Cooling_CompSysIntegration&prdtName=A-87.120.200
SWM | pH | Ion selective electrode | YSI Environmental | EXO pH Smart Sensor | 0-14 pH | Yes | https://www.ysi.com/Product/id-599701/EXO-pH-Smart-Sensor
SWM | pH | Ion selective electrode | YSI Environmental | EXO pH & ORP Smart Sensor | 0-14 pH | Yes | https://www.ysi.com/Product/id-599705/EXO-pH--ORP-Smart-Sensor
SWM | pH | Ion selective electrode | YSI Environmental | 6561 pH sensor | 0-14 pH | Yes | https://www.ysi.com/Accessory/id-6561/6561-pH-Sensor
SWM | Photosynthetic pigments | Fluorometry | bbe Moldaenke | Algae Online Analyser | 0-200 µg/L chlorophyll-a/l | Yes | http://ppsystems.com/on-line-analyzers/
SWM | Photosynthetic pigments | Fluorometry | Chelsea Technologies Group Ltd | TriLux Fluorometer | 0-100 µg/L (Chlorophyll a inacetone) | No | http://www.chelsea.co.uk/allproduct/marine/fluorometers/trilux-fluorometer
SWM | Photosynthetic pigments | Fluorometry | microLAN | ALGControl | 0-200 µg/L chl-a | Yes | http://www.microlan.nl/producten.php
SWM | Photosynthetic pigments | Fluorometry | OTT-Hydromet | Hydrolab MS5- Multiparameter Mini Sonde | 150-2,000,000 cells/mL (low sensitivity); 150-200,000 (medium sensitivity); 150-20,000 (high sensitivity) | Yes | http://www.ott.com/en-us/products/water-quality-2/hydrolab-ms5-mulitparameter-mini-sonde-57/
SWM | Photosynthetic pigments | Fluorometry | Turner Designs | Cyclops-7™ | 0-500 μg/L chlorophyll (blue excitation); >500 μg/L (red excitation); 0-4,5000 μg/L phycocyanin pigment | Yes | http://www.turnerdesigns.com/products/submersible-fluorometer/cyclops-7-submersible-fluorescence-and-turbidity-sensors
SWM | Photosynthetic pigments | Fluorometry | Turner Designs | Enviro-T2™ In-Line Fluorometer | 0-100 μg/L | Yes | http://www.turnerdesigns.com/products/online-and-inline-fluorometers/algaewatch-online-fluorometer
SWM | Photosynthetic pigments | Fluorometry | YSI Environmental | EXO Total Algae PC Smart Sensor | 0-100 RFU; 0-100 µg/L PC | Yes | https://www.ysi.com/Product/id-599102-01/EXO-Total-Algae-PC-Smart-Sensor
SWM | Photosynthetic pigments | Absorption spectroscopy | ZAPS Technologies | LiquID Station 1500-100 (Environmental/Source Water) | 0.3->100μg/L Chlorophyll a; 3->100 μg/L Chlorophyll b | No | http://www.zapstechnologies.com/industries/environmental/
DSM and SWM | Refractive index | Mach Zehnder interferometer | Optiqua | EventLab Online | 10-7 Refractive Index Units | No | http://www.optiqua.com/
SWM | Streaming current (zeta potential) | Streaming current sensor | Hach | AF7000 Streaming Current Monitor | 0.05-5 μA | No | http://www.hach.com/streaming-current/af7000-streaming-current-monitor/family?productCategoryId=35547372731
SWM | Streaming current (zeta potential) | Electrophoretic light scattering | Malvern | Zetasizer WT | -500 mV-+500 mV | No | http://www.malvern.com/en/products/product-range/zetasizer-range/zetasizer-wt/
DSM and SWM | Specific conductance | Conductivity bridge or cell | ATI Analytical Technology, Inc. | Q46C4 4E Conductivity Monitor | 0-2,000 μS | Yes | http://www.analyticaltechnology.com/analyticaltechnology/gas-water-monitors/product.aspx?ProductID=1078
DSM | Specific conductance | Conductivity bridge or cell | Hach | General Purpose Contacting Conductivity Sensor | 0-200,000 μS/cm | No | http://www.hach.com/general-purpose-contacting-conductivity-sensor-ryton-body-k-10-0-cell-constant/product?id=7640077976
DSM | Specific conductance | Conductivity bridge or cell | Intellitect | Intellisonde | 20-10,000 μS/cm | No | http://www.intellitect-water.co.uk/our-product
DSM and SWM | Specific conductance | Conductivity bridge or cell | s::can | condu::lyser™ | 0-5,000 μS/cm (drinking water); 0-500,000 μS/cm (surface water) | No | http://www.s-can.at/text.php?kat=5&id=39&langcode=
DSM | Specific conductance | Conductivity bridge or cell | SWAN Analytical Instruments | Swansensor Shurecon P | 0.1 μS/cm-100 mS/cm | Yes | http://www.swan-analytical-usa.com/Catalog/en/ProductDetail.aspx?subchapter=Chapter_potablewater&prdtGroup=Grp_Cond_Potable-Pool&prdtSubGroup=SubGrp_Conductivity_Potable_PartsSysIntegration&prdtName=A-87.342.110
DSM | Specific conductance | Conductivity bridge or cell | SWAN Analytical Instruments | Swansensor Shurecon S | 0.1 μS/cm-100 mS/cm | Yes | http://www.swan-analytical-usa.com/Catalog/en/ProductDetail.aspx?subchapter=Chapter_potablewater&prdtGroup=Grp_Cond_Potable-Pool&prdtSubGroup=SubGrp_Conductivity_Potable_PartsSysIntegration&prdtName=A-87.341.000
SWM | Specific conductance | Conductivity bridge or cell | YSI Environmental | TetraCon® | 10 μS/cm-500 mS/cm | No | https://www.ysi.com/tetracon
SWM | Specific conductance | Conductivity bridge or cell | YSI Environmental | EXO Conductivity and Temperature Smart Sensor | 0-200 mS/cm | Yes | https://www.ysi.com/Product/id-599870/EXO-Conductivity--Temperature-Smart-Sensor
SWM | Specific conductance | Conductivity bridge or cell | YSI Environmental | EXO Wiped Conductivity and Temperature Sensor | 0-100 mS/cm | Yes | https://www.ysi.com/WipedCT
SWM | Specific conductance | Conductivity bridge or cell | YSI Environmental | 6560 Temperature/ Conductivity Sensor | 0-100 mS/cm | No | https://www.ysi.com/Accessory/id-6560/6560-TemperatureConductivity-Sensor
DSM and SWM | Spectral absorbance | Absorption spectroscopy | Real Tech Inc. | Real Spectrum Sensor | 0-13 Abs/cm | No | http://realtechwater.com/spectrum-sensor/
DSM and SWM | Spectral absorbance | Absorption spectroscopy | s::can | spectro::lyser™ | 0-25 Abs/cm (drinking water); 0-500 Abs/cm (surface water); 0-70 Abs/cm (ground water) | No | http://www.s-can.at/text.php?kat=5&id=21&langcode=
DSM | Temperature | Thermocouple | Hach | Digital Differential pH Sensor | 0-50° C | No | http://www.hach.com/ph-orp-sensors/digital-differential-ph-sensors/family?productCategoryId=35546331624
SWM | Temperature | Thermocouple | s::can | oxi::lyser™ | 0-50° C | No | http://www.s-can.at/text.php?kat=5&id=36&langcode=
DSM | Temperature | Thermocouple | SWAN Analytical Instruments | Swansensor Pt 100 | 0-100° C | No | http://www.swan-analytical-usa.com/Catalog/en/ProductDetail.aspx?subchapter=Chapter_potablewater&prdtGroup=Group_pH_Potable&prdtSubGroup=Subgroup_pH_Potable-Pool-Cooling_CompSysIntegration&prdtName=A-87.010.200
SWM | Temperature | Thermistor | YSI Environmental | EXO Wiped Conductivity and Temperature Sensor | -5-50° C | No | https://www.ysi.com/WipedCT
SWM | Temperature | Thermistor | YSI Environmental | EXO Conductivity and Temperature Smart Sensor | -5-50° C | No | https://www.ysi.com/Product/id-599870/EXO-Conductivity--Temperature-Smart-Sensor
SWM | Temperature | Thermistor | YSI Environmental | 6560 Temperature/ Conductivity Sensor | -5-50° C | No | https://www.ysi.com/Accessory/id-6560/6560-TemperatureConductivity-Sensor
DSM and SWM | Total organic carbon/Dissolved organic carbon | Absorption spectroscopy | Real Tech Inc. | Real UV TOC Sensor | 0-1,000 mg/L TOC (TOC only) | No | http://realtechwater.com/uv-toc-sensor/
DSM and SWM | Total organic carbon/Dissolved organic carbon | Absorption spectroscopy | s::can | spectro::lyser™ | 0-8 mg/L TOC, 0-6 mg/L DOC (drinking water); 0-180 mg/L TOC, 0-140 mg/L DOC (surface water); 0-20 mg/L TOC, 0-15 mg/L DOC (ground water) | No | http://www.s-can.at/text.php?kat=5&id=21&langcode=
DSM and SWM | Total organic carbon/Dissolved organic carbon | Absorption spectroscopy | s::can | carbo::lyser™ | 0-20 mg/L TOC, 0-15 mg/L DOC (drinking water); 0-180 mg/L TOC, 0-140 mg/L DOC (surface water) | No | http://www.s-can.at/text.php?kat=5&id=22&langcode=
DSM and SWM | Total organic carbon/Dissolved organic carbon | Absorption spectroscopy | s::can | multi::lyser™ | 0-20 mg/L TOC, 0-15 mg/L DOC (drinking water); 0-180 mg/L TOC, 0-140 mg/L DOC (surface water) | No | http://www.s-can.at/text.php?kat=5&id=23&langcode=
DSM and SWM | Total organic carbon/Dissolved organic carbon | Absorption spectroscopy | s::can | i::scan™ | 0-25 mg/L TOC; 0-12 mg DOC/L | No | http://i-scan.at/
SWM | Total organic carbon/Dissolved organic carbon | Absorption spectroscopy | YSI Environmental | IQ SensorNet CarboVis® Sensor | 0.5-4,000.0 mg/L TOC | No | https://www.ysi.com/carbovis
DSM | Total organic carbon/Dissolved organic carbon | Absorption spectroscopy | ZAPS Technologies | LiquID Station 1000-200 (Finished Drinking Water) | 0.02-100 mg/L TOC (TOC only) | No | http://www.zapstechnologies.com/drinking-water-finished/
SWM | Total organic carbon/Dissolved organic carbon | Absorption spectroscopy | ZAPS Technologies | LiquID Station 1500-100 (Environmental/Source Water) | 0.02-100 mg/L TOC (TOC only) | No | http://www.zapstechnologies.com/industries/environmental/
DSM | Total organic carbon/Dissolved organic carbon | Nondispersive infrared sensor | Hach | astroTOC UV Analyzer | 0-20,000 mg/L TOC | No | http://www.hach.com/hach-astrotoc-uv-analyzer/product?id=7640581560&callback=qs
DSM | Total organic carbon/Dissolved organic carbon | Nondispersive infrared sensor | Hach | 1950Plus Online TOC Analyzer | 0-20,000 mg/L TOC | Yes | http://www.hach.com/1950plus-online-toc-analyzer/product-details?id=7640595299&callback=qs
DSM and SWM | Toxicity | Bioassay | bbe Moldaenke | DaphTox II | n/a | No | http://ppsystems.com/toximetersbiomonitors/
DSM and SWM | Toxicity | Bioassay | bbe Moldaenke | Algae Toixmeter II | 0.2-200 μg/L chlorophyll | Yes | http://ppsystems.com/toximetersbiomonitors/
DSM | Toxicity | Bioassay | bbe Moldaenke | Fish Toximeter | n/a | No | http://ppsystems.com/toximetersbiomonitors/
DSM | Toxicity | Bioassay | bbe Moldaenke | ToxProtect64 | n/a | No | http://ppsystems.com/toximetersbiomonitors/
SWM | Toxicity | Bioassay | microLAN | TOXcontrol Biomonitor | n/a | Yes | http://www.microlan.nl/producten.php?gekozenArtID=24
DSM and SWM | Turbidity | Absorption spectroscopy | s::can | spectro::lyser™ | 0-60 NTU (drinking water); 0-1,400 NTU (surface water); 0-170 NTU (ground water) | No | http://www.s-can.at/text.php?kat=5&id=21&langcode=
DSM and SWM | Turbidity | Absorption spectroscopy | s::can | carbo::lyser™ | 0-60 NTU (drinking water); 0-1,400 NTU (surface water); 0-170 NTU (ground water) | No | http://www.s-can.at/text.php?kat=5&id=22&langcode=
DSM and SWM | Turbidity | Absorption spectroscopy | s::can | nitro::lyser™ | 0-170 NTU (drinking water); 0-1,400 NTU (ground water) | No | http://www.s-can.at/text.php?kat=5&id=24&langcode=
DSM and SWM | Turbidity | Absorption spectroscopy | s::can | color::lyser™ | 0-170 NTU (drinking water); 0-1,400 NTU (ground water) | No | http://www.s-can.at/text.php?kat=5&id=30&langcode=
DSM and SWM | Turbidity | Absorption spectroscopy | s::can | multi::lyser™ | 0-170 NTU (drinking water); 0-1,400 NTU (ground water) | No | http://www.s-can.at/text.php?kat=5&id=23&langcode=
DSM and SWM | Turbidity | Absorption spectroscopy | s::can | uv::lyser™ | 0-170 NTU (drinking water); 0-1,400 NTU (ground water) | No | http://www.s-can.at/text.php?kat=5&id=25&langcode=
DSM and SWM | Turbidity | Absorption spectroscopy | s::can | i::scan™ | 0-800 NTU/FTU | No | http://www.s-can.at/bildliste1.php?kat=10&id=283&langcode=
DSM and SWM | Turbidity | Absorption spectroscopy | Turner Designs | Cyclops-7™ | 0-1,500 NTU | Yes | http://www.turnerdesigns.com/products/submersible-fluorometer/cyclops-7-submersible-fluorescence-and-turbidity-sensors
DSM | Turbidity | Absorption spectroscopy | ZAPS Technologies | LiquID Station 1000-200 (Finished Drinking Water) | 0.1-100 m-1 ATU | No | http://www.zapstechnologies.com/drinking-water-finished/
SWM | Turbidity | Absorption spectroscopy | ZAPS Technologies | LiquID Station 1500-100 (Environmental/Source Water) | 0.1-100 m-1 ATU | No | http://www.zapstechnologies.com/industries/environmental/
SWM | Turbidity | Fluorometry | microLAN | ALGControl | 0-200 NTU | Yes | http://www.microlan.nl/producten.php
DSM and SWM | Turbidity | Nephelometry | ATI Analytical Technology, Inc. | Q46/76 Turbidity Monitor | 0-400 NTU | No | http://www.analyticaltechnology.com/analyticaltechnology/gas-water-monitors/product.aspx?ProductID=1083
DSM and SWM | Turbidity | Nephelometry | Hach | 1720E Turbidimeter | 0.001-100 NTU | Yes | http://www.hach.com/1720e-turbidimeter-with-sc200-controller-2-channel/product-details?id=7640457955&callback=qs
DSM | Turbidity | Nephelometry | Intellitect | Intellisonde | 0-50 NTU | No | http://www.intellitect-water.co.uk/our-product
DSM | Turbidity | Nephelometry | SWAN Analytical Instruments | Swansensor Turbiwell 7027 | 0.000-200.0 FNU/NTU | No | http://www.swan-analytical-usa.com/Catalog/en/ProductGroupOverview.aspx?subchapter=Chapter_potablewater&prdtGroup=Group_TurbidityPotable&prdtSubGroup=SubGrp_MonAMI_Turbiwell_7027&prdtName=
DSM | Turbidity | Nephelometry | SWAN Analytical Instruments | Swansensor Turbiwell W/LED | 0.000-100.0 NTU | No | http://www.swan-analytical-usa.com/Catalog/en/ProductDetail.aspx?subchapter=Chapter_potablewater&prdtGroup=Group_TurbidityPotable&prdtSubGroup=Group_Turbiwell_SensorTransmitter&prdtName=A-87.532.251
DSM | Turbidity | Nephelometry | WTW | Turbidity Meter TURB 2000 | 0-1,000 NTU | Yes | http://www.wtw.com/en/products/product-categories/analyzer/drinking-water-analyzer/turb-2000.html
DSM | Turbidity | Nephelometry | WTW | Turbidity Meter TURB 2020 | 0-1,000 NTU | Yes | http://www.wtw.com/en/products/product-categories/analyzer/drinking-water-analyzer/turb-2020.html
DSM | Turbidity | Nephelometry | WTW | Turbidity Meter TURB 2100 | 0-1,000 NTU | Yes | http://www.wtw.com/en/products/product-categories/analyzer/drinking-water-analyzer/turb-2100.html
DSM | Turbidity | Nephelometry | WTW | Turbidity Meter TURB 2110 | 0-10 NTU | Yes | http://www.wtw.com/en/products/product-categories/analyzer/drinking-water-analyzer/turb-2110.html
DSM | Turbidity | Nephelometry | WTW | Turbidity Meter TURB 2120 | 0-1,000 NTU | Yes | http://www.wtw.com/en/products/product-categories/analyzer/drinking-water-analyzer/turb-2120.html
SWM | Turbidity | Nephelometry | YSI Environmental | EXO Turbidity Smart Sensor | 0-4,000 FNU | Yes | https://www.ysi.com/Product/id-599101-01/EXO-Turbidity-Smart-Sensor
SWM | Turbidity | Nephelometry | YSI Environmental | 6136 Turbidity Sensor | 0-1,000 NTU | Yes | https://www.ysi.com/Accessory/id-6136/6136-Turbidity-Sensor
DSM and SWM | Volatile organic compounds | Gas chromatography | Inficon | CMS5000 Monitoring Sytem | n/a | Yes | http://products.inficon.com/en-us/nav-products/Product/Detail/CMS5000-Monitoring-System?path=Products%2Fpg-ChemicalDetection
DSM | Volatile organic compounds | Headspace gas equilibrium | Modern Water, Inc. | MultiSensor1100 | 1-1,000 μg/L | No | http://www.modernwater-monitoring.com/product_online-thm-voc.html
DSM | Volatile organic compounds | Headspace gas equilibrium | Modern Water, Inc. | MultiSensor1200 | 1-1,000 μg/L | No | http://www.modernwater-monitoring.com/product_online-thm-voc.html
Instructions
Disclaimer
Contact EPA Staff

## Instructions
Instructions
The table in this file provides an overview of available online water quality monitoring instruments that have been used for source water and distribution system monitoring. The instrument list can be filtered according to the criteria specified in the column headings. To accomplish this, select the arrow next to the heading to be filtered and check the desired filter to apply. A pop-up box will appear with a detailed description of the table heading when the cursor is moved over the heading.
Return to List

## Disclaimer
Disclaimer
The Water Security Division of the U.S. Environmental Protection Agency (EPA) has developed this list to help drinking water utilities learn about available online water quality monitoring instruments. This list does not impose legally binding requirements on any party. Neither the U.S. Government nor any of its employees, contractors, or their employees make any warranty, expressed or implied, or assume any legal liability or responsibility for any third party's use of any product included in this list, or represent that its use by such a party would not infringe on privately owned rights. Mention of trade names or commercial products does not constitute endorsement or recommendation for use.
Return to List