## Slide 1: U.S. Environmental Protection Agency (EPA) Revised Total Coliform Rule (RTCR) Template Factsheets --Templates for Use By Primacy Agencies—
TOPICS COVERED (Each factsheet is two pages)
          Requirements for Small Systems on Monthly Monitoring
          Requirements for Small Systems on Quarterly/Annual Monitoring
          Requirements for Seasonal Systems
          Repeat Monitoring Requirements for Small Systems
          Level 1 & Level 2 Assessments and Corrective Actions

## Slide 2: Disclaimer
Office of Water (MC-4606M)
EPA 816-F-16-004
www.epa.gov/safewater
May 2016
Theses Template Factsheets provide guidance to states, tribes and the U.S. Environmental Protection Agency (EPA) exercising primary enforcement responsibility under the Safe Drinking Water Act (SDWA) and contains EPA’s current policy recommendations for complying with the Revised Total Coliform Rule (RTCR). This document is not a regulation itself, nor does it change or substitute for those provisions and regulations. Thus, it does not impose legally binding requirements on EPA, states or the regulated community. This guidance does not confer legal rights or impose legal obligations upon any member of the public. While EPA has made every effort to ensure the accuracy of the discussion in this guidance, the obligations of the regulated community are determined by statutes, regulations or other legally binding requirements. In the event of a conflict between the discussion in this document and any statute or regulation, this document would not be controlling. Mention of trade names or commercial products does not constitute endorsement or recommendation for their use. This is a living document and may be revised periodically without public notice. EPA welcomes public input on this document at any time. Guidance provided in this document reflects provisions published on February 13, 2013, at 78 Federal Register 10269 and the minor corrections published on February 26, 2014, at 79 Federal Register 10665.

## Slide 3: Revised Total Coliform Rule (RTCR) Factsheets --templates for Primacy Agencies—
PURPOSE: EPA has developed the attached five RTCR template factsheets for use by primacy agencies. Primacy agencies should use these factsheets when conducting RTCR training or outreach with small public water systems (PWSs) that serve 1,000 or fewer persons. As templates, these factsheets were designed to permit primacy agencies to change all parts and language as appropriate.
TOPICS COVERED (Each factsheet is two pages)
    Requirements for Small Systems on Monthly Monitoring
    Requirements for Small Systems on Quarterly/Annual Monitoring
    Requirements for Seasonal Systems
    Repeat Monitoring Requirements for Small Systems
    Level 1 & Level 2 Assessments and Corrective Actions
INSTRUCTIONS
NOTE: There are [placeholders] throughout the factsheets. Enter primacy agency specific information into these textbox placeholders, or delete the placeholders.
  For modifying text or graphics: There are two views in which changes can be made:
  (1) Normal: In this view, click into any [textbox] to edit text.
    Insert your state logo: Click in the center of the box in the upper left corner where it says, [“Click icon to add state logo”]. Browse to the location of the logo on your computer and Insert the image (e.g., jpg, png, gif). If part of your logo is cut off, click on Drawing Tools/Format/Crop and adjust the box so the whole image is viewable. Adjust the size as needed.
    Input state information into textbox = [“For assistance, Please Contact Your State]
    Input URL for the state drinking water program into textbox = [“For more information, visit our website at:” ]. Located in the footer of the 2nd page of each factsheet.
    Complete all [placeholders] with your primacy agency specific information: Throughout each factsheet there are placeholders. These placeholders are in square brackets (i.e., [ ]) and the font is colored for easy identification.
  (2) Slide master: Go into the “slide master” window to edit the top banner (e.g., image, top horizontal line, and text) and bottom banners. Each factsheet has its own slide master.
  Font types used are Tahoma for headers, Calibri for the body. and Century Gothic for the left sidebar.
  Font size used: no smaller than 12, except for the Seasonal Systems factsheet.
  For printing and distribution
  The factsheets are designed in MS PowerPoint. The design of the factsheets are to show on a computer screen from edge-to-edge.
  For best results, before printing, save the factsheet(s) as a PDF. To save as PDF: select File, select Save as PDF. If you do not convert to PDF, some of the text and diagrams may not be visible when printed. Select Print on Both Sides (Flip pages on long edge) and Shrink oversized pages from the print screen. If printing in black/white, print in [grayscale] for best results.
  If printing straight from MS PowerPoint, some text boxes and diagrams may not print in its entirety due to the oversize formatting. To fix, select Full Page Slides under the print layout from the print screen, and select Scale to Fit Paper.
  When sending electronically for mass distribution: Convert/save the file as a PDF before electronic distribution. If you do not convert, the recipient will be able to make changes to the factsheet.

## Slide 4: Requirements for Small Systems on Monthly Monitoring
NOTE
The sample siting plan is subject to review and revision by [State name/drinking water program office].
STEP 1: Develop/Update Your Sample Siting Plan*
  Contact your state for assistance.
      Develop a sample siting plan and have it ready for use by April 1, 2016. If you already have a sample siting plan for the Total Coliform Rule (TCR), update this plan to meet the requirements of the RTCR.
        List the locations where you will take your samples (routine and repeat): Any repeat sampling location that is also used for GWR triggered source water monitoring must be included.
        Include your routine collection schedule: For example, “[PWS_ID] will collect one routine total coliform sample every first Monday of the calendar month.”
        Update to reflect changes at your PWS: The sample siting plan is a living document and should be updated to reflect changes at your PWS such as: major changes in population; a new or additional water source; infrastructure changes, such as a change in the distribution system (i.e. extended/abandoned lines) or pressure zones; or changes in disinfection or other treatment.
STEP 2: Collect Your Drinking Water Samples
  Know your RTCR routine sampling requirements.
      Collect at least one 100 ml routine drinking water sample every calendar month.
      Immediately send your sample to a state-certified lab that performs total coliform drinking water analyses.
        Remember the lab must begin analyzing the drinking water sample no later than the 30th hour from the collection time.
        If necessary, ship the sample overnight and refrigerate or ice the sample using “blue” ice (cooled to about 4° to 10° C).
ATTENTION!
All PWSs must comply with the RTCR requirements starting April 1, 2016.
Are you a PWS? Contact your state at [Placeholder for state info/website].
For assistance, please contact your state:
Name/Dept.:
Phone:
Email:
Additional RTCR Factsheets:
Requirements for Small Systems on Quarterly/ Annual Monitoring
Requirements for Seasonal Systems
Repeat Monitoring Requirements for Small Systems
Level 1 & Level 2 Assessments and Corrective Actions
Step 1
  Develop/update your sample siting plan.
Step 2
  Collect your drinking water samples.
Step 3
  Conduct required actions.
RTCR
  What to Do?
Who Does this Factsheet Apply To?
  All public water systems (PWSs), regardless of source, that serve 1,000 people or fewer and collect at least one routine total coliform (TC) sample monthly.
(RTCR)
FACTSHEET: Revised Total Coliform Rule

## Slide 5: STEP 3: Conduct Actions Required As a Result of Your Sampling
For more information, visit our website at: [Placeholder for state URL info]
March 2016
NOTES
If you are missing any routine or repeat sample, contact your state.
** Call your state on the same day you learn of the EC+ result, or by the end of the next business day or [Placeholder for state after-hours phone line or an alternative notification procedure] and tell them you received an EC+ result.
NO
    Continue with routine monitoring schedule, according to your sample siting plan.
NO
Call your state! You have to perform a Level 2 Assessment if the PWS has any of the following occurrences:
TC+ Routine and EC+ Repeat sample;
EC+ Routine and TC+ Repeat sample;
The PWS fails to take and analyze all 3 required repeat samples following an EC+ routine sample; or,
The PWS fails to test for E. coli when any repeat sample is TC+.
Within 30 days after you learned your PWS has triggered an assessment, a completed assessment form must be submitted to the state. Download the state form at [Placeholder for state URL info]. See the RTCR Factsheet: Level 1 & 2 Assessments and Corrective Actions.
YES**
Were any of the samples E. coli-positive (EC+)?
If any repeat sample is TC+ (or TC is present):
Call your state immediately and tell them you triggered an assessment. The state will help you identify which type of assessment is required.
See the RTCR Factsheet: Level 1 & 2 Assessments and Corrective Actions.
NOTE: You may have to comply with other requirements triggered by a TC+ sample (e.g. Public Notification, Recordkeeping).
Contact your state for more information.
For each TC+ sample, do the following TWO ACTIONS:
Make sure the lab tests each TC+ sample for E. coli; AND
Within 24 hours of being notified of the TC+ sample, take 3 repeat samples; * See the RTCR Factsheet: Repeat Monitoring Requirements for Small Systems.
YES
Was your routine sample total coliform-positive (TC+)?
RTCR

## Slide 6: Requirements for Small Systems on Quarterly/Annual Monitoring
NOTE
The sample siting plan is subject to review and revisions by [State name/drinking water program office].
STEP 1: Develop/Update Your Sample Siting Plan*
  Contact your state for assistance.
      Develop a sample siting plan and have it ready for use by April 1, 2016. If you already have a sample siting plan in use for the Total Coliform Rule (TCR), update this plan to meet the requirements of the RTCR.
        List the locations where you will take your samples (routine and repeat): Any repeat sampling location that is also used for GWR triggered source water monitoring must be included.
        Include your routine collection schedule: for example, the first Monday of every calendar quarter between Jan. 1 – March 31, April 1 – June 30, July 1 – Sept. 30, and Oct. 1 – Dec. 31; or every calendar year from Jan. 1 – Dec. 31.
        update to reflect changes at your PWS: The sample siting plan is a living document and should be updated to reflect changes at your PWS such as: major changes in population; a new or additional water source; infrastructure changes, such as a change in the distribution system (i.e. extended/abandoned lines) or pressure zones; or, changes in disinfection or other treatment.
        STEP 2: Collect Your Drinking Water Samples
Know your RTCR routine sampling requirements.
      Collect at least one 100 ml routine drinking water sample every quarter or once per year depending on whether you are on a quarterly or annual monitoring schedule, starting April 1, 2016.
      Immediately send your sample to a state-certified lab that performs total coliform drinking water analysis.
        Remember the lab must begin analyzing the drinking water sample no later than the 30th hour from the collection time.
        If necessary, ship the sample overnight and refrigerate or ice the sample using “blue” ice (cooled to about 4° to 10° C).
ATTENTION!
All PWSs must comply with the RTCR requirements starting April 1, 2016.
Are you a PWS? Contact your state at [Placeholder for state info/website].
For assistance, please contact your state:
Name/Dept.:
Phone:
Email:
Additional RTCR Factsheets:
Requirements for Small Systems on Monthly Monitoring
Requirements for Seasonal Systems
Repeat Monitoring Requirements for Small Systems
Level 1 & Level 2 Assessments and Corrective Actions
Step 1
  Develop/update your sample siting plan.
Step 2
  Collect your drinking water samples.
Step 3
  Conduct required actions.
RTCR
  What to Do?
Who Does this Factsheet Apply To?
  ground water public water systems (PWSs) that serve 1,000 or fewer people and collect at least one routine total coliform (TC) sample quarterly or annually.
(RTCR)
FACTSHEET: Revised Total Coliform Rule

## Slide 7: STEP 3: Conduct Actions Required As a Result of Your Sampling
March 2016
For more information, visit our website at: [Placeholder for state URL info]
NOTES
*If you are missing any routine, repeat, or additional routine samples, contact your state.
**Call your state on the same day you learn of the EC+ result, or by the end of the next business day, or [Placeholder for state after-hours phone line or an alternative notification procedure] and tell them you received an EC+ result.
NO
    Continue with routine monitoring schedule, according to your sample siting plan.
NO
Call your state! You have to perform a Level 2 Assessment if the PWS has any of the following occurrences:
TC+ Routine and EC+ Repeat sample;
EC+ Routine and TC+ Repeat sample;
The PWS fails to take all 3 required repeat samples following an EC+ routine sample; or,
The PWS fails to test for E. coli when any repeat sample is TC+.
Within 30 days after you learned your PWS has triggered an assessment, a completed assessment form must be submitted to the state. Download the state form at [Placeholder for state website]. See the RTCR Factsheet: Level 1 & 2 Assessments and Corrective Actions.
YES**
Were any of the samples E. coli-positive (EC+)?
If any repeat sample is TC+ (or present for TC), call your state immediately and tell them you triggered an assessment. The state will help you identify which type of assessment is required.
See the RTCR Factsheet: Level 1 & 2 Assessments and Corrective Actions.
NOTE: You may have to comply with other requirements triggered by a TC+ sample (e.g., public Notification, Record Keeping).
For each TC+ routine sample, do the following THREE ACTIONS:
Make sure the lab tests each TC+ sample for E. coli; AND
Collect 3 repeat samples for each TC+ routine sample.* See RTCR Factsheet: Repeat Monitoring Requirements for Small Systems; AND
Take 3 additional routine samples the following month at your routine sample location(s). Collect at regular time intervals throughout the month or on a single day if taken from different sites. *
YES
Was your routine sample total coliform-positive (TC+)? **
RTCR

## Slide 8: Requirements for Seasonal Systems
Step 1: Conduct Start-Up Procedures
      You must conduct your state start-up procedures before delivering drinking water to your customers. Start-up procedures help reduce the presence of harmful bacteria in water. The checklist is available on our website at [Website placeholder].
  Flush all pipes until the water is clear
    Flushing the pipe lines in all areas of your water system helps remove buildup and dirty water that has gathered during the off season. Flushing the pipes helps the disinfectant work more effectively to kill bacteria and inactivate viruses.
  Clean all water storage tanks
    Drain and clean the tanks before delivering water to your customers. Harmful sediments may build up over time inside and along the walls of the water tanks. It is recommended that the tank be inspected and cleaned regularly. Contact the state for information about proper procedures for inspecting a tank.
  Disinfect
    Kill harmful bacteria and inactivate viruses by adding a disinfectant or by making sure the adequate disinfectant residual is present in all areas of your water pipes. Your system should be flushed thoroughly. Be sure to keep the highly chlorinated water away from surface water bodies such as lakes, streams, and ponds, as well as septic systems. Remember, you may not deliver water to your customers until proper disinfecting and flushing of your system is completed.
    Check our website [Website placeholder] or call the state to get more information about how to disinfect your water system.
  Inspect and Repair
    Consider having a qualified water system professional inspect and repair your water system before you deliver water to your customers. Some parts of your water system may have broken down or become worn out during the off season. This can create a situation where bacteria can enter the drinking water. You can find a list of state certified water system professionals to help with finding any defects at your water system at this website: [Website placeholder].
  Collect Samples
    Collect water samples and have them tested for the presence of bacteria and chlorine residuals at a state certified lab, after flushing, cleaning, disinfecting, and repairing your water system. Also, sample and test to determine if the adequate amount of disinfectant residual is present to help provide safer drinking water. You should find out your sample results before delivering water to your customers.
      Check our website [Website placeholder] or call the state to get more information about disinfectant residual levels.
NEW!
Attention!
Starting April 1, 2016, all seasonal systems must complete the state required startup procedures before serving water to the public. Your water system must complete and submit the state certification form confirming completion of these start-up procedures.
Additional RTCR Factsheets:
Requirements for Small Systems on Monthly Monitoring
Requirements for Small Systems on Quarterly/ Annual Monitoring
Repeat Monitoring Requirements for Small Systems
Level 1 & Level 2 Assessments and Corrective Actions
Step 1
  Conduct start-up procedures
Step 2
  Complete certification forms
Step 3
  Maintain good water quality
Step 4
  Complete shutdown procedures
RTCR
  What to Do?
Who Does this Factsheet Apply to?
  seasonal systems – a seasonal system is defined as a non-community water system that is not operated as a public water system (PWS) on a year-round basis and starts-up and shuts-down at the beginning and end of each operating season. Examples include campgrounds, fairgrounds, seasonal food service facilities, and ski areas.
(RTCR)
FACTSHEET: Revised Total Coliform Rule

## Slide 9: Step 2: Complete Certification Forms Each year before delivering water to your customers
      Contact your state if you need help understanding or following the Start-Up Procedures.
      Perform the items in the start-up procedures checklist. The checklist is available on our website at [Website placeholder].
      Complete the Start-Up Procedures Certification Form. The form is available on our website at [Website placeholder].
      Submit Start-Up Procedures Certification Form to the state.
    When you sign and submit this form, you are certifying that you have completed all
    of the start-up procedures, including:
      Flushed all pipes.
      Cleaned all water storage tanks (if applicable).
      Disinfected entire water system.
      Inspected water system.
      Repaired water system (if applicable).
      Collected samples to test for bacteria and disinfectant residual.
Step 3: Maintain good water quality and a good reputation with your customers
    If your water system does not complete all of the start-up procedures, you must notify your customers that your water system had a drinking water violation for failure to complete start-up procedures and tell them of any possible health risks.
    Contact your state for information on the proper public notification procedures (including language you must use), and timing.
Step 4: Complete Shutdown Procedures
    Similar to start-up procedures, completing shutdown procedures at the end of your business season will help you minimize repairs to the water system when your water system opens up again next season. To determine appropriate shutdown procedures for your water system, contact your state. In general, you should:
      Inspect your entire system and look for problems and damage that need attention or repairs.
      Turn off the power to your water supply pump and all treatment systems.
      If there is potential for your pressure tank or storage tank to freeze, drain it. If there is no potential for your tanks to freeze, you may choose to leave them full.
      Drain all of the water from your internal plumbing.
      Protect your distribution system by not leaving taps open in the off season.
March 2016
For more information, visit our website at: [Placeholder for state URL info]
RTCR
[State Drinking Water Contact Name]
[Department]
[Street Address]
[City]
[State]
[Postal code]

## Slide 10: Repeat Monitoring Requirements For Small Systems
NOTES
*CALL YOUR STATE on the same day you learned of the E. coli-positive (EC+) result, or by the end of the next business day if the result came in after business hours [Placeholder for state after-hours phone line or an alternative notification procedure] and tell them you received an EC+ result.
**Contact your state for an approved extension if logistical problems prevent collection within 24 hours.
reminder: analyze all repeat TC+ samples for E. coli.*
ATTENTION!
Collect all 3 repeat samples.
If you do not collect and analyze at least 3 repeat samples (for each routine TC+) you will have to perform a Level 1 or Level 2 assessment.
See the RTCR Factsheet: Level 1 & Level 2 Assessments and Corrective Actions.
Site A = 1 repeat
Original routine location that tested TC+
1
Site B = 1 repeat
upstream
2
Site C = 1 repeat
downstream
3
Step 1: Collect 3 repeat samples for each Routine TC+ Sample
    You must collect a set of 3 repeat samples after each TC+ routine sample. You must continue to collect a set of 3 repeat samples until either TC is not detected in one complete set of repeat samples or you trigger an assessment.
  Repeat Sampling Locations
    You must collect at least 3 repeat samples at the locations described in your sample siting plan: (1) 1 repeat sample at the original routine location, (2) 1 repeat sample within five service connections upstream, and (3) 1 repeat sample within five service connections downstream of the TC+ sample. You may choose alternative repeat sampling locations on a situational basis—contact your state for more information.
  Frequency & Timing
    Collect all 3 repeat samples within 24 hours** after receiving notification from the state-certified lab of the TC+ sample result. The repeat samples must be taken on the same day.
        Remember the lab must begin analyzing the drinking water sample no later than the 30th hour from the collection time.
        If necessary, ship the sample overnight and refrigerate or ice the sample using “blue” ice (cooled to about 4° to 10° C).
ATTENTION!
April 1, 2016, all public water systems (PWSs) must comply with the RTCR.
Are you a PWS? Contact your state at [Placeholder for state info/website].
For assistance, please contact your state:
Name/Dept.:
Phone:
Email:
Additional RTCR Factsheets:
Requirements for Small Systems on Monthly Monitoring
Requirements for Small Systems on Quarterly/ Annual Monitoring
Requirements for Seasonal Systems
Level 1 & Level 2 Assessments and Corrective Actions
Step 1
  Collect 3 repeat samples after each TC+ routine sample
Step 2
  Conduct required actions after collecting repeat samples
RTCR
  What to Do?
Who does this Factsheet Apply to?
  All Public water systems (PWSs) serving 1,000 or fewer people that are required to conduct repeat monitoring when a water sample is positive for total coliform (TC+) bacteria.
(RTCR)
FACTSHEET: Revised Total Coliform Rule

## Slide 11: Step 2: Conduct Actions Required As a Result of Your Repeat Sampling
March 2016
For more information, visit our website at: [Placeholder for state URL info]
NOTE
You are required to provide Tier 1 public notice within 24 hours in response to an E. coli MCL violation.
If Routine Sample Is: | And | Any Repeat Sample Is: | Action: What do your sample results mean? | Violation
TC+ EC- | & | TC+ EC- | The presence of total coliform bacteria in both your original routine sample and in your follow-up repeat sample suggests there could be a problem and your water may not be safe to use. Conduct a Level 1 or Level 2 assessment. Contact the state for help determining which type of assessment is required. | No MCL violation
TC+ EC- | & | TC+ EC? | The presence of total coliform bacteria in both your original routine sample and in your follow-up repeat sample suggests there could be a problem and because E. coli was not tested, it is unknown whether or not the water is safe to use. Notify the state within 24 hours of receiving sample results Conduct a Level 2 assessment. Issue a Public Notice (PN). | E. coli MCL violation*
TC+ EC- | & | TC+ EC+ | The presence of E. coli bacteria in your water is an indicator of fecal contamination and your water may not be safe to use. Notify the state within 24 hours of receiving sample results Conduct a Level 2 assessment. Issue a Public Notice (PN). | E. coli MCL violation*
TC+ EC- | & | Any or all repeat samples missing | The presence of total coliform bacteria in your original routine sample suggests there could be a problem and because repeat samples were not tested, it is unknown whether or not the water is safe to use. Conduct a Level 1 or Level 2 assessment. Contact the state for help determining which type of assessment is required. | No MCL violation
TC+ EC+ | & | TC+ | The presence of E. coli bacteria in your water is an indicator of fecal contamination and your water may not be safe to use. Notify the state within 24 hours of receiving sample results Conduct a Level 2 assessment. Issue a Public Notice (PN). | E. coli MCL violation*
TC+ EC+ | & | Any or all repeat samples missing | The presence of E. coli bacteria in your water is an indicator of fecal contamination and your water may not be safe to use. Notify the state within 24 hours of receiving sample results Conduct a Level 2 assessment. Issue a Public Notice (PN). | E. coli MCL violation*
You must complete an assessment and submit the form to the state within 30 days after you learned your PWS has triggered an assessment. See the RTCR Factsheet: Level 1 & Level 2 Assessments and Corrective Actions.
TC+ = Total coliform-positive or present; TC- =Total coliform-negative or absent
EC+ = E. coli-positive or present; EC- = E. coli-negative or absent; EC? = E. coli not analyzed
RTCR

## Slide 12: Level 1 & Level 2 Assessments and Corrective Actions
Examples of Common Causes of Contamination | Example Common Corrective Action(s)
Loss of system pressure | Maintenance of adequate pressure Valve maintenance Addition or upgrade of on-line monitoring & control
Cross connections | Maintenance of adequate pressure Installation of backflow prevention assembly/device Implementation/upgrade of cross connection control program
Cracks in well seal, casing, etc. | Replacement/repair of well components
What is an Assessment?
    When sampling results show that your PWS may be vulnerable to contamination, PWSs must perform an assessment (Level 1 or Level 2) and find and fix any “sanitary defects.” A sanitary defect can provide a pathway of entry for microbial contamination into the distribution system or indicate imminent failure in an existing barrier (e.g. cracked tank, rat droppings on wellheads, or broken seals).
    There are 5 basic elements to investigate during an assessment:
      Atypical events that may affect distributed water quality or indicate that distributed water quality was impaired;
      Changes in distribution system maintenance and operation, including water storage;
      Water source and treatment methods that affect distributed water quality;
      Inadequacies in sample sites, sampling protocol and sample processing; and
      Existing water quality monitoring data.
    A level 2 assessment is a more comprehensive and in-depth examination compared to a level 1 assessment because the cause of the Level 2 assessment is more critical and likely to result in a direct public health impact.
    A Level 2 assessment must be conducted by the state or a party approved by the state. A Level 1 assessment is typically conducted by the PWS.
    You have 30 days (after learning that you triggered the assessment) to complete, correct sanitary defects found, and submit the State-form. For sanitary defects found but NOT fixed within the 30 days, you must obtain a state-approved schedule for all incomplete corrective actions. After completing each scheduled corrective action, you must notify your state to avoid violations. Throughout the Assessment Process consult with your state to discuss progress.
ATTENTION!
April 1, 2016, all public water systems (PWSs) must comply with the RTCR.
Are you a PWS? Contact your state at [Placeholder for state info/website].
For assistance, please contact your state:
Name/Dept.:
Phone:
Email:
Additional RTCR Factsheets:
Requirements for Small Systems on Monthly Monitoring
Requirements for Small Systems on Quarterly/Annual Monitoring
Requirements for Seasonal Systems
Repeat Monitoring Requirements for Small Systems
  What is an Assessment?
  Throughout the Assessment Process.
  What to do if you are triggered to conduct an assessment.
RTCR
  What to know?
Who does this Factsheet Apply to?
  Public water systems (PWSs) serving 1,000 or fewer people that must conduct a Level 1 or Level 2 assessment.
(RTCR)
FACTSHEET: Revised Total Coliform Rule

## Slide 13: What to do if you triggered an assessment?
March 2016
For more information, visit our website at: [Placeholder for state URL info]
  NOTES—Your PWS will get a treatment technique violation if you:
      Fail to perform an assessment or take corrective action.
      You are required to provide Tier 2 public notice within 30 days in response to a treatment technique violation.
STEP 1: Call your state to select the appropriate person to conduct the assessment (the assessor).
Assessors may be the state, a third party or qualified staff from your system.
STEP 2: Ask the state for the Level 2 assessment form and determine the process for submission.
STEP 3: Have the assessment performed.
STEP 4: If sanitary defect(s) are found, fix them or propose and gain a state-approved schedule for fixing, if the sanitary defect(s) cannot be corrected within 30 days of triggering the assessment.
After completing each scheduled corrective action you must notify your state.
The PWS or state (at any time) may consult with each other to discuss progress or the corrective action(s) identified.
STEP 5: Submit the completed assessment form to the state within 30 days of learning that your system triggered the assessment.
You have to do a Level 2 Assessment if you have either:
E. coli MCL violation:
Two Level 1 triggers in a rolling 12-month period or for systems on annual monitoring, a Level 1 trigger in two consecutive years.
Your state approves the party that will conduct the assessment.
Routine | Repeat
TC+ & EC- | E. coli-positive (EC+)
TC+ & EC- | TC+ but not analyzed for EC
TC+ & EC+ | TC+
TC+ & EC+ | One or more samples is missing
Assessment
Level
STEP 1: Call your state, and verify the appropriate person to conduct the assessment (the assessor).
STEP 2: Ask the state for the Level 1 assessment form and determine the process for submission.
STEP 3: Perform the assessment.
STEP 4: If sanitary defect(s) are found, fix them or propose and gain a state-approved schedule for fixing, if the sanitary defect(s) cannot be corrected within 30 days of triggering the assessment.
After completing each scheduled corrective action you must notify your state.
The PWS or state (at any time) may consult with each other to discuss progress or the corrective action(s) identified.
STEP 5: Submit the completed assessment form to the state within 30 days of learning that your system triggered the assessment.
You have to do a Level 1 Assessment if you:
Fail to collect and analyze at least 3 repeat samples for each routine TC+; or
Have two or more TC+ samples (use routine and repeat results in your calculation) in one month.
Your system conducts the assessment.
TC+
TC+
Assessment
Level
    Within 30 days of learning that your PWS triggered an assessment, a completed state assessment form must be submitted to your state. The process for completing and submitting the required form depends on the type of assessment. In both cases, your state will review the completed assessment form to determine if the likely cause of the trigger has been identified and to ensure the problem is corrected.
RTCR