## Source Parameters
Equipment ID | Description | Stack Height | Stack Inside Diameter | Exit Gas Flow Rate | Exit Gas Temperature | Distance to Facility Boundary | Peak Hour NOx Emission Rate | Annual PTE NOx Emission Rate | Hourly-Averaged NOx | Annual-Averaged NOx | Notes | Clustered Stacks Modeled as Single Point Source (g/sec)
|  | (feet) | (inches) | (cfm) | (Deg F) | (Feet) | (lbs/hour) | (tons/year) | (gram/second) | (gram/second) |  | Hourly | Annual
New NOx Emission Sources
Cogen-1 | CHP gas engine at the central utility plant | 58.125 | 24 | 7486.4 | 644 | 166.5026 | 0.18592 | 0.84006 | 0.023426 | 0.024166
Cogen-2 | CHP gas engine at the central utility plant | 58.125 | 24 | 7486.4 | 644 | 166.5026 | 0.18592 | 0.84006 | 0.023426 | 0.024166
WH3 | 1.3 MMBtu/hr water heater, stack 6" above the tower roof top | 197.5 | 6 | 283 | 200 | 429.0682 | 0.040784 | 0.07592 | 0.0051387 | 0.002184 | Identical sources at the same location, used a single point source (WH3_5) in AERMOD to represent these identical units. | 0.015416 | 0.0065519
WH4 | 1.3 MMBtu/hr water heater, stack 6" above the tower roof top | 197.5 | 6 | 283 | 200 | 429.0682 | 0.040784 | 0.07592 | 0.0051387 | 0.002184
WH5 | 1.3 MMBtu/hr water heater, stack 6" above the tower roof top | 197.5 | 6 | 283 | 200 | 429.0682 | 0.040784 | 0.07592 | 0.0051387 | 0.002184
WH6 | 1.3 MMBtu/hr water heater, stack by the side of podium mechanical room | 15 | 6 | 283 | 200 | 520.6037 | 0.040784 | 0.07592 | 0.0051387 | 0.002184 | Identical sources at the same location, used a single point source (WH6_8) in AERMOD to represent these identical units. | 0.015416 | 0.0065519
WH7 | 1.3 MMBtu/hr water heater, stack by the side of podium mechanical room | 15 | 6 | 283 | 200 | 520.6037 | 0.040784 | 0.07592 | 0.0051387 | 0.002184
WH8 | 1.3 MMBtu/hr water heater, stack by the side of podium mechanical room | 15 | 6 | 283 | 200 | 520.6037 | 0.040784 | 0.07592 | 0.0051387 | 0.002184
WH9 | 0.4 MMBTU/hr water heater, stack 6" above the tower roof top | 197.5 | 6 | 90 | 200 | 429.0682 | 0.012549 | 0.02336 | 0.0015811 | 0.00067199 | Identical sources at the same location, used a single point source (WH9_11) in AERMOD to represent these identical units. | 0.0047434 | 0.002016
WH10 | 0.4 MMBTU/hr water heater, stack 6" above the tower roof top | 197.5 | 6 | 90 | 200 | 429.0682 | 0.012549 | 0.02336 | 0.0015811 | 0.00067199
WH11 | 0.4 MMBTU/hr water heater, stack 6" above the tower roof top | 197.5 | 6 | 90 | 200 | 429.0682 | 0.012549 | 0.02336 | 0.0015811 | 0.00067199
WH12 | 2 MMBTU/hr water heater, stack 6" above the existing casino mechanical room's roof top | 27 | 10 | 452 | 200 | 141.0761 | 0.062745 | 0.1168 | 0.0079057 | 0.0033599 | Identical sources at the same location, used a single point source (WH12_13) in AERMOD to represent these identical units. | 0.015811 | 0.0067199
WH13 | 2 MMBTU/hr water heater, stack 6" above the existing casino mechanical room's roof top | 27 | 10 | 452 | 200 | 141.0761 | 0.062745 | 0.1168 | 0.0079057 | 0.0033599
EG-7 | New parking garage emergency generator, ground-level north of the garage | 8.2425 | 4.875 | 770.519 | 836.8 | 251.8701 | 0.0082192 | 0.12709 | 0.0010356 | 0.003656
EG8 | New 2 MW Tier 4 emergency generator, stack extend above the central utility plant | 25 | 36 | 16301.3 | 920.6 | 166.5026 | 0.057732 | 0.56687 | 0.0072742 | 0.016307
EG9 | New 2 MW Tier 4 emergency generator, stack extend above the central utility plant | 25 | 36 | 16301.3 | 920.6 | 166.5026 | 0.057732 | 0.56687 | 0.0072742 | 0.016307
Existing NOx Emission Sources Remain Unchanged
EG-1 | Existing Tier 2 backup generator at the central utility plant | 25 | 18 | 11060.6 | 763.5 | 166.5026 | 0.43904 | 1.923 | 0.055318 | 0.055318
EG-2 | Existing Tier 1 backup generator at the central utility plant | 25 | 18 | 11060.6 | 763.5 | 166.5026 | 0.71774 | 3.1437 | 0.090433 | 0.090433
BO-1 | Existing 15 MMBTU/hr boiler the existing casino mechanical room | 26.5 | 24 | 5340 | 300 | 141.0761 | 0.47059 | 0.29412 | 0.059293 | 0.0084608 | Identical sources at the same location, used a single point source (BO1_3) in AERMOD to represent these identical units. | 0.17788 | 0.025382
BO-2 | Existing 15 MMBTU/hr boiler the existing casino mechanical room | 26.5 | 24 | 5340 | 300 | 141.0761 | 0.47059 | 0.29412 | 0.059293 | 0.0084608
BO-3 | Existing 15 MMBTU/hr boiler the existing casino mechanical room | 26.5 | 24 | 5340 | 300 | 141.0761 | 0.47059 | 0.29412 | 0.059293 | 0.0084608
WH-1 | Existing water heater the existing casino mechanical room | 26.5 | 6 | 283 | 200 | 141.0761 | 0.13725 | 0.085784 | 0.017294 | 0.0024677 | Identical sources at the same location, used a single point source (WH1_2) in AERMOD to represent these identical units. | 0.034588 | 0.0049354
WH-2 | Existing water heater the existing casino mechanical room | 26.5 | 6 | 283 | 200 | 141.0761 | 0.13725 | 0.085784 | 0.017294 | 0.0024677
FP-1 | Existing fire pump by the existing casino building | 10 | 6 | 581 | 1033 | 77.0997 | 0.010815 | 0.047368 | 0.0013626 | 0.0013626
1 | Cogen1, Cogen-2, EG-8 and EG-9 information were provided by Vanderweil; water heater information were provided by NV5; EG-7 information were based on manufacturer specification sheets
2 | For EG-7, the exit gas flow rate were adjusted from the normalized condition to actual condition using the following ideal gas law calculations:
| 0.34659 | P1/P2
| 2.6369 | T2/T1
| 770.519 | V2 = (P1/P2)*(T2/T1)* V1. Adjusted dry exit volume based on exit temp and pressure

## Model Summary-Final
Summary of Model Results and Compare to NAAQS and CAAQS (unit in ug/m3)
| 1-hr 8th Highest | 1-hr highest | Annual
1 Project - Max | 41.6116 | 51.0501 | 1.9746
2 Background - Max. of Recent 3 Years | 106.22 | 134.232 | 31.208
Total (Project + Background) | 147.8316 | 185.2821 | 33.1826
NAAQS Threshold | 188 | -- | 100
CAAQS Threshold | -- | 339 | 53
Exceed Threshold? | No | No | No
1. AERMOD modeling used the SCAQMD's Redland MET data, the USEPA ozone data for San Bernadino (downloaded from EPA AirData), and the default NO2/Nox ratios of 0.5 instack and 0.9 atmosphere equilibrium, respectively.Detailed AERMOD input and output files are provided in the CD.
2. The UTM (X,Y) coordinates in units of meters for the modeled maximum NO2 concentrations are, (478927.66, 3778760.00) for the maximum 1-hour 8th highest concentration of 41.6 ug/m3, (478596.21, 3778698.88) for the maximum 1-hour highest concentration of 51.1 ug/m3, and (478738.08, 3778846.76) for the maximum annual-average value of 2.0 ug/m3.
3. SCAQMD Monitoring Data (Units in PPB, multiple by 1.88 to convert to ug/m3)
| 1-hr 8th Highest | 1-hr highest | Annual
2017 | 1-hr | 1-hr | AAM
Central San Bernardino Valley 2 | 56.5 | 65.8 | 15.9
2016 | 1-hr | 1-hr | AAM
Central San Bernardino Valley 2 | 51.4 | 60.1 | 16.6
2015 | 1-hr | 1-hr | AAM
Central San Bernardino Valley 2 | 52.7 | 71.4 | 15.2
3-year Maximum (ppb)
Central San Bernardino Valley 2 | 56.5 | 71.4 | 16.6
3-year Maximum (ug/m3)
Central San Bernardino Valley 2 | 106.22 | 134.232 | 31.208
Note on B3: Tina Su: 478927.66, 3778760.00
Note on C3: Tina Su: 478596.21, 3778698.88
Note on D3: Tina Su: 478738.08, 3778846.76