## User Input Sheet
CUECost
Coal Utility Environmental Cost
Version 1, November 25, 1998 (revised 2-9-00 as CUECost3.xls)
Developed for EPA
by Raytheon Engineers & Constructors and Eastern Research Group
| Current Date: | 2026-07-29 12:49
GoTo Buttons |  |  |  | Print Options
Inputs:
Calculations and Costs:
APC Technology Choices | [8 empty] | Description of Input
|  | Suggested | Default
Description | Units | Range | Values | Input 1 | Input 2 | Input 3 | Input 4 | Input 5
FGD Process | Integer | 1 or 2 | 1 | 2 | 2 | 2 | 2 | 2
(1 = LSFO, 2 = LSD)
Particulate Control | Integer | 1 or 2 | 1 | 1 | 1 | 1 | 1 | 1
(1 = Fabric Filter, 2 = ESP)
NOx Control | Integer | 1 - 4 | 1 | 1 | 1 | 1 | 1 | 1
(1 = SCR, 2 = SNCR, 3 = LNBs, 4 = NGR)
INPUTS | [8 empty] | Description of Input
Default
Description | Units | Range | Values | Input 1 | Input 2 | Input 3 | Input 4 | Input 5
General Plant Technical Inputs
Location - State | Abbrev. | All States | PA | PA | PA | PA | PA | PA
MW Equivalent of Flue Gas to Control System | MW | 100-2000 | 500 | 500 | 500 | 500 | 500 | 500 | Gross Plant Generation (MW) minus auxiliary power requirements. Prior to control system retrofit.
Net Plant Heat Rate (w/o APC) | Btu/kWhr |  | 10500 | 10500 | 10500 | 10500 | 10500 | 10500
Plant Capacity Factor | % | 40-90% | 65% | 65% | 65% | 65% | 65% | 65%
Percent Excess Air in Boiler | % |  | 120% | 120% | 120% | 120% | 120% | 120% | Excess O2.
Air Heater Inleakage | % |  | 12% | 12% | 12% | 12% | 12% | 12%
Air Heater Outlet Gas Temperature | °F |  | 300 | 300 | 300 | 300 | 300 | 300
Inlet Air Temperature | °F |  | 80 | 80 | 80 | 80 | 80 | 80
Ambient Absolute Pressure | In. of Hg |  | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4
Pressure After Air Heater | In. of H2O |  | -12 | -12 | -12 | -12 | -12 | -12
Moisture in Air | lb/lb dry air |  | 0.013 | 0.013 | 0.013 | 0.013 | 0.013 | 0.013
Ash Split:
Fly Ash | % |  | 80% | 80% | 80% | 80% | 80% | 80%
Bottom Ash | % |  | 20% | 20% | 20% | 20% | 20% | 20%
Seismic Zone | Integer | 1-5 | 1 | 1 | 1 | 1 | 1 | 1 | See Map.
Retrofit Factor | Integer | 1.0-3.0 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3
(1.0 = new, 1.3 = medium, 1.6 = difficult)
Select Coal | Integer | 1-8 | 1 | 1 | 2 | 3 | 4 | 5
Is Selected Coal a Powder River Basin Coal? | Yes / No | See Column K | Yes | Yes | No | No | No | No | This question is necessary for a correct SCA calculation.
Coals Available in Library
Coal 1, Wyoming PRB: 8,227 Btu, 0.37% S, 5.32% ash
Coal 2, Armstrong, PA: 13,100 Btu, 2.6% S, 9.1% ash
Coal 3, Jefferson, OH: 11,922 Btu, 3.43% S, 13% ash
Coal 4, Logan, WV: 12,058 Btu, 0.89% S, 16.6% ash
Coal 5, No. 6 Illinois: 10,100 Btu, 4% S, 16% ash
Coal 6, Rosebud, MT: 8,789 Btu, 0.56% S, 8.15% ash
Coal 7, Lignite, ND: 7,500 Btu, 0.94% S, 5.9% ash
Coal 8, "User Specified": Btu, 0% S, 0% ash
Economic Inputs
Cost Basis -Year Dollars | Year |  | 1998 | 1998 | 1998 | 1998 | 1998 | 1998 | Date of Startup.
Sevice Life (levelization period) | Years |  | 30 | 30 | 30 | 30 | 30 | 30
Inflation Rate | % |  | 3% | 3% | 3% | 3% | 3% | 3%
After Tax Discount Rate (current $'s) | % |  | 9.2% | 9.2% | 9.2% | 9.2% | 9.2% | 9.2%
AFDC Rate (current $'s) | % |  | 10.8% | 10.8% | 10.8% | 10.8% | 10.8% | 10.8%
First-year Carrying Charge (current $'s) | % |  | 22.3% | 22.3% | 22.3% | 22.3% | 22.3% | 22.3%
Levelized Carrying Charge (current $'s) | % |  | 16.9% | 16.9% | 16.9% | 16.9% | 16.9% | 16.9%
First-year Carrying Charge (constant $'s) | % |  | 15.7% | 15.7% | 15.7% | 15.7% | 15.7% | 15.7%
Levelized Carrying Charge (constant $'s) | % |  | 11.7% | 11.7% | 11.7% | 11.7% | 11.7% | 11.7%
Sales Tax | % |  | 6% | 6% | 6% | 6% | 6% | 6%
Escalation Rates:
Consumables (O&M) | % |  | 3% | 3% | 3% | 3% | 3% | 3%
Capital Costs:
Is Chem. Eng. Cost Index available? | Yes / No |  | Yes | Yes | Yes | Yes | Yes | Yes
If "Yes" input cost basis CE Plant Index. | Integer |  | 388 | 388 | 388 | 388 | 388 | 388 | The default CE Index value is the published January 1998 value.
If "No" input escalation rate. | % |  | 3% | 3% | 3% | 3% | 3% | 3%
Construction Labor Rate | $/hr |  | 35 | 35 | 35 | 35 | 35 | 35
Prime Contractor's Markup | % |  | 3% | 3% | 3% | 3% | 3% | 3% | Percent of Total Process Capital. (covers construction labor fee).
Operating Labor Rate | $/hr |  | 30 | 30 | 30 | 30 | 30 | 30
Power Cost | Mills/kWh |  | 25 | 25 | 25 | 25 | 25 | 25
Steam Cost | $/1000 lbs |  | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
Limestone Forced Oxidation (LSFO) Inputs
SO2 Removal Required | % | 90-98% | 95% | 95% | 95% | 95% | 95% | 95%
L/G Ratio | gal / 1000 acf | 95-160 | 125 | 125 | 125 | 125 | 125 | 125
Design Scrubber with Dibasic Acid Addition? | Integer | 1 or 2 | 2 | 2 | 1 | 2 | 2 | 2
(1 = yes, 2 = no)
Adiabatic Saturation Temperature | °F | 100-170 | 127 | 127 | 127 | 127 | 127 | 127
Reagent Feed Ratio | Factor | 1.0-2.0 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05
(Mole CaCO3 / Mole SO2 removed)
Scrubber Slurry Solids Concentration | Wt. % |  | 15% | 15% | 15% | 15% | 15% | 15%
Stacking, Landfill, Wallboard | Integer | 1,2,3 | 1 | 1 | 1 | 1 | 1 | 1
(1 = stacking, 2 = landfill, 3 = wallboard)
Number of Absorbers | Integer | 1-6 | 1 | 1 | 1 | 1 | 1 | 1
(Max. Capacity = 700 MW per absorber)
Absorber Material | Integer | 1 or 2 | 1 | 1 | 1 | 1 | 1 | 1
(1 = alloy, 2 = RLCS)
Absorber Pressure Drop | in. H2O |  | 6 | 6 | 6 | 6 | 6 | 6
Reheat Required ? | Integer | 1 or 2 | 1 | 1 | 1 | 1 | 1 | 1
(1 = yes, 2 = no)
Amount of Reheat | °F | 0-50 | 25 | 25 | 25 | 25 | 25 | 25
Reagent Bulk Storage | Days |  | 60 | 60 | 60 | 60 | 60 | 60
Reagent Cost (delivered) | $/ton |  | 15 | 15 | 15 | 15 | 15 | 15
Landfill Disposal Cost | $/ton |  | 30 | 30 | 30 | 30 | 30 | 30
Stacking Disposal Cost | $/ton |  | 6 | 6 | 6 | 6 | 6 | 6
Credit for Gypsum Byproduct | $/ton |  | 2 | 2 | 2 | 2 | 2 | 2
Maintenance Factors by Area (% of Installed Cost)
Reagent Feed | % |  | 5% | 5% | 5% | 5% | 5% | 5%
SO2 Removal | % |  | 5% | 5% | 5% | 5% | 5% | 5%
Flue Gas Handling | % |  | 5% | 5% | 5% | 5% | 5% | 5%
Waste / Byproduct | % |  | 5% | 5% | 5% | 5% | 5% | 5%
Support Equipment | % |  | 5% | 5% | 5% | 5% | 5% | 5%
Contingency by Area (% of Installed Cost)
Reagent Feed | % |  | 20% | 20% | 20% | 20% | 20% | 20%
SO2 Removal | % |  | 20% | 20% | 20% | 20% | 20% | 20%
Flue Gas Handling | % |  | 20% | 20% | 20% | 20% | 20% | 20%
Waste / Byproduct | % |  | 20% | 20% | 20% | 20% | 20% | 20%
Support Equipment | % |  | 20% | 20% | 20% | 20% | 20% | 20%
General Facilities by Area (% of Installed Cost)
Reagent Feed | % |  | 10% | 10% | 10% | 10% | 10% | 10%
SO2 Removal | % |  | 10% | 10% | 10% | 10% | 10% | 10%
Flue Gas Handling | % |  | 10% | 10% | 10% | 10% | 10% | 10%
Waste / Byproduct | % |  | 10% | 10% | 10% | 10% | 10% | 10%
Support Equipment | % |  | 10% | 10% | 10% | 10% | 10% | 10%
Engineering Fees by Area (% of Installed Cost)
Reagent Feed | % |  | 10% | 10% | 10% | 10% | 10% | 10%
SO2 Removal | % |  | 10% | 10% | 10% | 10% | 10% | 10%
Flue Gas Handling | % |  | 10% | 10% | 10% | 10% | 10% | 10%
Waste / Byproduct | % |  | 10% | 10% | 10% | 10% | 10% | 10%
Support Equipment | % |  | 10% | 10% | 10% | 10% | 10% | 10%
Lime Spray Dryer (LSD) Inputs
SO2 Removal Required | % | 90-95% | 90% | 90% | 90% | 90% | 90% | 90%
Adiabatic Saturation Temperature | °F | 100-170 | 127 | 127 | 127 | 127 | 127 | 127
Flue Gas Approach to Saturation | °F | 10.-50 | 20 | 20 | 20 | 20 | 20 | 20
Spray Dryer Outlet Temperature | °F | 110-220 | 147 | 147 | 147 | 147 | 147 | 147
Reagent Feed Ratio | Factor | Calc. Based on %S | 0.9 | 0.91837 | 1.5 | 1.7549 | 1.0103 | 1.9364
(Mole CaO / Mole Inlet SO2)
Recycle Rate | Factor | Calculated | 30 | 30 | 1.4 | 0.66 | 9 | 0.49
(lb recycle / lb lime feed)
Recycle Slurry Solids Concentration | Wt. % | 10-50 | 35% | 35% | 35% | 35% | 35% | 35%
Number of Absorbers | Integer | 1-7 | 2 | 2 | 2 | 2 | 2 | 2
(Max. Capacity = 300 MW per spray dryer)
Absorber Material | Integer | 1 or 2 | 1 | 1 | 1 | 1 | 1 | 1
(1 = alloy, 2 = RLCS)
Spray Dryer Pressure Drop | in. H2O |  | 5 | 5 | 5 | 5 | 5 | 5
Reagent Bulk Storage | Days |  | 60 | 60 | 60 | 60 | 60 | 60
Reagent Cost (delivered) | $/ton |  | 65 | 65 | 65 | 65 | 65 | 65
Dry Waste Disposal Cost | $/ton |  | 30 | 30 | 30 | 30 | 30 | 30
Maintenance Factors by Area (% of Installed Cost)
Reagent Feed | % |  | 5% | 5% | 5% | 5% | 5% | 5%
SO2 Removal | % |  | 5% | 5% | 5% | 5% | 5% | 5%
Flue Gas Handling | % |  | 5% | 5% | 5% | 5% | 5% | 5%
Waste / Byproduct | % |  | 5% | 5% | 5% | 5% | 5% | 5%
Support Equipment | % |  | 5% | 5% | 5% | 5% | 5% | 5%
Contingency by Area (% of Installed Cost)
Reagent Feed | % |  | 20% | 20% | 20% | 20% | 20% | 20%
SO2 Removal | % |  | 20% | 20% | 20% | 20% | 20% | 20%
Flue Gas Handling | % |  | 20% | 20% | 20% | 20% | 20% | 20%
Waste / Byproduct | % |  | 20% | 20% | 20% | 20% | 20% | 20%
Support Equipment | % |  | 20% | 20% | 20% | 20% | 20% | 20%
General Facilities by Area (% of Installed Cost)
Reagent Feed | % |  | 10% | 10% | 10% | 10% | 10% | 10%
SO2 Removal | % |  | 10% | 10% | 10% | 10% | 10% | 10%
Flue Gas Handling | % |  | 10% | 10% | 10% | 10% | 10% | 10%
Waste / Byproduct | % |  | 10% | 10% | 10% | 10% | 10% | 10%
Support Equipment | % |  | 10% | 10% | 10% | 10% | 10% | 10%
Engineering Fees by Area (% of Installed Cost)
Reagent Feed | % |  | 10% | 10% | 10% | 10% | 10% | 10%
SO2 Removal | % |  | 10% | 10% | 10% | 10% | 10% | 10%
Flue Gas Handling | % |  | 10% | 10% | 10% | 10% | 10% | 10%
Waste / Byproduct | % |  | 10% | 10% | 10% | 10% | 10% | 10%
Support Equipment | % |  | 10% | 10% | 10% | 10% | 10% | 10%
Particulate Control Inputs
Outlet Particulate Emission Limit | lbs/MMBtu |  | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
Fabric Filter:
Pressure Drop | in. H2O |  | 6 | 6 | 6 | 6 | 6 | 6
Type (1 = Reverse Gas, 2 = Pulse Jet) | Integer |  | 2 | 2 | 2 | 2 | 2 | 2
Gas-to-Cloth Ratio | ACFM/ft2 |  | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
Bag Material (RGFF fiberglass only) | Integer |  | 2 | 2 | 2 | 2 | 2 | 2
(1 = Fiberglass, 2 = Nomex, 3 = Ryton)
Bag Diameter | inches | 5 - 14 | 6 | 6 | 6 | 6 | 6 | 6
Bag Length | feet | 15 - 35 | 20 | 20 | 20 | 20 | 20 | 20
Bag Reach |  |  | 3 | 3 | 3 | 3 | 3 | 3
Compartments out of Service | % |  | 10% | 10% | 10% | 10% | 10% | 10%
Bag Life | Years | 1 - 10 | 5 | 5 | 5 | 5 | 5 | 5
Maintenance (% of installed cost) | % |  | 5% | 5% | 5% | 5% | 5% | 5%
Contingency (% of installed cost) | % |  | 20% | 20% | 20% | 20% | 20% | 20%
General Facilities (% of installed cost) | % |  | 10% | 10% | 10% | 10% | 10% | 10%
Engineering Fees (% of installed cost) | % |  | 10% | 10% | 10% | 10% | 10% | 10%
ESP:
Strength of the electric field in the ESP = E | kV/cm |  | 10 | 10 | 10 | 10 | 10 | 10
Plate Spacing | in. |  | 12 | 12 | 12 | 12 | 12 | 12
Plate Height | ft. |  | 36 | 36 | 36 | 36 | 36 | 36
Pressure Drop | in. H2O |  | 3 | 3 | 3 | 3 | 3 | 3
Maintenance (% of installed cost) | % |  | 5% | 5% | 5% | 5% | 5% | 5%
Contingency (% of installed cost) | % |  | 20% | 20% | 20% | 20% | 20% | 20%
General Facilities (% of installed cost) | % |  | 10% | 10% | 10% | 10% | 10% | 10%
Engineering Fees (% of installed cost) | % |  | 10% | 10% | 10% | 10% | 10% | 10%
NOx Control Inputs
See Source Keys @ bottom of
Selective Catalytic Reduction (SCR) Inputs | [10 empty] | Constants_CC Sheet.
[10 empty] | IAPCS name | Range Source | Default Source
NH3/NOX Stoichiometric Ratio | NH3/NOX | 0.7-1.0 | 0.9 | D | D | D | D | D | IAPCS Names and a list of sources are contained in columns L, M, and N. | NH3:NOX ratio
NOX Reduction Efficiency | Fraction | 0.60-0.90 | 0.7 | D | D | D | D | D | " | n | b | c
Inlet NOx | lbs/MMBtu |  | 0.9 | D | D | D | D | D | " | NOx
Space Velocity (Calculated if zero) | 1/hr |  | 0 | D | D | D | D | D | " | SV | i | i
Overall Catalyst Life | years | 2-5 | 3 | D | D | D | D | D | " | N | d | c
Ammonia Cost | $/ton |  | 205.66 | D | D | D | D | D | " | UCNH3 | d | a
Catalyst Cost | $/ft3 |  | 356.34 | D | D | D | D | D | " | UCCAT | d | a
Solid Waste Disposal Cost | $/ton |  | 11.48 | D | D | D | D | D | " | UCWASTE |  | a
Maintenance (% of installed cost) | % |  | 1.5% | D | D | D | D | D | " |  |  | a
Contingency (% of installed cost) | % |  | 20% | D | D | D | D | D | " |  |  | f
General Facilities (% of installed cost) | % |  | 5% | D | D | D | D | D | " |  |  | f
Engineering Fees (% of installed cost) | % |  | 10% | D | D | D | D | D | " |  |  | f
Number of Reactors | integer |  | 2 | D | D | D | D | D | " | Nr,tot
Number of Air Preheaters | integer |  | 1 | D | D | D | D | D | " | Nt,aph
Selective NonCatalytic Reduction (SNCR) Inputs
Reagent | integer | 1:Urea 2:Ammonia | 1 | D | D | D | D | D | " |  | -- | --
Number of Injector Levels | integer |  | 3 | D | D | D | D | D | " | NIL |  | f
Number of Injectors | integer |  | 18 | D | D | D | D | D
Number of Lance Levels | integer |  | 0 | D | D | D | D | D | " | NLL |  | f
Number of Lances | integer |  | 0 | D | D | D | D | D
Steam or Air Injection for Ammonia | integer | 1: Steam, 2: Air | 1 | D | D | D | D | D | " |  |  | --
NOX Reduction Efficiency | fraction | 0.30-0.70 | 0.5 | D | D | D | D | D | " | n | b | c
Inlet NOx | lbs/MMBtu |  | 0.9 | D | D | D | D | D | " | NOx
NH3/NOX Stoichiometric Ratio | NH3/NOX | 0.8-2.0 | 1.2 | D | D | D | D | D | " | NH3:NOX ratio
Urea/NOX Stoichiometric Ratio | Urea/NOX | 0.8-2.0 | 1.2 | D | D | D | D | D | Urea provides 2 moles of Ammonia for every mole of Urea. | UREA:NOX ratio | f | c
Urea Cost | $/ton |  | 224.95 | D | D | D | D | D | " | UCUREA |  | g
Ammonia Cost | $/ton |  | 205.66 | D | D | D | D | D | " | UCNH3 |  | a
Water Cost | $/1,000 gal |  | 0.407 | D | D | D | D | D | " | UCH2O |  | a
Maintenance (% of installed cost) | % |  | 1.5% | D | D | D | D | D | " |  |  | a
Contingency (% of installed cost) | % |  | 20% | D | D | D | D | D | " |  |  | e
General Facilities (% of installed cost) | % |  | 5% | D | D | D | D | D | " |  |  | e
Engineering Fees (% of installed cost) | % |  | 10% | D | D | D | D | D | " |  |  | e
Low NOX Burner Technology Inputs
NOX Reduction Efficiency | fraction | 0.15-0.60 | 0.35 | D | D | D | D | D | " | n | i | g
Boiler Type | T:T-fired, W:Wall |  | T | D | D | D | D | D | "
Retrofit Difficulty | L:Low, A:Average, H:High |  | A | D | D | D | D | D | "
Maintenance Labor (% of installed cost) | % |  | 0.8% | D | D | D | D | D | " |  |  | g
Maintenance Materials (% of installed cost) | % |  | 1.2% | D | D | D | D | D | " |  |  | g
Natural Gas Reburning Inputs
NOX Reduction Efficiency | fraction | 0.55-0.65 | 0.61 | D | D | D | D | D | " | n | i
Gas Reburn Fraction | fraction | 0.08 - 0.20 | 0.15 | D | D | D | D | D | " |  |  | i
Waste Disposal Cost | $/ton |  | 11.48 | D | D | D | D | D | " | UCWASTE |  | a
Natural Gas Cost | $/MMBtu |  | 2.31 | D | D | D | D | D | " | UCGAS |  | a
Maintenance (% of installed cost) | % |  | 1.5% | D | D | D | D | D | " |  |  | a
Contingency (% of installed cost) | % |  | 20% | D | D | D | D | D | " |  |  | e
General Facilities (% of installed cost) | % |  | 2% | D | D | D | D | D | " |  |  | e
Engineering Fees (% of installed cost) | % |  | 10% | D | D | D | D | D | " |  |  | e
Default Values will be selected when "D" is input.
APC Technology Choices
General Plant Technical Inputs
Economic Inputs
LSFO Inputs
LSD Inputs
Particulate Control Inputs
NOx Control Inputs
Cost Summary
SCR Calculations
SNCR Calculations
Low NOx Burner Calculations
Natural Gas Reburning Calculations
LSFO Material Balances
LSFO Cost Calculations
LSD Material Balances
LSD Cost Calculations
Fabric Filter Calculations
ESP Calculations
Fuel and Combustion Calculations
Coal Analysis Library
Cost Summary
Input Summary
NOx Control Calculations
Particulate Control Calculations
LSFO Calculations
LSD Calculations
Combustion Calculations
Coal Analysis Library
Print ALL

## Input & Calculation Summary
APC Technology Choices
Description | Units | Input 1 | Input 2 | Input 3 | Input 4 | Input 5
FGD Process | Integer | 2 | 2 | 2 | 2 | 2
(1 = LSFO, 2 = LSD)
Particulate Control | Integer | 1 | 1 | 1 | 1 | 1
(1 = Fabric Filter, 2 = ESP)
NOx Control | Integer | 1 | 1 | 1 | 1 | 1
(1 = SCR, 2 = SNCR, 3 = LNBs, 4 = NGR)
INPUTS
Description | Units | Input 1 | Input 2 | Input 3 | Input 4 | Input 5
General Plant Technical Inputs
Location - State | Abbrev. | PA | PA | PA | PA | PA
MW Equivalent of Flue Gas to Control System | MW | 500 | 500 | 500 | 500 | 500
Net Plant Heat Rate | Btu/kWhr | 10500 | 10500 | 10500 | 10500 | 10500
Plant Capacity Factor | % | 65% | 65% | 65% | 65% | 65%
Total Air Downstream of Economizer | % | 120% | 120% | 120% | 120% | 120%
Air Heater Leakage | % | 12% | 12% | 12% | 12% | 12%
Air Heater Outlet Gas Temperature | °F | 300 | 300 | 300 | 300 | 300
Inlet Air Temperature | °F | 80 | 80 | 80 | 80 | 80
Ambient Absolute Pressure | In. of Hg | 29.4 | 29.4 | 29.4 | 29.4 | 29.4
Pressure After Air Heater | In. of H2O | -12 | -12 | -12 | -12 | -12
Moisture in Air | lb/lb dry air | 0.013 | 0.013 | 0.013 | 0.013 | 0.013
Ash Split:
Fly Ash | % | 80% | 80% | 80% | 80% | 80%
Bottom Ash | % | 20% | 20% | 20% | 20% | 20%
Seismic Zone | Integer | 1 | 1 | 1 | 1 | 1
Retrofit Factor | Integer | 1.3 | 1.3 | 1.3 | 1.3 | 1.3
(1.0 = new, 1.3 = medium, 1.6 = difficult)
Select Coal | Integer | 1 | 2 | 3 | 4 | 5
Is Selected Coal a Powder River Basin Coal? | Yes / No | Yes | No | No | No | No
Economic Inputs
Cost Basis -Year Dollars | Year | 1998 | 1998 | 1998 | 1998 | 1998
Sevice Life (levelization period) | Years | 30 | 30 | 30 | 30 | 30
Inflation Rate | % | 3% | 3% | 3% | 3% | 3%
After Tax Discount Rate (current $'s) | % | 9.2% | 9.2% | 9.2% | 9.2% | 9.2%
AFDC Rate (current $'s) | % | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
First-year Carrying Charge (current $'s) | % | 22.3% | 22.3% | 22.3% | 22.3% | 22.3%
Levelized Carrying Charge (current $'s) | % | 16.9% | 16.9% | 16.9% | 16.9% | 16.9%
First-year Carrying Charge (constant $'s) | % | 15.7% | 15.7% | 15.7% | 15.7% | 15.7%
Levelized Carrying Charge (constant $'s) | % | 11.7% | 11.7% | 11.7% | 11.7% | 11.7%
Sales Tax | % | 6% | 6% | 6% | 6% | 6%
Escalation Rates:
Consumables (O&M) | % | 3% | 3% | 3% | 3% | 3%
Capital Costs:
Is Chem. Eng. Cost Index available? | Yes / No | Yes | Yes | Yes | Yes | Yes
If "Yes" input cost basis CE Plant Index. | Integer | 388 | 388 | 388 | 388 | 388
If "No" input escalation rate. | % | 3% | 3% | 3% | 3% | 3%
Construction Labor Rate | $/hr | 35 | 35 | 35 | 35 | 35
Prime Contractor's Markup | % | 3% | 3% | 3% | 3% | 3%
Operating Labor Rate | $/hr | 30 | 30 | 30 | 30 | 30
Power Cost | Mills/kWh | 25 | 25 | 25 | 25 | 25
Steam Cost | $/1000 lbs | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
Limestone Forced Oxidation (LSFO) Inputs
SO2 Removal Required | % | 95% | 95% | 95% | 95% | 95%
L/G Ratio | gal / 1000 acf | 125 | 125 | 125 | 125 | 125
Design Scrubber with Dibasic Acid Addition? | Integer | 2 | 1 | 2 | 2 | 2
(1 = yes, 2 = no)
Adiabatic Saturation Temperature | °F | 127 | 127 | 127 | 127 | 127
Reagent Feed Ratio | Factor | 1.05 | 1.05 | 1.05 | 1.05 | 1.05
(Mole CaCO3 / Mole SO2 removed)
Scrubber Slurry Solids Concentration | Wt. % | 15% | 15% | 15% | 15% | 15%
Stacking, Landfill, Wallboard | Integer | 1 | 1 | 1 | 1 | 1
(1 = stacking, 2 = lanfill, 3 = wallboard)
Number of Absorbers | Integer | 1 | 1 | 1 | 1 | 1
(Max. Capacity = 700 MW per absorber)
Absorber Material | Integer | 1 | 1 | 1 | 1 | 1
(1 = alloy, 2 = RLCS)
Absorber Pressure Drop | in. H2O | 6 | 6 | 6 | 6 | 6
Reheat Required ? | Integer | 1 | 1 | 1 | 1 | 1
(1 = yes, 2 = no)
Amount of Reheat | °F | 25 | 25 | 25 | 25 | 25
Reagent Bulk Storage | Days | 60 | 60 | 60 | 60 | 60
Reagent Cost (delivered) | $/ton | 15 | 15 | 15 | 15 | 15
Landfill Disposal Cost | $/ton | 30 | 30 | 30 | 30 | 30
Stacking Disposal Cost | $/ton | 6 | 6 | 6 | 6 | 6
Credit for Gypsum Byproduct | $/ton | 2 | 2 | 2 | 2 | 2
Maintenance Factors by Area (% of Installed Cost)
Reagent Feed | % | 5% | 5% | 5% | 5% | 5%
SO2 Removal | % | 5% | 5% | 5% | 5% | 5%
Flue Gas Handling | % | 5% | 5% | 5% | 5% | 5%
Waste / Byproduct | % | 5% | 5% | 5% | 5% | 5%
Support Equipment | % | 5% | 5% | 5% | 5% | 5%
Contingency by Area (% of Installed Cost)
Reagent Feed | % | 20% | 20% | 20% | 20% | 20%
SO2 Removal | % | 20% | 20% | 20% | 20% | 20%
Flue Gas Handling | % | 20% | 20% | 20% | 20% | 20%
Waste / Byproduct | % | 20% | 20% | 20% | 20% | 20%
Support Equipment | % | 20% | 20% | 20% | 20% | 20%
General Facilities by Area (% of Installed Cost)
Reagent Feed | % | 10% | 10% | 10% | 10% | 10%
SO2 Removal | % | 10% | 10% | 10% | 10% | 10%
Flue Gas Handling | % | 10% | 10% | 10% | 10% | 10%
Waste / Byproduct | % | 10% | 10% | 10% | 10% | 10%
Support Equipment | % | 10% | 10% | 10% | 10% | 10%
Engineering Fees by Area (% of Installed Cost)
Reagent Feed | % | 10% | 10% | 10% | 10% | 10%
SO2 Removal | % | 10% | 10% | 10% | 10% | 10%
Flue Gas Handling | % | 10% | 10% | 10% | 10% | 10%
Waste / Byproduct | % | 10% | 10% | 10% | 10% | 10%
Support Equipment | % | 10% | 10% | 10% | 10% | 10%
Lime Spray Dryer (LSD) Inputs
SO2 Removal Required | % | 90% | 90% | 90% | 90% | 90%
Adiabatic Saturation Temperature | °F | 127 | 127 | 127 | 127 | 127
Flue Gas Approach to Saturation | °F | 20 | 20 | 20 | 20 | 20
Spray Dryer Outlet Temperature | °F | 147 | 147 | 147 | 147 | 147
Reagent Feed Ratio | Factor | 0.91837 | 1.5 | 1.7549 | 1.0103 | 1.9364
(Mole CaO / Mole Inlet SO2)
Recycle Rate | Factor | 30 | 1.4 | 0.66 | 9 | 0.49
(lb recycle / lb lime feed)
Recycle Slurry Solids Concentration | Wt. % | 35% | 35% | 35% | 35% | 35%
Number of Absorbers | Integer | 2 | 2 | 2 | 2 | 2
(Max. Capacity = 300 MW per spray dryer)
Absorber Material | Integer | 1 | 1 | 1 | 1 | 1
(1 = alloy, 2 = RLCS)
Spray Dryer Pressure Drop | in. H2O | 5 | 5 | 5 | 5 | 5
Reagent Bulk Storage | Days | 60 | 60 | 60 | 60 | 60
Reagent Cost (delivered) | $/ton | 65 | 65 | 65 | 65 | 65
Dry Waste Disposal Cost | $/ton | 30 | 30 | 30 | 30 | 30
Maintenance Factors by Area (% of Installed Cost)
Reagent Feed | % | 5% | 5% | 5% | 5% | 5%
SO2 Removal | % | 5% | 5% | 5% | 5% | 5%
Flue Gas Handling | % | 5% | 5% | 5% | 5% | 5%
Waste / Byproduct | % | 5% | 5% | 5% | 5% | 5%
Support Equipment | % | 5% | 5% | 5% | 5% | 5%
Contingency by Area (% of Installed Cost)
Reagent Feed | % | 20% | 20% | 20% | 20% | 20%
SO2 Removal | % | 20% | 20% | 20% | 20% | 20%
Flue Gas Handling | % | 20% | 20% | 20% | 20% | 20%
Waste / Byproduct | % | 20% | 20% | 20% | 20% | 20%
Support Equipment | % | 20% | 20% | 20% | 20% | 20%
General Facilities by Area (% of Installed Cost)
Reagent Feed | % | 10% | 10% | 10% | 10% | 10%
SO2 Removal | % | 10% | 10% | 10% | 10% | 10%
Flue Gas Handling | % | 10% | 10% | 10% | 10% | 10%
Waste / Byproduct | % | 10% | 10% | 10% | 10% | 10%
Support Equipment | % | 10% | 10% | 10% | 10% | 10%
Engineering Fees by Area (% of Installed Cost)
Reagent Feed | % | 10% | 10% | 10% | 10% | 10%
SO2 Removal | % | 10% | 10% | 10% | 10% | 10%
Flue Gas Handling | % | 10% | 10% | 10% | 10% | 10%
Waste / Byproduct | % | 10% | 10% | 10% | 10% | 10%
Support Equipment | % | 10% | 10% | 10% | 10% | 10%
Particulate Control Inputs
Outlet Particulate Emission Limit | lbs/MMBtu | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
Fabric Filter:
Pressure Drop | in. H2O | 6 | 6 | 6 | 6 | 6
Type (1 = Reverse Gas, 2 = Pulse Jet) | Integer | 2 | 2 | 2 | 2 | 2
Gas-to-Cloth Ratio | ACFM/ft2 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
Bag Material (RGFF fiberglass only) | Integer | 2 | 2 | 2 | 2 | 2
(1 = Fiberglass, 2 = Nomex, 3 = Ryton)
Bag Diameter | inches | 6 | 6 | 6 | 6 | 6
Bag Length | feet | 20 | 20 | 20 | 20 | 20
Bag Reach |  | 3 | 3 | 3 | 3 | 3
Compartments out of Service | % | 10% | 10% | 10% | 10% | 10%
Bag Life | Years | 5 | 5 | 5 | 5 | 5
Maintenance (% of installed cost) | % | 5% | 5% | 5% | 5% | 5%
Contingency (% of installed cost) | % | 20% | 20% | 20% | 20% | 20%
General Facilities (% of installed cost) | % | 10% | 10% | 10% | 10% | 10%
Engineering Fees (% of installed cost) | % | 10% | 10% | 10% | 10% | 10%
ESP:
Strength of the electric field in the ESP = E | kV/cm | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Plate Spacing | in. | 12 | 12 | 12 | 12 | 12
Plate Height | ft. | 36 | 36 | 36 | 36 | 36
Pressure Drop | in. H2O | 3 | 3 | 3 | 3 | 3
Maintenance (% of installed cost) | % | 5% | 5% | 5% | 5% | 5%
Contingency (% of installed cost) | % | 20% | 20% | 20% | 20% | 20%
General Facilities (% of installed cost) | % | 10% | 10% | 10% | 10% | 10%
Engineering Fees (% of installed cost) | % | 10% | 10% | 10% | 10% | 10%
NOx Control Inputs
Selective Catalytic Reduction (SCR) Inputs
NH3/NOX Stoichiometric Ratio | NH3/NOX | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
NOX Reduction Efficiency | Fraction | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
Inlet NOx | lbs/MMBtu | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
Space Velocity (Calculated if zero) | 1/hr | 0 | 0 | 0 | 0 | 0
Overall Catalyst Life | years | 3 | 3 | 3 | 3 | 3
Ammonia Cost | $/ton | 205.66 | 205.66 | 205.66 | 205.66 | 205.66
Catalyst Cost | $/ft3 | 356.34 | 356.34 | 356.34 | 356.34 | 356.34
Solid Waste Disposal Cost | $/ton | 11.48 | 11.48 | 11.48 | 11.48 | 11.48
Maintenance (% of installed cost) | % | 1.5% | 1.5% | 1.5% | 1.5% | 1.5%
Contingency (% of installed cost) | % | 20% | 20% | 20% | 20% | 20%
General Facilities (% of installed cost) | % | 5% | 5% | 5% | 5% | 5%
Engineering Fees (% of installed cost) | % | 10% | 10% | 10% | 10% | 10%
Number of Reactors | integer | 2 | 2 | 2 | 2 | 2
Number of Air Preheaters | integer | 1 | 1 | 1 | 1 | 1
Selective NonCatalytic Reduction (SNCR) Inputs
Reagent | 1:Urea 2:Ammonia | 1 | 1 | 1 | 1 | 1
Number of Injector Levels | integer | 3 | 3 | 3 | 3 | 3
Number of Injectors | integer | 18 | 18 | 18 | 18 | 18
Number of Lance Levels | integer | 0 | 0 | 0 | 0 | 0
Number of Lances | integer | 0 | 0 | 0 | 0 | 0
Steam or Air Injection for Ammonia | integer | 1 | 1 | 1 | 1 | 1
NOX Reduction Efficiency | Fraction | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Inlet NOx | lbs/MMBtu | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
NH3/NOX Stoichiometric Ratio | NH3/NOX | 1.2 | 1.2 | 1.2 | 1.2 | 1.2
Urea/NOX Stoichiometric Ratio | Urea/NOX | 1.2 | 1.2 | 1.2 | 1.2 | 1.2
Urea Cost | $/ton | 224.95 | 224.95 | 224.95 | 224.95 | 224.95
Ammonia Cost | $/ton | 205.66 | 205.66 | 205.66 | 205.66 | 205.66
Water Cost | $/1,000 gal | 0.407 | 0.407 | 0.407 | 0.407 | 0.407
Maintenance (% of installed cost) | % | 1.5% | 1.5% | 1.5% | 1.5% | 1.5%
Contingency (% of installed cost) | % | 20% | 20% | 20% | 20% | 20%
General Facilities (% of installed cost) | % | 5% | 5% | 5% | 5% | 5%
Engineering Fees (% of installed cost) | % | 10% | 10% | 10% | 10% | 10%
Low NOX Burner Technology Inputs
NOX Reduction Efficiency | fraction | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
Boiler Type | T:T-fired, W:Wall | T | T | T | T | T
Retrofit Difficulty | L:Low, A:Average, H:High | A | A | A | A | A
Maintenance Labor (% of installed cost) | % | 0.8% | 0.8% | 0.8% | 0.8% | 0.8%
Maintenance Materials (% of installed cost) | % | 1.2% | 1.2% | 1.2% | 1.2% | 1.2%
Natural Gas Reburning Inputs
NOX Reduction Efficiency | fraction | 0.61 | 0.61 | 0.61 | 0.61 | 0.61
Gas Reburn Fraction | fraction | 0.15 | 0.15 | 0.15 | 0.15 | 0.15
Waste Disposal Cost | $/ton | 11.48 | 11.48 | 11.48 | 11.48 | 11.48
Natural Gas Cost | $/MMBtu | 2.31 | 2.31 | 2.31 | 2.31 | 2.31
Maintenance (% of installed cost) | % | 1.5% | 1.5% | 1.5% | 1.5% | 1.5%
Contingency (% of installed cost) | % | 20% | 20% | 20% | 20% | 20%
General Facilities (% of installed cost) | % | 2% | 2% | 2% | 2% | 2%
Engineering Fees (% of installed cost) | % | 10% | 10% | 10% | 10% | 10%
SUMMARY OF COSTS
Description | Units | Input 1 | Input 2 | Input 3 | Input 4 | Input 5
APC Technologies
NOx Control |  | SCR | SCR | SCR | SCR | SCR
Particulate Control |  | PJFF | PJFF | PJFF | PJFF | PJFF
SO2 Control |  | LSD | LSD | LSD | LSD | LSD
NOx Control Costs |  | SCR | SCR | SCR | SCR | SCR
Total Capital Requirement (TCR) | $ | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| $/kW | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
First Year Costs
Fixed O&M | $ | 500634.9832 | 488195.5038 | 488981.6874 | 487649.1153 | 491842.1635
| $/kW-Yr | 1.0013 | 0.97639 | 0.97796 | 0.9753 | 0.98368
| Mills/kWH | 0.17585 | 0.17148 | 0.17175 | 0.17129 | 0.17276
| $/ton NOx removed | 176.2361 | 108.0224 | 109.6428 | 130.6171 | 121.5715
Variable O&M | $ | 4259548.0293 | 4055447.598 | 4068207.7509 | 4046590.5812 | 4114793.934
| $/kW-Yr | 8.5191 | 8.1109 | 8.1364 | 8.0932 | 8.2296
| Mills/kWH | 1.4962 | 1.4245 | 1.4289 | 1.4214 | 1.4453
| $/ton NOx removed | 1499.4677 | 897.3434 | 912.2015 | 1083.8819 | 1017.0779
Fixed Charges | $ | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| $/kW-Yr | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| Mills/kWH | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| $/ton NOx removed | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
TOTAL | $ | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| $/kW-Yr | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| Mills/kWH | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| $/ton NOx removed | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Levelized Current Dollars
Fixed O&M | $/kW-Yr | 1.3625 | 1.3287 | 1.3308 | 1.3272 | 1.3386
| Mills/kWH | 0.23929 | 0.23335 | 0.23372 | 0.23309 | 0.23509
| $/ton NOx removed | 239.8248 | 146.9985 | 149.2037 | 177.7458 | 165.4364
Variable O&M | $/kW-Yr | 11.5929 | 11.0374 | 11.0722 | 11.0133 | 11.199
| Mills/kWH | 2.036 | 1.9384 | 1.9445 | 1.9342 | 1.9668
| $/ton NOx removed | 2040.4989 | 1221.1189 | 1241.3379 | 1474.9634 | 1384.0553
Fixed Charges | $/kW-Yr | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| Mills/kWH | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| $/ton NOx removed | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
TOTAL | $/kW-Yr | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| Mills/kWH | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| $/ton NOx removed | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Levelized Constant Dollars
Fixed O&M | $/kW-Yr | 1.0013 | 0.97639 | 0.97796 | 0.9753 | 0.98368
| Mills/kWH | 0.17585 | 0.17148 | 0.17175 | 0.17129 | 0.17276
| $/ton NOx removed | 176.2361 | 108.0224 | 109.6428 | 130.6171 | 121.5715
Variable O&M | $/kW-Yr | 8.5191 | 8.1109 | 8.1364 | 8.0932 | 8.2296
| Mills/kWH | 1.4962 | 1.4245 | 1.4289 | 1.4214 | 1.4453
| $/ton NOx removed | 1499.4677 | 897.3434 | 912.2015 | 1083.8819 | 1017.0779
Fixed Charges | $/kW-Yr | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| Mills/kWH | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| $/ton NOx removed | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
TOTAL | $/kW-Yr | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| Mills/kWH | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| $/ton NOx removed | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Particulate Control Costs |  | PJFF | PJFF | PJFF | PJFF | PJFF
Total Capital Requirement (TCR) | $ | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| $/kW | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
First Year Costs
Fixed O&M | $ | 1305111.8782 | 1195395.0992 | 1267338.3589 | 1211053.8294 | 1390371.983
| $/kW-Yr | 2.6102 | 2.3908 | 2.5347 | 2.4221 | 2.7807
| Mills/kWH | 0.45842 | 0.41988 | 0.44515 | 0.42538 | 0.48836
| $/ton PM removed | 3.1626 | 3.6917 | 2.9258 | 3.3365 | 2.2901
Variable O&M | $ | 1271669.2072 | 1172584.0899 | 1191454.1573 | 1163013.4679 | 1235651.4006
| $/kW-Yr | 2.5433 | 2.3452 | 2.3829 | 2.326 | 2.4713
| Mills/kWH | 0.44667 | 0.41187 | 0.41849 | 0.4085 | 0.43402
| $/ton PM removed | 3.0815 | 3.6212 | 2.7506 | 3.2041 | 2.0353
Fixed Charges | $ | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| $/kW-Yr | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| Mills/kWH | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| $/ton PM removed | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
TOTAL | $ | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| $/kW-Yr | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| Mills/kWH | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| $/ton PM removed | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Levelized Current Dollars
Fixed O&M | $/kW-Yr | 3.552 | 3.2534 | 3.4492 | 3.296 | 3.7841
| Mills/kWH | 0.62382 | 0.57138 | 0.60577 | 0.57886 | 0.66457
| $/ton PM removed | 4.3037 | 5.0237 | 3.9815 | 4.5403 | 3.1164
Variable O&M | $/kW-Yr | 3.461 | 3.1913 | 3.2427 | 3.1653 | 3.363
| Mills/kWH | 0.60784 | 0.56047 | 0.56949 | 0.5559 | 0.59062
| $/ton PM removed | 4.1934 | 4.9278 | 3.7431 | 4.3602 | 2.7696
Fixed Charges | $/kW-Yr | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| Mills/kWH | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| $/ton PM removed | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
TOTAL | $/kW-Yr | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| Mills/kWH | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| $/ton PM removed | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Levelized Constant Dollars
Fixed O&M | $/kW-Yr | 2.6102 | 2.3908 | 2.5347 | 2.4221 | 2.7807
| Mills/kWH | 0.45842 | 0.41988 | 0.44515 | 0.42538 | 0.48836
| $/ton PM removed | 3.1626 | 3.6917 | 2.9258 | 3.3365 | 2.2901
Variable O&M | $/kW-Yr | 2.5433 | 2.3452 | 2.3829 | 2.326 | 2.4713
| Mills/kWH | 0.44667 | 0.41187 | 0.41849 | 0.4085 | 0.43402
| $/ton PM removed | 3.0815 | 3.6212 | 2.7506 | 3.2041 | 2.0353
Fixed Charges | $/kW-Yr | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| Mills/kWH | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| $/ton PM removed | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
TOTAL | $/kW-Yr | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| Mills/kWH | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| $/ton PM removed | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
SO2 Control Costs |  | LSD | LSD | LSD | LSD | LSD
Total Capital Requirement (TCR) | $ | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| $/kW | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
First Year Costs
Fixed O&M | $ | 4808262.9219 | 5208226.3034 | 5595017.3685 | 4788487.5683 | 6060795.7385
| $/kW-Yr | 9.6165 | 10.4165 | 11.19 | 9.577 | 12.1216
| Mills/kWH | 1.6889 | 1.8294 | 1.9652 | 1.6819 | 2.1288
| $/ton SO2 removed | 397.7869 | 97.6361 | 72.3567 | 241.3827 | 56.9395
Variable O&M | $ | 4542731.9874 | 13724195.405 | 22229418.4867 | 8466036.3578 | 32837601.5904
| $/kW-Yr | 9.0855 | 27.4484 | 44.4588 | 16.9321 | 65.6752
| Mills/kWH | 1.5956 | 4.8206 | 7.808 | 2.9737 | 11.5341
| $/ton SO2 removed | 375.8196 | 257.2808 | 287.4787 | 426.7641 | 308.5001
Fixed Charges | $ | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| $/kW-Yr | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| Mills/kWH | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| $/ton SO2 removed | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
TOTAL | $ | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| $/kW-Yr | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| Mills/kWH | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| $/ton SO2 removed | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Levelized Current Dollars
Fixed O&M | $/kW-Yr | 13.0863 | 14.1749 | 15.2276 | 13.0325 | 16.4952
| Mills/kWH | 2.2983 | 2.4894 | 2.6743 | 2.2888 | 2.897
| $/ton SO2 removed | 541.3146 | 132.8647 | 98.4642 | 328.4773 | 77.4841
Variable O&M | $/kW-Yr | 12.3636 | 37.3522 | 60.5003 | 23.0414 | 89.3718
| Mills/kWH | 2.1713 | 6.5599 | 10.6253 | 4.0466 | 15.6958
| $/ton SO2 removed | 511.4211 | 350.1117 | 391.2054 | 580.7472 | 419.8117
Fixed Charges | $/kW-Yr | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| Mills/kWH | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| $/ton SO2 removed | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
TOTAL | $/kW-Yr | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| Mills/kWH | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| $/ton SO2 removed | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Levelized Constant Dollars
Fixed O&M | $/kW-Yr | 9.6165 | 10.4165 | 11.19 | 9.577 | 12.1216
| Mills/kWH | 1.6889 | 1.8294 | 1.9652 | 1.6819 | 2.1288
| $/ton SO2 removed | 397.7869 | 97.6361 | 72.3567 | 241.3827 | 56.9395
Variable O&M | $/kW-Yr | 9.0855 | 27.4484 | 44.4588 | 16.9321 | 65.6752
| Mills/kWH | 1.5956 | 4.8206 | 7.808 | 2.9737 | 11.5341
| $/ton SO2 removed | 375.8196 | 257.2808 | 287.4787 | 426.7641 | 308.5001
Fixed Charges | $/kW-Yr | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| Mills/kWH | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| $/ton SO2 removed | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
TOTAL | $/kW-Yr | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| Mills/kWH | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| $/ton SO2 removed | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!

## NOX Cost & Tech. Results
SCR (high-dust) - Preliminary |  | Case1 | Case2 | Case3 | Case4 | Case5 |  | Equations (bold indicates existing cuecost model parameter, blue indicates new input value from NOX User Input Sheet, normal text parameters are calculated on this sheet)
Ammonia Injection Rate | lb/hr | 1574.2755 | 1574.2755 | 1574.2755 | 1574.2755 | 1574.2755 | NH3= 3.702 x 10-4 * NH3:NOX ratio * BSIZE * HTR * NOx | =3.702x10^4*NH3:NOX ratio * BSIZE(MW) * HTR (Btu/kWh) * NOX(lb/10^6 Btu)
Space Velocity | 1/hr | 2839.6346 | 2839.6346 | 2839.6346 | 2839.6346 | 2839.6346 | If SV is not input then SV =6131.06/3 * (n)^-0.241 * (NH3:NOx ratio)^-2.306 | = 6131.06 / 3 * (NOX reduction eff) ^ -0.241 * (NH3:NOX ratio) ^-2.306
Gross Catalyst Volume | ft3 | 24663.6635 | 23106.502 | 23203.8542 | 23038.9284 | 23559.2783 | CV = Q/SV | = flue gas volume flow rate (scfm) * 60min/hr / space velocity (1/hr)
SCR Capital Costs |  | Case1 | Case2 | Case3 | Case4 | Case5
Cost Basis (Year) |  | 1998 | 1998 | 1998 | 1998 | 1998
Reactor Housing and Installation | $ | 4055272.4153 | 3927985.7149 | 3936069.6608 | 3922364.2873 | 3965437.2581 | DCr=18.65* Nr,tot * (CV/Nr,tot)^0.489*1000*Retrofit Factor | DCr=18.65* Number of Reactors * (Gross Catalyst Volume/Number of Reactors)^0.489*1000*Retrofit Factor
Ammonia Handling and Injection | $ | 1917146.6577 | 1917146.6577 | 1917146.6577 | 1917146.6577 | 1917146.6577 | DCnh3=50.8(NH3 (lb/hr))^0.482*1000*Retrofit Factor | DCnh3=50.8(Ammonia Injection Rate (lb/hr))^0.482*1000*Retrofit Factor
Flue Gas Handling:Ductwork and Fans | $ | 5112798.4889 | 4886548.899 | 4900827.761 | 4876626.8985 | 4952803.8257 | DCfgh=143.66*(Gfg)^0.694*Retrofit Factor*1989 CI/1982 CI (Note: IAPCS Eqution used) | DCfgh=143.66*(Flue gas (SCFM) * (750+460)/(70+460) )^0.694*Retrofit Factor*108.7/91.8, Gfg = flue gas ACFM, assume maximum operating SCR temperature, 750 deg F; atmospheric pressure
Air Preheater Modifications | $ | 1271465.6172 | 1206829.4925 | 1210895.4665 | 1204005.2236 | 1225711.1498 | Dcaph,mod=1370*Nt,aph(UAt,aph/4.4/10^6/Nt,aph)^0.8 *1000*Retrofit Factor | Dcaph,mod = 1370*No. air preheaters * (SCFM economizer exit*60(m/hr)*7.9 *(Tair heater outlet-725)*(ln(125/(Tair heater outlet-Tinlet air temperature))/0.7302/530/(125-Tair heater outlet+Tinlet air)/4.4/10^6/No. air preheaters)^0.8 *1000*Retrofit Factor,
Misc. Other Direct Capital Costs | $ | 416261.6537 | 416261.6537 | 416261.6537 | 416261.6537 | 416261.6537 | DCmisc=(100+300 * (BSIZE/550)^0.6) * 1,000*Retrofit Factor | DCmisc=(100+300 * (BSIZE(MW)/550)^0.6) * 1,000*Retrofit Factor
Equipment Capital Cost Subtotal | $ | 12772944.8328 | 12354772.4178 | 12381201.1997 | 12336404.7208 | 12477360.545 | =sum(Direct Capital Costs) | capital costs=SUM(direct capital costs)
Instruments & Controls | $ | 255458.8967 | 247095.4484 | 247624.024 | 246728.0944 | 249547.2109 | =0.02*Equipment Capital Cost Subtotal | =0.02*capital costs
Taxes | $ | 766376.69 | 741286.3451 | 742872.072 | 740184.2832 | 748641.6327 | =Equipment Capital Cost Subtotal * Sales Tax % | =capital costs*(Sales Tax)
Freight | $ | 638647.2416 | 617738.6209 | 619060.06 | 616820.236 | 623868.0273 | =0.05 * Equipment Capital Cost Subtotal | =0.05*capital costs
Total Direct Cost |  | 14433427.6611 | 13960892.8321 | 13990757.3557 | 13940137.3345 | 14099417.4159
Total Direct Cost with Retrofit Factor | $ | 18763455.9594 | 18149160.6817 | 18187984.5624 | 18122178.5349 | 18329242.6406 |  | Total Direct Cost with Retrofit Factor= Total Direct Cost*Def_RetroFact
General Facilities | $ | 938172.798 | 907458.0341 | 909399.2281 | 906108.9267 | 916462.132 | =Total Direct Cost with Retrofit Factor * General Facilities (%) | =Total Direct Cost with Retrofit Factor*(General Facilities)
Engineering Fees | $ | 1876345.5959 | 1814916.0682 | 1818798.4562 | 1812217.8535 | 1832924.2641 | =Total Direct Cost with Retrofit Factor * Engineering (%) | =Total Direct Cost with Retrofit Factor*(Engineering Fees)
Contingency | $ | 3752691.1919 | 3629832.1363 | 3637596.9125 | 3624435.707 | 3665848.5281 | =Total Direct Cost with Retrofit Factor * Contingency (%) | =Total Direct Cost with Retrofit Factor*(Contingency)
Total Plant Cost (TPC) | $ | 25330665.5452 | 24501366.9203 | 24553779.1592 | 24464941.0221 | 24744477.5648 |  | Total Plant Cost (TPC)=SUM(four lines above)
Total Plant Cost (TPC) w/ Prime Contractor's Markup | $ | 26090585.5115 | 25236407.9279 | 25290392.534 | 25198889.2527 | 25486811.8918
Total Cash Expended (TCE) | $ | 25338043.4089 | 24508503.2408 | 24560930.7454 | 24472066.733 | 24751684.6942 |  | Total Cash Expended (TCE)=Total Plant Cost (TPC)*VLOOKUP(2,Constants_CC!AFDC / TCE FACTORS FOR CASE 1,3)
Allow. for Funds During Constr. (AFDC) | $ | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Allow. for Funds During Constr. (AFDC)=Total Plant Cost (TPC)*VLOOKUP(2,Constants_CC!AFDC / TCE FACTORS FOR CASE 1,2)
Total Plant Investment (TPI) | $ | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Total Plant Investment (TPI)=Total Cash Expended (TCE)+Allow. for Funds During Constr. (AFDC)
Preproduction Costs | $ | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | =0.02*TPI+(Op. Lab,$/yr+Maint.,$/yr)/12+(Ammonia,$/yr)/(12*CF) | =0.02*TPI+(Op. Lab,$/yr+Maint.,$/yr)/12+(Ammonia,$/yr)/(12*CF)
Inventory Capital
Initial Ammonia(60 days) | $ | 151522.2537 | 151522.2537 | 151522.2537 | 151522.2537 | 151522.2537 | =NH3(lb/hr) * 24(hours/day) * UCNH3($/ton) / 2000(lb/ton) * 60days * CF | =60*24/2000*Ammonia Injection rate (lb/hr)*Ammonia Cost ($/ton)*CF
Initial Catalyst | $ | 8788649.8691 | 8233770.9398 | 8268461.4101 | 8209691.7548 | 8395113.2316 | DCcat=CV (cf)* UC cat($/cf) | DCcat=Gross Catalyst Volume (cf)* UC cat($/cf)
Total Capital Requirement (TCR) | $ | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Total Capital Requirement (TCR)=SUM(Total Plant Investment (TPI), Preproduction Costs, Inventory Capital)
| $/kW | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | =Total Capital Requirement (TCR)/(BSIZE(MW)*1000)
SCR O&M Costs |  | Case1 | Case2 | Case3 | Case4 | Case5 |  | Equations (bold indicates existing cuecost model parameter, blue indicates new input value from NOX User Input Sheet, normal text parameters are calculated on this sheet)
Cost Basis (Year) |  | 1998 | 1998 | 1998 | 1998 | 1998
Ammonia | $/yr | 921760.3766 | 921760.3766 | 921760.3766 | 921760.3766 | 921760.3766 | =(8,760/2,000) * (NH3 * CF * UCNH3) | = (8,760/2,000) * (NH3 Injection rate (lb/hr) * Capacity Factor * Cost rate NH3($/ton))
Catalyst Replacement | $/yr | 2929549.9564 | 2744590.3133 | 2756153.8034 | 2736563.9183 | 2798371.0772 | = CV * UCCAT/ N | = catalyst volume (ft3) * Catalyst cost rate ($/ft3) / catalyst life (yr)
Catalyst Disposal | $/yr | 2265.1109 | 2122.1011 | 2131.042 | 2115.8952 | 2163.6841 | = 48 / 2,000 * Catalyst Replacement Cost * UCWASTE/UCCAT | = 48 / 2,000 * waste disposal rate ($/ton)* Catalyst Replacement Cost($/yr) / Catalyst cost rate ($/ft3)
Electricity | $/yr | 286797.4091 | 267799.6306 | 268987.3525 | 266975.2147 | 273323.6196 | = [-545,133 + 5.801*Qfg] * (CF/0.628) * UCELEC | = [-545,133 + 5.801* flue gas flow rate (acfm)] * (Capacity Factor/0.628) * electricity rate (mills/kWh)*$/1000mills
High-dust SCR Steam | $/yr | 119175.1764 | 119175.1764 | 119175.1764 | 119175.1764 | 119175.1764 | = [-14.91 + 33.29 * NH3 *CF] * UCSTEAM | = [-14.91 + 33.29 * Ammonia Injection Rate (lb/hr) * Capacity Factor] * Steam Rate ($/MMBtu)
Operating Labor | $/yr | 120675 | 120675 | 120675 | 120675 | 120675 | = (1,341 + 5.363 * BSIZE) * UCOL | = (1,341 + 5.363 * BSIZE(MW) ) * Operating Labor Wage ($/labor-hr)
Maintenance | $/yr | 379959.9832 | 367520.5038 | 368306.6874 | 366974.1153 | 371167.1635 | = Maintenance Cost % * TPC | =Maintenance(% capital cost/year) * total plant cost ($)
Total O&M Costs | $/yr | 4760183.0125 | 4543643.1018 | 4557189.4383 | 4534239.6965 | 4606636.0974
SNCR - Preliminary |  | Case1 | Case2 | Case3 | Case4 | Case5 |  | Equations (bold indicates existing cuecost model parameter, blue indicates new input value from NOX User Input Sheet, normal text parameters are calculated on this sheet)
Number of Wall Injectors | integer | 18 | 18 | 18 | 18 | 18 | Ni = (8.6 + 0.03* BSIZE - 0.013*n)* NIL | = (8.6 + 0.03* BSIZE (MW) - 0.013* NOX Reduction Eff.)* No. Injection Levels
Number of Lances | integer | 0 | 0 | 0 | 0 | 0 | Nl = (2 + 0.013 BSIZE)* NLL | = (2 + 0.013 BSIZE(MW))* No. Lance Levels
Urea Injection Rate | lb/hr | 3685.5 | 3685.5 | 3685.5 | 3685.5 | 3685.5 | UREA = 6.5*10^-4 * UREA:NOX * BSIZE * HTR * NOx | = 6.5^10-4 * UREA:NOX ratio * BSIZE(MW)* HTR (Btu/kWh) * NOX(lb/10^6 Btu)
Ammonia Injection Rate | lb/hr | 2099.034 | 2099.034 | 2099.034 | 2099.034 | 2099.034 | NH3 = 3.702 x 10-4 * NH3:NOX ratio * BSIZE * HTR * NOx | =3.702x10^4*NH3:NOX ratio * BSIZE(MW) * HTR (Btu/kWh) * NOX(lb/10^6 Btu)
SNCR Capital Costs |  | Case1 | Case2 | Case3 | Case4 | Case5
Cost Basis (Year) |  | 1998 | 1998 | 1998 | 1998 | 1998
Urea Based SNCR Costs
Urea Storage & Handling | $ | 471758.3919 | 471758.3919 | 471758.3919 | 471758.3919 | 471758.3919 | =If Urea based, then = 38143*(UREA/8.7)^0.417*(0.915), else 0 | =(38143*(UREA injection rate (lb/hour)/8.7)^0.417)*(0.915)
Urea Injection | $ | 304184.432 | 304184.432 | 304184.432 | 304184.432 | 304184.432 | =If Urea based, then = (117809+10477*Ni+53111*Nl)*(0.915), else 0 | =(117809+10477*No. Injectors+53111*No. lances)*(0.915)
Controls/Miscellaneous | $ | 164053.7889 | 164053.7889 | 164053.7889 | 164053.7889 | 164053.7889 | =If Urea based, then = (96082+106*BSIZE+898*Ni+2433*Nl)*(0.915), else 0 | =(96082+106*BSIZE(MW)+898*No. injectors+2433*No. lances)*(0.915)
Air Heater Modifications | $ | 983911.9846 | 949252.743 | 953329.0001 | 945675.7312 | 960771.1741 | =If Urea based, then = 11.2*(Economizer Outlet (ACFM))^0.772*(0.915), else 0 | ACFM AirHeater Inlet = Economizer outlet (wet lb/hour)*0.7302(atm-cf/lbmol/d R)*(678+460)d R/29(lb/lbmol)/1atm; 678 d F is average from Acid Rain Study
Ammonia Based SNCR Costs
Ammonia Storage, Handling, Injection, Controls | $ | 0 | 0 | 0 | 0 | 0 | =If Amonia based then = 63822*(BSIZE)^0.6*(0.655), else 0 | =(63822*(BSIZE(MW))^0.6)*(0.655)
Air Heater Modifications | $ | 0 | 0 | 0 | 0 | 0 | =If Amonia based then = 11.2*(Economizer Outlet (ACFM))^0.772*(0.655), else 0 | ACFM AirHeater Inlet = Economizer outlet (wet lb/hour)*0.7302(atm-cf/lbmol/d R)*(678+460)d R/29(lb/lbmol)/1atm; 678 d F is average from Acid Rain Study
Total Direct Cost | $ | 1923908.5975 | 1889249.3559 | 1893325.613 | 1885672.3441 | 1900767.787 |  | Total Direct Cost=Installation+Purchased Equipment Cost Subtotal
Total Direct Cost with Retrofit Factor | $ | 2501081.1768 | 2456024.1627 | 2461323.2969 | 2451374.0474 | 2470998.1231 |  | Total Direct Cost with Retrofit Factor= Total Direct Cost*Def_RetroFact
General Facilities | $ | 125054.0588 | 122801.2081 | 123066.1648 | 122568.7024 | 123549.9062 |  | =Total Direct Cost with Retrofit Factor*(General Facilities)
Engineering Fees | $ | 250108.1177 | 245602.4163 | 246132.3297 | 245137.4047 | 247099.8123 |  | =Total Direct Cost with Retrofit Factor*(Engineering Fees)
Contingency | $ | 500216.2354 | 491204.8325 | 492264.6594 | 490274.8095 | 494199.6246 |  | =Total Direct Cost with Retrofit Factor*(Contingency)
Total Plant Cost (TPC) | $ | 3376459.5886 | 3315632.6196 | 3322786.4509 | 3309354.964 | 3335847.4661 |  | Total Plant Cost (TPC)=SUM(four lines above)
Total Plant Cost (TPC) w/ Prime Contractor's Markup | $ | 3477753.3763 | 3415101.5982 | 3422470.0444 | 3408635.6129 | 3435922.8901
Total Cash Expended (TCE) | $ | 3377443.0235 | 3316598.3378 | 3323754.2527 | 3310318.8538 | 3336819.0722 |  | Total Cash Expended (TCE)=Total Plant Cost (TPC)*VLOOKUP(2,Constants_CC!AFDC / TCE FACTORS FOR CASE 1,3)
Allow. for Funds During Constr. (AFDC) | $ | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Allow. for Funds During Constr. (AFDC)=Total Plant Cost (TPC)*VLOOKUP(2,Constants_CC!AFDC / TCE FACTORS FOR CASE 1,2)
Total Plant Investment (TPI) | $ | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Total Plant Investment (TPI)=Total Cash Expended (TCE)+Allow. for Funds During Constr. (AFDC)
Preproduction Costs | $ | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | =0.02*TPI+(Op. Lab,$/yr+Maint.,$/yr)/12+(Reagent,$/yr+Water,$/yr)/(12*CF)
Inventory Capital | $ | 387996.9093 | 387996.9093 | 387996.9093 | 387996.9093 | 387996.9093 |  | IF UREA =60*24/2000*Urea Injection rate (lb/hr)*Urea Cost ($/ton); IF AMMONIA =60*24/2000*Ammonia Injection rate (lb/hr)*Ammonia Cost ($/ton)*CF
Total Capital Requirement (TCR) | $ | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Total Capital Requirement (TCR)=SUM(Total Plant Investment (TPI), Preproduction Costs, Inventory Capital)
| $/kW | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | =Total Capital Requirement (TCR)/(BSIZE(MW)*1000)
SNCR O&M Costs |  | Case1 | Case2 | Case3 | Case4 | Case5
Cost Basis (Year) |  | 1998 | 1998 | 1998 | 1998 | 1998
Operating and Supervisory Labor | $/yr | 65700 | 65700 | 65700 | 65700 | 65700 | = 0.25* 8,760 *UCOL | = 0.25 * 8,760 * supervisory and labor wage rate ($/hr)
Maintenance Labor and Materials | $/yr | 50646.8938 | 49734.4893 | 49841.7968 | 49640.3245 | 50037.712 | =Maintenance Cost %* TPC | = Maintenance(% capital cost/year) * total plant cost ($)
Reagent | $/yr | 2360314.5316 | 2360314.5316 | 2360314.5316 | 2360314.5316 | 2360314.5316 | IF UREA =Urea *8760* CF/2,000 * UCUREA*(1+ Esc. Consumables O&M)^(Cost Basis year-1998); IF AMMONIA = NH3 *8760* CF/2,000 * UCHN3 | (IF UREA =Injection rate of pure Urea(lb/hr) *8760* CF/2,000 * Urea cost rate ($/ton)*(1+ Esc. Consumables O&M)^(Cost Basis year-1998); IF AMMONIA = Injection rate of ammonia (lb/hr) *8760* CF/2,000 * Ammonia cost rate ($/ton))
Electricity | $/yr | 1592.8965 | 1592.8965 | 1592.8965 | 1592.8965 | 1592.8965 | IF UREA (5.97 + 0.29* NI + 0.87* NL) *8760* CF*UCELEC*(1+ Esc. Consumables O&M)^(Cost Basis year-1998); IF AMMONIA Steam ((BSIZE* 0.12 * 8,760 * CF)*UCELEC; if Ammonia Air:(BSIZE *4.23 * 8,760 * CF))*UCELE | (IF UREA = (5.97 + 0.29* No. Wall Injectors + 0.87* No. Lances) * 8760* CF * Electricity cost ($/kWh); IF AMMONIA and steam = ((BSIZE* 0.12 * 8,760 * CF)* Electricity cost ($/kWh)), IF AMMONIA and air = (BSIZE *4.23 * 8,760 * CF))*UCELE
Water | $/yr | 2502.8546 | 2502.8546 | 2502.8546 | 2502.8546 | 2502.8546 | IF AMMONIA = (1.0 * NI + 2.5* NL) *60 *8760* CF/1,000 * UCH2O | IF AMMONIA = (1.0 * No. Wall Injectors + 2.5* No. Lances) *60 *8760* CF/1,000 * Water cost rate ($/1000 gal)
Steam (for steam atomization) | $/yr | 0 | 0 | 0 | 0 | 0 | IF UREA and Steam = BSIZE * 99.2 * 8,760* CF/1,000*UCSTEAM | IF UREAand steam =BSIZE(MW) * 99.2 * 8,760* CF/1,000 * Steam atomization cost rate ($/1000 lb)
Total O&M Costs | $/yr | 2480757.1765 | 2479844.772 | 2479952.0795 | 2479750.6072 | 2480147.9947
Low NOX Burner Technology Capital Costs |  | Case1 | Case2 | Case3 | Case4 | Case5
Cost Basis (Year) |  | 1998 | 1998 | 1998 | 1998 | 1998
Total Capital Requirement with Retrofit (TCR) | $ | 9618182.6117 | 9618182.6117 | 9618182.6117 | 9618182.6117 | 9618182.6117 | IF(Boiler Type="T",IF(RD="H",57.04*(300/BSIZE)^0.679, IF(RD="L",11.71,21.2*(300/BSIZE)^0.35)), IF(Boiler Type="W",IF(RD="H",27.72*(300/BSIZE)^0.573, IF(RD="L",6.53*(300/BSIZE)^0.857,15.37*(300/BSIZE)^0.35))),0)*1000*BSIZE*388/357.6
| $/kW | 19.2364 | 19.2364 | 19.2364 | 19.2364 | 19.2364 |  | =Total Capital Requirement (TCR)/(BSIZE(MW)*1000)
Low NOX Burner Technology O&M Costs |  | Case1 | Case2 | Case3 | Case4 | Case5 |  | Equations (bold indicates existing cuecost model parameter, blue indicates new input value from NOX User Input Sheet, normal text parameters are calculated on this sheet)
Cost Basis (Year) |  | 1998 | 1998 | 1998 | 1998 | 1998
Maintenance Labor | $/yr | 76945.4609 | 76945.4609 | 76945.4609 | 76945.4609 | 76945.4609 | =0.008 * TPC | =0.008/yr * Total Plant Costs ($)
Maintenance Materials | $/yr | 115418.1913 | 115418.1913 | 115418.1913 | 115418.1913 | 115418.1913 | =0.012 * TPC | =0.012/yr * Total Plant Costs ($)
Control, Administration, Overhead | $/yr | 23083.6383 | 23083.6383 | 23083.6383 | 23083.6383 | 23083.6383 | =0.3*Maintenance Labor Cost | =0.3*Maintenance Labor Cost($/year)
Total O&M Costs | $/yr | 215447.2905 | 215447.2905 | 215447.2905 | 215447.2905 | 215447.2905
Natural Gas Reburning - Preliminary |  | Case1 | Case2 | Case3 | Case4 | Case5
Fraction of heat input as reburn fuel | fraction | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | if(input>0,input, if(NOx=0,0.15,RBFRAC =(n - 0.48) / 0.86 | RBFRAC =(Nox Reduction Efficiency - 0.48) / 0.86
Bottom Ash Rate | tons/yr | 966.5335 | 1038.2857 | 1629.8251 | 2057.6883 | 2367.802 | BA = BAF * ASH * (500/HHV) * Qin * 8,760 * CF/2,000 | BA = Bottom ash Factor * percent ash in coal (%wt) * (500/HHV) * boiler heat input (MMBtu/hr) * 8,760 * CF/2,000
Natural Gas Reburning Capital Costs |  | Case1 | Case2 | Case3 | Case4 | Case5
Cost Basis (Year) |  | 1998 | 1998 | 1998 | 1998 | 1998
Gas Pipeline from Fenceline to Boiler | $ | 1343264.4631 | 1343264.4631 | 1343264.4631 | 1343264.4631 | 1343264.4631 | =372.7*EXP(.00264*MW)*1000 replaced by 1923*MW+276519 (nk 1/24/00) | =372.7*EXP(.00624*MW Output)*1000
Fuel Injectors, Overfire Air Ports and Associated Piping, Valves, Windbox and Control Dampers | $ | 3389036.236 | 3389036.236 | 3389036.236 | 3389036.236 | 3389036.236 | =(BSIZE/500)^0.214*(BSIZE*3237.657+1504675) | =(BSIZE/500)^0.214*(BSIZE*m+b), m= 3237.657, b= 1504675
Total Direct Cost | $ | 4732300.6991 | 4732300.6991 | 4732300.6991 | 4732300.6991 | 4732300.6991 |  | Total Direct Cost=Installation+Purchased Equipment Cost Subtotal
Total Direct Cost with Retrofit Factor | $ | 6151990.9088 | 6151990.9088 | 6151990.9088 | 6151990.9088 | 6151990.9088 |  | Total Direct Cost with Retrofit Factor= Total Direct Cost*Def_RetroFact
General Facilities | $ | 123039.8182 | 123039.8182 | 123039.8182 | 123039.8182 | 123039.8182 |  | =Total Direct Cost with Retrofit Factor*(General Facilities)
Engineering Fees | $ | 615199.0909 | 615199.0909 | 615199.0909 | 615199.0909 | 615199.0909 |  | =Total Direct Cost with Retrofit Factor*(Engineering Fees)
Contingency | $ | 1230398.1818 | 1230398.1818 | 1230398.1818 | 1230398.1818 | 1230398.1818 |  | =Total Direct Cost with Retrofit Factor*(Contingency)
Total Plant Cost (TPC) | $ | 8120627.9997 | 8120627.9997 | 8120627.9997 | 8120627.9997 | 8120627.9997 |  | Total Plant Cost (TPC)=SUM(four lines above)
Total Plant Cost (TPC) w/ Prime Contractor's Markup | $ | 8364246.8397 | 8364246.8397 | 8364246.8397 | 8364246.8397 | 8364246.8397
Total Cash Expended (TCE) | $ | 8122993.2311 | 8122993.2311 | 8122993.2311 | 8122993.2311 | 8122993.2311 |  | Total Cash Expended (TCE)=Total Plant Cost (TPC)*VLOOKUP(2,Constants_CC!AFDC / TCE FACTORS FOR CASE 1,3)
Allow. for Funds During Constr. (AFDC) | $ | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Allow. for Funds During Constr. (AFDC)=Total Plant Cost (TPC)*VLOOKUP(2,Constants_CC!AFDC / TCE FACTORS FOR CASE 1,2)
Total Plant Investment (TPI) | $ | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Total Plant Investment (TPI)=Total Cash Expended (TCE)+Allow. for Funds During Constr. (AFDC)
Preproduction Costs | $ | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | =0.02*TPI+(Maint.,$/yr)/12+(Waste Disp.,$/yr)/(12*CF)
Inventory Capital | $ | 0 | 0 | 0 | 0 | 0 |  | 0
Total Capital Requirement (TCR) | $ | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Total Capital Requirement (TCR)=SUM(Total Plant Investment (TPI), Preproduction Costs, Inventory Capital)
| $/kW | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | =Total Capital Requirement (TCR)/(BSIZE(MW)*1000)
Natural Gas Reburning O&M Costs |  | Case1 | Case2 | Case3 | Case4 | Case5
Cost Basis (Year) |  | 1998 | 1998 | 1998 | 1998 | 1998
Electrical Consumption Savings | $/yr | -147925.4665 | -92899.4513 | -102078.7462 | -100927.4185 | -120493.3478 | =9.51 * 10^7 * Qin * CF * RBFRAC/HHV * UCELEC | =9.51 * 10^7 * boiler heat input(MMBtu/hr) * CF * Fraction of heat input as reburn fuel / HHV(Btu/lb) * Electricity Rate($/kW)
Maintenance | $/yr | 121601.295 | 121601.295 | 121601.295 | 121601.295 | 121601.295 | =Maintenance (% capital cost)*TPC-1387.5*RBFRAC*(BSIZE/500)^0.6 | =Maintenance(% capital cost) * Total Plant Cost($) - 1387.5 * Fraction of heat input as reburn fuel * (BSIZE(MW) / 500)^0.6
Waste Disposal Savings | $/yr | -139444.3093 | -148952.8211 | -230693.3232 | -289740.2456 | -332574.7152 | = [BA * RBFRAC + 4.336 * RBFRAC *PPHPRT * CF] * UCWASTE | = [Bottom ash rate(tons/year) * fraction of heat input as reburn fuel + 4.336 * fraction of heat input as reburn fuel * fly ash rate (ton/hr) * 2000 * CF] * Waste Disposal Rate($/ton)
Natural Gas Consumption | $/yr | 3632060.25 | 3632060.25 | 3632060.25 | 3632060.25 | 3632060.25 | = Qin * RBFRAC * 8,760 * CF * UCGAS | = boiler heat input(MMBtu/hr) * fraction of heat input as reburn fuel * 8,760 * CF * Unit cost of gas ($/mmBtu)
Total O&M Costs |  | 3466291.7693 | 3511809.2726 | 3420889.4756 | 3362993.8809 | 3300593.482

## LSFO Cost & Tech. Results
LSFO Material Balance - Preliminary |  |  | Case1 | Case 2 | Case 3 | Case 4 | Case 5
Flue Gas, Downstream of ID Fans
Temperature | °F |  | 295 | 295 | 295 | 295 | 295
Pressure | in. H2O |  | 10 | 10 | 10 | 10 | 10
Flow Rate | SCFM |  | 1307230.2751 | 1224628.8161 | 1229791.3084 | 1221075.8898 | 1248646.3335
Flow Rate | ACFM |  | 1884488.6884 | 1765411.3398 | 1772853.5315 | 1760289.4805 | 1800034.7268
CO2 | lb/hr |  | 1120919.593 | 1045412.0567 | 1055109.6603 | 1047495.1261 | 1048927.3597
N2 | lb/hr |  | 4084072.3846 | 4052345.0935 | 4061257.919 | 4030484.7626 | 4067354.248
SO2 | lb/hr |  | 4717.4548 | 20818.5066 | 30178.1437 | 7742.1619 | 41541.8791
O2 | lb/hr |  | 327881.1806 | 318570.7451 | 319514.6126 | 317252.3559 | 321553.7589
HCl | lb/hr |  | 65.6286 | 0 | 452.8827 | 447.7748 | 534.581
Other Gases | lb/hr |  | 1425.4136 | 2267.747 | 2237.8287 | 1873.3623 | 2030.0577
H2O | lb/hr |  | 450880.4571 | 267413.5611 | 269037.0701 | 274852.3078 | 317031.3818
Fly Ash | lb/hr |  | 157.5 | 157.5 | 157.5 | 157.5 | 157.5
Total (gas only) | lb/hr |  | 5989962.1123 | 5706827.7101 | 5737788.1173 | 5680147.8513 | 5798973.2664
Flue Gas, to Absorber
Temperature | °F |  | 295 | 295 | 295 | 295 | 295
Pressure | in. H2O |  | 10 | 10 | 10 | 10 | 10
Flow Rate | SCFM |  | 1307230.2751 | 1224628.8161 | 1229791.3084 | 1221075.8898 | 1248646.3335
Flow Rate | ACFM |  | 1884488.6884 | 1765411.3398 | 1772853.5315 | 1760289.4805 | 1800034.7268
CO2 | lb/hr |  | 1120919.593 | 1045412.0567 | 1055109.6603 | 1047495.1261 | 1048927.3597
N2 | lb/hr |  | 4084072.3846 | 4052345.0935 | 4061257.919 | 4030484.7626 | 4067354.248
SO2 | lb/hr |  | 4717.4548 | 20818.5066 | 30178.1437 | 7742.1619 | 41541.8791
O2 | lb/hr |  | 327881.1806 | 318570.7451 | 319514.6126 | 317252.3559 | 321553.7589
HCl | lb/hr |  | 65.6286 | 0 | 452.8827 | 447.7748 | 534.581
Other Gases | lb/hr |  | 1425.4136 | 2267.747 | 2237.8287 | 1873.3623 | 2030.0577
H2O | lb/hr |  | 450880.4571 | 267413.5611 | 269037.0701 | 274852.3078 | 317031.3818
Fly Ash | lb/hr |  | 157.5 | 157.5 | 157.5 | 157.5 | 157.5
Total (gas only) | lb/hr |  | 5989962.1123 | 5706827.7101 | 5737788.1173 | 5680147.8513 | 5798973.2664
Flue Gas, from Absorbers (total)
Temperature | °F |  | 127 | 127 | 127 | 127 | 127
Pressure | in. H2O |  | 4 | 4 | 4 | 4 | 4
Flow Rate | SCFM |  | 1338259.3766 | 1330939.0822 | 1344225.1561 | 1312603.6534 | 1356202.3874
Flow Rate | ACFM |  | 1522197.3313 | 1513870.8941 | 1528983.0813 | 1493015.34 | 1542606.5312
CO2 | lb/hr |  | 1124037.9681 | 1058998.902 | 1075078.2385 | 1052818.1585 | 1076361.5938
N2 | lb/hr |  | 4098917.8536 | 4117859.3397 | 4156226.2266 | 4054848.7532 | 4198083.3607
SO2 | lb/hr |  | 235.8727 | 1040.9253 | 1508.9072 | 387.1081 | 2077.094
O2 | lb/hr |  | 331238.9463 | 333388.8346 | 340994.6564 | 322763.0321 | 351122.2238
HCl | lb/hr |  | 0 | 0 | 0 | 0 | 0
Other Gases | lb/hr |  | 1425.4136 | 2267.747 | 2237.8287 | 1873.3623 | 2030.0577
H2O | lb/hr |  | 527512.9984 | 519172.6406 | 521356.5044 | 516411.5863 | 522285.1907
Fly Ash | lb/hr |  | 157.5 | 157.5 | 157.5 | 157.5 | 157.5
Total (gas only) | lb/hr |  | 6083369.0528 | 6032728.3892 | 6097402.3618 | 5949102.0004 | 6151959.5207
Heat Capacities
O2 | Btu/lbmol°F |  | 7.2129 | 7.2129 | 7.2129 | 7.2129 | 7.2129
CO2 | Btu/lbmol°F |  | 9.3543 | 9.3543 | 9.3543 | 9.3543 | 9.3543
N2 | Btu/lbmol°F |  | 6.9989 | 6.9989 | 6.9989 | 6.9989 | 6.9989
H2O | Btu/lbmol°F |  | 8.0694 | 8.0694 | 8.0694 | 8.0694 | 8.0694
NO | Btu/lbmol°F |  | 7.1644 | 7.1644 | 7.1644 | 7.1644 | 7.1644
SO2 | Btu/lbmol°F |  | 9.8301 | 9.8301 | 9.8301 | 9.8301 | 9.8301
HCl | Btu/lbmol°F |  | 6.951 | 6.951 | 6.951 | 6.951 | 6.951
O2 | Btu/lb°F |  | 0.22541 | 0.22541 | 0.22541 | 0.22541 | 0.22541
CO2 | Btu/lb°F |  | 0.21255 | 0.21255 | 0.21255 | 0.21255 | 0.21255
N2 | Btu/lb°F |  | 0.24978 | 0.24978 | 0.24978 | 0.24978 | 0.24978
H2O | Btu/lb°F |  | 0.44792 | 0.44792 | 0.44792 | 0.44792 | 0.44792
NO | Btu/lb°F |  | 0.23874 | 0.23874 | 0.23874 | 0.23874 | 0.23874
SO2 | Btu/lb°F |  | 0.15344 | 0.15344 | 0.15344 | 0.15344 | 0.15344
HCl | Btu/lb°F |  | 0.19064 | 0.19064 | 0.19064 | 0.19064 | 0.19064
Reheated Gas Temperature: | °C |  | 66.6667 | 66.6667 | 66.6667 | 66.6667 | 66.6667
| K |  | 339.6667 | 339.6667 | 339.6667 | 339.6667 | 339.6667
FGD Outlet Temperature: | °C |  | 52.7778 | 52.7778 | 52.7778 | 52.7778 | 52.7778
| K |  | 325.7778 | 325.7778 | 325.7778 | 325.7778 | 325.7778
Total Btu/hr | Btu/hr |  | 39352031.5532 | 39051549.5247 | 39445509.1622 | 38529571.1952 | 39782120.3992
Hot Reheat Air
Temperature | °F |  | 440 | 440 | 440 | 440 | 440
Pressure | in. H2O |  | 1 | 1 | 1 | 1 | 1
Flow Rate | SCFM |  | 120816.9768 | 119894.4494 | 121103.9679 | 118291.8931 | 122137.4178
Flow Rate | ACFM |  | 212274.4713 | 210653.5979 | 212778.7124 | 207837.9192 | 214594.4756
N2 | lb/hr |  | 414522.3917 | 411357.205 | 415507.0566 | 405858.8432 | 419052.8175
O2 | lb/hr |  | 125009.5512 | 124055.0103 | 125306.5014 | 122396.8423 | 126375.8139
H2O | lb/hr |  | 7106.2971 | 7052.0353 | 7123.1776 | 6957.775 | 7183.9637
Total | lb/hr |  | 546638.24 | 542464.2505 | 547936.7355 | 535213.4605 | 552612.5951
Heat Capacities of Hot Reheat Air
O2 | Btu/lbmol°F |  | 7.3317 | 7.3317 | 7.3317 | 7.3317 | 7.3317
N2 | Btu/lbmol°F |  | 7.113 | 7.113 | 7.113 | 7.113 | 7.113
H2O | Btu/lbmol°F |  | 8.3379 | 8.3379 | 8.3379 | 8.3379 | 8.3379
O2 | Btu/lb°F |  | 0.22912 | 0.22912 | 0.22912 | 0.22912 | 0.22912
N2 | Btu/lb°F |  | 0.25385 | 0.25385 | 0.25385 | 0.25385 | 0.25385
H2O | Btu/lb°F |  | 0.46282 | 0.46282 | 0.46282 | 0.46282 | 0.46282
Heated Temperature: | °C |  | 226.6667 | 226.6667 | 226.6667 | 226.6667 | 226.6667
| K |  | 499.6667 | 499.6667 | 499.6667 | 499.6667 | 499.6667
FGD Outlet Temperature: | °C |  | 66.6667 | 66.6667 | 66.6667 | 66.6667 | 66.6667
| K |  | 339.6667 | 339.6667 | 339.6667 | 339.6667 | 339.6667
Heat Capacities of Inlet Reheat Air
O2 | Btu/lbmol°F |  | 7.3043 | 7.3043 | 7.3043 | 7.3043 | 7.3043
N2 | Btu/lbmol°F |  | 7.0867 | 7.0867 | 7.0867 | 7.0867 | 7.0867
H2O | Btu/lbmol°F |  | 8.276 | 8.276 | 8.276 | 8.276 | 8.276
O2 | Btu/lb°F |  | 0.22827 | 0.22827 | 0.22827 | 0.22827 | 0.22827
N2 | Btu/lb°F |  | 0.25291 | 0.25291 | 0.25291 | 0.25291 | 0.25291
H2O | Btu/lb°F |  | 0.45938 | 0.45938 | 0.45938 | 0.45938 | 0.45938
Heated Temperature: | °C |  | 226.6667 | 226.6667 | 226.6667 | 226.6667 | 226.6667
| K |  | 499.6667 | 499.6667 | 499.6667 | 499.6667 | 499.6667
Inlet Air Temperature: | °C |  | 26.6667 | 26.6667 | 26.6667 | 26.6667 | 26.6667
| K |  | 299.6667 | 299.6667 | 299.6667 | 299.6667 | 299.6667
Required Heat | Btu/hr |  | 49190039.4415 | 48814436.9059 | 49306886.4527 | 48161963.9941 | 49727650.499
Oxidation Air (total)
Temperature | °F |  | 60 | 60 | 60 | 60 | 60
Pressure | in. H2O |  | 0 | 0 | 0 | 0 | 0
Flow Rate | SCFM |  | 4325.7085 | 19089.6986 | 27672.0939 | 7099.2382 | 38092.1633
Flow Rate | ACFM |  | 4402.2176 | 19427.3395 | 28161.5322 | 7224.8029 | 38765.9022
N2 | lb/hr |  | 14845.469 | 65514.2462 | 94968.3076 | 24363.9906 | 130729.1127
O2 | lb/hr |  | 4477.0209 | 19757.4526 | 28640.0584 | 7347.5682 | 39424.6198
H2O | lb/hr |  | 251.1924 | 1108.5321 | 1606.9088 | 412.2503 | 2211.9985
Total (gas only) | lb/hr |  | 19573.6823 | 86380.2309 | 125215.2747 | 32123.809 | 172365.731
Limestone to Ball Mill
Temperature | °F |  | 80 | 80 | 80 | 80 | 80
Wt.% Solids | wt. % |  | 100% | 100% | 100% | 100% | 100%
Inerts | lb/hr |  | 362.5833 | 1600.1091 | 2319.4903 | 625.3727 | 3192.9063
CaCO3 | lb/hr |  | 7351.9547 | 32444.766 | 47031.3664 | 12680.4284 | 64741.2695
Total | lb/hr |  | 7714.538 | 34044.8751 | 49350.8566 | 13305.8011 | 67934.1758
Limestone Slurry to Limestone Slurry Tank
Temperature | °F |  | 90 | 90 | 90 | 90 | 90
Flow Rate | GPM |  | 27.5299 | 121.4916 | 176.1122 | 47.4827 | 242.4281
Wt.% Solids | wt. % |  | 40% | 40% | 40% | 40% | 40%
Inerts | lb/hr |  | 362.5833 | 1600.1091 | 2319.4903 | 625.3727 | 3192.9063
CaCO3 | lb/hr |  | 7351.9547 | 32444.766 | 47031.3664 | 12680.4284 | 64741.2695
H2O | lb/hr |  | 11571.8069 | 51067.3127 | 74026.285 | 19958.7016 | 101901.2637
Total | lb/hr |  | 19286.3449 | 85112.1878 | 123377.1416 | 33264.5027 | 169835.4395
Limestone Slurry to Reaction Mix Tank (total)
Temperature | °F |  | 68 | 68 | 68 | 68 | 68
Flow Rate | GPM |  | 64.2364 | 283.4805 | 410.9284 | 110.793 | 565.6656
Wt.% Solids | wt. % |  | 20% | 20% | 20% | 20% | 20%
Inerts | lb/hr |  | 362.5833 | 1600.1091 | 2319.4903 | 625.3727 | 3192.9063
CaCO3 | lb/hr |  | 7351.9547 | 32444.766 | 47031.3664 | 12680.4284 | 64741.2695
H2O | lb/hr |  | 30858.1518 | 136179.5005 | 197403.4266 | 53223.2044 | 271736.7031
Total | lb/hr |  | 38572.6898 | 170224.3756 | 246754.2832 | 66529.0055 | 339670.8789
Slurry to Absorber
Temperature | °F |  | 126 | 126 | 126 | 126 | 126
Flow Rate | GPM |  | 187950.1673 | 104676.3635 | 188788.0237 | 184346.9812 | 190470.151
Wt.% Solids | wt. % |  | 15% | 15% | 15% | 15% | 15%
CaSO3*1/2H2O | lb/hr |  | 0 | 0 | 0 | 0 | 0
CaSO4*2H2O | lb/hr |  | 15305569.1082 | 8530789.7838 | 15372869.3991 | 14529687.6555 | 15511675.894
Inerts | lb/hr |  | 460753.3947 | 256807.8537 | 462779.3787 | 459676.1235 | 466957.9599
CaCl2 | lb/hr |  | 126934.43 | 0 | 137528.4335 | 500954.1171 | 118995.4646
CaCO3 | lb/hr |  | 330413.5555 | 247961.3826 | 322816.2084 | 422329.1783 | 343563.6471
H2O | lb/hr |  | 91934132.7682 | 51201501.1137 | 92343962.7114 | 90171666.7545 | 93166760.1389
Total | lb/hr |  | 108157803.2567 | 60237060.1338 | 108639956.131 | 106084313.8289 | 109607953.1046
Slurry from Rxn Tank to Thickener
Temperature | °F |  | 126 | 126 | 126 | 126 | 126
Flow Rate | GPM |  | 147.9047 | 652.2137 | 946.2219 | 250.7974 | 1302.3728
Wt.% Solids | wt. % |  | 15% | 15% | 15% | 15% | 15%
CaSO3*1/2H2O | lb/hr |  | 0 | 0 | 0 | 0 | 0
CaSO4*2H2O | lb/hr |  | 12044.4984 | 53153.3379 | 77050.1507 | 19767.1117 | 106063.7816
Inerts | lb/hr |  | 362.5833 | 1600.1091 | 2319.4903 | 625.3727 | 3192.9063
CaCl2 | lb/hr |  | 99.8892 | 0 | 689.3044 | 681.5299 | 813.6522
CaCO3 | lb/hr |  | 260.0142 | 1544.9889 | 1617.9827 | 574.5635 | 2349.1762
H2O | lb/hr |  | 72346.2488 | 319024.47 | 462835.926 | 122675.2738 | 637043.9255
Total | lb/hr |  | 85113.2339 | 375322.9059 | 544512.8541 | 144323.8516 | 749463.4417
LSFO Equipment Capital Costs |  |  | Case1 | Case 2 | Case 3 | Case 4 | Case 5
Cost Basis (Year) |  |  | 1998 | 1998 | 1998 | 1998 | 1998
Sizing Criteria
Reagent Feed System | $ | kpph Reag. | 7615854.4631 | 8944721.9363 | 9511755.2063 | 7942769.2466 | 10056797.5928
Ball Mill & Hydroclone System | $ | TPH Reag. | 1941840.6157 | 2245942.0857 | 2427959.745 | 2005462.9968 | 2654131.1785
DBA Acid Tank (pump, heater, agitator) | $ | gpm DBA | 0 | 249991.4819 | 0 | 0 | 0
SO2 Removal System | $ | kpph SO2 | 2065414.9561 | 2556256.465 | 2808289.1313 | 2163921.7934 | 3088928.758
Absorber Tower | $ | kACFM | 16158564.694 | 15574725.1555 | 15611708.1207 | 15549233.2506 | 15746209.6186 |  |  | Calculated Number of Spray Pumps
Spray Pumps | $ | slurry gpm | 2412210.2573 | 1384547.9298 | 2418607.0146 | 2384568.5889 | 2431414.925 | 5 | 3 | 5 | 5 | 5
Flue Gas Handling System | $ | * | 6778862.2752 | 6636724.502 | 6655348.5666 | 6616893.13 | 6695850.494
ID Fans | $ | ACFM | 2318005.5677 | 2216761.811 | 2223151.3334 | 2212359.477 | 2246416.2851 |  |  | Calculated No. of ID Fans and Flue Gas Flow per Fan
Waste / Byproduct Handling System | $ | kpph SO2 | 89044.5298 | 116165.2746 | 130964.0017 | 94299.8225 | 147976.1202 | 995631.9052 | 932719.7698 | 936651.703 | 930013.7379 | 951012.3438
Thickener System | $ | TPH solids | 172132.8042 | 368431.3518 | 482871.8558 | 212183.014 | 621500.9456 | 2 | 2 | 2 | 2 | 2
Support Equipment | $ | MW | 1945399 | 1945399 | 1945399 | 1945399 | 1945399
Chimney | $ | ACFM | 4662722.0078 | 4654190.2783 | 4669652.1024 | 4632682.4364 | 4683503.7371
TOTAL | $ |  | 46160051.171 | 46893857.2719 | 48885706.0778 | 45759772.7561 | 50318128.6548
* Based on flue gas flow and reheat temperature.
Capital Costs with Retrofit Factors
Reagent Feed System | $ |  | 9900610.802 | 11628138.5172 | 12365281.7682 | 10325600.0206 | 13073836.8706
Ball Mill & Hydroclone System | $ |  | 2524392.8004 | 2919724.7115 | 3156347.6685 | 2607101.8958 | 3450370.532
DBA Acid Tank (pump, heater, agitator) | $ |  | 0 | 324988.9265 | 0 | 0 | 0
SO2 Removal System | $ |  | 2685039.443 | 3323133.4045 | 3650775.8707 | 2813098.3315 | 4015607.3854
Absorber Tower | $ |  | 21006134.1022 | 20247142.7021 | 20295220.5569 | 20214003.2258 | 20470072.5042
Spray Pumps | $ |  | 3135873.3345 | 1799912.3088 | 3144189.119 | 3099939.1655 | 3160839.4025
Flue Gas Handling System | $ |  | 8812520.9577 | 8627741.8525 | 8651953.1366 | 8601961.069 | 8704605.6422
ID Fans | $ |  | 3013407.238 | 2881790.3542 | 2890096.7334 | 2876067.3201 | 2920341.1706
Waste / Byproduct Handling System | $ |  | 115757.8888 | 151014.8569 | 170253.2022 | 122589.7692 | 192368.9563
Thickener System | $ |  | 223772.6455 | 478960.7574 | 627733.4126 | 275837.9182 | 807951.2293
Support Equipment | $ |  | 2529018.7 | 2529018.7 | 2529018.7 | 2529018.7 | 2529018.7
Chimney | $ |  | 6061538.6101 | 6050447.3618 | 6070547.7332 | 6022487.1673 | 6088554.8582
TOTAL | $ |  | 60008066.5223 | 60962014.4535 | 63551417.9012 | 59487704.5829 | 65413567.2513
General Facilities
Reagent Feed System | $ |  | 990061.0802 | 1162813.8517 | 1236528.1768 | 1032560.0021 | 1307383.6871
Ball Mill & Hydroclone System | $ |  | 252439.28 | 291972.4711 | 315634.7669 | 260710.1896 | 345037.0532
DBA Acid Tank (pump, heater, agitator) | $ |  | 0 | 32498.8927 | 0 | 0 | 0
SO2 Removal System | $ |  | 268503.9443 | 332313.3405 | 365077.5871 | 281309.8331 | 401560.7385
Absorber Tower | $ |  | 2100613.4102 | 2024714.2702 | 2029522.0557 | 2021400.3226 | 2047007.2504
Spray Pumps | $ |  | 313587.3334 | 179991.2309 | 314418.9119 | 309993.9166 | 316083.9402
Flue Gas Handling System | $ |  | 881252.0958 | 862774.1853 | 865195.3137 | 860196.1069 | 870460.5642
ID Fans | $ |  | 301340.7238 | 288179.0354 | 289009.6733 | 287606.732 | 292034.1171
Waste / Byproduct Handling System | $ |  | 11575.7889 | 15101.4857 | 17025.3202 | 12258.9769 | 19236.8956
Thickener System | $ |  | 22377.2645 | 47896.0757 | 62773.3413 | 27583.7918 | 80795.1229
Support Equipment | $ |  | 252901.87 | 252901.87 | 252901.87 | 252901.87 | 252901.87
Chimney | $ |  | 606153.861 | 605044.7362 | 607054.7733 | 602248.7167 | 608855.4858
TOTAL | $ |  | 6000806.6522 | 6096201.4453 | 6355141.7901 | 5948770.4583 | 6541356.7251
Engineering Fees
Reagent Feed System | $ |  | 990061.0802 | 1162813.8517 | 1236528.1768 | 1032560.0021 | 1307383.6871
Ball Mill & Hydroclone System | $ |  | 252439.28 | 291972.4711 | 315634.7669 | 260710.1896 | 345037.0532
DBA Acid Tank (pump, heater, agitator) | $ |  | 0 | 32498.8927 | 0 | 0 | 0
SO2 Removal System | $ |  | 268503.9443 | 332313.3405 | 365077.5871 | 281309.8331 | 401560.7385
Absorber Tower | $ |  | 2100613.4102 | 2024714.2702 | 2029522.0557 | 2021400.3226 | 2047007.2504
Spray Pumps | $ |  | 313587.3334 | 179991.2309 | 314418.9119 | 309993.9166 | 316083.9402
Flue Gas Handling System | $ |  | 881252.0958 | 862774.1853 | 865195.3137 | 860196.1069 | 870460.5642
ID Fans | $ |  | 301340.7238 | 288179.0354 | 289009.6733 | 287606.732 | 292034.1171
Waste / Byproduct Handling System | $ |  | 11575.7889 | 15101.4857 | 17025.3202 | 12258.9769 | 19236.8956
Thickener System | $ |  | 22377.2645 | 47896.0757 | 62773.3413 | 27583.7918 | 80795.1229
Support Equipment | $ |  | 252901.87 | 252901.87 | 252901.87 | 252901.87 | 252901.87
Chimney | $ |  | 606153.861 | 605044.7362 | 607054.7733 | 602248.7167 | 608855.4858
TOTAL | $ |  | 6000806.6522 | 6096201.4453 | 6355141.7901 | 5948770.4583 | 6541356.7251
Contingency
Reagent Feed System | $ |  | 1980122.1604 | 2325627.7034 | 2473056.3536 | 2065120.0041 | 2614767.3741
Ball Mill & Hydroclone System | $ |  | 504878.5601 | 583944.9423 | 631269.5337 | 521420.3792 | 690074.1064
DBA Acid Tank (pump, heater, agitator) | $ |  | 0 | 64997.7853 | 0 | 0 | 0
SO2 Removal System | $ |  | 537007.8886 | 664626.6809 | 730155.1741 | 562619.6663 | 803121.4771
Absorber Tower | $ |  | 4201226.8204 | 4049428.5404 | 4059044.1114 | 4042800.6452 | 4094014.5008
Spray Pumps | $ |  | 627174.6669 | 359982.4618 | 628837.8238 | 619987.8331 | 632167.8805
Flue Gas Handling System | $ |  | 1762504.1915 | 1725548.3705 | 1730390.6273 | 1720392.2138 | 1740921.1284
ID Fans | $ |  | 602681.4476 | 576358.0708 | 578019.3467 | 575213.464 | 584068.2341
Waste / Byproduct Handling System | $ |  | 23151.5778 | 30202.9714 | 34050.6404 | 24517.9538 | 38473.7913
Thickener System | $ |  | 44754.5291 | 95792.1515 | 125546.6825 | 55167.5836 | 161590.2459
Support Equipment | $ |  | 505803.74 | 505803.74 | 505803.74 | 505803.74 | 505803.74
Chimney | $ |  | 1212307.722 | 1210089.4724 | 1214109.5466 | 1204497.4335 | 1217710.9716
TOTAL | $ |  | 12001613.3045 | 12192402.8907 | 12710283.5802 | 11897540.9166 | 13082713.4503
Total Plant Cost (TPC) | $ |  | 84011293.1312 | 85346820.2349 | 88971985.0616 | 83282786.4161 | 91578994.1518
Total Plant Cost (TPC) w/ Prime Contractor's Markup | $ |  | 86531631.9251 | 87907224.8419 | 91641144.6135 | 85781270.0086 | 94326363.9763
Total Cash Expended (TCE) | $ |  | 84035762.4399 | 85371678.532 | 88997899.232 | 83307043.5384 | 91605667.6452
Allow. for Funds During Constr. (AFDC) | $ |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Total Plant Investment (TPI) | $ |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Preproduction Costs | $ |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Inventory Capital | $ |  | 83317.0099 | 367684.6512 | 532989.2517 | 143702.6518 | 733689.0984
Total Capital Requirement (TCR) | $ |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| $/kW |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Maintenance Cost by Area |  |  | Case1 | Case 2 | Case 3 | Case 4 | Case 5
TPC w/o Retrofit Factor
Reagent Feed System | $ |  | 10966830.4269 | 12880399.5882 | 13696927.4971 | 11437587.7151 | 14481788.5336
Ball Mill & Hydroclone System | $ |  | 2796250.4866 | 3234156.6035 | 3496262.0328 | 2887866.7153 | 3821948.897
DBA Acid Tank (pump, heater, agitator) | $ |  | 0 | 359987.734 | 0 | 0 | 0
SO2 Removal System | $ |  | 2974197.5369 | 3681009.3096 | 4043936.349 | 3116047.3825 | 4448057.4116
Absorber Tower | $ |  | 23268333.1594 | 22427604.2239 | 22480859.6938 | 22390895.8809 | 22674541.8508
Spray Pumps | $ |  | 3473582.7705 | 1993749.019 | 3482794.101 | 3433778.7679 | 3501237.4919
Flue Gas Handling System | $ |  | 9761561.6762 | 9556883.2828 | 9583701.9359 | 9528326.1072 | 9642024.7113
ID Fans | $ |  | 3337928.0175 | 3192137.0078 | 3201337.92 | 3185797.6468 | 3234839.4505
Waste / Byproduct Handling System | $ |  | 128224.1229 | 167277.9954 | 188588.1625 | 135791.7444 | 213085.6131
Thickener System | $ |  | 247871.238 | 530541.1466 | 695335.4724 | 305543.5402 | 894961.3617
Support Equipment | $ |  | 2801374.56 | 2801374.56 | 2801374.56 | 2801374.56 | 2801374.56
Chimney | $ |  | 6714319.6912 | 6702034.0008 | 6724299.0275 | 6671062.7084 | 6744245.3814
TOTAL | $ |  | 66470473.6862 | 67527154.4716 | 70395416.752 | 65894072.7688 | 72458105.2629
First Year Maintenance Costs
Reagent Feed System | $ |  | 548341.5213 | 644019.9794 | 684846.3749 | 571879.3858 | 724089.4267
Ball Mill & Hydroclone System | $ |  | 139812.5243 | 161707.8302 | 174813.1016 | 144393.3358 | 191097.4448
DBA Acid Tank (pump, heater, agitator) | $ |  | 0 | 17999.3867 | 0 | 0 | 0
SO2 Removal System | $ |  | 148709.8768 | 174847.9422 | 202196.8175 | 155802.3691 | 222402.8706
Absorber Tower | $ |  | 1163416.658 | 1065311.2006 | 1124042.9847 | 1119544.794 | 1133727.0925
Spray Pumps | $ |  | 173679.1385 | 94703.0784 | 174139.7051 | 171688.9384 | 175061.8746
Flue Gas Handling System | $ |  | 488078.0838 | 477844.1641 | 479185.0968 | 476416.3054 | 482101.2356
ID Fans | $ |  | 166896.4009 | 159606.8504 | 160066.896 | 159289.8823 | 161741.9725
Waste / Byproduct Handling System | $ |  | 6411.2061 | 8363.8998 | 9429.4081 | 6789.5872 | 10654.2807
Thickener System | $ |  | 12393.5619 | 26527.0573 | 34766.7736 | 15277.177 | 44748.0681
Support Equipment | $ |  | 140068.728 | 140068.728 | 140068.728 | 140068.728 | 140068.728
Chimney | $ |  | 335715.9846 | 335101.7 | 336214.9514 | 333553.1354 | 337212.2691
TOTAL | $ |  | 3323523.6843 | 3306101.8172 | 3519770.8376 | 3294703.6384 | 3622905.2631
LSFO O&M Data and Costs |  |  | Case1 | Case 2 | Case 3 | Case 4 | Case 5
Cost Basis (Year) |  |  | 1998 | 1998 | 1998 | 1998 | 1998
Parameters
Reagent Required | lbs/hr |  | 7714.538 | 34044.8751 | 49350.8566 | 13305.8011 | 67934.1758
| lbs/MMBtu |  | 1.4694 | 6.4847 | 9.4002 | 2.5344 | 12.9398
DBA Required | lbs/hr |  | 0 | 197.7758 | 0 | 0 | 0
Percent SO2 Removal | % |  | 95% | 95% | 95% | 95% | 95%
FGD Sludge to Disposal | lbs/hr, dry |  | 12766.9851 | 56298.4359 | 81676.9281 | 21648.5777 | 112419.5163
Steam to FGD System | lbs/hr |  | 57522.7909 | 57083.5616 | 57659.4317 | 56320.5604 | 58151.4729
Total FGD Power Consumption | kW |  | 10000 | 8231 | 10000 | 10000 | 10000
FGD Byproduct | lbs/hr |  | 0 | 0 | 0 | 0 | 0
Fixed O&M Costs
Number of Operators |  |  | 28.1261 | 28.1261 | 28.1261 | 28.1261 | 28.1261
(40 hrs/week)
Operating Labor Cost ** | $/yr |  | 1755067.544 | 1755067.544 | 1755067.544 | 1755067.544 | 1755067.544
Maint. Labor & Matls. Cost | $/yr |  | 3323523.6843 | 3306101.8172 | 3519770.8376 | 3294703.6384 | 3622905.2631
Admin. & Support Labor | $/yr |  | 925343.1053 | 923252.4813 | 948892.7637 | 921884.6998 | 961268.8948
TOTAL | $/yr |  | 6003934.3336 | 5984421.8425 | 6223731.1453 | 5971655.8823 | 6339241.7019
Variable Operating Costs **
Reagent Costs | $/yr |  | 329449.3432 | 1453886.3918 | 2107528.3329 | 568224.2357 | 2901128.9767
DBA Costs | $/yr |  | 0 | 242119.1276 | 0 | 0 | 0
Disposal Costs | $/yr |  | 218085.6392 | 961689.8817 | 1395205.2861 | 369801.0049 | 1920350.1767
Credit for Byproduct | $/yr |  | 0 | 0 | 0 | 0 | 0
Steam Costs | $/yr |  | 1146371.7006 | 1137618.3 | 1149094.815 | 1122412.4476 | 1158900.7026
Power Costs | $/yr |  | 1423500 | 1171682.85 | 1423500 | 1423500 | 1423500
TOTAL | $/yr |  | 3117406.683 | 4966996.5511 | 6075328.434 | 3483937.6881 | 7403879.856
** These costs assume inputs are in current dollars (no escalation included).
Intermediate Material Balance Calcs. |  |  | Case1 | Case 2 | Case 3 | Case 4 | Case 5
Sulfite Reaction
SO2 | lbmole/hr |  | 69.9561 | 308.7218 | 447.5177 | 114.8101 | 616.0328
CaCO3 | lbmole/hr |  | 69.9561 | 308.7218 | 447.5177 | 114.8101 | 616.0328
H2O | lbmole/hr |  | 34.978 | 154.3609 | 223.7588 | 57.405 | 308.0164
CaSO3*1/2H2O | lbmole/hr |  | 69.9561 | 308.7218 | 447.5177 | 114.8101 | 616.0328
CO2 | lbmole/hr |  | 69.9561 | 308.7218 | 447.5177 | 114.8101 | 616.0328
SO2 | lb/hr |  | 4481.5821 | 19777.5813 | 28669.2365 | 7355.0538 | 39464.7852
CaCO3 | lb/hr |  | 7001.8616 | 30899.7771 | 44791.7775 | 11491.2698 | 61658.3519
H2O | lb/hr |  | 630.1412 | 2780.8639 | 4031.0917 | 1034.1711 | 5549.02
CaSO3*1/2H2O | lb/hr |  | 9034.8201 | 39871.3862 | 57796.8655 | 14827.7075 | 79560.5727
CO2 | lb/hr |  | 3078.7669 | 13586.8453 | 19695.2537 | 5052.7906 | 27111.6029
Sulfate Reaction
CaSO3*1/2H2O | lbmole/hr |  | 69.9561 | 308.7218 | 447.5177 | 114.8101 | 616.0328
O2 | lbmole/hr |  | 34.978 | 154.3609 | 223.7588 | 57.405 | 308.0164
H2O | lbmole/hr |  | 104.9341 | 463.0827 | 671.2765 | 172.2151 | 924.0492
CaSO4*2H2O | lbmole/hr |  | 69.9561 | 308.7218 | 447.5177 | 114.8101 | 616.0328
CaSO3*1/2H2O | lb/hr |  | 9034.8201 | 39871.3862 | 57796.8655 | 14827.7075 | 79560.5727
O2 | lb/hr |  | 1119.2552 | 4939.3632 | 7160.0146 | 1836.892 | 9856.155
H2O | lb/hr |  | 1890.4237 | 8342.5916 | 12093.2751 | 3102.5133 | 16647.0601
CaSO4*2H2O | lb/hr |  | 12044.4984 | 53153.3379 | 77050.1507 | 19767.1117 | 106063.7816
Water in Absorber
Mole Fraction H2O in Absorber | % |  | 0.13886 | 0.13886 | 0.13886 | 0.13886 | 0.13886
Moles H2O in Absorber | lbmole |  | 29280.4235 | 28818.3648 | 28933.3768 | 28658.9631 | 28983.8062
DBA Feed Calculations
SO2 Removed | lbs/hr |  | 4481.5821 | 19777.5813 | 28669.2365 | 7355.0538 | 39464.7852
DBA Added | lbs/hr |  | 0 | 197.7758 | 0 | 0 | 0
DBA Added | GPM |  | 0 | 0.26349 | 0 | 0 | 0

## LSD Cost & Tech. Results
LSD Material Balance - Preliminary |  |  | Case1 | Case 2 | Case 3 | Case 4 | Case 5
Flue Gas, Downstream of Air Heater
Temperature | °F |  | 300 | 300 | 300 | 300 | 300
Pressure | in. H2O |  | -12 | -12 | -12 | -12 | -12
Flow Rate | SCFM |  | 1307230.2751 | 1224628.8161 | 1229791.3084 | 1221075.8898 | 1248646.3335
Flow Rate | ACFM |  | 2004450.9879 | 1877793.4439 | 1885709.3887 | 1872345.5386 | 1914620.8777
CO2 | lb/hr |  | 1120919.593 | 1045412.0567 | 1055109.6603 | 1047495.1261 | 1048927.3597
N2 | lb/hr |  | 4084072.3846 | 4052345.0935 | 4061257.919 | 4030484.7626 | 4067354.248
SO2 | lb/hr |  | 4717.4548 | 20818.5066 | 30178.1437 | 7742.1619 | 41541.8791
O2 | lb/hr |  | 327881.1806 | 318570.7451 | 319514.6126 | 317252.3559 | 321553.7589
HCl | lb/hr |  | 65.6286 | 0 | 452.8827 | 447.7748 | 534.581
Other Gases | lb/hr |  | 1425.4136 | 2267.747 | 2237.8287 | 1873.3623 | 2030.0577
H2O | lb/hr |  | 450880.4571 | 267413.5611 | 269037.0701 | 274852.3078 | 317031.3818
Fly Ash | lb/hr |  | 28389.0075 | 30322.74 | 46955.16 | 58969.7325 | 67685.5725
Total (gas only) | lb/hr |  | 5989962.1123 | 5706827.7101 | 5737788.1173 | 5680147.8513 | 5798973.2664
Flue Gas, to Spray Dryer
Temperature | °F |  | 300 | 300 | 300 | 300 | 300
Pressure | in. H2O |  | -12 | -12 | -12 | -12 | -12
Flow Rate | SCFM |  | 653615.1376 | 612314.4081 | 614895.6542 | 610537.9449 | 624323.1667
Flow Rate | ACFM |  | 1002225.494 | 938896.7219 | 942854.6944 | 936172.7693 | 957310.4388
CO2 | lb/hr |  | 560459.7965 | 522706.0284 | 527554.8302 | 523747.563 | 524463.6799
N2 | lb/hr |  | 2042036.1923 | 2026172.5468 | 2030628.9595 | 2015242.3813 | 2033677.124
SO2 | lb/hr |  | 2358.7274 | 10409.2533 | 15089.0719 | 3871.0809 | 20770.9396
O2 | lb/hr |  | 163940.5903 | 159285.3726 | 159757.3063 | 158626.178 | 160776.8795
HCl | lb/hr |  | 32.8143 | 0 | 226.4414 | 223.8874 | 267.2905
Other Gases | lb/hr |  | 712.7068 | 1133.8735 | 1118.9144 | 936.6812 | 1015.0289
H2O | lb/hr |  | 225440.2285 | 133706.7806 | 134518.5351 | 137426.1539 | 158515.6909
Fly Ash | lb/hr |  | 14194.5037 | 15161.37 | 23477.58 | 29484.8662 | 33842.7862
Total (gas only) | lb/hr |  | 2994981.0562 | 2853413.8551 | 2868894.0586 | 2840073.9257 | 2899486.6332
Flue Gas, from Spray Dryers (total)
Temperature | °F |  | 147 | 147 | 147 | 147 | 147
Pressure | in. H2O |  | -17 | -17 | -17 | -17 | -17
Flow Rate | SCFM |  | 1402194.0741 | 1292635.6996 | 1313498.5241 | 1282054.7153 | 1362366.532
Flow Rate | ACFM |  | 1739624.1128 | 1603701.1378 | 1629584.4824 | 1590573.8997 | 1690212.2989
CO2 | lb/hr |  | 1120919.593 | 1045412.0567 | 1055109.6603 | 1047495.1261 | 1048927.3597
N2 | lb/hr |  | 4084072.3846 | 4052345.0935 | 4061257.919 | 4030484.7626 | 4067354.248
SO2 | lb/hr |  | 1320.8873 | 5829.1818 | 8449.8802 | 2167.8053 | 11631.7262
O2 | lb/hr |  | 327669.1112 | 317634.8658 | 318157.9783 | 316904.3132 | 319686.2769
HCl | lb/hr |  | 0 | 0 | 0 | 0 | 0
Other Gases | lb/hr |  | 1425.4136 | 2267.747 | 2237.8287 | 1873.3623 | 2030.0577
H2O | lb/hr |  | 722080.2712 | 465318.232 | 514007.2747 | 450070.9969 | 650129.7534
Fly Ash | lb/hr |  | 145107.743 | 113893.9175 | 152302.2225 | 127650.7176 | 213404.6632
Total (gas only) | lb/hr |  | 6257487.6609 | 5888807.177 | 5959220.5413 | 5848996.3665 | 6099759.422
Flue Gas Downstream of Particulate Control Device
Temperature | °F |  | 147 | 147 | 147 | 147 | 147
Pressure | in. H2O |  | -23 | -23 | -23 | -23 | -23
Flow Rate | SCFM |  | 1401065.0181 | 1291422.7907 | 1311831.5239 | 1280993.0022 | 1360044.4947
Flow Rate | ACFM |  | 1765866.7838 | 1627676.5036 | 1653399.1528 | 1614531.0628 | 1714165.5574
CO2 | lb/hr |  | 1120919.593 | 1045412.0567 | 1055109.6603 | 1047495.1261 | 1048927.3597
N2 | lb/hr |  | 4084072.3846 | 4052345.0935 | 4061257.919 | 4030484.7626 | 4067354.248
SO2 | lb/hr |  | 471.7455 | 2081.8507 | 3017.8144 | 774.2162 | 4154.1879
O2 | lb/hr |  | 327616.0939 | 317400.896 | 317818.8197 | 316817.3026 | 319219.4064
HCl | lb/hr |  | 0 | 0 | 0 | 0 | 0
Other Gases | lb/hr |  | 1425.4136 | 2267.747 | 2237.8287 | 1873.3623 | 2030.0577
H2O | lb/hr |  | 719134.1495 | 463050.2429 | 510979.3435 | 447488.865 | 645883.852
Fly Ash | lb/hr |  | 157.5 | 157.5 | 157.5 | 157.5 | 157.5
Total (gas only) | lb/hr |  | 6253639.38 | 5882557.8868 | 5950421.3857 | 5844933.6347 | 6087569.1119
Flue Gas Downstream of ID Fans
Temperature | °F |  | 152 | 152 | 152 | 152 | 152
Pressure | in. H2O |  | 1 | 1 | 1 | 1 | 1
Flow Rate | SCFM |  | 1401065.0181 | 1291422.7907 | 1311831.5239 | 1280993.0022 | 1360044.4947
Flow Rate | ACFM |  | 1673928.8946 | 1542933.3375 | 1567316.7656 | 1530472.2995 | 1624919.4349
CO2 | lb/hr |  | 1120919.593 | 1045412.0567 | 1055109.6603 | 1047495.1261 | 1048927.3597
N2 | lb/hr |  | 4084072.3846 | 4052345.0935 | 4061257.919 | 4030484.7626 | 4067354.248
SO2 | lb/hr |  | 471.7455 | 2081.8507 | 3017.8144 | 774.2162 | 4154.1879
O2 | lb/hr |  | 327616.0939 | 317400.896 | 317818.8197 | 316817.3026 | 319219.4064
HCl | lb/hr |  | 0 | 0 | 0 | 0 | 0
Other Gases | lb/hr |  | 1425.4136 | 2267.747 | 2237.8287 | 1873.3623 | 2030.0577
H2O | lb/hr |  | 719134.1495 | 463050.2429 | 510979.3435 | 447488.865 | 645883.852
Fly Ash | lb/hr |  | 157.5 | 157.5 | 157.5 | 157.5 | 157.5
Total (gas only) | lb/hr |  | 6253639.38 | 5882557.8868 | 5950421.3857 | 5844933.6347 | 6087569.1119
Lime to Ball Mill
Temperature | °F |  | 60 | 60 | 60 | 60 | 60
Wt.% Solids | wt. % |  | 100% | 100% | 100% | 100% | 100%
Inerts | lb/hr |  | 421.385 | 3037.356 | 5150.9965 | 760.8118 | 7824.1269
CaO | lb/hr |  | 3792.4654 | 27336.2037 | 46358.9687 | 6847.3059 | 70417.1418
Total | lb/hr |  | 4213.8504 | 30373.5596 | 51509.9653 | 7608.1177 | 78241.2687
Water to Ball Mill
Temperature | °F |  | 60 | 60 | 60 | 60 | 60
Flow Rate | GPM |  | 27.7645 | 200.1276 | 339.3927 | 50.1289 | 515.5219
Wt.% Solids | wt. % |  | 0% | 0% | 0% | 0% | 0%
H2O | lb/hr |  | 13893.3719 | 100143.84 | 169832.1099 | 25084.5185 | 257967.1657
Total | lb/hr |  | 13893.3719 | 100143.84 | 169832.1099 | 25084.5185 | 257967.1657
Lime Slurry to Head Tanks (Total)
Temperature | °F |  | 110 | 110 | 110 | 110 | 110
Flow Rate | GPM |  | 27.835 | 200.6355 | 340.254 | 50.2562 | 516.8302
Wt.% Solids | wt. % |  | 30% | 30% | 30% | 30% | 30%
Ca(OH)2 | lb/hr |  | 5010.7808 | 36117.8581 | 61251.6161 | 9046.9776 | 93038.3884
Inerts | lb/hr |  | 421.385 | 3037.356 | 5150.9965 | 760.8118 | 7824.1269
H2O | lb/hr |  | 12675.0537 | 91362.1661 | 154939.4295 | 22884.8419 | 235345.8689
Total | lb/hr |  | 18107.2196 | 130517.3802 | 221342.0421 | 32692.6312 | 336208.3841
Lime Slurry from Head Tank
Temperature | °F |  | 110 | 110 | 110 | 110 | 110
Flow Rate | GPM |  | 278.8189 | 189.9096 | 240.0794 | 167.0686 | 336.9674
Wt.% Solids | wt. % |  | 36.16% | 33.48% | 32.09% | 35.41% | 31.58%
CaSO3*1/2H2O | lb/hr |  | 10343.0977 | 6406.5765 | 4472.4374 | 4535.1559 | 4621.3445
CaSO4*2H2O | lb/hr |  | 4596.1964 | 2846.9115 | 1987.4318 | 2015.3022 | 2053.6021
Flyash / Inerts | lb/hr |  | 47058.23 | 9433.2477 | 8559.7562 | 26716.1893 | 10575.2827
Ca(OH)2 | lb/hr |  | 2612.2151 | 21727.1332 | 34495.3516 | 4848.2811 | 51559.9309
CaCl2 | lb/hr |  | 4072.4011 | 2058.6472 | 1402.6947 | 1967.2691 | 1248.2338
H2O | lb/hr |  | 121282.8884 | 84376.998 | 107766.5315 | 73120.0554 | 151805.182
Total | lb/hr |  | 189965.0287 | 126849.5142 | 158684.2031 | 113202.253 | 221863.5759
Lime Slurry to Atomizer
Temperature | °F |  | 104 | 104 | 104 | 104 | 104
Flow Rate | GPM |  | 305.9923 | 217.3397 | 267.5898 | 194.3675 | 364.4872
Wt.% Solids | wt. % |  | 33.58% | 30.03% | 29.39% | 31.37% | 29.63%
CaSO3*1/2H2O | lb/hr |  | 10343.0977 | 6406.5765 | 4472.4374 | 4535.1559 | 4621.3445
CaSO4*2H2O | lb/hr |  | 4596.1964 | 2846.9115 | 1987.4318 | 2015.3022 | 2053.6021
Flyash / Inerts | lb/hr |  | 47058.23 | 9433.2477 | 8559.7562 | 26716.1893 | 10575.2827
Ca(OH)2 | lb/hr |  | 2612.2151 | 21727.1332 | 34495.3516 | 4848.2811 | 51559.9309
CaCl2 | lb/hr |  | 4072.4011 | 2058.6472 | 1402.6947 | 1967.2691 | 1248.2338
H2O | lb/hr |  | 135853.0384 | 98947.148 | 122336.6815 | 87690.2054 | 166375.332
Total | lb/hr |  | 204535.1787 | 141419.6642 | 173254.3531 | 127772.403 | 236433.7259
Solids from Spray Dryers (Total)
Temperature | °F |  | 150 | 150 | 150 | 150 | 150
Wt.% Solids | wt. % |  | 98% | 98% | 98% | 98% | 98%
CaSO3*1/2H2O | lb/hr |  | 2582.2428 | 3547.7573 | 4182.9211 | 1749.8714 | 5455.7482
CaSO4*2H2O | lb/hr |  | 1147.4797 | 1576.5286 | 1858.7784 | 777.5961 | 2424.3888
Flyash / Inerts | lb/hr |  | 12170.6727 | 4918.8888 | 5853.7587 | 10695.001 | 8226.1287
Ca(OH)2 | lb/hr |  | 122.7981 | 2611.705 | 4337.7066 | 279.4147 | 6791.7113
CaCl2 | lb/hr |  | 99.8892 | 0 | 689.3044 | 681.5299 | 813.6522
H2O | lb/hr |  | 329.0425 | 258.2629 | 345.3565 | 289.4574 | 483.9108
Total | lb/hr |  | 16452.1251 | 12913.1426 | 17267.8257 | 14472.8705 | 24195.54
Baghouse/ESP Solids to Recycle
Particulate Removal Efficiency | % |  | 99.89% | 99.86% | 99.9% | 99.88% | 99.93%
Temperature | °F |  | 150 | 150 | 150 | 150 | 150
Wt.% Solids | wt. % |  | 98% | 98% | 98% | 98% | 98%
CaSO3*1/2H2O | lb/hr |  | 18103.9525 | 9265.3957 | 4761.9538 | 7320.4405 | 3786.9408
CaSO4*2H2O | lb/hr |  | 8044.913 | 4117.2944 | 2116.0851 | 3253.0083 | 1682.8154
Flyash / Inerts | lb/hr |  | 81524.4023 | 10910.2507 | 6114.7571 | 41976.5659 | 5100.3098
Ca(OH)2 | lb/hr |  | 90.8513 | 4724.7033 | 3401.3804 | 370.17 | 3289.762
CaCl2 | lb/hr |  | 8044.913 | 4117.2944 | 2116.0851 | 3253.0083 | 1682.8154
H2O | lb/hr |  | 2199.2677 | 592.1968 | 334.575 | 1080.0038 | 282.8536
Total | lb/hr |  | 109963.3869 | 29609.8409 | 16728.7514 | 54000.1884 | 14142.6816
Recycle Solids to Slurry Tank
Temperature | °F |  | 150 | 150 | 150 | 150 | 150
Wt.% Solids | wt. % |  | 98% | 98% | 98% | 98% | 98%
CaSO3*1/2H2O | lb/hr |  | 20686.1953 | 12813.153 | 8944.8748 | 9070.3119 | 9242.689
CaSO4*2H2O | lb/hr |  | 9192.3928 | 5693.823 | 3974.8635 | 4030.6044 | 4107.2042
Flyash / Inerts | lb/hr |  | 93695.075 | 15829.1394 | 11968.5158 | 52671.5669 | 13326.4385
Ca(OH)2 | lb/hr |  | 213.6493 | 7336.4083 | 7739.087 | 649.5847 | 10081.4734
CaCl2 | lb/hr |  | 8144.8023 | 4117.2944 | 2805.3895 | 3934.5381 | 2496.4675
H2O | lb/hr |  | 2528.3102 | 850.4597 | 679.9315 | 1369.4612 | 766.7644
Total | lb/hr |  | 134460.425 | 46640.2779 | 36112.6622 | 71726.0672 | 40021.037
Blowdown Water to Recycle Solids Tank
Temperature | °F |  | 60 | 60 | 60 | 60 | 60
Flow Rate | GPM |  | 454.3613 | 152.9604 | 119.7316 | 243.7766 | 134.8876
Wt.% Solids | wt. % |  | 0% | 0% | 0% | 0% | 0%
H2O | lb/hr |  | 227362.4129 | 76541.3703 | 59913.702 | 121985.8077 | 67497.7306
Total | lb/hr |  | 227362.4129 | 76541.3703 | 59913.702 | 121985.8077 | 67497.7306
Recycle Slurry to Head Tanks (Total)
Temperature | °F |  | 110 | 110 | 110 | 110 | 110
Flow Rate | GPM |  | 535.6053 | 182.3455 | 142.1476 | 286.7512 | 159.1597
Wt.% Solids | wt. % |  | 35% | 35% | 35% | 35% | 35%
CaSO3*1/2H2O | lb/hr |  | 20686.1953 | 12813.153 | 8944.8748 | 9070.3119 | 9242.689
CaSO4*2H2O | lb/hr |  | 9192.3928 | 5693.823 | 3974.8635 | 4030.6044 | 4107.2042
Flyash / Inerts | lb/hr |  | 93695.075 | 15829.1394 | 11968.5158 | 52671.5669 | 13326.4385
Ca(OH)2 | lb/hr |  | 213.6493 | 7336.4083 | 7739.087 | 649.5847 | 10081.4734
CaCl2 | lb/hr |  | 8144.8023 | 4117.2944 | 2805.3895 | 3934.5381 | 2496.4675
H2O | lb/hr |  | 229890.7232 | 77391.83 | 60593.6335 | 123355.2689 | 68264.4951
Total | lb/hr |  | 361822.8379 | 123181.6482 | 96026.3641 | 193711.8749 | 107518.7676
Dry Solids
Temperature | °F |  | 100 | 100 | 100 | 100 | 100
Wt.% Solids | wt. % |  | 98% | 98% | 98% | 98% | 98%
CaSO3*1/2H2O | lb/hr |  | 6393.5099 | 28278.3644 | 41050.1499 | 10513.4661 | 56576.186
CaSO4*2H2O | lb/hr |  | 2841.1051 | 12566.15 | 18241.5904 | 4671.9036 | 25140.9462
Flyash / Inerts | lb/hr |  | 28690.8995 | 33298.5287 | 52022.6091 | 59604.3508 | 75384.0212
Ca(OH)2 | lb/hr |  | 32.0846 | 14419.9867 | 29321.4053 | 531.6305 | 49148.4287
CaCl2 | lb/hr |  | 199.7785 | 0 | 1378.6088 | 1363.0597 | 1627.3044
H2O | lb/hr |  | 776.6834 | 1807.4088 | 2884.1849 | 1551.0792 | 4225.7803
Total | lb/hr |  | 38934.061 | 90370.4386 | 144898.5484 | 78235.4899 | 212102.6667
Solids to Landfill
Temperature | °F |  | 100 | 100 | 100 | 100 | 100
Wt.% Solids | wt. % |  | 80% | 80% | 80% | 80% | 80%
CaSO3*1/2H2O | lb/hr |  | 6393.5099 | 28278.3644 | 41050.1499 | 10513.4661 | 56576.186
CaSO4*2H2O | lb/hr |  | 2841.1051 | 12566.15 | 18241.5904 | 4671.9036 | 25140.9462
Flyash / Inerts | lb/hr |  | 28690.8995 | 33298.5287 | 52022.6091 | 59604.3508 | 75384.0212
Ca(OH)2 | lb/hr |  | 32.0846 | 14419.9867 | 29321.4053 | 531.6305 | 49148.4287
CaCl2 | lb/hr |  | 199.7785 | 0 | 1378.6088 | 1363.0597 | 1627.3044
H2O | lb/hr |  | 9539.3444 | 22140.7574 | 35503.5909 | 19171.1027 | 51969.2216
Total | lb/hr |  | 47696.7219 | 110703.7872 | 177517.9545 | 95855.5133 | 259846.1081
LSD Equipment Capital Costs |  |  | Case1 | Case 2 | Case 3 | Case 4 | Case 5
Cost Basis (Year) |  |  | 1998 | 1998 | 1998 | 1998 | 1998
Sizing Criteria
Reagent Feed System | $ | * | 4690431.9586 | 9322351.8985 | 12988373.6544 | 5311035.4905 | 17599879.0627
SO2 Removal System | $ | Wt. % S | 1596996.2709 | 1443731.9707 | 1452641.0696 | 1509904.9007 | 1471137.7412
Spray Dryers | $ | kACFM | 17550563.8613 | 17154941.771 | 17181947.0614 | 17136179.6595 | 17277996.784
Flue Gas Handling System | $ | kACFM | 5219175.0254 | 4991444.4426 | 5028991.8647 | 4971738.0389 | 5120125.4531 |  |  | Calculated No. of ID Fans and Flue Gas Flow per Fan
ID Fans | $ | ACFM | 1715354.5445 | 1622333.6141 | 1639831.8083 | 1613357.5543 | 1680831.4987 | 1765866.7838 | 1627676.5036 | 1653399.1528 | 1614531.0628 | 1714165.5574
Waste / Byproduct Handling System | $ | kpph SO2 | 1049229.0123 | 2376001.8756 | 3390949.9672 | 1176161.2449 | 4251699.4944 | 1 | 1 | 1 | 1 | 1
Support Equipment | $ | MW | 2404066.2 | 2404066.2 | 2404066.2 | 2404066.2 | 2404066.2
Chimney | $ | ACFM | 4813026.552 | 4683835.0146 | 4708421.3449 | 4671170.2563 | 4765508.1907
TOTAL | $ |  | 39038843.4251 | 43998706.7871 | 48795222.9706 | 38793613.3451 | 54571244.4248
* Based on lbs/hr of lime feed and GPM of lime slurry.
Capital Costs with Retrofit Factors
Reagent Feed System | $ |  | 6097561.5462 | 12119057.4681 | 16884885.7508 | 6904346.1376 | 22879842.7815
SO2 Removal System | $ |  | 2076095.1522 | 1876851.5619 | 1888433.3905 | 1962876.3709 | 1912479.0635
Spray Dryers | $ |  | 22815733.0197 | 22301424.3023 | 22336531.1799 | 22277033.5574 | 22461395.8193
Flue Gas Handling System | $ |  | 6784927.5331 | 6488877.7754 | 6537689.4241 | 6463259.4506 | 6656163.089
ID Fans | $ |  | 2229960.9078 | 2109033.6983 | 2131781.3508 | 2097364.8206 | 2185080.9484
Waste / Byproduct Handling System | $ |  | 1363997.716 | 3088802.4383 | 4408234.9574 | 1529009.6184 | 5527209.3427
Support Equipment | $ |  | 3125286.06 | 3125286.06 | 3125286.06 | 3125286.06 | 3125286.06
Chimney | $ |  | 6256934.5176 | 6088985.5189 | 6120947.7484 | 6072521.3331 | 6195160.6479
TOTAL | $ |  | 50750496.4526 | 57198318.8233 | 63433789.8618 | 50431697.3487 | 70942617.7523
General Facilities
Reagent Feed System | $ |  | 609756.1546 | 1211905.7468 | 1688488.5751 | 690434.6138 | 2287984.2782
SO2 Removal System | $ |  | 207609.5152 | 187685.1562 | 188843.339 | 196287.6371 | 191247.9064
Spray Dryers | $ |  | 2281573.302 | 2230142.4302 | 2233653.118 | 2227703.3557 | 2246139.5819
Flue Gas Handling System | $ |  | 678492.7533 | 648887.7775 | 653768.9424 | 646325.9451 | 665616.3089
ID Fans | $ |  | 222996.0908 | 210903.3698 | 213178.1351 | 209736.4821 | 218508.0948
Waste / Byproduct Handling System | $ |  | 136399.7716 | 308880.2438 | 440823.4957 | 152900.9618 | 552720.9343
Support Equipment | $ |  | 312528.606 | 312528.606 | 312528.606 | 312528.606 | 312528.606
Chimney | $ |  | 625693.4518 | 608898.5519 | 612094.7748 | 607252.1333 | 619516.0648
TOTAL | $ |  | 5075049.6453 | 5719831.8823 | 6343378.9862 | 5043169.7349 | 7094261.7752
Engineering Fees
Reagent Feed System | $ |  | 609756.1546 | 1211905.7468 | 1688488.5751 | 690434.6138 | 2287984.2782
SO2 Removal System | $ |  | 207609.5152 | 187685.1562 | 188843.339 | 196287.6371 | 191247.9064
Spray Dryers | $ |  | 2281573.302 | 2230142.4302 | 2233653.118 | 2227703.3557 | 2246139.5819
Flue Gas Handling System | $ |  | 678492.7533 | 648887.7775 | 653768.9424 | 646325.9451 | 665616.3089
ID Fans | $ |  | 222996.0908 | 210903.3698 | 213178.1351 | 209736.4821 | 218508.0948
Waste / Byproduct Handling System | $ |  | 136399.7716 | 308880.2438 | 440823.4957 | 152900.9618 | 552720.9343
Support Equipment | $ |  | 312528.606 | 312528.606 | 312528.606 | 312528.606 | 312528.606
Chimney | $ |  | 625693.4518 | 608898.5519 | 612094.7748 | 607252.1333 | 619516.0648
TOTAL | $ |  | 5075049.6453 | 5719831.8823 | 6343378.9862 | 5043169.7349 | 7094261.7752
Contingency
Reagent Feed System | $ |  | 1219512.3092 | 2423811.4936 | 3376977.1502 | 1380869.2275 | 4575968.5563
SO2 Removal System | $ |  | 415219.0304 | 375370.3124 | 377686.6781 | 392575.2742 | 382495.8127
Spray Dryers | $ |  | 4563146.6039 | 4460284.8605 | 4467306.236 | 4455406.7115 | 4492279.1639
Flue Gas Handling System | $ |  | 1356985.5066 | 1297775.5551 | 1307537.8848 | 1292651.8901 | 1331232.6178
ID Fans | $ |  | 445992.1816 | 421806.7397 | 426356.2702 | 419472.9641 | 437016.1897
Waste / Byproduct Handling System | $ |  | 272799.5432 | 617760.4877 | 881646.9915 | 305801.9237 | 1105441.8685
Support Equipment | $ |  | 625057.212 | 625057.212 | 625057.212 | 625057.212 | 625057.212
Chimney | $ |  | 1251386.9035 | 1217797.1038 | 1224189.5497 | 1214504.2666 | 1239032.1296
TOTAL | $ |  | 10150099.2905 | 11439663.7647 | 12686757.9724 | 10086339.4697 | 14188523.5505
Total Plant Cost (TPC) | $ |  | 71050695.0336 | 80077646.3526 | 88807305.8065 | 70604376.2881 | 99319664.8532
Total Plant Cost (TPC) w/ Prime Contractor's Markup | $ |  | 73182215.8846 | 82479975.7431 | 91471524.9807 | 72722507.5768 | 102299254.7988
Total Cash Expended (TCE) | $ |  | 71071389.4108 | 80100969.9389 | 88833172.0121 | 70624940.6696 | 99348592.9109
Allow. for Funds During Constr. (AFDC) | $ |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Total Plant Investment (TPI) | $ |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Preproduction Costs | $ |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Inventory Capital | $ |  | 197208.1986 | 1421482.5912 | 2410666.374 | 356059.9063 | 3661691.374
Total Capital Requirement (TCR) | $ |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| $/kW |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Maintenance Cost by Area |  |  | Case1 | Case 2 | Case 3 | Case 4 | Case 5
TPC w/o Retrofit Factor
Reagent Feed System | $ |  | 6754222.0204 | 13424186.7339 | 18703258.0624 | 7647891.1063 | 25343825.8503
SO2 Removal System | $ |  | 2299674.6302 | 2078974.0378 | 2091803.1402 | 2174263.057 | 2118438.3473
Spray Dryers | $ |  | 25272811.9603 | 24703116.1503 | 24742003.7685 | 24676098.7097 | 24880315.369
Flue Gas Handling System | $ |  | 7515612.0366 | 7187679.9974 | 7241748.2851 | 7159302.7761 | 7372980.6524
ID Fans | $ |  | 2470110.5441 | 2336160.4043 | 2361357.804 | 2323234.8782 | 2420397.3582
Waste / Byproduct Handling System | $ |  | 1510889.7777 | 3421442.7008 | 4882967.9528 | 1693672.1927 | 6122447.2719
Support Equipment | $ |  | 3461855.328 | 3461855.328 | 3461855.328 | 3461855.328 | 3461855.328
Chimney | $ |  | 6930758.2349 | 6744722.421 | 6780126.7367 | 6726485.169 | 6862331.7946
TOTAL | $ |  | 56215934.5321 | 63358137.7734 | 70265121.0777 | 55862803.217 | 78582591.9718
First Year Maintenance Costs
Reagent Feed System | $ |  | 337711.101 | 671209.3367 | 935162.9031 | 382394.5553 | 1267191.2925
SO2 Removal System | $ |  | 114983.7315 | 103948.7019 | 104590.157 | 108713.1529 | 105921.9174
Spray Dryers | $ |  | 1263640.598 | 1235155.8075 | 1237100.1884 | 1233804.9355 | 1244015.7685
Flue Gas Handling System | $ |  | 375780.6018 | 359383.9999 | 362087.4143 | 357965.1388 | 368649.0326
ID Fans | $ |  | 123505.5272 | 116808.0202 | 118067.8902 | 116161.7439 | 121019.8679
Waste / Byproduct Handling System | $ |  | 75544.4889 | 171072.135 | 244148.3976 | 84683.6096 | 306122.3636
Support Equipment | $ |  | 173092.7664 | 173092.7664 | 173092.7664 | 173092.7664 | 173092.7664
Chimney | $ |  | 346537.9117 | 337236.121 | 339006.3368 | 336324.2585 | 343116.5897
TOTAL | $ |  | 2810796.7266 | 3167906.8887 | 3513256.0539 | 2793140.1608 | 3929129.5986
LSD O&M Data and Costs |  |  | Case1 | Case 2 | Case 3 | Case 4 | Case 5
Cost Basis (Year) |  |  | 1998 | 1998 | 1998 | 1998 | 1998
Parameters
Reagent Required | lbs/hr |  | 4213.8504 | 30373.5596 | 51509.9653 | 7608.1177 | 78241.2687
| lbs/MMBtu |  | 0.80264 | 5.7854 | 9.8114 | 1.4492 | 14.9031
Percent SO2 Removal | % |  | 90% | 90% | 90% | 90% | 90%
FGD Solids - dry | lbs/hr |  | 38157.3776 | 88563.0298 | 142014.3636 | 76684.4107 | 207876.8865
- wetted | lbs/hr |  | 47696.7219 | 110703.7872 | 177517.9545 | 95855.5133 | 259846.1081
Fresh Water to FGD | gpm |  | 27.7645 | 200.1276 | 339.3927 | 50.1289 | 515.5219
Blowdown Water to FGD | gpm |  | 500.9897 | 222.7116 | 214.0353 | 308.1055 | 259.4151
Total FGD Power Consumption | kW |  | 3500 | 3500 | 3500 | 3500 | 3500
Fixed O&M Costs
Number of Operators |  |  | 20.4656 | 20.4656 | 20.4656 | 20.4656 | 20.4656
(40 hrs/week)
Operating Labor Cost ** | $/yr |  | 1277054.2986 | 1277054.2986 | 1277054.2986 | 1277054.2986 | 1277054.2986
Maint. Labor & Matls. Cost | $/yr |  | 2810796.7266 | 3167906.8887 | 3513256.0539 | 2793140.1608 | 3929129.5986
Admin. & Support Labor | $/yr |  | 720411.8968 | 763265.1162 | 804707.016 | 718293.1089 | 854611.8414
TOTAL | $/yr |  | 4808262.9219 | 5208226.3034 | 5595017.3685 | 4788487.5683 | 6060795.7385
Variable Operating Costs **
Reagent Costs | $/yr |  | 779794.0854 | 5620779.0794 | 9532176.6207 | 1407920.2128 | 14478937.9747
Disposal Costs | $/yr |  | 3259021.6171 | 7564168.3741 | 12129446.7917 | 6549615.5156 | 17754764.8717
Credit for Byproduct | $/yr |  | 0 | 0 | 0 | 0 | 0
Steam Costs | $/yr |  | 0 | 0 | 0 | 0 | 0
Fresh Water Costs | $/yr |  | 5691.2849 | 41022.9514 | 69570.0744 | 10275.6294 | 105673.744
Power Costs | $/yr |  | 498225 | 498225 | 498225 | 498225 | 498225
TOTAL | $/yr |  | 4542731.9874 | 13724195.405 | 22229418.4867 | 8466036.3578 | 32837601.5904
** These costs assume inputs are in current dollars (no escalation included).
Intermediate Material Balance Calcs. |  |  | Case1 | Case 2 | Case 3 | Case 4 | Case 5
FGD Reactions in Spray Dryer (80% of SO2 Removal)
Sulfite Reaction | 60%
SO2 | lbmole/hr |  | 19.8823 | 87.742 | 127.1892 | 32.6302 | 175.083
Ca(OH)2 | lbmole/hr |  | 19.8823 | 87.742 | 127.1892 | 32.6302 | 175.083
H2O | lbmole/hr |  | 9.9411 | 43.871 | 63.5946 | 16.3151 | 87.5415
CaSO3*1/2H2O | lbmole/hr |  | 19.8823 | 87.742 | 127.1892 | 32.6302 | 175.083
SO2 | lb/hr |  | 1273.7128 | 5620.9968 | 8148.0988 | 2090.3837 | 11216.3074
Ca(OH)2 | lb/hr |  | 1473.1696 | 6501.2155 | 9424.0485 | 2417.7269 | 12972.7225
H2O | lb/hr |  | 179.0928 | 790.3508 | 1145.6787 | 293.9223 | 1577.0899
CaSO3*1/2H2O | lb/hr |  | 2567.791 | 11331.8677 | 16426.4776 | 4214.1906 | 22611.9522
Sulfate Reaction | 20%
Ca(OH)2 | lbmole/hr |  | 6.6274 | 29.2473 | 42.3964 | 10.8767 | 58.361
SO2 | lbmole/hr |  | 6.6274 | 29.2473 | 42.3964 | 10.8767 | 58.361
O2 | lbmole/hr |  | 3.3137 | 14.6237 | 21.1982 | 5.4384 | 29.1805
H2O | lbmole/hr |  | 6.6274 | 29.2473 | 42.3964 | 10.8767 | 58.361
CaSO4*2H2O | lbmole/hr |  | 6.6274 | 29.2473 | 42.3964 | 10.8767 | 58.361
Ca(OH)2 | lb/hr |  | 491.0565 | 2167.0718 | 3141.3495 | 805.909 | 4324.2408
SO2 | lb/hr |  | 424.5709 | 1873.6656 | 2716.0329 | 696.7946 | 3738.7691
O2 | lb/hr |  | 106.0347 | 467.9397 | 678.3172 | 174.0214 | 933.741
H2O | lb/hr |  | 119.3952 | 526.9005 | 763.7858 | 195.9482 | 1051.3933
CaSO4*2H2O | lb/hr |  | 1141.0577 | 5035.5794 | 7299.488 | 1872.6737 | 10048.1477
FGD Reactions in Particulate Control (20% of SO2 Removal)
Sulfite Reaction | 15%
SO2 | lbmole/hr |  | 9.9411 | 43.871 | 63.5946 | 16.3151 | 87.5415
Ca(OH)2 | lbmole/hr |  | 9.9411 | 43.871 | 63.5946 | 16.3151 | 87.5415
H2O | lbmole/hr |  | 4.9706 | 21.9355 | 31.7973 | 8.1576 | 43.7708
CaSO3*1/2H2O | lbmole/hr |  | 9.9411 | 43.871 | 63.5946 | 16.3151 | 87.5415
SO2 | lb/hr |  | 636.8564 | 2810.4984 | 4074.0494 | 1045.1919 | 5608.1537
Ca(OH)2 | lb/hr |  | 736.5848 | 3250.6078 | 4712.0243 | 1208.8634 | 6486.3613
H2O | lb/hr |  | 89.5464 | 395.1754 | 572.8393 | 146.9612 | 788.545
CaSO3*1/2H2O | lb/hr |  | 1283.8955 | 5665.9338 | 8213.2388 | 2107.0953 | 11305.9761
Sulfate Reaction | 5%
Ca(OH)2 | lbmole/hr |  | 3.3137 | 14.6237 | 21.1982 | 5.4384 | 29.1805
SO2 | lbmole/hr |  | 3.3137 | 14.6237 | 21.1982 | 5.4384 | 29.1805
O2 | lbmole/hr |  | 1.6569 | 7.3118 | 10.5991 | 2.7192 | 14.5903
H2O | lbmole/hr |  | 3.3137 | 14.6237 | 21.1982 | 5.4384 | 29.1805
CaSO4*2H2O | lbmole/hr |  | 3.3137 | 14.6237 | 21.1982 | 5.4384 | 29.1805
Ca(OH)2 | lb/hr |  | 245.5283 | 1083.5359 | 1570.6748 | 402.9545 | 2162.1204
SO2 | lb/hr |  | 212.2855 | 936.8328 | 1358.0165 | 348.3973 | 1869.3846
O2 | lb/hr |  | 53.0174 | 233.9698 | 339.1586 | 87.0107 | 466.8705
H2O | lb/hr |  | 59.6976 | 263.4503 | 381.8929 | 97.9741 | 525.6966
CaSO4*2H2O | lb/hr |  | 570.5289 | 2517.7897 | 3649.744 | 936.3369 | 5024.0739
Solids in Spray Dryer
CaSO3*1/2H2O | lb/hr |  | 12911.2141 | 17738.7867 | 20914.6053 | 8749.357 | 27278.7409
CaSO4*2H2O | lb/hr |  | 5737.3987 | 7882.6431 | 9293.8921 | 3887.9806 | 12121.944
Inerts | lb/hr |  | 61352.8096 | 24594.4438 | 32715.3155 | 56882.6542 | 45198.9046
Ca(OH)2 | lb/hr |  | 613.9903 | 13058.5249 | 21688.533 | 1397.0736 | 33958.5567
H2O | lb/hr
TOTAL | lb/hr |  | 80615.4128 | 63274.3986 | 84612.3458 | 70917.0653 | 118558.1462
Spray Dryer Solids Removal
CaSO3*1/2H2O | lb/hr |  | 1291.1214 | 1773.8787 | 2091.4605 | 874.9357 | 2727.8741
CaSO4*2H2O | lb/hr |  | 573.7399 | 788.2643 | 929.3892 | 388.7981 | 1212.1944
Inerts | lb/hr |  | 6135.281 | 2459.4444 | 3271.5315 | 5688.2654 | 4519.8905
Ca(OH)2 | lb/hr |  | 61.399 | 1305.8525 | 2168.8533 | 139.7074 | 3395.8557
H2O | lb/hr |  | 164.5213 | 129.1314 | 172.6783 | 144.7287 | 241.9554
TOTAL | lb/hr |  | 8061.5413 | 6327.4399 | 8461.2346 | 7091.7065 | 11855.8146
Solids in Baghouse/ESP
CaSO3*1/2H2O | lb/hr |  | 24524.0808 | 37595.75 | 45859.5283 | 17855.9378 | 60407.7097
CaSO4*2H2O | lb/hr |  | 10897.8466 | 16706.5473 | 20378.7497 | 7934.7019 | 26843.573
Inerts | lb/hr |  | 110435.0574 | 44269.9989 | 58887.5679 | 102388.7775 | 81358.0282
Ca(OH)2 | lb/hr |  | 123.0695 | 19171.2012 | 32756.6603 | 902.9145 | 52476.9205
H2O | lb/hr
TOTAL | lb/hr |  | 145980.0543 | 117743.4973 | 157882.5062 | 129082.3318 | 221086.2315
Components of Baghouse/ESP Solids
CaSO3*1/2H2O | lb/hr |  | 24497.4624 | 37543.7601 | 45812.1037 | 17833.9065 | 60363.1268
CaSO4*2H2O | lb/hr |  | 10886.0181 | 16683.4444 | 20357.6755 | 7924.9118 | 26823.7616
Inerts | lb/hr |  | 110315.1911 | 44208.7794 | 58826.6706 | 102262.4466 | 81297.9832
Ca(OH)2 | lb/hr |  | 122.9359 | 19144.69 | 32722.7857 | 901.8005 | 52438.1907
H2O | lb/hr |  | 2975.9512 | 2399.6056 | 3218.7599 | 2631.083 | 4508.6339
TOTAL | lb/hr |  | 148797.5587 | 119980.2795 | 160937.9954 | 131554.1484 | 225431.6962
Total Waste Solids Out
CaSO3*1/2H2O | lb/hr |  | 6419.4774 | 28329.6692 | 41066.1939 | 10535.4764 | 56529.8806
CaSO4*2H2O | lb/hr |  | 2852.6443 | 12588.9484 | 18248.7199 | 4681.6844 | 25120.3693
Inerts | lb/hr |  | 28910.2818 | 33360.096 | 52795.4609 | 60412.0741 | 76323.3516
Ca(OH)2 | lb/hr |  | 33.5316 | 14447.1397 | 29377.9552 | 532.9123 | 49252.802
H2O | lb/hr |  | NA | NA | NA | NA | NA
TOTAL | lb/hr |  | 38215.9351 | 88725.8532 | 141488.3299 | 76162.1472 | 207226.4035
CaSO3*1/2H2O | wt. % |  | 16.8% | 31.93% | 29.02% | 13.83% | 27.28%
CaSO4*2H2O | wt. % |  | 7.465% | 14.19% | 12.9% | 6.147% | 12.12%
Inerts | wt. % |  | 75.65% | 37.6% | 37.31% | 79.32% | 36.83%
Ca(OH)2 | wt. % |  | 0.08774% | 16.28% | 20.76% | 0.6997% | 23.77%
H2O | wt. % |  | NA | NA | NA | NA | NA
TOTAL | wt. % |  | 100% | 100% | 100% | 100% | 100%
Waste Out Gas Stream
CaSO3*1/2H2O | lb/hr |  | 26.4567 | 50.2889 | 45.7135 | 21.7869 | 42.9649
CaSO4*2H2O | lb/hr |  | 11.7567 | 22.347 | 20.3139 | 9.6815 | 19.0924
Inerts | lb/hr |  | 119.1484 | 59.2185 | 58.7701 | 124.9295 | 58.0087
Ca(OH)2 | lb/hr |  | 0.13819 | 25.6456 | 32.7025 | 1.102 | 37.434
H2O | lb/hr |  | NA | NA | NA | NA | NA
TOTAL | lb/hr |  | 157.5 | 157.5 | 157.5 | 157.5 | 157.5
Dry Solids
CaSO3*1/2H2O | lb/hr |  | 6393.0207 | 28279.3803 | 41020.4804 | 10513.6895 | 56486.9157
CaSO4*2H2O | lb/hr |  | 2840.8877 | 12566.6014 | 18228.406 | 4672.0028 | 25101.2769
Inerts | lb/hr |  | 28791.1333 | 33300.8774 | 52736.6908 | 60287.1446 | 76265.3429
Ca(OH)2 | lb/hr |  | 33.3934 | 14421.4941 | 29345.2526 | 531.8103 | 49215.368
H2O | lb/hr |  | 776.7028 | 1807.5174 | 2884.3027 | 1551.1152 | 4225.896
TOTAL | lb/hr |  | 38835.1379 | 90375.8707 | 144215.1325 | 77555.7624 | 211294.7995
ITERATION 1
Assumed Composition of Recycle Solids to Slurry Tank
CaSO3*1/2H2O | lb/hr |  | 20810.4576 | 13305.804 | 9669.9694 | 9282.4112 | 10249.2248
CaSO4*2H2O | lb/hr |  | 9247.6116 | 5912.744 | 4297.0762 | 4124.8557 | 4554.4818
Inerts | lb/hr |  | 93720.4309 | 15668.4815 | 12431.8921 | 53226.8019 | 13837.9062
Ca(OH)2 | lb/hr |  | 108.7016 | 6785.4943 | 6917.7078 | 469.529 | 8929.8444
H2O | lb/hr |  | 2528.3102 | 850.4597 | 679.9315 | 1369.4612 | 766.7644
TOTAL | lb/hr |  | 126415.5119 | 42522.9835 | 33996.5771 | 68473.0589 | 38338.2217
Composition of Recycle Slurry to Head Tanks
CaSO3*1/2H2O | lb/hr |  | 20810.4576 | 13305.804 | 9669.9694 | 9282.4112 | 10249.2248
CaSO4*2H2O | lb/hr |  | 9247.6116 | 5912.744 | 4297.0762 | 4124.8557 | 4554.4818
Inerts | lb/hr |  | 93720.4309 | 15668.4815 | 12431.8921 | 53226.8019 | 13837.9062
Ca(OH)2 | lb/hr |  | 108.7016 | 6785.4943 | 6917.7078 | 469.529 | 8929.8444
H2O | lb/hr |  | 230076.2317 | 77391.83 | 61873.7703 | 124620.9672 | 69775.5634
TOTAL | lb/hr |  | 353963.4334 | 119064.3538 | 95190.4158 | 191724.5649 | 107347.0206
Composition of Slurry from Head Tank
CaSO3*1/2H2O | lb/hr |  | 10405.2288 | 6652.902 | 4834.9847 | 4641.2056 | 5124.6124
CaSO4*2H2O | lb/hr |  | 4623.8058 | 2956.372 | 2148.5381 | 2062.4278 | 2277.2409
Inerts | lb/hr |  | 47070.908 | 9352.9188 | 8791.4443 | 26993.8068 | 10831.0165
Ca(OH)2 | lb/hr |  | 2559.7412 | 21451.6762 | 34084.6619 | 4758.2533 | 50984.1164
H2O | lb/hr |  | 121375.6427 | 84376.998 | 108406.5999 | 73752.9045 | 152560.7162
TOTAL | lb/hr |  | 186035.3265 | 124790.867 | 158266.229 | 112208.5981 | 221777.7024
Solids in Spray Dryer
CaSO3*1/2H2O | lb/hr |  | 12973.0198 | 17984.7697 | 21261.4623 | 8855.3962 | 27736.5646
CaSO4*2H2O | lb/hr |  | 5764.8635 | 7991.9514 | 9448.0261 | 3935.1016 | 12325.3886
Inerts | lb/hr |  | 61315.3564 | 24514.2888 | 32613.6765 | 56819.438 | 45080.6289
Ca(OH)2 | lb/hr |  | 562.1731 | 12783.3888 | 21289.181 | 1307.1296 | 33415.5641
H2O | lb/hr |  | NA | NA | NA | NA | NA
TOTAL | lb/hr |  | 80615.4128 | 63274.3986 | 84612.3458 | 70917.0653 | 118558.1462
Composition of Solids from Spray Dryers
CaSO3*1/2H2O | lb/hr |  | 1297.302 | 1798.477 | 2126.1462 | 885.5396 | 2773.6565
CaSO4*2H2O | lb/hr |  | 576.4864 | 799.1951 | 944.8026 | 393.5102 | 1232.5389
Inerts | lb/hr |  | 6131.5356 | 2451.4289 | 3261.3677 | 5681.9438 | 4508.0629
Ca(OH)2 | lb/hr |  | 56.2173 | 1278.3389 | 2128.9181 | 130.713 | 3341.5564
H2O | lb/hr |  | 164.5213 | 129.1314 | 172.6783 | 144.7287 | 241.9554
TOTAL | lb/hr |  | 8226.0625 | 6456.5713 | 8633.9128 | 7236.4352 | 12097.77
Solids in Baghouse/ESP
CaSO3*1/2H2O | lb/hr |  | 24635.3311 | 38038.5192 | 46483.8709 | 18046.8084 | 61231.7925
CaSO4*2H2O | lb/hr |  | 10947.2833 | 16903.3021 | 20656.1909 | 8019.5197 | 27209.7734
Inerts | lb/hr |  | 110367.6414 | 44125.7198 | 58704.6178 | 102274.9884 | 81145.132
Ca(OH)2 | lb/hr |  | 29.7985 | 18675.9562 | 32037.8268 | 741.0154 | 51499.5337
H2O | lb/hr
TOTAL | lb/hr |  | 145980.0543 | 117743.4973 | 157882.5062 | 129082.3318 | 221086.2315
CaSO3*1/2H2O | wt % |  | 16.88% | 32.31% | 29.44% | 13.98% | 27.7%
CaSO4*2H2O | wt % |  | 7.499% | 14.36% | 13.08% | 6.213% | 12.31%
Inerts | wt % |  | 75.6% | 37.48% | 37.18% | 79.23% | 36.7%
Ca(OH)2 | wt % |  | 0.02041% | 15.86% | 20.29% | 0.5741% | 23.29%
H2O | wt %
TOTAL | wt % |  | 100% | 100% | 100% | 100% | 100%
Dry Solids
CaSO3*1/2H2O | lb/hr |  | 6422.673 | 28613.1216 | 41610.7155 | 10626.0964 | 57349.5692
CaSO4*2H2O | lb/hr |  | 2854.0644 | 12714.9071 | 18490.6908 | 4721.9535 | 25484.617
Inerts | lb/hr |  | 28773.929 | 33192.0014 | 52550.2954 | 60220.2819 | 76000.3615
Ca(OH)2 | lb/hr |  | 7.7688 | 14048.323 | 28679.1282 | 436.3154 | 48234.3559
H2O | lb/hr |  | 776.7028 | 1807.5174 | 2884.3027 | 1551.1152 | 4225.896
TOTAL | lb/hr |  | 38835.1379 | 90375.8707 | 144215.1325 | 77555.7624 | 211294.7995
Solids Out Stack
CaSO3*1/2H2O | lb/hr |  | 26.5794 | 50.8824 | 46.3713 | 22.0198 | 43.621
CaSO4*2H2O | lb/hr |  | 11.8112 | 22.6108 | 20.6061 | 9.785 | 19.384
Inerts | lb/hr |  | 119.0773 | 59.0249 | 58.5624 | 124.791 | 57.8071
Ca(OH)2 | lb/hr |  | 0.03215 | 24.982 | 31.9602 | 0.90415 | 36.6878
H2O | lb/hr
TOTAL | lb/hr |  | 157.5 | 157.5 | 157.5 | 157.5 | 157.5
Composition of Baghouse/ESP Solids to Recycle
CaSO3*1/2H2O | lb/hr |  | 18186.0787 | 9374.5153 | 4826.7841 | 7398.6921 | 3838.6023
CaSO4*2H2O | lb/hr |  | 8081.4077 | 4165.7842 | 2144.894 | 3287.7812 | 1705.7723
Inerts | lb/hr |  | 81474.6351 | 10874.6934 | 6095.7599 | 41929.9155 | 5086.9634
Ca(OH)2 | lb/hr |  | 21.9976 | 4602.6512 | 3326.7383 | 303.7958 | 3228.49
H2O | lb/hr |  | 2199.2677 | 592.1968 | 334.575 | 1080.0038 | 282.8536
TOTAL | lb/hr |  | 109963.3869 | 29609.8409 | 16728.7514 | 54000.1884 | 14142.6816
Calculated Composition of Recycle Solids to Slurry Tank
CaSO3*1/2H2O | lb/hr |  | 20780.6826 | 12971.4692 | 9079.0766 | 9169.7713 | 9385.9152
CaSO4*2H2O | lb/hr |  | 9234.3804 | 5764.1745 | 4034.4992 | 4074.8015 | 4170.8501
Inerts | lb/hr |  | 93737.7064 | 15777.5511 | 12618.4952 | 53293.8031 | 14103.0892
Ca(OH)2 | lb/hr |  | 134.4322 | 7159.329 | 7584.5745 | 565.2217 | 9911.6028
H2O | lb/hr |  | 2528.3102 | 850.4597 | 679.9315 | 1369.4612 | 766.7644
TOTAL | lb/hr |  | 126415.5119 | 42522.9835 | 33996.5771 | 68473.0589 | 38338.2217
ITERATION 2
Assumed Composition of Recycle Solids to Slurry Tank
CaSO3*1/2H2O | lb/hr |  | 20750.9077 | 12637.1344 | 8488.1838 | 9057.1315 | 8522.6056
CaSO4*2H2O | lb/hr |  | 9221.1492 | 5615.6051 | 3771.9222 | 4024.7474 | 3787.2183
Inerts | lb/hr |  | 93759.2095 | 16019.0033 | 13045.2302 | 53375.1502 | 14726.5598
Ca(OH)2 | lb/hr |  | 155.9353 | 7400.7811 | 8011.3094 | 646.5687 | 10535.0734
H2O | lb/hr |  | 2528.3102 | 850.4597 | 679.9315 | 1369.4612 | 766.7644
TOTAL | lb/hr |  | 126415.5119 | 42522.9835 | 33996.5771 | 68473.0589 | 38338.2217
Composition of Recycle Slurry to Head Tanks
CaSO3*1/2H2O | lb/hr |  | 20750.9077 | 12637.1344 | 8488.1838 | 9057.1315 | 8522.6056
CaSO4*2H2O | lb/hr |  | 9221.1492 | 5615.6051 | 3771.9222 | 4024.7474 | 3787.2183
Inerts | lb/hr |  | 93759.2095 | 16019.0033 | 13045.2302 | 53375.1502 | 14726.5598
Ca(OH)2 | lb/hr |  | 155.9353 | 7400.7811 | 8011.3094 | 646.5687 | 10535.0734
H2O | lb/hr |  | 230076.2317 | 77391.83 | 61873.7703 | 124620.9672 | 69775.5634
TOTAL | lb/hr |  | 353963.4334 | 119064.3538 | 95190.4158 | 191724.5649 | 107347.0206
Composition of Slurry from Head Tank
CaSO3*1/2H2O | lb/hr |  | 10375.4538 | 6318.5672 | 4244.0919 | 4528.5657 | 4261.3028
CaSO4*2H2O | lb/hr |  | 4610.5746 | 2807.8025 | 1885.9611 | 2012.3737 | 1893.6092
Inerts | lb/hr |  | 47090.2973 | 9528.1796 | 9098.1133 | 27067.981 | 11275.3434
Ca(OH)2 | lb/hr |  | 2583.3581 | 21759.3196 | 34631.4628 | 4846.7732 | 51786.7309
H2O | lb/hr |  | 121375.6427 | 84376.998 | 108406.5999 | 73752.9045 | 152560.7162
TOTAL | lb/hr |  | 186035.3265 | 124790.867 | 158266.229 | 112208.5981 | 221777.7024
Solids in Spray Dryer
CaSO3*1/2H2O | lb/hr |  | 12943.2448 | 17650.4349 | 20670.5694 | 8742.7563 | 26873.255
CaSO4*2H2O | lb/hr |  | 5751.6324 | 7843.3819 | 9185.4491 | 3885.0474 | 11941.7569
Inerts | lb/hr |  | 61334.7456 | 24689.5496 | 32920.3455 | 56893.6121 | 45524.9557
Ca(OH)2 | lb/hr |  | 585.79 | 13091.0322 | 21835.9818 | 1395.6495 | 34218.1786
H2O | lb/hr |  | NA | NA | NA | NA | NA
TOTAL | lb/hr |  | 80615.4128 | 63274.3986 | 84612.3458 | 70917.0653 | 118558.1462
Composition of Solids from Spray Dryers
CaSO3*1/2H2O | lb/hr |  | 1294.3245 | 1765.0435 | 2067.0569 | 874.2756 | 2687.3255
CaSO4*2H2O | lb/hr |  | 575.1632 | 784.3382 | 918.5449 | 388.5047 | 1194.1757
Inerts | lb/hr |  | 6133.4746 | 2468.955 | 3292.0346 | 5689.3612 | 4552.4956
Ca(OH)2 | lb/hr |  | 58.579 | 1309.1032 | 2183.5982 | 139.5649 | 3421.8179
H2O | lb/hr |  | 164.5213 | 129.1314 | 172.6783 | 144.7287 | 241.9554
TOTAL | lb/hr |  | 8226.0625 | 6456.5713 | 8633.9128 | 7236.4352 | 12097.77
Solids in Baghouse/ESP
CaSO3*1/2H2O | lb/hr |  | 24581.7362 | 37436.7166 | 45420.2637 | 17844.0566 | 59677.8352
CaSO4*2H2O | lb/hr |  | 10923.4671 | 16635.8771 | 20183.5523 | 7929.4222 | 26519.2363
Inerts | lb/hr |  | 110402.5421 | 44441.1893 | 59256.622 | 102408.5018 | 81944.9203
Ca(OH)2 | lb/hr |  | 72.3089 | 19229.7143 | 33022.0682 | 900.3512 | 52944.2398
H2O | lb/hr
TOTAL | lb/hr |  | 145980.0543 | 117743.4973 | 157882.5062 | 129082.3318 | 221086.2315
CaSO3*1/2H2O | wt % |  | 16.84% | 31.8% | 28.77% | 13.82% | 26.99%
CaSO4*2H2O | wt % |  | 7.483% | 14.13% | 12.78% | 6.143% | 11.99%
Inerts | wt % |  | 75.63% | 37.74% | 37.53% | 79.34% | 37.06%
Ca(OH)2 | wt % |  | 0.04953% | 16.33% | 20.92% | 0.6975% | 23.95%
H2O | wt %
TOTAL | wt % |  | 100% | 100% | 100% | 100% | 100%
Dry Solids
CaSO3*1/2H2O | lb/hr |  | 6408.7003 | 28160.437 | 40658.612 | 10506.7146 | 55894.136
CaSO4*2H2O | lb/hr |  | 2847.8553 | 12513.7462 | 18067.6014 | 4668.9034 | 24837.8614
Inerts | lb/hr |  | 28783.028 | 33429.3022 | 53044.4301 | 60298.8956 | 76749.4415
Ca(OH)2 | lb/hr |  | 18.8516 | 14464.8679 | 29560.1864 | 530.1335 | 49587.4646
H2O | lb/hr |  | 776.7028 | 1807.5174 | 2884.3027 | 1551.1152 | 4225.896
TOTAL | lb/hr |  | 38835.1379 | 90375.8707 | 144215.1325 | 77555.7624 | 211294.7995
Solids Out Stack
CaSO3*1/2H2O | lb/hr |  | 26.5216 | 50.0774 | 45.3102 | 21.7725 | 42.514
CaSO4*2H2O | lb/hr |  | 11.7855 | 22.253 | 20.1347 | 9.6751 | 18.8921
Inerts | lb/hr |  | 119.1149 | 59.4469 | 59.1131 | 124.9539 | 58.3769
Ca(OH)2 | lb/hr |  | 0.078015 | 25.7227 | 32.9421 | 1.0986 | 37.717
H2O | lb/hr
TOTAL | lb/hr |  | 157.5 | 157.5 | 157.5 | 157.5 | 157.5
Composition of Baghouse/ESP Solids to Recycle
CaSO3*1/2H2O | lb/hr |  | 18146.5143 | 9226.2022 | 4716.3415 | 7315.5695 | 3741.1852
CaSO4*2H2O | lb/hr |  | 8063.8264 | 4099.8779 | 2095.8162 | 3250.8437 | 1662.4828
Inerts | lb/hr |  | 81500.3992 | 10952.4402 | 6153.0789 | 41984.6524 | 5137.1019
Ca(OH)2 | lb/hr |  | 53.3792 | 4739.1238 | 3428.9398 | 369.1191 | 3319.0581
H2O | lb/hr |  | 2199.2677 | 592.1968 | 334.575 | 1080.0038 | 282.8536
TOTAL | lb/hr |  | 109963.3869 | 29609.8409 | 16728.7514 | 54000.1884 | 14142.6816
Calculated Composition of Recycle Solids to Slurry Tank
CaSO3*1/2H2O | lb/hr |  | 20735.1633 | 12756.2892 | 8850.4554 | 9064.1208 | 9115.8362
CaSO4*2H2O | lb/hr |  | 9214.1528 | 5668.5543 | 3932.906 | 4027.8532 | 4050.8342
Inerts | lb/hr |  | 93767.3484 | 15890.3501 | 12737.148 | 53363.3748 | 14242.093
Ca(OH)2 | lb/hr |  | 170.5372 | 7357.3302 | 7796.1362 | 648.249 | 10162.6939
H2O | lb/hr |  | 2528.3102 | 850.4597 | 679.9315 | 1369.4612 | 766.7644
TOTAL | lb/hr |  | 126415.5119 | 42522.9835 | 33996.5771 | 68473.0589 | 38338.2217
ITERATION 3
Assumed Composition of Recycle Solids to Slurry Tank
CaSO3*1/2H2O | lb/hr |  | 20719.4189 | 12875.444 | 9212.727 | 9071.11 | 9709.0667
CaSO4*2H2O | lb/hr |  | 9207.1564 | 5721.5035 | 4093.8899 | 4030.9591 | 4314.45
Inerts | lb/hr |  | 93778.7188 | 15804.2981 | 12475.5202 | 53358.3272 | 13813.6698
Ca(OH)2 | lb/hr |  | 181.9076 | 7271.2782 | 7534.5084 | 643.2014 | 9734.2707
H2O | lb/hr |  | 2528.3102 | 850.4597 | 679.9315 | 1369.4612 | 766.7644
TOTAL | lb/hr |  | 126415.5119 | 42522.9835 | 33996.5771 | 68473.0589 | 38338.2217
Composition of Recycle Slurry to Head Tanks
CaSO3*1/2H2O | lb/hr |  | 20719.4189 | 12875.444 | 9212.727 | 9071.11 | 9709.0667
CaSO4*2H2O | lb/hr |  | 9207.1564 | 5721.5035 | 4093.8899 | 4030.9591 | 4314.45
Inerts | lb/hr |  | 93778.7188 | 15804.2981 | 12475.5202 | 53358.3272 | 13813.6698
Ca(OH)2 | lb/hr |  | 181.9076 | 7271.2782 | 7534.5084 | 643.2014 | 9734.2707
H2O | lb/hr |  | 230076.2317 | 77391.83 | 61873.7703 | 124620.9672 | 69775.5634
TOTAL | lb/hr |  | 353963.4334 | 119064.3538 | 95190.4158 | 191724.5649 | 107347.0206
Composition of Slurry from Head Tank
CaSO3*1/2H2O | lb/hr |  | 10359.7094 | 6437.722 | 4606.3635 | 4535.555 | 4854.5334
CaSO4*2H2O | lb/hr |  | 4603.5782 | 2860.7517 | 2046.9449 | 2015.4795 | 2157.225
Inerts | lb/hr |  | 47100.0519 | 9420.827 | 8813.2584 | 27059.5695 | 10818.8984
Ca(OH)2 | lb/hr |  | 2596.3442 | 21694.5681 | 34393.0623 | 4845.0895 | 51386.3295
H2O | lb/hr |  | 121375.6427 | 84376.998 | 108406.5999 | 73752.9045 | 152560.7162
TOTAL | lb/hr |  | 186035.3265 | 124790.867 | 158266.229 | 112208.5981 | 221777.7024
Solids in Spray Dryer
CaSO3*1/2H2O | lb/hr |  | 12927.5004 | 17769.5897 | 21032.841 | 8749.7456 | 27466.4856
CaSO4*2H2O | lb/hr |  | 5744.636 | 7896.3311 | 9346.4329 | 3888.1533 | 12205.3727
Inerts | lb/hr |  | 61344.5003 | 24582.197 | 32635.4906 | 56885.2007 | 45068.5107
Ca(OH)2 | lb/hr |  | 598.7761 | 13026.2808 | 21597.5813 | 1393.9658 | 33817.7772
H2O | lb/hr |  | NA | NA | NA | NA | NA
TOTAL | lb/hr |  | 80615.4128 | 63274.3986 | 84612.3458 | 70917.0653 | 118558.1462
Composition of Solids from Spray Dryers
CaSO3*1/2H2O | lb/hr |  | 1292.75 | 1776.959 | 2103.2841 | 874.9746 | 2746.6486
CaSO4*2H2O | lb/hr |  | 574.4636 | 789.6331 | 934.6433 | 388.8153 | 1220.5373
Inerts | lb/hr |  | 6134.45 | 2458.2197 | 3263.5491 | 5688.5201 | 4506.8511
Ca(OH)2 | lb/hr |  | 59.8776 | 1302.6281 | 2159.7581 | 139.3966 | 3381.7777
H2O | lb/hr |  | 164.5213 | 129.1314 | 172.6783 | 144.7287 | 241.9554
TOTAL | lb/hr |  | 8226.0625 | 6456.5713 | 8633.9128 | 7236.4352 | 12097.77
Solids in Baghouse/ESP
CaSO3*1/2H2O | lb/hr |  | 24553.3962 | 37651.1953 | 46072.3527 | 17856.6373 | 60745.6502
CaSO4*2H2O | lb/hr |  | 10910.8736 | 16731.1857 | 20473.3232 | 7935.0128 | 26993.7448
Inerts | lb/hr |  | 110420.1005 | 44247.9547 | 58743.883 | 102393.3612 | 81123.3193
Ca(OH)2 | lb/hr |  | 95.684 | 19113.1617 | 32592.9474 | 897.3206 | 52223.5173
H2O | lb/hr
TOTAL | lb/hr |  | 145980.0543 | 117743.4973 | 157882.5062 | 129082.3318 | 221086.2315
CaSO3*1/2H2O | wt % |  | 16.82% | 31.98% | 29.18% | 13.83% | 27.48%
CaSO4*2H2O | wt % |  | 7.474% | 14.21% | 12.97% | 6.147% | 12.21%
Inerts | wt % |  | 75.64% | 37.58% | 37.21% | 79.32% | 36.69%
Ca(OH)2 | wt % |  | 0.06555% | 16.23% | 20.64% | 0.6952% | 23.62%
H2O | wt %
TOTAL | wt % |  | 100% | 100% | 100% | 100% | 100%
Dry Solids
CaSO3*1/2H2O | lb/hr |  | 6401.3118 | 28321.7709 | 41242.3389 | 10514.1223 | 56894.2494
CaSO4*2H2O | lb/hr |  | 2844.572 | 12585.4387 | 18326.9941 | 4672.1952 | 25282.2851
Inerts | lb/hr |  | 28787.6056 | 33283.9483 | 52585.4443 | 60289.9807 | 75979.9317
Ca(OH)2 | lb/hr |  | 24.9457 | 14377.1953 | 29176.0525 | 528.3491 | 48912.4374
H2O | lb/hr |  | 776.7028 | 1807.5174 | 2884.3027 | 1551.1152 | 4225.896
TOTAL | lb/hr |  | 38835.1379 | 90375.8707 | 144215.1325 | 77555.7624 | 211294.7995
Solids Out Stack
CaSO3*1/2H2O | lb/hr |  | 26.491 | 50.3643 | 45.9607 | 21.7878 | 43.2747
CaSO4*2H2O | lb/hr |  | 11.7719 | 22.3805 | 20.4237 | 9.6819 | 19.2301
Inerts | lb/hr |  | 119.1338 | 59.1884 | 58.6016 | 124.9354 | 57.7916
Ca(OH)2 | lb/hr |  | 0.10323 | 25.5668 | 32.514 | 1.0949 | 37.2036
H2O | lb/hr
TOTAL | lb/hr |  | 157.5 | 157.5 | 157.5 | 157.5 | 157.5
Composition of Baghouse/ESP Solids to Recycle
CaSO3*1/2H2O | lb/hr |  | 18125.5935 | 9279.0601 | 4784.053 | 7320.7272 | 3808.1262
CaSO4*2H2O | lb/hr |  | 8054.5297 | 4123.3665 | 2125.9054 | 3253.1357 | 1692.2296
Inerts | lb/hr |  | 81513.361 | 10904.8179 | 6099.8372 | 41978.4451 | 5085.596
Ca(OH)2 | lb/hr |  | 70.635 | 4710.3996 | 3384.3808 | 367.8766 | 3273.8763
H2O | lb/hr |  | 2199.2677 | 592.1968 | 334.575 | 1080.0038 | 282.8536
TOTAL | lb/hr |  | 109963.3869 | 29609.8409 | 16728.7514 | 54000.1884 | 14142.6816
Calculated Composition of Recycle Solids to Slurry Tank
CaSO3*1/2H2O | lb/hr |  | 20711.0936 | 12832.978 | 8990.6212 | 9070.6764 | 9301.4233
CaSO4*2H2O | lb/hr |  | 9203.4569 | 5702.6327 | 3995.192 | 4030.7663 | 4133.3041
Inerts | lb/hr |  | 93782.2611 | 15821.2573 | 12626.9353 | 53355.4853 | 14099.2981
Ca(OH)2 | lb/hr |  | 190.3902 | 7315.6558 | 7703.8971 | 646.6698 | 10037.4317
H2O | lb/hr |  | 2528.3102 | 850.4597 | 679.9315 | 1369.4612 | 766.7644
TOTAL | lb/hr |  | 126415.5119 | 42522.9835 | 33996.5771 | 68473.0589 | 38338.2217
ITERATION 4
Assumed Composition of Recycle Solids to Slurry Tank
CaSO3*1/2H2O | lb/hr |  | 20702.7682 | 12790.512 | 8768.5154 | 9070.6764 | 8893.7798
CaSO4*2H2O | lb/hr |  | 9199.7573 | 5683.762 | 3896.4941 | 4030.7663 | 3952.1583
Inerts | lb/hr |  | 93788.2735 | 15851.9257 | 12787.3371 | 53355.4853 | 14393.6928
Ca(OH)2 | lb/hr |  | 196.4026 | 7346.3242 | 7864.2989 | 646.6698 | 10331.8264
H2O | lb/hr |  | 2528.3102 | 850.4597 | 679.9315 | 1369.4612 | 766.7644
TOTAL | lb/hr |  | 126415.5119 | 42522.9835 | 33996.5771 | 68473.0589 | 38338.2217
Composition of Recycle Slurry to Head Tanks
CaSO3*1/2H2O | lb/hr |  | 20702.7682 | 12790.512 | 8768.5154 | 9070.6764 | 8893.7798
CaSO4*2H2O | lb/hr |  | 9199.7573 | 5683.762 | 3896.4941 | 4030.7663 | 3952.1583
Inerts | lb/hr |  | 93788.2735 | 15851.9257 | 12787.3371 | 53355.4853 | 14393.6928
Ca(OH)2 | lb/hr |  | 196.4026 | 7346.3242 | 7864.2989 | 646.6698 | 10331.8264
H2O | lb/hr |  | 230076.2317 | 77391.83 | 61873.7703 | 124620.9672 | 69775.5634
TOTAL | lb/hr |  | 353963.4334 | 119064.3538 | 95190.4158 | 191724.5649 | 107347.0206
Composition of Slurry from Head Tank
CaSO3*1/2H2O | lb/hr |  | 10351.3841 | 6395.256 | 4384.2577 | 4535.3382 | 4446.8899
CaSO4*2H2O | lb/hr |  | 4599.8787 | 2841.881 | 1948.247 | 2015.3832 | 1976.0791
Inerts | lb/hr |  | 47104.8293 | 9444.6408 | 8969.1668 | 27058.1485 | 11108.9098
Ca(OH)2 | lb/hr |  | 2603.5917 | 21732.0911 | 34557.9575 | 4846.8237 | 51685.1074
H2O | lb/hr |  | 121375.6427 | 84376.998 | 108406.5999 | 73752.9045 | 152560.7162
TOTAL | lb/hr |  | 186035.3265 | 124790.867 | 158266.229 | 112208.5981 | 221777.7024
Solids in Spray Dryer
CaSO3*1/2H2O | lb/hr |  | 12919.1751 | 17727.1237 | 20810.7352 | 8749.5287 | 27058.8422
CaSO4*2H2O | lb/hr |  | 5740.9364 | 7877.4604 | 9247.735 | 3888.0569 | 12024.2269
Inerts | lb/hr |  | 61349.2776 | 24606.0108 | 32791.399 | 56883.7797 | 45358.5222
Ca(OH)2 | lb/hr |  | 606.0236 | 13063.8037 | 21762.4766 | 1395.7 | 34116.555
H2O | lb/hr |  | NA | NA | NA | NA | NA
TOTAL | lb/hr |  | 80615.4128 | 63274.3986 | 84612.3458 | 70917.0653 | 118558.1462
Composition of Solids from Spray Dryers
CaSO3*1/2H2O | lb/hr |  | 1291.9175 | 1772.7124 | 2081.0735 | 874.9529 | 2705.8842
CaSO4*2H2O | lb/hr |  | 574.0936 | 787.746 | 924.7735 | 388.8057 | 1202.4227
Inerts | lb/hr |  | 6134.9278 | 2460.6011 | 3279.1399 | 5688.378 | 4535.8522
Ca(OH)2 | lb/hr |  | 60.6024 | 1306.3804 | 2176.2477 | 139.57 | 3411.6555
H2O | lb/hr |  | 164.5213 | 129.1314 | 172.6783 | 144.7287 | 241.9554
TOTAL | lb/hr |  | 8226.0625 | 6456.5713 | 8633.9128 | 7236.4352 | 12097.77
Solids in Baghouse/ESP
CaSO3*1/2H2O | lb/hr |  | 24538.4107 | 37574.7564 | 45672.5622 | 17856.247 | 60011.892
CaSO4*2H2O | lb/hr |  | 10904.2144 | 16697.2183 | 20295.667 | 7934.8393 | 26667.6822
Inerts | lb/hr |  | 110428.6997 | 44290.8195 | 59024.5182 | 102390.8034 | 81645.3399
Ca(OH)2 | lb/hr |  | 108.7295 | 19180.7031 | 32889.7588 | 900.4421 | 52761.3174
H2O | lb/hr
TOTAL | lb/hr |  | 145980.0543 | 117743.4973 | 157882.5062 | 129082.3318 | 221086.2315
CaSO3*1/2H2O | wt % |  | 16.81% | 31.91% | 28.93% | 13.83% | 27.14%
CaSO4*2H2O | wt % |  | 7.47% | 14.18% | 12.85% | 6.147% | 12.06%
Inerts | wt % |  | 75.65% | 37.62% | 37.39% | 79.32% | 36.93%
Ca(OH)2 | wt % |  | 0.07448% | 16.29% | 20.83% | 0.6976% | 23.86%
H2O | wt %
TOTAL | wt % |  | 100% | 100% | 100% | 100% | 100%
Dry Solids
CaSO3*1/2H2O | lb/hr |  | 6397.4049 | 28264.2725 | 40884.4607 | 10513.8924 | 56207.0129
CaSO4*2H2O | lb/hr |  | 2842.8359 | 12559.8879 | 18167.9625 | 4672.093 | 24976.8956
Inerts | lb/hr |  | 28789.8475 | 33316.1919 | 52836.659 | 60288.4746 | 76468.8551
Ca(OH)2 | lb/hr |  | 28.3468 | 14428.0009 | 29441.7476 | 530.1871 | 49416.1399
H2O | lb/hr |  | 776.7028 | 1807.5174 | 2884.3027 | 1551.1152 | 4225.896
TOTAL | lb/hr |  | 38835.1379 | 90375.8707 | 144215.1325 | 77555.7624 | 211294.7995
Solids Out Stack
CaSO3*1/2H2O | lb/hr |  | 26.4748 | 50.262 | 45.5619 | 21.7873 | 42.752
CaSO4*2H2O | lb/hr |  | 11.7647 | 22.3351 | 20.2465 | 9.6817 | 18.9978
Inerts | lb/hr |  | 119.1431 | 59.2458 | 58.8815 | 124.9323 | 58.1635
Ca(OH)2 | lb/hr |  | 0.11731 | 25.6571 | 32.8101 | 1.0987 | 37.5867
H2O | lb/hr
TOTAL | lb/hr |  | 157.5 | 157.5 | 157.5 | 157.5 | 157.5
Composition of Baghouse/ESP Solids to Recycle
CaSO3*1/2H2O | lb/hr |  | 18114.5309 | 9260.2219 | 4742.5396 | 7320.5672 | 3762.1271
CaSO4*2H2O | lb/hr |  | 8049.6138 | 4114.9953 | 2107.458 | 3253.0646 | 1671.7888
Inerts | lb/hr |  | 81519.7091 | 10915.3819 | 6128.9777 | 41977.3965 | 5118.3213
Ca(OH)2 | lb/hr |  | 80.2653 | 4727.045 | 3415.2011 | 369.1563 | 3307.5908
H2O | lb/hr |  | 2199.2677 | 592.1968 | 334.575 | 1080.0038 | 282.8536
TOTAL | lb/hr |  | 109963.3869 | 29609.8409 | 16728.7514 | 54000.1884 | 14142.6816
Calculated Composition of Recycle Solids to Slurry Tank
CaSO3*1/2H2O | lb/hr |  | 20698.366 | 12805.6466 | 8904.6867 | 9070.473 | 9173.8955
CaSO4*2H2O | lb/hr |  | 9197.8011 | 5690.4874 | 3957.005 | 4030.676 | 4076.6342
Inerts | lb/hr |  | 93789.5646 | 15836.5841 | 12687.2575 | 53354.1524 | 14190.0257
Ca(OH)2 | lb/hr |  | 201.47 | 7339.8058 | 7767.6964 | 648.2963 | 10130.9018
H2O | lb/hr |  | 2528.3102 | 850.4597 | 679.9315 | 1369.4612 | 766.7644
TOTAL | lb/hr |  | 126415.5119 | 42522.9835 | 33996.5771 | 68473.0589 | 38338.2217
ITERATION 5
Assumed Composition of Recycle Solids to Slurry Tank
CaSO3*1/2H2O | lb/hr |  | 20693.9637 | 12820.7812 | 9040.8579 | 9070.473 | 9454.0112
CaSO4*2H2O | lb/hr |  | 9195.8448 | 5697.2128 | 4017.5158 | 4030.676 | 4201.1101
Inerts | lb/hr |  | 93792.7439 | 15825.654 | 12588.9164 | 53354.1524 | 13987.7299
Ca(OH)2 | lb/hr |  | 204.6493 | 7328.8758 | 7669.3553 | 648.2963 | 9928.606
H2O | lb/hr |  | 2528.3102 | 850.4597 | 679.9315 | 1369.4612 | 766.7644
TOTAL | lb/hr |  | 126415.5119 | 42522.9835 | 33996.5771 | 68473.0589 | 38338.2217
Composition of Recycle Slurry to Head Tanks
CaSO3*1/2H2O | lb/hr |  | 20693.9637 | 12820.7812 | 9040.8579 | 9070.473 | 9454.0112
CaSO4*2H2O | lb/hr |  | 9195.8448 | 5697.2128 | 4017.5158 | 4030.676 | 4201.1101
Inerts | lb/hr |  | 93792.7439 | 15825.654 | 12588.9164 | 53354.1524 | 13987.7299
Ca(OH)2 | lb/hr |  | 204.6493 | 7328.8758 | 7669.3553 | 648.2963 | 9928.606
H2O | lb/hr |  | 230076.2317 | 77391.83 | 61873.7703 | 124620.9672 | 69775.5634
TOTAL | lb/hr |  | 353963.4334 | 119064.3538 | 95190.4158 | 191724.5649 | 107347.0206
Composition of Slurry from Head Tank
CaSO3*1/2H2O | lb/hr |  | 10346.9818 | 6410.3906 | 4520.429 | 4535.2365 | 4727.0056
CaSO4*2H2O | lb/hr |  | 4597.9224 | 2848.6064 | 2008.7579 | 2015.338 | 2100.5551
Inerts | lb/hr |  | 47107.0645 | 9431.505 | 8869.9565 | 27057.4821 | 10905.9284
Ca(OH)2 | lb/hr |  | 2607.7151 | 21723.3669 | 34460.4857 | 4847.637 | 51483.4972
H2O | lb/hr |  | 121375.6427 | 84376.998 | 108406.5999 | 73752.9045 | 152560.7162
TOTAL | lb/hr |  | 186035.3265 | 124790.867 | 158266.229 | 112208.5981 | 221777.7024
Solids in Spray Dryer
CaSO3*1/2H2O | lb/hr |  | 12914.7728 | 17742.2583 | 20946.9065 | 8749.427 | 27338.9578
CaSO4*2H2O | lb/hr |  | 5738.9802 | 7884.1858 | 9308.2459 | 3888.0117 | 12148.7028
Inerts | lb/hr |  | 61351.5128 | 24592.875 | 32692.1887 | 56883.1133 | 45155.5407
Ca(OH)2 | lb/hr |  | 610.147 | 13055.0796 | 21665.0048 | 1396.5133 | 33914.9449
H2O | lb/hr |  | NA | NA | NA | NA | NA
TOTAL | lb/hr |  | 80615.4128 | 63274.3986 | 84612.3458 | 70917.0653 | 118558.1462
Composition of Solids from Spray Dryers
CaSO3*1/2H2O | lb/hr |  | 1291.4773 | 1774.2258 | 2094.6907 | 874.9427 | 2733.8958
CaSO4*2H2O | lb/hr |  | 573.898 | 788.4186 | 930.8246 | 388.8012 | 1214.8703
Inerts | lb/hr |  | 6135.1513 | 2459.2875 | 3269.2189 | 5688.3113 | 4515.5541
Ca(OH)2 | lb/hr |  | 61.0147 | 1305.508 | 2166.5005 | 139.6513 | 3391.4945
H2O | lb/hr |  | 164.5213 | 129.1314 | 172.6783 | 144.7287 | 241.9554
TOTAL | lb/hr |  | 8226.0625 | 6456.5713 | 8633.9128 | 7236.4352 | 12097.77
Solids in Baghouse/ESP
CaSO3*1/2H2O | lb/hr |  | 24530.4866 | 37601.9987 | 45917.6705 | 17856.0639 | 60516.1002
CaSO4*2H2O | lb/hr |  | 10900.6932 | 16709.3241 | 20404.5866 | 7934.758 | 26891.7389
Inerts | lb/hr |  | 110432.7231 | 44267.175 | 58845.9396 | 102389.6039 | 81279.9733
Ca(OH)2 | lb/hr |  | 116.1515 | 19164.9995 | 32714.3096 | 901.906 | 52398.4191
H2O | lb/hr
TOTAL | lb/hr |  | 145980.0543 | 117743.4973 | 157882.5062 | 129082.3318 | 221086.2315
CaSO3*1/2H2O | wt % |  | 16.8% | 31.94% | 29.08% | 13.83% | 27.37%
CaSO4*2H2O | wt % |  | 7.467% | 14.19% | 12.92% | 6.147% | 12.16%
Inerts | wt % |  | 75.65% | 37.6% | 37.27% | 79.32% | 36.76%
Ca(OH)2 | wt % |  | 0.07957% | 16.28% | 20.72% | 0.6987% | 23.7%
H2O | wt %
TOTAL | wt % |  | 100% | 100% | 100% | 100% | 100%
Dry Solids
CaSO3*1/2H2O | lb/hr |  | 6395.339 | 28284.7646 | 41103.873 | 10513.7847 | 56679.2533
CaSO4*2H2O | lb/hr |  | 2841.9179 | 12568.9941 | 18265.4635 | 4672.0451 | 25186.7466
Inerts | lb/hr |  | 28790.8965 | 33298.4061 | 52676.8018 | 60287.7684 | 76126.6536
Ca(OH)2 | lb/hr |  | 30.2818 | 14416.1885 | 29284.6917 | 531.049 | 49076.2501
H2O | lb/hr |  | 776.7028 | 1807.5174 | 2884.3027 | 1551.1152 | 4225.896
TOTAL | lb/hr |  | 38835.1379 | 90375.8707 | 144215.1325 | 77555.7624 | 211294.7995
Solids Out Stack
CaSO3*1/2H2O | lb/hr |  | 26.4663 | 50.2984 | 45.8064 | 21.7871 | 43.1112
CaSO4*2H2O | lb/hr |  | 11.7609 | 22.3513 | 20.3552 | 9.6816 | 19.1575
Inerts | lb/hr |  | 119.1475 | 59.2141 | 58.7034 | 124.9308 | 57.9032
Ca(OH)2 | lb/hr |  | 0.12532 | 25.6361 | 32.6351 | 1.1005 | 37.3282
H2O | lb/hr
TOTAL | lb/hr |  | 157.5 | 157.5 | 157.5 | 157.5 | 157.5
Composition of Baghouse/ESP Solids to Recycle
CaSO3*1/2H2O | lb/hr |  | 18108.6813 | 9266.9357 | 4767.9911 | 7320.4922 | 3793.7357
CaSO4*2H2O | lb/hr |  | 8047.0144 | 4117.9787 | 2118.7679 | 3253.0312 | 1685.8349
Inerts | lb/hr |  | 81522.6792 | 10909.5547 | 6110.4345 | 41976.9047 | 5095.4166
Ca(OH)2 | lb/hr |  | 85.7443 | 4723.1749 | 3396.9828 | 369.7565 | 3284.8408
H2O | lb/hr |  | 2199.2677 | 592.1968 | 334.575 | 1080.0038 | 282.8536
TOTAL | lb/hr |  | 109963.3869 | 29609.8409 | 16728.7514 | 54000.1884 | 14142.6816
Calculated Composition of Recycle Solids to Slurry Tank
CaSO3*1/2H2O | lb/hr |  | 20691.6358 | 12815.3873 | 8957.3724 | 9070.3776 | 9261.5273
CaSO4*2H2O | lb/hr |  | 9194.8104 | 5694.8159 | 3980.4171 | 4030.6336 | 4115.5754
Inerts | lb/hr |  | 93792.9817 | 15828.1297 | 12648.8722 | 53353.5274 | 14126.5247
Ca(OH)2 | lb/hr |  | 207.7737 | 7334.1908 | 7729.9838 | 649.0592 | 10067.8298
H2O | lb/hr |  | 2528.3102 | 850.4597 | 679.9315 | 1369.4612 | 766.7644
TOTAL | lb/hr |  | 126415.5119 | 42522.9835 | 33996.5771 | 68473.0589 | 38338.2217
ITERATION 6
Assumed Composition of Recycle Solids to Slurry Tank
CaSO3*1/2H2O | lb/hr |  | 20689.308 | 12809.9935 | 8873.8869 | 9070.3776 | 9069.0434
CaSO4*2H2O | lb/hr |  | 9193.776 | 5692.419 | 3943.3184 | 4030.6336 | 4030.0407
Inerts | lb/hr |  | 93794.6628 | 15832.0251 | 12709.1643 | 53353.5274 | 14265.534
Ca(OH)2 | lb/hr |  | 209.4549 | 7338.0862 | 7790.2759 | 649.0592 | 10206.8391
H2O | lb/hr |  | 2528.3102 | 850.4597 | 679.9315 | 1369.4612 | 766.7644
TOTAL | lb/hr |  | 126415.5119 | 42522.9835 | 33996.5771 | 68473.0589 | 38338.2217
Composition of Recycle Slurry to Head Tanks
CaSO3*1/2H2O | lb/hr |  | 20689.308 | 12809.9935 | 8873.8869 | 9070.3776 | 9069.0434
CaSO4*2H2O | lb/hr |  | 9193.776 | 5692.419 | 3943.3184 | 4030.6336 | 4030.0407
Inerts | lb/hr |  | 93794.6628 | 15832.0251 | 12709.1643 | 53353.5274 | 14265.534
Ca(OH)2 | lb/hr |  | 209.4549 | 7338.0862 | 7790.2759 | 649.0592 | 10206.8391
H2O | lb/hr |  | 230076.2317 | 77391.83 | 61873.7703 | 124620.9672 | 69775.5634
TOTAL | lb/hr |  | 353963.4334 | 119064.3538 | 95190.4158 | 191724.5649 | 107347.0206
Composition of Slurry from Head Tank
CaSO3*1/2H2O | lb/hr |  | 10344.654 | 6404.9967 | 4436.9435 | 4535.1888 | 4534.5217
CaSO4*2H2O | lb/hr |  | 4596.888 | 2846.2095 | 1971.6592 | 2015.3168 | 2015.0204
Inerts | lb/hr |  | 47108.0239 | 9434.6905 | 8930.0804 | 27057.1696 | 11044.8304
Ca(OH)2 | lb/hr |  | 2610.1178 | 21727.9722 | 34520.946 | 4848.0184 | 51622.6137
H2O | lb/hr |  | 121375.6427 | 84376.998 | 108406.5999 | 73752.9045 | 152560.7162
TOTAL | lb/hr |  | 186035.3265 | 124790.867 | 158266.229 | 112208.5981 | 221777.7024
Solids in Spray Dryer
CaSO3*1/2H2O | lb/hr |  | 12912.445 | 17736.8644 | 20863.421 | 8749.3793 | 27146.474
CaSO4*2H2O | lb/hr |  | 5737.9457 | 7881.7889 | 9271.1471 | 3887.9905 | 12063.1681
Inerts | lb/hr |  | 61352.4723 | 24596.0605 | 32752.3126 | 56882.8008 | 45294.4428
Ca(OH)2 | lb/hr |  | 612.5497 | 13059.6848 | 21725.465 | 1396.8947 | 34054.0614
H2O | lb/hr |  | NA | NA | NA | NA | NA
TOTAL | lb/hr |  | 80615.4128 | 63274.3986 | 84612.3458 | 70917.0653 | 118558.1462
Composition of Solids from Spray Dryers
CaSO3*1/2H2O | lb/hr |  | 1291.2445 | 1773.6864 | 2086.3421 | 874.9379 | 2714.6474
CaSO4*2H2O | lb/hr |  | 573.7946 | 788.1789 | 927.1147 | 388.7991 | 1206.3168
Inerts | lb/hr |  | 6135.2472 | 2459.6061 | 3275.2313 | 5688.2801 | 4529.4443
Ca(OH)2 | lb/hr |  | 61.255 | 1305.9685 | 2172.5465 | 139.6895 | 3405.4061
H2O | lb/hr |  | 164.5213 | 129.1314 | 172.6783 | 144.7287 | 241.9554
TOTAL | lb/hr |  | 8226.0625 | 6456.5713 | 8633.9128 | 7236.4352 | 12097.77
Solids in Baghouse/ESP
CaSO3*1/2H2O | lb/hr |  | 24526.2965 | 37592.2897 | 45767.3966 | 17855.9781 | 60169.6292
CaSO4*2H2O | lb/hr |  | 10898.8312 | 16705.0097 | 20337.8088 | 7934.7198 | 26737.7764
Inerts | lb/hr |  | 110434.4502 | 44272.909 | 58954.1627 | 102389.0414 | 81529.997
Ca(OH)2 | lb/hr |  | 120.4765 | 19173.2889 | 32823.1381 | 902.5926 | 52648.8288
H2O | lb/hr
TOTAL | lb/hr |  | 145980.0543 | 117743.4973 | 157882.5062 | 129082.3318 | 221086.2315
CaSO3*1/2H2O | wt % |  | 16.8% | 31.93% | 28.99% | 13.83% | 27.22%
CaSO4*2H2O | wt % |  | 7.466% | 14.19% | 12.88% | 6.147% | 12.09%
Inerts | wt % |  | 75.65% | 37.6% | 37.34% | 79.32% | 36.88%
Ca(OH)2 | wt % |  | 0.08253% | 16.28% | 20.79% | 0.6992% | 23.81%
H2O | wt %
TOTAL | wt % |  | 100% | 100% | 100% | 100% | 100%
Dry Solids
CaSO3*1/2H2O | lb/hr |  | 6394.2466 | 28277.4614 | 40969.3531 | 10513.7341 | 56354.7493
CaSO4*2H2O | lb/hr |  | 2841.4324 | 12565.7487 | 18205.6864 | 4672.0227 | 25042.5457
Inerts | lb/hr |  | 28791.3467 | 33302.7193 | 52773.6793 | 60287.4371 | 76360.8252
Ca(OH)2 | lb/hr |  | 31.4094 | 14422.4239 | 29382.1111 | 531.4533 | 49310.7833
H2O | lb/hr |  | 776.7028 | 1807.5174 | 2884.3027 | 1551.1152 | 4225.896
TOTAL | lb/hr |  | 38835.1379 | 90375.8707 | 144215.1325 | 77555.7624 | 211294.7995
Solids Out Stack
CaSO3*1/2H2O | lb/hr |  | 26.4618 | 50.2855 | 45.6565 | 21.787 | 42.8643
CaSO4*2H2O | lb/hr |  | 11.7589 | 22.3455 | 20.2885 | 9.6816 | 19.0478
Inerts | lb/hr |  | 119.1493 | 59.2218 | 58.8113 | 124.9301 | 58.0813
Ca(OH)2 | lb/hr |  | 0.12998 | 25.6472 | 32.7436 | 1.1013 | 37.5066
H2O | lb/hr
TOTAL | lb/hr |  | 157.5 | 157.5 | 157.5 | 157.5 | 157.5
Composition of Baghouse/ESP Solids to Recycle
CaSO3*1/2H2O | lb/hr |  | 18105.5881 | 9264.5429 | 4752.387 | 7320.457 | 3772.0156
CaSO4*2H2O | lb/hr |  | 8045.6399 | 4116.9155 | 2111.8339 | 3253.0156 | 1676.183
Inerts | lb/hr |  | 81523.9541 | 10910.9679 | 6121.6721 | 41976.6741 | 5111.0905
Ca(OH)2 | lb/hr |  | 88.9371 | 4725.2178 | 3408.2833 | 370.038 | 3300.5389
H2O | lb/hr |  | 2199.2677 | 592.1968 | 334.575 | 1080.0038 | 282.8536
TOTAL | lb/hr |  | 109963.3869 | 29609.8409 | 16728.7514 | 54000.1884 | 14142.6816
Calculated Composition of Recycle Solids to Slurry Tank
CaSO3*1/2H2O | lb/hr |  | 20688.0771 | 12811.9158 | 8925.0712 | 9070.3329 | 9201.3104
CaSO4*2H2O | lb/hr |  | 9193.229 | 5693.2732 | 3966.0633 | 4030.6137 | 4088.8166
Inerts | lb/hr |  | 93794.4486 | 15830.18 | 12672.1347 | 53353.2342 | 14169.979
Ca(OH)2 | lb/hr |  | 211.447 | 7337.1548 | 7753.3763 | 649.4169 | 10111.3512
H2O | lb/hr |  | 2528.3102 | 850.4597 | 679.9315 | 1369.4612 | 766.7644
TOTAL | lb/hr |  | 126415.5119 | 42522.9835 | 33996.5771 | 68473.0589 | 38338.2217
ITERATION 7
Assumed Composition of Recycle Solids to Slurry Tank
CaSO3*1/2H2O | lb/hr |  | 20686.8462 | 12813.8381 | 8976.2555 | 9070.3329 | 9333.5773
CaSO4*2H2O | lb/hr |  | 9192.682 | 5694.1275 | 3988.8082 | 4030.6137 | 4147.5925
Inerts | lb/hr |  | 93795.3375 | 15828.7917 | 12635.1701 | 53353.2342 | 14074.4576
Ca(OH)2 | lb/hr |  | 212.336 | 7335.7665 | 7716.4117 | 649.4169 | 10015.8298
H2O | lb/hr |  | 2528.3102 | 850.4597 | 679.9315 | 1369.4612 | 766.7644
TOTAL | lb/hr |  | 126415.5119 | 42522.9835 | 33996.5771 | 68473.0589 | 38338.2217
Composition of Recycle Slurry to Head Tanks
CaSO3*1/2H2O | lb/hr |  | 20686.8462 | 12813.8381 | 8976.2555 | 9070.3329 | 9333.5773
CaSO4*2H2O | lb/hr |  | 9192.682 | 5694.1275 | 3988.8082 | 4030.6137 | 4147.5925
Inerts | lb/hr |  | 93795.3375 | 15828.7917 | 12635.1701 | 53353.2342 | 14074.4576
Ca(OH)2 | lb/hr |  | 212.336 | 7335.7665 | 7716.4117 | 649.4169 | 10015.8298
H2O | lb/hr |  | 230076.2317 | 77391.83 | 61873.7703 | 124620.9672 | 69775.5634
TOTAL | lb/hr |  | 353963.4334 | 119064.3538 | 95190.4158 | 191724.5649 | 107347.0206
Composition of Slurry from Head Tank
CaSO3*1/2H2O | lb/hr |  | 10343.4231 | 6406.9191 | 4488.1277 | 4535.1664 | 4666.7887
CaSO4*2H2O | lb/hr |  | 4596.341 | 2847.0637 | 1994.4041 | 2015.3069 | 2073.7963
Inerts | lb/hr |  | 47108.3613 | 9433.0738 | 8893.0833 | 27057.023 | 10949.2922
Ca(OH)2 | lb/hr |  | 2611.5584 | 21726.8123 | 34484.0139 | 4848.1973 | 51527.1091
H2O | lb/hr |  | 121375.6427 | 84376.998 | 108406.5999 | 73752.9045 | 152560.7162
TOTAL | lb/hr |  | 186035.3265 | 124790.867 | 158266.229 | 112208.5981 | 221777.7024
Solids in Spray Dryer
CaSO3*1/2H2O | lb/hr |  | 12911.2141 | 17738.7867 | 20914.6053 | 8749.357 | 27278.7409
CaSO4*2H2O | lb/hr |  | 5737.3987 | 7882.6431 | 9293.8921 | 3887.9806 | 12121.944
Inerts | lb/hr |  | 61352.8096 | 24594.4438 | 32715.3155 | 56882.6542 | 45198.9046
Ca(OH)2 | lb/hr |  | 613.9903 | 13058.5249 | 21688.533 | 1397.0736 | 33958.5567
H2O | lb/hr |  | NA | NA | NA | NA | NA
TOTAL | lb/hr |  | 80615.4128 | 63274.3986 | 84612.3458 | 70917.0653 | 118558.1462
Composition of Solids from Spray Dryers
CaSO3*1/2H2O | lb/hr |  | 1291.1214 | 1773.8787 | 2091.4605 | 874.9357 | 2727.8741
CaSO4*2H2O | lb/hr |  | 573.7399 | 788.2643 | 929.3892 | 388.7981 | 1212.1944
Inerts | lb/hr |  | 6135.281 | 2459.4444 | 3271.5315 | 5688.2654 | 4519.8905
Ca(OH)2 | lb/hr |  | 61.399 | 1305.8525 | 2168.8533 | 139.7074 | 3395.8557
H2O | lb/hr |  | 164.5213 | 129.1314 | 172.6783 | 144.7287 | 241.9554
TOTAL | lb/hr |  | 8226.0625 | 6456.5713 | 8633.9128 | 7236.4352 | 12097.77
Solids in Baghouse/ESP
CaSO3*1/2H2O | lb/hr |  | 24524.0808 | 37595.75 | 45859.5283 | 17855.9378 | 60407.7097
CaSO4*2H2O | lb/hr |  | 10897.8466 | 16706.5473 | 20378.7497 | 7934.7019 | 26843.573
Inerts | lb/hr |  | 110435.0574 | 44269.9989 | 58887.5679 | 102388.7775 | 81358.0282
Ca(OH)2 | lb/hr |  | 123.0695 | 19171.2012 | 32756.6603 | 902.9145 | 52476.9205
H2O | lb/hr
TOTAL | lb/hr |  | 145980.0543 | 117743.4973 | 157882.5062 | 129082.3318 | 221086.2315
CaSO3*1/2H2O | wt % |  | 16.8% | 31.93% | 29.05% | 13.83% | 27.32%
CaSO4*2H2O | wt % |  | 7.465% | 14.19% | 12.91% | 6.147% | 12.14%
Inerts | wt % |  | 75.65% | 37.6% | 37.3% | 79.32% | 36.8%
Ca(OH)2 | wt % |  | 0.08431% | 16.28% | 20.75% | 0.6995% | 23.74%
H2O | wt %
TOTAL | wt % |  | 100% | 100% | 100% | 100% | 100%
Dry Solids
CaSO3*1/2H2O | lb/hr |  | 6393.6689 | 28280.0642 | 41051.8261 | 10513.7104 | 56577.735
CaSO4*2H2O | lb/hr |  | 2841.1757 | 12566.9053 | 18242.3353 | 4672.0121 | 25141.6346
Inerts | lb/hr |  | 28791.505 | 33300.5303 | 52714.0659 | 60287.2818 | 76199.7596
Ca(OH)2 | lb/hr |  | 32.0854 | 14420.8534 | 29322.6026 | 531.6429 | 49149.7743
H2O | lb/hr |  | 776.7028 | 1807.5174 | 2884.3027 | 1551.1152 | 4225.896
TOTAL | lb/hr |  | 38835.1379 | 90375.8707 | 144215.1325 | 77555.7624 | 211294.7995
Solids Out Stack
CaSO3*1/2H2O | lb/hr |  | 26.4594 | 50.2901 | 45.7484 | 21.7869 | 43.034
CaSO4*2H2O | lb/hr |  | 11.7578 | 22.3476 | 20.3294 | 9.6815 | 19.1231
Inerts | lb/hr |  | 119.15 | 59.2179 | 58.7449 | 124.9298 | 57.9588
Ca(OH)2 | lb/hr |  | 0.13278 | 25.6444 | 32.6773 | 1.1017 | 37.3841
H2O | lb/hr
TOTAL | lb/hr |  | 157.5 | 157.5 | 157.5 | 157.5 | 157.5
Composition of Baghouse/ESP Solids to Recycle
CaSO3*1/2H2O | lb/hr |  | 18103.9525 | 9265.3957 | 4761.9538 | 7320.4405 | 3786.9408
CaSO4*2H2O | lb/hr |  | 8044.913 | 4117.2944 | 2116.0851 | 3253.0083 | 1682.8154
Inerts | lb/hr |  | 81524.4023 | 10910.2507 | 6114.7571 | 41976.5659 | 5100.3098
Ca(OH)2 | lb/hr |  | 90.8513 | 4724.7033 | 3401.3804 | 370.17 | 3289.762
H2O | lb/hr |  | 2199.2677 | 592.1968 | 334.575 | 1080.0038 | 282.8536
TOTAL | lb/hr |  | 109963.3869 | 29609.8409 | 16728.7514 | 54000.1884 | 14142.6816
Calculated Composition of Recycle Solids to Slurry Tank
CaSO3*1/2H2O | lb/hr |  | 20686.1953 | 12813.153 | 8944.8748 | 9070.3119 | 9242.689
CaSO4*2H2O | lb/hr |  | 9192.3928 | 5693.823 | 3974.8635 | 4030.6044 | 4107.2042
Inerts | lb/hr |  | 93794.9643 | 15829.1394 | 12657.8202 | 53353.0968 | 14140.0907
Ca(OH)2 | lb/hr |  | 213.6493 | 7336.4083 | 7739.087 | 649.5847 | 10081.4734
H2O | lb/hr |  | 2528.3102 | 850.4597 | 679.9315 | 1369.4612 | 766.7644
TOTAL | lb/hr |  | 126415.5119 | 42522.9835 | 33996.5771 | 68473.0589 | 38338.2217

## FF ESP Cost & Tech. Results
Fabric Filter - Preliminary |  |  | Case1 | Case 2 | Case 3 | Case 4 | Case 5
Flue Gas, Upstream of Fabric Filter
Temperature | °F |  | 147 | 147 | 147 | 147 | 147
Pressure | in. H2O |  | -17 | -17 | -17 | -17 | -17
Flow Rate | SCFM |  | 1402194.0741 | 1292635.6996 | 1313498.5241 | 1282054.7153 | 1362366.532
Flow Rate | ACFM |  | 1739624.1128 | 1603701.1378 | 1629584.4824 | 1590573.8997 | 1690212.2989
CO2 | lb/hr |  | 1120919.593 | 1045412.0567 | 1055109.6603 | 1047495.1261 | 1048927.3597
N2 | lb/hr |  | 4084072.3846 | 4052345.0935 | 4061257.919 | 4030484.7626 | 4067354.248
SO2 | lb/hr |  | 1320.8873 | 5829.1818 | 8449.8802 | 2167.8053 | 11631.7262
O2 | lb/hr |  | 327669.1112 | 317634.8658 | 318157.9783 | 316904.3132 | 319686.2769
HCl | lb/hr |  | 0 | 0 | 0 | 0 | 0
Other Gases | lb/hr |  | 1425.4136 | 2267.747 | 2237.8287 | 1873.3623 | 2030.0577
H2O | lb/hr |  | 722080.2712 | 465318.232 | 514007.2747 | 450070.9969 | 650129.7534
Fly Ash | lb/hr |  | 145107.743 | 113893.9175 | 152302.2225 | 127650.7176 | 213404.6632
Total (gas only) | lb/hr |  | 6257487.6609 | 5888807.177 | 5959220.5413 | 5848996.3665 | 6099759.422
Total Fabric Required | Ft2 |  | 497035.4608 | 458200.3251 | 465595.5664 | 454449.6856 | 482917.7997
Surface Area per Bag | Ft2 |  | 31.416 | 31.416 | 31.416 | 31.416 | 31.416
Required No. of Bags (no spare compartments) |  |  | 15821.0931 | 14584.9352 | 14820.3325 | 14465.5489 | 15371.715
Final No. of Bags |  |  | 17403.2024 | 16043.4287 | 16302.3658 | 15912.1038 | 16908.8865
No. of Casings |  |  | 1 | 1 | 1 | 1 | 1
Fabric Filter Dimensions (per Casing) | Ft2 |  | 17085.594 | 15750.6362 | 16004.8476 | 15621.7079 | 16600.2994
Length | Ft |  | 184.8545 | 177.486 | 178.9125 | 176.7581 | 182.2103
Width | Ft |  | 92.4273 | 88.743 | 89.4563 | 88.379 | 91.1052
Capital Cost |  |  | Case1 | Case 2 | Case 3 | Case 4 | Case 5
Cost Basis (Year) |  |  | 1998 | 1998 | 1998 | 1998 | 1998
Fabric Filter | $ |  | 6250411.0463 | 5900180.1263 | 5967519.8309 | 5865906.66 | 6124047.3702
Bags | $ |  | 916791.3589 | 845159.2126 | 858799.8759 | 838241.0868 | 890751.0645
Ash Handling System | $ |  | 1942058.6345 | 1571194.2207 | 2027539.2316 | 1734644.4718 | 2753522.6862
ID Fan(s) | $ |  | 770689.892 | 732840.0008 | 740139.1003 | 729120.9767 | 757065.3984
Equipment Cost Subtotal | $ |  | 9879950.9317 | 9049373.5605 | 9593998.0386 | 9167913.1953 | 10525386.5193
Instruments & Controls | $ |  | 197599.0186 | 180987.4712 | 191879.9608 | 183358.2639 | 210507.7304
Taxes | $ |  | 592797.0559 | 542962.4136 | 575639.8823 | 550074.7917 | 631523.1912
Freight | $ |  | 493997.5466 | 452468.678 | 479699.9019 | 458395.6598 | 526269.326
Purchased Equipment Cost Subtotal | $ |  | 11164344.5528 | 10225792.1233 | 10841217.7836 | 10359741.9107 | 11893686.7668
Installation | $ |  | 7480110.8504 | 6851280.7226 | 7263615.915 | 6941027.0801 | 7968770.1337
Total Direct Cost | $ |  | 18644455.4032 | 17077072.8459 | 18104833.6987 | 17300768.9908 | 19862456.9005
Total Direct Cost with Retrofit Factor | $ |  | 24237792.0241 | 22200194.6997 | 23536283.8083 | 22490999.6881 | 25821193.9707
General Facilities | $ |  | 2423779.2024 | 2220019.47 | 2353628.3808 | 2249099.9688 | 2582119.3971
Engineering Fees | $ |  | 2423779.2024 | 2220019.47 | 2353628.3808 | 2249099.9688 | 2582119.3971
Contingency | $ |  | 4847558.4048 | 4440038.9399 | 4707256.7617 | 4498199.9376 | 5164238.7941
Total Plant Cost (TPC) | $ |  | 33932908.8338 | 31080272.5796 | 32950797.3316 | 31487399.5633 | 36149671.5589
Total Plant Cost (TPC) w/ Prime Contractor's Markup | $ |  | 34950896.0988 | 32012680.757 | 33939321.2515 | 32432021.5502 | 37234161.7057
Total Cash Expended (TCE) | $ |  | 34441902.4663 | 31546476.6683 | 33445059.2916 | 31959710.5567 | 36691916.6323
Allow. for Funds During Constr. (AFDC) | $ |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Total Plant Investment (TPI) | $ |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Preproduction Costs | $ |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Inventory Capital | $ |  | 0 | 0 | 0 | 0 | 0
Total Capital Requirement (TCR) | $ |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| $/kW |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
O&M Data and Costs |  |  | Case1 | Case 2 | Case 3 | Case 4 | Case 5
Cost Basis (Year) |  |  | 1998 | 1998 | 1998 | 1998 | 1998
Power Required Excluding ID Fan(s) | kW |  | 736.1646 | 680.5765 | 691.1734 | 675.2 | 715.9737
ID Fan Power for FF Delta P | kW |  | 1756.8305 | 1619.5631 | 1645.7025 | 1606.306 | 1706.9299
Total Power | kW |  | 2492.9951 | 2300.1396 | 2336.8759 | 2281.506 | 2422.9037
Power Cost ** | $/yr |  | 354877.8483 | 327424.8773 | 332654.2814 | 324772.3811 | 344900.3361
Maintenance Costs | $/yr |  | 1305111.8782 | 1195395.0992 | 1267338.3589 | 1211053.8294 | 1390371.983
Periodic Replacement Items | $/yr |  | 916791.3589 | 845159.2126 | 858799.8759 | 838241.0868 | 890751.0645
First Year Cost. Bags Replaced Every |  |  | 5 Years | 5 Years | 5 Years | 5 Years | 5 Years
** These costs assume inputs are in current dollars (no escalation included).
ESP |  |  | Case1 | Case 2 | Case 3 | Case 4 | Case 5
Flue Gas, Upstream of ESP
Temperature | °F |  | 147 | 147 | 147 | 147 | 147
Pressure | in. H2O |  | -17 | -17 | -17 | -17 | -17
Flow Rate | SCFM |  | 1402194.0741 | 1292635.6996 | 1313498.5241 | 1282054.7153 | 1362366.532
Flow Rate | ACFM |  | 1739624.1128 | 1603701.1378 | 1629584.4824 | 1590573.8997 | 1690212.2989
CO2 | lb/hr |  | 1120919.593 | 1045412.0567 | 1055109.6603 | 1047495.1261 | 1048927.3597
N2 | lb/hr |  | 4084072.3846 | 4052345.0935 | 4061257.919 | 4030484.7626 | 4067354.248
SO2 | lb/hr |  | 1320.8873 | 5829.1818 | 8449.8802 | 2167.8053 | 11631.7262
O2 | lb/hr |  | 327669.1112 | 317634.8658 | 318157.9783 | 316904.3132 | 319686.2769
HCl | lb/hr |  | 0 | 0 | 0 | 0 | 0
Other Gases | lb/hr |  | 1425.4136 | 2267.747 | 2237.8287 | 1873.3623 | 2030.0577
H2O | lb/hr |  | 722080.2712 | 465318.232 | 514007.2747 | 450070.9969 | 650129.7534
Fly Ash | lb/hr |  | 145107.743 | 113893.9175 | 152302.2225 | 127650.7176 | 213404.6632
Total (gas only) | lb/hr |  | 6257487.6609 | 5888807.177 | 5959220.5413 | 5848996.3665 | 6099759.422
Inlet Particulate Loading | lb/hr |  | 145107.743 | 113893.9175 | 152302.2225 | 127650.7176 | 213404.6632
| gr/ft3 |  | 9.7315 | 8.2856 | 10.9038 | 9.363 | 14.7302
Overall PM Collection Efficiency | % |  | 99.89% | 99.86% | 99.9% | 99.88% | 99.93%
ESP Requirements
k | dimensionless |  | 0.451 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | k = power factor in modified Deustch-Anderson equation
E | kV/cm |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | E = the strength of the electric field in the ESP
Ash Composition
Na2O | wt% in Ash |  | 1.68 | 0.9 | 0.4 | 0.4 | 0.6 | weight percent of Na2O in the flyash -- from coal library
Fe | wt% in Ash |  | 6.07 | 20.2 | 9 | 9 | 20 | weight percent of Fe2O3 in the flyash -- from coal library
MgO | wt% in Ash |  | 31.97 | 5.9 | 6.5 | 6.5 | 6.5 | weight percent of MgO in the flyash -- from coal library
CaO | wt% in Ash |  | 0 | 0 | 0 | 0 | 0 | weight percent of CaO in the flyash -- from coal library
Flue Gas Composition
H2O | Vol% |  | 18.569 | 12.9307 | 14.1319 | 12.57 | 17.3826 | volume percent of H2O in flue gas on a wet basis -- from CUECost combustion calculations
SO2 | ppm |  | 95.5227 | 455.5279 | 653.3104 | 170.2591 | 874.5703 | volume percent of SO2 in flue gas on a wet basis -- from CUECost combustion calculations
SO3 | ppm |  | 0.70687 | 3.3709 | 4.8345 | 1.2599 | 6.4718 | volume percent of SO3 in flue gas: SO3 = 0.74%* SO2
Flue Gas Temperature
TF | °F |  | 147 | 147 | 147 | 147 | 147 | flue gas temperature in the ESP (degrees F)
TC | °C |  | 63.8889 | 63.8889 | 63.8889 | 63.8889 | 63.8889 | flue gas temperature in the ESP (degrees C)
TK | Kelvin |  | 337.0389 | 337.0389 | 337.0389 | 337.0389 | 337.0389 | flue gas temperature in the ESP (Kelvin); note: the temperature in Kelvin is used in resistivity calculations
Resistivity Calculations
Volume Resistivity
rv1 | Log10(ohm-cm) |  | 9.1269 | 8.2256 | 9.2842 | 9.2842 | 8.6149 | rv1 = 8.9434 - 1.8916 * Log10(Na2O) - 0.9696 * Log10(Fe) + 1.237 * (Log10(MgO + CaO) - Log10(2.5))
rv2 | Log10(ohm-cm) |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | rv2 = rv1 + (E - 2.0) * (-0.03); note: 0.03 is a correction factor for the electric field
iv | Log10(ohm-cm) |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | iv = rv2 - 4334.5 / 625
rv | Log10(ohm-cm) |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | rv = iv + 4334.5 / TK
rv(TK=1000/2.4) | Log10(ohm-cm) |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | rv = iv + 4334.5 / (1000/2.4)
Volume Resistivity | ohm-cm |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | volume resistivity = 10^rv
Surface Resistivity
rs1 | Log10(ohm-cm) |  | 10.2705 | 10.8759 | 11.6625 | 11.6625 | 11.2692 | rs1 = 10.7737 - 2.2334 * Log10(Na2O)
rs2 | Log10(ohm-cm) |  | 9.0457 | 10.3728 | 11.0056 | 11.2055 | 10.1962 | rs2 = rs1 + (H2O - 9.0) * (-0.128)
rs3 | Log10(ohm-cm) |  | 7.8153 | 5.9 | 6.5 | 6.5 | 6.5 | rs3: if (MgO + CaO) > 10.0 then rs3 = rs2 + 0.56 - 0.056 * (MgO + CaO) else rs3 = rs2
rs4 | Log10(ohm-cm) |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | rs4 = rs3 + (E - 2.0) * (-0.03)
rs4(with E=12) | Log10(ohm-cm) |  | 7.5153 | 5.6 | 6.2 | 6.2 | 6.2 | rs4(with E = 12.0) = rs3 + (12.0 - 2.0) * (-0.03)
rs0 | Log10(ohm-cm) |  | 9.878 | 7.2452 | 7.9981 | 7.7993 | 8.4117 | rs0 = rs4(with E = 12.0) + Log10(Exp(1)) * 7.3895E-4 * Exp(2303.3 / 385) * H2O
rs | Log10(ohm-cm) |  | 4.3429 | 3.3908 | 3.7856 | 4.0525 | 3.2302 | rs = rs0 - Log10(Exp(1)) * 7.3895E-4 * Exp(2303.3 / TK) * H2O
Surface Resistivity | ohm-cm |  | 22022.2728 | 2459.3954 | 6103.7073 | 11283.6697 | 1699.1483 | surface resistivity = 10^rs
rvs1 | ohm-cm |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | rvs1 = 10^(rv + rs) / (10^rv + 10^rs); note: combined volume and surface resistivity
rs2(with H2O=10) | Log10(ohm-cm) |  | 10.1425 | 10.7479 | 11.5345 | 11.5345 | 11.1412 | rs2(with H2O = 10) = rs1 + (10 - 9.0) * (-0.128)
rs3(with H2O=10) | Log10(ohm-cm) |  | 8.9122 | 5.9 | 6.5 | 6.5 | 6.5 | rs3(with H2O = 10): if (MgO + CaO) > 10.0 then rs3 = rs2(with H2O=10) + 0.56 - 0.056 * (MgO + CaO) else rs3 = rs2(with H2O=10)
rs4(with H2O = 10) | Log10(ohm-cm) |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | rs4(with H2O = 10) = rs3(with H2O = 10) + (E - 2.0) * (-0.03)
rs4(with H2O = 10, E = 12) | Log10(ohm-cm) |  | 8.6122 | 5.6 | 6.2 | 6.2 | 6.2 | rs4(with H2O = 10, with E = 12.0) = rs3(with H2O=10) + (12.0 - 2.0) * (-0.03)
rs0(with H2O = 10) | Log10(ohm-cm) |  | 9.8845 | 6.8724 | 7.4724 | 7.4724 | 7.4724 | rs0 = rs4(with H2O = 10, with E = 12.0) + Log10(Exp(1)) * 7.3895E-4 * Exp(2303.3 / 385) * 10
rs(with H2O = 10, TK = 1000/2.4) | Log10(ohm-cm) |  | 9.077 | 6.0649 | 6.6649 | 6.6649 | 6.6649 | rs(with H2O = 10, T = 1000/2.4) = rs0 (with H2O = 10) - Log10(Exp(1)) * 7.3895E-4 * Exp(2303.3 / (1000/2.4)) * 10
rvs1(with H2O=10, TK = 1000/2.4) | ohm-cm |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | rvs1 = 10^(rv + rs) / (10^rv + 10^rs)
rvs2 | Log10(ohm-cm) |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | rvs2 = Log10(rvs1(with H2O = 10 and TK = 1000/2.4)) + (-8) * (-0.03)
Acid Resistivity
ia1 | Log10(ohm-cm) |  | 0.2915 | 0.2915 | 0.2915 | 0.2915 | 0.2915 | ia1: if ((MgO + CaO) < 5 and Fe < 1) then ia1 = 2.6354 else ia1 = 0.2915
ra1 | Log10(ohm-cm) |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | ra1 = ia1 + 0.7669 * rvs2
sa |  |  | -2.0502 | -2.0502 | -2.0502 | -2.0502 | -2.0502 | sa: if ((MgO + CaO) < 5 and Fe < 1) then sa = -5.0 else sa = -2.0502
ia2 | Log10(ohm-cm) |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | ia2 = ra1 - sa*Log10(4)
ra2 | Log10(ohm-cm) |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | ra2 = ia2 + sa*Log10(SO3)
acid_v | index value |  | 1 | 2 | 2 | 1 | 2 | acid_v: if SO3 < 2.75 then acid_v = 1, else if SO3 > 6.5 then acid_v = 3, else acid_v = 2
atom_v | index value |  | 1 | 3 | 3 | 3 | 3 | atom_v: if (Na2O > 1 and (MgO + CaO) > 5) then atom_v = 1, else if (Fe < 1 and (MgO + CaO) < 3 then atom_v = 2, else atom_v = 3
sa1 |  |  | -4.74 | -28.39 | -28.39 | -4.85 | -28.39 | sa1 = Lookup (acid_v, atom_v); note: the lookup table is located below
ia3 | Log10(ohm-cm) |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | ia3 = ra2 - sa1 * 2.4
ra3 | Log10(ohm-cm) |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | ra3 = ia3 + sa1 * 1000 / TK
ra | Log10(ohm-cm) |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | ra = 1.95 + 0.76 * ra3
Acid Resistivity | ohm-cm |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | acid resistivity = 10^ra
Total Resistivity
rvsa | ohm-cm |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | rvsa = 10^(rv + rs + ra)/(10^rv * 10^rs + 10^rv * 10^ra + 10^rs * 10_ra)
Migration Velocity
wk | 1000ft/minute |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | wk = 0.1232972 - 0.003323934*ln(rvsa)
Specific Collection Area
SCA | ft2/1000acfm |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SCA = (-ln(1 - h))^(1/k) / wk
Total Collector Plate Area | ft2 |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
ESP Footprint Area | ft2 |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Capital Cost |  |  | Case1 | Case 2 | Case 3 | Case 4 | Case 5
Cost Basis (Year) |  |  | 1998 | 1998 | 1998 | 1998 | 1998
ESP | $ |  | 7611043.4453 | 7075234.1003 | 7177614.6545 | 7023245.0997 | 7416777.39
Ash Handling System | $ |  | 1942058.6345 | 1571194.2207 | 2027539.2316 | 1734644.4718 | 2753522.6862
ID Fan(s) | $ |  | 770689.892 | 732840.0008 | 740139.1003 | 729120.9767 | 757065.3984
Equipment Cost Subtotal | $ |  | 10323791.9718 | 9379268.3218 | 9945292.9863 | 9487010.5482 | 10927365.4745
Instruments & Controls | $ |  | 206475.8394 | 187585.3664 | 198905.8597 | 189740.211 | 218547.3095
Taxes | $ |  | 619427.5183 | 562756.0993 | 596717.5792 | 569220.6329 | 655641.9285
Freight | $ |  | 516189.5986 | 468963.4161 | 497264.6493 | 474350.5274 | 546368.2737
Purchased Equipment Cost Subtotal | $ |  | 11665884.9281 | 10598573.2037 | 11238181.0745 | 10720321.9195 | 12347922.9862
Installation | $ |  | 9449366.7918 | 8584844.295 | 9102926.6704 | 8683460.7548 | 10001817.6189
Total Direct Cost | $ |  | 21115251.7199 | 19183417.4986 | 20341107.7449 | 19403782.6742 | 22349740.6051
Total Direct Cost with Retrofit Factor | $ |  | 27449827.2359 | 24938442.7482 | 26443440.0684 | 25224917.4765 | 29054662.7866
General Facilities | $ |  | 2744982.7236 | 2493844.2748 | 2644344.0068 | 2522491.7477 | 2905466.2787
Engineering Fees | $ |  | 2744982.7236 | 2493844.2748 | 2644344.0068 | 2522491.7477 | 2905466.2787
Contingency | $ |  | 5489965.4472 | 4987688.5496 | 5288688.0137 | 5044983.4953 | 5810932.5573
Total Plant Cost (TPC) | $ |  | 38429758.1303 | 34913819.8475 | 37020816.0957 | 35314884.4671 | 40676527.9013
Total Plant Cost (TPC) w/ Prime Contractor's Markup | $ |  | 39582650.8742 | 35961234.443 | 38131440.5786 | 36374331.0011 | 41896823.7383
Total Cash Expended (TCE) | $ |  | 39006204.5022 | 35437527.1452 | 37576128.3371 | 35844607.7341 | 41286675.8198
Allow. for Funds During Constr. (AFDC) | $ |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Total Plant Investment (TPI) | $ |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Preproduction Costs | $ |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Inventory Capital | $ |  | 0 | 0 | 0 | 0 | 0
Total Capital Requirement (TCR) | $ |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| $/kW |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
O&M Data and Costs |  |  | Case1 | Case 2 | Case 3 | Case 4 | Case 5
Cost Basis (Year) |  |  | 1998 | 1998 | 1998 | 1998 | 1998
Power Required Excluding ID Fan(s) | kW |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
ID Fan Power for FF Delta P | kW |  | 878.4152 | 809.7816 | 822.8512 | 803.153 | 853.465
Total Power | kW |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Power Cost ** | $/yr |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Maintenance Costs | $/yr |  | 1478067.6204 | 1342839.2249 | 1423877.5421 | 1358264.7872 | 1564481.8424
** These costs assume inputs are in current dollars (no escalation included).

## Constants_CC
PRELIMINARY VERSION
|  |  | Coal 1, Wyoming PRB: 8,227 Btu, 0.37% S, 5.32% ash | Coal 2, Armstrong, PA: 13,100 Btu, 2.6% S, 9.1% ash | Coal 3, Jefferson, OH: 11,922 Btu, 3.43% S, 13% ash | Coal 4, Logan, WV: 12,058 Btu, 0.89% S, 16.6% ash | Coal 5, No. 6 Illinois: 10,100 Btu, 4% S, 16% ash | Coal 6, Rosebud, MT: 8,789 Btu, 0.56% S, 8.15% ash | Coal 7, Lignite, ND: 7,500 Btu, 0.94% S, 5.9% ash | Coal 8, "User Specified": Btu, 0% S, 0% ash
COAL ANALYSIS LIBRARY
| Index Number |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
1 | Coal Name |  | Wyoming PRB | Armstrong, PA | Jefferson, OH | Logan, WV | No. 6 Illinois | Rosebud, MT | Lignite, ND | "User Specified" |  |  |  | 1
2 | Coal Cost | $/MMBtu | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
3 | PROXIMATE ANALYSIS (ASTM, as rec'd) | [10 empty] | SCA |  | #VALUE!
4 | Moisture - Enter below in Ultimate Analysis | [10 empty] | Total Collection Plate Area |  | #VALUE!
5 | Volatile Matter | wt% | 31.39 | 36.2 | 37.2 | 35.4 | 33 | 36.4 | 42 | 0
6 | Fixed Carbon | wt% | 33.05 | 48.7 | 44.8 | 43 | 39 | 30.3 | 20.1 | 0
7 | Ash - Enter below in Ultimate Analysis | [12 empty] | Current | Previous | Raytheon
8 |  |  | 100 | 100 | 100 | 100 | 100 | 100.05 | 100 | 0 |  |  |  | SCA | SCA | SCA
9
10 | COAL ULTIMATE ANALYSIS (ASTM, as rec'd) | [9 empty] | Coal 1, Wyoming PRB: 8,227 Btu, 0.37% S, 5.32% ash |  | 1 |  | 477 | 619
11 | Moisture | wt% | 30.24 | 6 | 5 | 5 | 12 | 25.2 | 32 | 0 | Coal 2, Armstrong, PA: 13,100 Btu, 2.6% S, 9.1% ash |  | 2 |  | 483 | 301
12 | Carbon | wt% | 48.18 | 71.55 | 65.72 | 65.99 | 55.35 | 51.52 | 45.06 | 0 | Coal 3, Jefferson, OH: 11,922 Btu, 3.43% S, 13% ash |  | 3 |  | 523 | 348
13 | Hydrogen | wt% | 3.31 | 4.88 | 4.53 | 4.75 | 4 | 3.29 | 2.8 | 0 | Coal 4, Logan, WV: 12,058 Btu, 0.89% S, 16.6% ash |  | 4 |  | 544 | 624
14 | Nitrogen | wt% | 0.7 | 1.4 | 1.21 | 0.7 | 1.08 | 0.69 | 1.5 | 0 | Coal 5, No. 6 Illinois: 10,100 Btu, 4% S, 16% ash |  | 5 |  | 556 | 327
15 | Chlorine | wt% | 0.01 | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | Coal 6, Rosebud, MT: 8,789 Btu, 0.56% S, 8.15% ash |  | 6 |  | 508 | 530
16 | Sulfur | wt% | 0.37 | 2.6 | 3.43 | 0.89 | 4 | 0.56 | 0.94 | 0 | Coal 7, Lignite, ND: 7,500 Btu, 0.94% S, 5.9% ash |  | 7 |  | 494 | 411
17 | Ash | wt% | 5.32 | 9.1 | 13 | 16.6 | 16 | 8.15 | 5.9 | 0
18 | Oxygen | wt% | 11.87 | 4.47 | 7.01 | 5.97 | 7.47 | 10.49 | 11.7 | 0
19 | TOTAL | wt% | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 0
20
21 | Modified Mott Spooner HHV (Btu/lb) - calc | Btu/lb | 8227 | 13100 | 11922 | 12058 | 10100 | 8789 | 7500 | 0
22
23 | COAL ASH ANALYSIS (ASTM, as rec'd)
24 | SiO2 | wt% | 35.51 | 46.92 | 51.35 | 50.68 | 50.82 | 27 | 29.8 | 0
25 | Al2O3 | wt% | 17.11 | 21 | 30 | 29 | 19.06 | 19 | 10 | 0
26 | TiO2 | wt% | 1.26 | 2.4 | 1.8 | 1.7 | 0.83 | 1.08 | 0.4 | 0
27 | Fe2O3 | wt% | 6.07 | 20.2 | 9 | 9 | 20 | 9 | 9 | 0
28 | CaO | wt% | 26.67 | 3.25 | 4.5 | 5.5 | 3.43 | 18.5 | 21.4 | 0
29 | MgO | wt% | 5.3 | 2.65 | 2 | 1 | 3.07 | 2.4 | 10.5 | 0
30 | Na2O | wt% | 1.68 | 0.9 | 0.4 | 0.4 | 0.6 | 2.8 | 4.4 | 0
31 | K2O | wt% | 2.87 | 0.3 | 0.2 | 0.9 | 0.37 | 0.45 | 0.49 | 0
32 | P2O5 | wt% | 0.97 | 0 | 0.16 | 0.6 | 0.17 | 0.42 | 0 | 0
33 | SO3 | wt% | 1.56 | 1.38 | 0.59 | 1.22 | 1.22 | 18.85 | 14.01 | 0
34 | Other Unaccounted for | wt% | 1 | 1 | 0 | 0 | 0.43 | 0.5 | 0 | 0
35 | TOTAL | wt% | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 0
36
LIMESTONE ANALYSIS
| CaCO3 = | wt% | 1: 95.3
| CaO = | wt%
| Ca(OH)2 = | wt%
| CaSO4 = | wt% | 1: 0
| MgCO3 = | wt% | 1: 1.32
| MgO = | wt%
| Mg(OH)2 = | wt%
| SiO2 = | wt% | 1: 0.77
| Al2O3 = | wt% | 1: 0.25
| Fe2O3 = | wt% | 1: 0.09
| Na2O = | wt% | 1: 0.03
| K2O = | wt% | 1: 0.06
| TiO2 = | wt%
| P2O5 = | wt%
| SO3 = | wt%
| CO2 = | wt%
| H2O = | wt%
| Unknown = | wt% | 1: 2.18
| TOTAL = | wt% | 1: 100
LIME ANALYSIS
| CaCO3 = | wt% | 1: 0
| CaO = | wt% | 1: 90
| Ca(OH)2 = | wt%
| CaSO4 = | wt% | 1: 0
| MgCO3 = | wt% | 1: 0
| MgO = | wt% | 1: 5
| Mg(OH)2 = | wt%
| SiO2 = | wt% | 1: 1.26
| Al2O3 = | wt% | 1: 3
| Fe2O3 = | wt% | 1: 0.2
| Na2O = | wt% | 1: 0.1
| K2O = | wt% | 1: 0.02
| TiO2 = | wt%
| P2O5 = | wt%
| SO3 = | wt%
| CO2 = | wt%
| H2O = | wt%
| Unknown = | wt% | 1: 0.42
| TOTAL = | wt% | 1: 100
| Recycle Rate Lookup Table | % S | 1: lb recyle/lb lime
|  | 0 | 1: 30
|  | 0.4801 | 1: 28.5
|  | 0.5001 | 1: 23.5
|  | 0.5501 | 1: 19.5
|  | 0.6001 | 1: 16.5
|  | 0.6501 | 1: 14.5
|  | 0.7001 | 1: 12.5
|  | 0.7501 | 1: 11.25
|  | 0.8001 | 1: 10
|  | 0.8501 | 1: 9
|  | 0.9001 | 1: 8.25
|  | 0.9501 | 1: 7.5
|  | 1.0001 | 1: 5.5
|  | 1.2001 | 1: 4.25
|  | 1.4001 | 1: 3.3
|  | 1.6001 | 1: 2.75
|  | 1.8001 | 1: 2.25
|  | 2.0001 | 1: 1.85
|  | 2.2001 | 1: 1.6
|  | 2.4001 | 1: 1.4
|  | 2.6001 | 1: 1.2
2.8001 | bar: 1
|  | 3.0001 | 1: 0.66
|  | 3.5001 | 1: 0.49
|  | 4.0001 | 1: 0.34
|  | 4.5001 | 1: 0.3
MOLECULAR WEIGHTS
|  | Variable | 1: Molecular
| Description | Name | 1: Weight
| Air | Air_MolWt | 1: 28.8555
| H2O | H2O_MolWt | 1: 18.0153
| C | C_MolWt | 1: 12.0112
| H2 | H2_MolWt | 1: 2.0159
| N2 | N2_MolWt | 1: 28.02
| Cl2 | Cl2_MolWt | 1: 70.906
| S | S_MolWt | 1: 32.064
| Ash | Ash_MolWt | bar: 1
| O2 | O2_MolWt | 1: 31.9988
| Ca | Ca_MolWt | 1: 40.08
| Mg | Mg_MolWt | 1: 24.312
| CO2 | CO2_MolWt | 1: 44.01
| NO2 | NO2_MolWt | 1: 46.0088
| NO | NO_MolWt | 1: 30.0094
| HCl | HCl_MolWt | 1: 36.461
| SO2 | SO2_MolWt | 1: 64.0628
| SO3 | SO3_MolWt | 1: 80.0622
| CaCO3 | CaCO3_MolWt | 1: 100.0894
| CaSO4 | CaSO4_MolWt | 1: 136.1416
| CaO | CaO_MolWt | 1: 56.0794
| Ca(OH)2 | Ca_OH_2_MolWt | 1: 74.0947
| CaSO3*½H2O | CaSO3halfH2O_MolWt | 1: 129.1499
| CaSO4*2 H2O (gypsum) | CaSO4_2H2O_MolWt | 1: 172.1723
| Na | Na_MolWt | 1: 22.99
| Na2CO3 | Na2CO3_MolWt | 1: 105.9894
| H2SO4 | H2SO4_MolWt | 1: 98.0775
| CH4 | CH4_MolWt | 1: 16.043
| CaCl2 | CaCl2_MolWt | 1: 110.99
WATER SATURATION PRESSURES
|  | Pressure | 1: Pressure
| Temperature, °F | " HgA | 1: psia
| 120 | 3.4456 | 1: 1.6924
| 121 | 3.5425 | 1: 1.74
| 122 | 3.6419 | 1: 1.7888
| 123 | 3.7435 | 1: 1.8387
| 124 | 3.8473 | 1: 1.8897
| 125 | 3.9538 | 1: 1.942
| 126 | 4.0627 | 1: 1.9955
| 127 | 4.1743 | 1: 2.0503
| 128 | 4.2885 | 1: 2.1064
| 129 | 4.4053 | 1: 2.1638
| 130 | 4.5259 | 1: 2.223
| 131 | 4.648 | 1: 2.283
| 132 | 4.7732 | 1: 2.3445
| 133 | 4.9013 | 1: 2.4074
| 134 | 5.0322 | 1: 2.4717
| 135 | 5.1662 | 1: 2.5375
| 136 | 5.303 | 1: 2.6047
| 137 | 5.4431 | 1: 2.6735
| 138 | 5.5862 | 1: 2.7438
| 139 | 5.7326 | 1: 2.8157
| 140 | 5.8822 | 1: 2.8892
| 141 | 6.0351 | 1: 2.9643
| 142 | 6.1915 | 1: 3.0411
| 143 | 6.3511 | 1: 3.1195
| 144 | 6.5144 | 1: 3.1997
| 145 | 6.6811 | 1: 3.2816
SATURATION (ASME)
|  | Saturation | 1: Water; 2: Steam
|  | Temperature | 1: Enthalpy; 2: Enthalpy
| Pressure (psia) | (°F) | 1: (Btu/lb); 3: Index
| 300 | 417.35 | 1: 393.99; 2: 1202.9; 3: 0
| 400 | 444.6 | 1: 424.18; 2: 1204.6; 3: 1
| 500 | 467.01 | 1: 449.52; 2: 1204.7; 3: 2
| 600 | 486.2 | 1: 471.7; 2: 1203.7; 3: 3
| 1500 | 596.2 | 1: 611.68; 2: 1170.1; 3: 4
| 1600 | 604.87 | 1: 624.2; 2: 1164.5; 3: 5
| 1700 | 613.13 | 1: 636.45; 2: 1158.6; 3: 6
| 1800 | 621.02 | 1: 648.49; 2: 1152.3; 3: 7
| 1900 | 628.56 | 1: 660.36; 2: 1145.6; 3: 8
| 2400 | 662.11 | 1: 718.95; 2: 1103.7; 3: 9
| 2500 | 668.11 | 1: 731.71; 2: 1093.3; 3: 10
| 2600 | 673.91 | 1: 744.5; 2: 1082; 3: 11
| 2700 | 679.53 | 1: 757.3; 2: 1069.7; 3: 12
| 2800 | 684.96 | 1: 770.7; 2: 1055.8; 3: 13
| 2900 | 690.22 | 1: 785.1; 2: 1039.8; 3: 14
| 3000 | 695.33 | 1: 801.84; 2: 1020.3; 3: 15
| 3100 | 700.28 | 1: 824; 2: 993.3; 3: 16
| 3200 | 705.08 | 1: 875.5; 2: 931.6; 3: 17
| 3208.2 | 705.47 | 1: 906; 2: 906; 3: 18
| 3300 | 730 | 1: 1104.1; 2: 1104.1; 3: 19
| 3400 | 730 | 1: 1079.3; 2: 1079.3; 3: 20
| 3500 | 730 | 1: 1048.6; 2: 1048.6; 3: 21
| 4000 | 770 | 1: 1099.9; 2: 1099.9; 3: 22
Heat Capacity Results; Used in Efficiency Calculations
|  | Case 1 | 1: Case 2; 2: Case 3; 3: Case 4; 4: Case 5
| O2 - Based on °K | 7.2514 | 1: 7.2514; 2: 7.2514; 3: 7.2514; 4: 7.2514
| CO2 - Based on °K | 9.6671 | 1: 9.6671; 2: 9.6671; 3: 9.6671; 4: 9.6671
| N2 - Based on °K | 7.036 | 1: 7.036; 2: 7.036; 3: 7.036; 4: 7.036
| H2O - Based on °C | 8.1566 | 1: 8.1566; 2: 8.1566; 3: 8.1566; 4: 8.1566
| NO - Based on °C | 7.2156 | 1: 7.2156; 2: 7.2156; 3: 7.2156; 4: 7.2156
| SO2 - Based on °C | 10.0536 | 1: 10.0536; 2: 10.0536; 3: 10.0536; 4: 10.0536
| HCl - Based on °C | 6.9536 | 1: 6.9536; 2: 6.9536; 3: 6.9536; 4: 6.9536
| STACK OUTLET TEMP, °C | 148.8889 | 1: 148.8889; 2: 148.8889; 3: 148.8889; 4: 148.8889
| STACK OUTLET TEMP, °K | 421.8889 | 1: 421.8889; 2: 421.8889; 3: 421.8889; 4: 421.8889
| REFERENCE TEMP, °C | 26.6667 | 1: 26.6667; 2: 26.6667; 3: 26.6667; 4: 26.6667
| REFERENCE TEMP, °K | 299.6667 | 1: 299.6667; 2: 299.6667; 3: 299.6667; 4: 299.6667
ESP Section Lookup Table
| Efficiency | No. of Sections
| 0 | 2
| 0.965 | 3
| 0.99 | 4
| 0.998 | 5
| 0.999 | 6
ESP SCA Ratio Lookup Table
| No. of Sections | SCA Ratio (Avg.)
| 2 | 2.6
| 3 | 2.65
| 4 | 2.89
| 5 | 2.96
| 6 | 3.09
Lookup Table for Acid Resistivity Calculations
Atom_v
| Acid_v | 1 | 1: 2; 2: 3
| 1 | -4.74 | 1: -4.85; 2: -4.85
| 2 | -28.39 | 1: -28.39; 2: -28.39
| 3 | -8.67 | 1: -9.71; 2: -10.59
CONSTANTS
Variable
| Description | Name | 1: Value
| Degree Kelvin Conversion | degK | 1: 460
| " H2O / " Hg Conversion | inH2O_inHg | 1: 13.615
| Standard Atmospheric Pressure, " Hg | SAPress_inHg | 1: 29.92
| Standard Atmospheric Temperature, deg. F | SATemp_degF | 1: 70
| cubic feet per mole @ 60 deg F | cubft_60 | 1: 379.63
| cubic feet per mole @ 69 deg F | cubft_69 | 1: 386
| cubic feet per mole @ 70 deg F | cubft_70 | 1: 386.704
| kW per Horsepower | kW_Hp | 1: 0.746
Chemical Engineering Cost Index
| Year | Index
| 1979 | 238.7
| 1980 | 261.2
| 1981 | 297
| 1982 | 314
| 1983 | 317
| 1984 | 322.7
| 1985 | 325.3
| 1986 | 318.4
| 1987 | 323.8
| 1988 | 342.5
| 1989 | 355.4
| 1990 | 357.6
| 1991 | 361.3
| 1992 | 358.2
| 1993 | 359.2
| 1994 | 368.1
| 1995 | 381.1
| 1996 | 381.7
| 1997 | 386.5
| FUEL AND COMBUSTION CALCULATIONS |  |  | Case1 | Case 2 | Case 3 | Case 4 | Case 5
FUEL ANALYSIS FOR SPECIFIED COALS
PROXIMATE ANALYSIS (wt. %)
| Moisture | wt% |  | 30.24 | 6 | 5 | 5 | 12
| Volatile Matter | wt% |  | 31.39 | 36.2 | 37.2 | 35.4 | 33
| Fixed Carbon | wt% |  | 33.05 | 48.7 | 44.8 | 43 | 39
| Ash | wt% |  | 5.32 | 9.1 | 13 | 16.6 | 16
| TOTAL |  |  | 100 | 100 | 100 | 100 | 100
COAL ULTIMATE ANALYSIS (wt. %)
| Moisture | wt% |  | 30.24 | 6 | 5 | 5 | 12
| Carbon | wt% |  | 48.18 | 71.55 | 65.72 | 65.99 | 55.35
| Hydrogen | wt% |  | 3.31 | 4.88 | 4.53 | 4.75 | 4
| Nitrogen | wt% |  | 0.7 | 1.4 | 1.21 | 0.7 | 1.08
| Chlorine | wt% |  | 0.01 | 0 | 0.1 | 0.1 | 0.1
| Sulfur | wt% |  | 0.37 | 2.6 | 3.43 | 0.89 | 4
| Ash | wt% |  | 5.32 | 9.1 | 13 | 16.6 | 16
| Oxygen | wt% |  | 11.87 | 4.47 | 7.01 | 5.97 | 7.47
| TOTAL |  |  | 100 | 100 | 100 | 100 | 100
HIGHER HEATING VALUE (HHV)
| Modified Mott Spooner - calc | Btu/lb |  | 8227 | 13100 | 11922 | 12058 | 10100
| COAL COST | $/MMBtu |  | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
COAL ASH ANALYSIS (ASTM, as rec'd)
| SiO2 | wt% |  | 35.51 | 46.92 | 51.35 | 50.68 | 50.82
| Al2O3 | wt% |  | 17.11 | 21 | 30 | 29 | 19.06
| TiO2 | wt% |  | 1.26 | 2.4 | 1.8 | 1.7 | 0.83
| Fe2O3 | wt% |  | 6.07 | 20.2 | 9 | 9 | 20
| CaO | wt% |  | 26.67 | 3.25 | 4.5 | 5.5 | 3.43
| MgO | wt% |  | 5.3 | 2.65 | 2 | 1 | 3.07
| Na2O | wt% |  | 1.68 | 0.9 | 0.4 | 0.4 | 0.6
| K2O | wt% |  | 2.87 | 0.3 | 0.2 | 0.9 | 0.37
| P2O5 | wt% |  | 0.97 | 0 | 0.16 | 0.6 | 0.17
| SO3 | wt% |  | 1.56 | 1.38 | 0.59 | 1.22 | 1.22
| Other Unaccounted for | wt% |  | 1 | 1 | 0 | 0 | 0.43
| TOTAL | wt% |  | 100 | 100 | 100 | 100 | 100
PROXIMATE ANALYSIS (lbs/MMBtu)
| Moisture | lbs/MMBtu |  | 36.757 | 4.5802 | 4.1939 | 4.1466 | 11.8812
| Volatile Matter | lbs/MMBtu |  | 38.1549 | 27.6336 | 31.2028 | 29.3581 | 32.6733
| Fixed Carbon | lbs/MMBtu |  | 40.1726 | 37.1756 | 37.5776 | 35.661 | 38.6139
| Ash | lbs/MMBtu |  | 6.4665 | 6.9466 | 10.9042 | 13.7668 | 15.8416
| TOTAL | lbs/MMBtu |  | 121.551 | 76.3359 | 83.8785 | 82.9325 | 99.0099
COAL ULTIMATE ANALYSIS (lbs/MMBtu)
| Moisture | lbs/MMBtu |  | 36.757 | 4.5802 | 4.1939 | 4.1466 | 11.8812
| Carbon | lbs/MMBtu |  | 58.5633 | 54.6183 | 55.125 | 54.7272 | 54.802
| Hydrogen | lbs/MMBtu |  | 4.0233 | 3.7252 | 3.7997 | 3.9393 | 3.9604
| Nitrogen | lbs/MMBtu |  | 0.85086 | 1.0687 | 1.0149 | 0.58053 | 1.0693
| Chlorine | lbs/MMBtu |  | 0.012155 | 0 | 0.083879 | 0.082932 | 0.09901
| Sulfur | lbs/MMBtu |  | 0.44974 | 1.9847 | 2.877 | 0.7381 | 3.9604
| Ash | lbs/MMBtu |  | 6.4665 | 6.9466 | 10.9042 | 13.7668 | 15.8416
| Oxygen | lbs/MMBtu |  | 14.4281 | 3.4122 | 5.8799 | 4.9511 | 7.396
| TOTAL | lbs/MMBtu |  | 121.551 | 76.3359 | 83.8785 | 82.9325 | 99.0099
COAL ULTIMATE ANALYSIS (lbmoles/MMBtu)
| Moisture | lbmoles/MMBtu |  | 2.0403 | 0.25424 | 0.2328 | 0.23017 | 0.6595
| Carbon | lbmoles/MMBtu |  | 4.8757 | 4.5473 | 4.5895 | 4.5564 | 4.5626
| Hydrogen | lbmoles/MMBtu |  | 1.9958 | 1.8479 | 1.8848 | 1.9541 | 1.9645
| Nitrogen | lbmoles/MMBtu |  | 0.030366 | 0.038141 | 0.036222 | 0.020718 | 0.038162
| Chlorine | lbmoles/MMBtu |  | 0.00017143 | 0 | 0.001183 | 0.0011696 | 0.0013964
| Sulfur | lbmoles/MMBtu |  | 0.014026 | 0.061899 | 0.089728 | 0.02302 | 0.12352
| Ash | lbmoles/MMBtu |  | 6.4665 | 6.9466 | 10.9042 | 13.7668 | 15.8416
| Oxygen | lbmoles/MMBtu |  | 0.4509 | 0.10664 | 0.18375 | 0.15473 | 0.23113
Flue Gas, Downstream Of Economizer
Flue Gas (lb-moles/MMBtu)
| CO2 | lbmoles/MMBtu |  | 4.8514 | 4.5246 | 4.5665 | 4.5336 | 4.5398
| NOx | lbmoles/MMBtu |  | 0.0090474 | 0.014394 | 0.014204 | 0.011891 | 0.012885
| HCl | lbmoles/MMBtu |  | 0.00034285 | 0 | 0.0023659 | 0.0023392 | 0.0027927
| SO2 | lbmoles/MMBtu |  | 0.014026 | 0.061899 | 0.089728 | 0.02302 | 0.12352
| Total O2 Req'd - * | lbmoles/MMBtu |  | 6.5057 | 6.5018 | 6.515 | 6.469 | 6.5128
| N2 | lbmoles/MMBtu |  | 24.4997 | 24.49 | 24.5377 | 24.3504 | 24.5321
| O2 | lbmoles/MMBtu |  | 1.0843 | 1.0836 | 1.0858 | 1.0782 | 1.0855
| H20 | lbmoles/MMBtu |  | 4.6811 | 2.7468 | 2.7636 | 2.8257 | 3.2698
| Total Dry | lbmoles/MMBtu |  | 30.4587 | 30.1745 | 30.2964 | 29.9993 | 30.2966
| Total Wet | lbmoles/MMBtu |  | 35.1399 | 32.9213 | 33.06 | 32.825 | 33.5664
Wet Flue Gas PPMV & % Vol
| % O2 | % Vol |  | 3.0856 | 3.2916 | 3.2844 | 3.2846 | 3.2338
| % CO2 | % Vol |  | 13.8059 | 13.7436 | 13.8129 | 13.8114 | 13.5248
| % N2 | % Vol |  | 69.7204 | 74.3896 | 74.2218 | 74.1823 | 73.0854
| NOx | ppmv |  | 257.4685 | 437.2211 | 429.6427 | 362.2432 | 383.8726
| HCL | ppmv |  | 9.7568 | 0 | 71.5641 | 71.2634 | 83.1996
| SO2 | ppmv |  | 399.1557 | 1880.215 | 2714.0919 | 701.2811 | 3679.733
| % H2O | % Vol |  | 13.3215 | 8.3435 | 8.3594 | 8.6083 | 9.7413
Dry Flue Gas PPMV & % Vol
| % O2 | % Vol |  | 3.5598 | 3.5912 | 3.584 | 3.5939 | 3.5828
| % CO2 | % Vol |  | 15.9277 | 14.9947 | 15.0729 | 15.1123 | 14.9845
| % N2 | % Vol |  | 80.4356 | 81.1613 | 80.9923 | 81.1696 | 80.9733
| NOx | ppmv |  | 297.0383 | 477.0213 | 468.8343 | 396.3633 | 425.3028
| HCL | ppmv |  | 11.2563 | 0 | 78.0921 | 77.9758 | 92.179
| SO2 | ppmv |  | 460.5012 | 2051.3708 | 2961.6688 | 767.3354 | 4076.8747
| % H2O | % Vol |  | 0 | 0 | 0 | 0 | 0
Flue Gas, Air & Ash Downstream Of Economizer
Flue Gas (lbs/MMBtu)
| O2 | lbs/MMBtu |  | 34.6958 | 34.6749 | 34.7451 | 34.4998 | 34.7335
| CO2 | lbs/MMBtu |  | 213.5085 | 199.1261 | 200.9733 | 199.5229 | 199.7957
| N2 | lbs/MMBtu |  | 686.4806 | 686.2103 | 687.5471 | 682.297 | 687.3906
| NOx | lbs/MMBtu |  | 0.27151 | 0.43195 | 0.42625 | 0.35683 | 0.38668
| HCl | lbs/MMBtu |  | 0.012501 | 0 | 0.086263 | 0.08529 | 0.10182
| SO2 | lbs/MMBtu |  | 0.89856 | 3.9654 | 5.7482 | 1.4747 | 7.9127
| H2O | lbs/MMBtu |  | 84.3325 | 49.4842 | 49.7873 | 50.9054 | 58.9068
| Gas Dry | lbs/MMBtu |  | 935.8675 | 924.4087 | 929.5262 | 918.2365 | 930.321
| Gas Wet | lbs/MMBtu |  | 1020.1999 | 973.8929 | 979.3135 | 969.1418 | 989.2278
| % H2O | wt% |  | 8.2663 | 5.0811 | 5.0839 | 5.2526 | 5.9548
| Theoretical Wet Air | lbs/MMBtu |  | 754.627 | 754.1723 | 755.6996 | 750.3646 | 755.4472
| Actual Total Wet Air | lbs/MMBtu |  | 905.5524 | 905.0068 | 906.8395 | 900.4375 | 906.5366
| Mol Wt Wet, Lb/Lb-Mol | lbs/lb-mole |  | 29.0325 | 29.5825 | 29.6223 | 29.5245 | 29.4708
| Total Ash | lbs/MMBtu |  | 6.7593 | 7.2197 | 11.1798 | 14.0404 | 16.1156
| Fly Ash | lbs/MMBtu |  | 5.4074 | 5.7758 | 8.9438 | 11.2323 | 12.8925
| Bottom Ash | lbs/MMBtu |  | 1.3519 | 1.4439 | 2.236 | 2.8081 | 3.2231
| NOx - Flue Gas | lbs/MMBtu |  | 0.27151 | 0.43195 | 0.42625 | 0.35683 | 0.38668
| Carbon Loss | lbmoles/MMBtu |  | 0.024379 | 0.022737 | 0.022947 | 0.022782 | 0.022813
* - Theoretical + Excess O2 Required for Combustion, Not O2 in Flue Gas
Gases, Downstream Of Air Heater
Flue Gas (lb-moles/MMBtu)
| CO2 | lbmoles/MMBtu |  | 4.8514 | 4.5246 | 4.5665 | 4.5336 | 4.5398
| NOx | lbmoles/MMBtu |  | 0.0090474 | 0.014394 | 0.014204 | 0.011891 | 0.012885
| HCl | lbmoles/MMBtu |  | 0.00034285 | 0 | 0.0023659 | 0.0023392 | 0.0027927
| SO2 | lbmoles/MMBtu |  | 0.014026 | 0.061899 | 0.089728 | 0.02302 | 0.12352
| N2 | lbmoles/MMBtu |  | 27.763 | 27.5473 | 27.6079 | 27.3987 | 27.6493
| O2 | lbmoles/MMBtu |  | 1.9517 | 1.8963 | 1.9019 | 1.8885 | 1.9141
| H2O | lbmoles/MMBtu |  | 4.7672 | 2.8274 | 2.8445 | 2.906 | 3.352
| Total Dry Flue Gas | lbmoles/MMBtu |  | 34.5895 | 34.0445 | 34.1827 | 33.858 | 34.2424
| Total Wet Flue Gas | lbmoles/MMBtu |  | 39.3567 | 36.8718 | 37.0272 | 36.764 | 37.5944
| Dry Air Addition | lbmoles/MMBtu |  | 4.1308 | 3.87 | 3.8863 | 3.8587 | 3.9458
| Wet Air Addition | lbmoles/MMBtu |  | 4.2168 | 3.9506 | 3.9672 | 3.939 | 4.028
Wet Flue Gas PPMV & % Vol
| % O2 | % Vol |  | 4.9591 | 5.143 | 5.1366 | 5.1368 | 5.0914
| % CO2 | % Vol |  | 12.3267 | 12.2711 | 12.3329 | 12.3316 | 12.0757
| % N2 | % Vol |  | 70.542 | 74.7109 | 74.5611 | 74.5258 | 73.5465
| PPMV NOx | ppmv |  | 229.8826 | 390.376 | 383.6096 | 323.4314 | 342.7434
| PPMV HCL | ppmv |  | 8.7114 | 0 | 63.8965 | 63.6281 | 74.2853
| PPMV SO2 | ppmv |  | 356.389 | 1678.7634 | 2423.2963 | 626.1438 | 3285.4759
| % H2O | % Vol |  | 12.1127 | 7.6681 | 7.6823 | 7.9045 | 8.9162
| TOTAL |  |  | 100 | 100 | 100 | 100 | 100
Dry Flue Gas PPMV & % Vol
| % O2 | % Vol |  | 5.6426 | 5.5701 | 5.5641 | 5.5776 | 5.5898
| % CO2 | % Vol |  | 14.0255 | 13.2902 | 13.3592 | 13.39 | 13.2578
| % N2 | % Vol |  | 80.2642 | 80.9156 | 80.7658 | 80.9224 | 80.7459
| NOx | ppmv |  | 261.5652 | 422.7964 | 415.5319 | 351.1914 | 376.2944
| HCL | ppmv |  | 9.912 | 0 | 69.2137 | 69.0892 | 81.5571
| SO2 | ppmv |  | 405.5069 | 1818.1832 | 2624.9522 | 679.8854 | 3607.0898
| % H2O | % Vol |  | 0 | 0 | 0 | 0 | 0
| TOTAL |  |  | 100 | 100 | 100 | 100 | 100
Flue Gas & Air Downstream Of Air Heater
Flue Gas (lbs/MMBtu)
| O2 | lbs/MMBtu |  | 62.4536 | 60.6801 | 60.8599 | 60.429 | 61.2483
| CO2 | lbs/MMBtu |  | 213.5085 | 199.1261 | 200.9733 | 199.5229 | 199.7957
| N2 | lbs/MMBtu |  | 777.9185 | 771.8753 | 773.5729 | 767.7114 | 774.7341
| NOx | lbs/MMBtu |  | 0.27151 | 0.43195 | 0.42625 | 0.35683 | 0.38668
| HCl | lbs/MMBtu |  | 0.012501 | 0 | 0.086263 | 0.08529 | 0.10182
| SO2 | lbs/MMBtu |  | 0.89856 | 3.9654 | 5.7482 | 1.4747 | 7.9127
| H2O | lbs/MMBtu |  | 85.882 | 50.9359 | 51.2452 | 52.3528 | 60.3869
| Gas Dry | lbs/MMBtu |  | 1055.0632 | 1036.0789 | 1041.6669 | 1029.5801 | 1044.1794
| Gas Wet | lbs/MMBtu |  | 1140.9452 | 1087.0148 | 1092.912 | 1081.9329 | 1104.5663
| Wt % H2O | wt% |  | 7.5273 | 4.6859 | 4.6889 | 4.8388 | 5.467
| Total Wet Air | lbs/MMBtu |  | 1026.2975 | 1018.1285 | 1020.4378 | 1013.2284 | 1021.875
| Mol Wt Wet, Lb/Lb-Mol | lbs/lb-mole |  | 28.9899 | 29.4809 | 29.5165 | 29.4291 | 29.3812
Boiler Losses & Efficiencies
| Dry Gas | % |  | 5.6452 | 5.5449 | 5.5705 | 5.5139 | 5.5805
| Moisture | % |  | 8.272 | 4.3701 | 4.4017 | 4.5352 | 5.4233
| Carbon | % |  | 0.41287 | 0.38506 | 0.38863 | 0.38583 | 0.38635
| Radiation | % |  | 0.17298 | 0.17298 | 0.17298 | 0.17298 | 0.17298
| Manufacturers Margin | % |  | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
| Ash Losses | % |  | 0 | 0 | 0 | 0 | 0
| Total Losses | % |  | 16.0031 | 11.973 | 12.0339 | 12.1078 | 13.0632
| Boiler Efficiency | % |  | 83.9969 | 88.027 | 87.9661 | 87.8922 | 86.9368
Coal Flow Rates
| Btu Input Rate to Boiler | MMBtu/hr |  | 5250 | 5250 | 5250 | 5250 | 5250
| Coal Input Rate to Boiler | tons/hr |  | 319.0714 | 200.3817 | 220.1812 | 217.6978 | 259.901
| Coal Input Rate to Boiler | lbs/MMBtu |  | 121.551 | 76.3359 | 83.8785 | 82.9325 | 99.0099
Economizer Outlet
| Flue Gas | SCFM/MMBtu |  | 13340.1509 | 12497.909 | 12550.5651 | 12461.3596 | 12742.8079
| Flue Gas | SCFM |  | 1167263.2005 | 1093567.0396 | 1098174.4492 | 1090368.9663 | 1114995.6916
| Wet Flue Gas | lb/hr |  | 5356049.5429 | 5112937.7532 | 5141395.987 | 5087994.6911 | 5193445.9239
| Wet Air | SCFM |  | 1042446.0237 | 1041817.8697 | 1043927.6259 | 1036557.8105 | 1043578.9899
| Wet Air | lb/hr |  | 4754150.2888 | 4751285.5473 | 4760907.2429 | 4727296.668 | 4759317.2629
| Total Air | % |  | 120% | 120% | 120% | 120% | 120%
| Excess Air | % |  | 20% | 20% | 20% | 20% | 20%
Air Heater Outlet
| Flue Gas | SCFM/MMBtu |  | 14940.969 | 13997.6581 | 14056.6329 | 13956.7228 | 14271.9449
| Flue Gas | SCFM |  | 1307334.7846 | 1224795.0844 | 1229955.3831 | 1221213.2423 | 1248795.1746
| Wet Flue Gas | lb/hr |  | 5989962.1123 | 5706827.7101 | 5737788.1173 | 5680147.8513 | 5798973.2664
| Wet Air | SCFM |  | 1181444.2698 | 1172040.3427 | 1174698.7514 | 1166399.4554 | 1176353.1967
| Wet Air | lb/hr |  | 5388061.8173 | 5345174.5291 | 5357298.3939 | 5319448.8559 | 5364843.611
| Wet Air Leakage | SCFM |  | 138998.2462 | 130222.473 | 130771.1255 | 129841.6449 | 132774.2069
| Wet Air Leakage | lb/hr |  | 633911.5285 | 593888.9817 | 596391.151 | 592152.1879 | 605526.3482
| Equivalent Total Air | % |  | 136% | 135% | 135% | 135% | 135.3%
| Equivalent Excess Air | % |  | 36% | 35% | 35.03% | 35.03% | 35.27%
| Flue Gas Temperature | °F |  | 300 | 300 | 300 | 300 | 300
| Pressure | in. H2O |  | -12 | -12 | -12 | -12 | -12
| Flue Gas | ACFM |  | 2004611.2383 | 1878048.3925 | 1885960.9738 | 1872556.1491 | 1914849.1044
Ash Parameters
| Fly Ash | tons/hr |  | 14.1945 | 15.1614 | 23.4776 | 29.4849 | 33.8428
| Bottom Ash | tons/hr |  | 3.5487 | 3.7902 | 5.8695 | 7.3713 | 8.4606
| Total Ash | tons/hr |  | 17.7432 | 18.9516 | 29.3471 | 36.8561 | 42.3034
| ECONOMIC FACTORS |  |  | CASE 1 | CASE 2 | CASE 3 | CASE 4 | CASE 5
| Construction Period | Years |  | 3 | 3 | 3 | 3 | 3
Current Dollars
| P/A Factor |  |  | 10.0942 | 10.0942 | 10.0942 | 10.0942 | 10.0942
| A/P (Annuity) Factor |  |  | 0.099067 | 0.099067 | 0.099067 | 0.099067 | 0.099067
P/AE (Present Worth) Factors
| Consumables (O&M) |  |  | 13.7363 | 13.7363 | 13.7363 | 13.7363 | 13.7363
| Capital Costs |  |  | 13.7363 | 13.7363 | 13.7363 | 13.7363 | 13.7363
Levelization Factors
| Consumables (O&M) |  |  | 1.3608 | 1.3608 | 1.3608 | 1.3608 | 1.3608
| Capital Costs |  |  | 1.3608 | 1.3608 | 1.3608 | 1.3608 | 1.3608
Constant Dollars
| P/A Factor |  |  | 13.7363 | 13.7363 | 13.7363 | 13.7363 | 13.7363
| A/P (Annuity) Factor |  |  | 0.0728 | 0.0728 | 0.0728 | 0.0728 | 0.0728
P/AE (Present Worth) Factors
| Consumables (O&M) |  |  | 13.7363 | 13.7363 | 13.7363 | 13.7363 | 13.7363
| Capital Costs |  |  | 13.7363 | 13.7363 | 13.7363 | 13.7363 | 13.7363
Levelization Factors
Consumables (O&M) | bar: 2 to 6
Capital Costs | bar: 2 to 6
| Z = (1 + i) / (1 + e) |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
AFDC / TCE FACTORS FOR CASE 1
|  |  | AFDC | TCE
| Unit Size, MW | Years | 1: Factor; 2: Factor
| 0 | 1 | 1: #VALUE!; 2: 1
| 160 | 2 | 1: #VALUE!; 2: 0.98544
| 400 | 3 | 1: #VALUE!; 2: 0.97116
| 725 | 4 | 1: #VALUE!; 2: 0.95715
| 1300 | 5 | 1: #VALUE!; 2: 0.94342
| 2000 | 6 | 1: #VALUE!; 2: 0.92995
AFDC / TCE FACTORS FOR CASE 2
|  |  | AFDC | TCE
| Unit Size, MW | Years | 1: Factor; 2: Factor
| 0 | 1 | 1: #VALUE!; 2: 1
| 160 | 2 | 1: #VALUE!; 2: 0.98544
| 400 | 3 | 1: #VALUE!; 2: 0.97116
| 725 | 4 | 1: #VALUE!; 2: 0.95715
| 1300 | 5 | 1: #VALUE!; 2: 0.94342
| 2000 | 6 | 1: #VALUE!; 2: 0.92995
AFDC / TCE FACTORS FOR CASE 3
|  |  | AFDC | TCE
| Unit Size, MW | Years | 1: Factor; 2: Factor
| 0 | 1 | 1: #VALUE!; 2: 1
| 160 | 2 | 1: #VALUE!; 2: 0.98544
| 400 | 3 | 1: #VALUE!; 2: 0.97116
| 725 | 4 | 1: #VALUE!; 2: 0.95715
| 1300 | 5 | 1: #VALUE!; 2: 0.94342
| 2000 | 6 | 1: #VALUE!; 2: 0.92995
AFDC / TCE FACTORS FOR CASE 4
|  |  | AFDC | TCE
| Unit Size, MW | Years | 1: Factor; 2: Factor
| 0 | 1 | 1: #VALUE!; 2: 1
| 160 | 2 | 1: #VALUE!; 2: 0.98544
| 400 | 3 | 1: #VALUE!; 2: 0.97116
| 725 | 4 | 1: #VALUE!; 2: 0.95715
| 1300 | 5 | 1: #VALUE!; 2: 0.94342
| 2000 | 6 | 1: #VALUE!; 2: 0.92995
AFDC / TCE FACTORS FOR CASE 5
|  |  | AFDC | TCE
| Unit Size, MW | Years | 1: Factor; 2: Factor
| 0 | 1 | 1: #VALUE!; 2: 1
| 160 | 2 | 1: #VALUE!; 2: 0.98544
| 400 | 3 | 1: #VALUE!; 2: 0.97116
| 725 | 4 | 1: #VALUE!; 2: 0.95715
| 1300 | 5 | 1: #VALUE!; 2: 0.94342
| 2000 | 6 | 1: #VALUE!; 2: 0.92995
Source Key for Nox Defaults
a | Table 2-1, "Cost Estimates for Selected Applications of NOX control Technologies on Stationary Combustion Boilers: Draft Report" March 1996. EPA, Acid Rain Division, Cost year 1995
b | Table 1-5, "Cost Estimates for Selected Applications of NOX control Technologies on Stationary Combustion Boilers: Draft Report" March 1996. EPA, Acid Rain Division
c | Section 3.0, "Cost Estimates for Selected Applications of NOX control Technologies on Stationary Combustion Boilers: Draft Report" March 1996. EPA, Acid Rain Division, Cost year 1995
d | Pg. B4-21-25 "Investigation of Performance and cost of NOX controls as Applied to Group 2 Boilers: Revised Draft Report", EPA, Acid Rain Division, August 1996
e | Table B2-1 "Investigation of Performance and cost of NOX controls as Applied to Group 2 Boilers: Revised Draft Report", EPA, Acid Rain Division, August 1996
f | Pg. B4-17-19 "Investigation of Performance and cost of NOX controls as Applied to Group 2 Boilers: Revised Draft Report", EPA, Acid Rain Division, August 1996
g | IAPCS default for cost year 06/96
h | "Development of the Integrated Environmental Control Model:Performance Models of Selective Reduction(SCR) Nox Control Systems; Quarterly Progress Report" Center for Energy and Environmental Studies, Carnegie Mellon University, July 1994
i | IAPCS equations