## Core
USEPA GHD Asset Management Training Workshops 2006
This workbook is copyrighted by GHD. It is intended for the use of and licensed for use by utility staff and public officials. Feel free to modify it to fit your organization, but please assure proper citation.
[5 empty] | What is the State of My Assets? | [12 empty] | Required LOS? |  | Which Are Most "Critical"? |  |  |  | What Strategies? | [5 empty] | What Funding Strategy?
Asset Register and Hierarchy |  |  |  |  | Installed Date | Asset Class | Original Cost | Estimated Effective Life | Condition Rating | Effect Life Adjust Factor | Calc Residual Physical Life | Judgment Resid Life | % Asset Consumed (Physical) | Annual Dep | Accum Dep | Current Performance | Current Reliability | Current LOS? | Minimum Condition | Backup Reduction (Redundancy) | Probability of Failure | Consequence of Failure | BRE Rating | Renewal Strategy | Maint Strategy | Future Maintenance % Change | Cost of Renewal Option | Recommended Renewal Date | Present Value of Renewal Cost | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025
Current Year | 2006 |  |  |  | Year |  | $ | Years | 1 to 10 |  |  |  | % | $ | $ |  |  |  |  | % | Rating | 1 to 10 |  |  |  | % | $
Level 1 | Level 2 | Level 3 | Level 4 | Level 5 | Act or Est | Tab A | Act or Est | Calculated | Tab A | Tab B | Calculated |  | Calculated | Calculated | Calculated | Tab A | Tab A |  | Tab A | Tab D | Calculated | Tab C | Calculated | Tab F |  | Tab E | Estimate | Calculated | 2.5%
Sanitation System
Disposal System
Treatment Plants
Collection Systems
Sewer Mains
Pump Station
|  |  | Incoming Sewer | [14 empty] | Avg 1500 cfm; peak 2100cfm
|  |  |  | Pipes | 1963 | 3 | 1725 | 100 | 4 | 0% | 57 |  | 43% | 17.25 | 741.75 | 1 | 1 |  | 2 | 0% | 4 | 5 | 20 | 2 |  | 25% | 0 | 2063 | 0
|  |  |  | Manhole | 1963 | 3 | 340 | 100 | 3 | 0% | 57 |  | 43% | 3.4 | 146.2 | 1 | 1 |  | 2 | 0% | 4 | 5 | 20 | 5 | CBM | 0% | 2200 | 2063 | 538.471
|  |  |  | Influent Gate Valve | 1986 | 5 | 442 | 30 | 5 | 0% | 10 |  | 66.67% | 14.7333 | 294.6667 | 1 | 1 |  | 2 | 0% | 7 | 5 | 35 | 7 | CBM | 50% | 2600 | 2016 | 2031.1158 | What Funding Strategy? 2016: 2600
|  |  | Incoming Power | [14 empty] | 20 kw peak
|  |  |  | Pole & Transformer | 2006 | 4 | 0 | 40 | 1 | 0% | 40 |  | 0% | 0 | 0 | 4 | 2 |  | 2 | 0% | 0 | 5 | 0 | 1 |  | -25% | 0 | 2046 | 0
|  |  |  | Connection | 2006 | 7 | 0 | 35 | 1 | 0% | 35 |  | 0% | 0 | 0 | 1 | 1 |  | 2 | 0% | 0 | 5 | 0 | 1 |  | 0% | 0 | 2041 | 0
Control system
|  |  |  | Incoming Telephone | 1985 | 8 | 85 | 25 | 4 | 0% | 4 |  | 84% | 3.4 | 71.4 | 1 | 1 |  | 2 | 0% | 8 | 2 | 16 | 1 | RTF/CM | 0% | 500 | 2010 | 452.9753 | What Funding Strategy? 2010: 500
|  |  |  | PLC | 1983 | 8 | 8600 | 25 | 4 | 0% | 2 |  | 92% | 344 | 7912 | 1 | 1 |  | 2 | 0% | 9 | 2 | 18 | 8 | RTF/CM | 0% | 5000 | 2008 | 4759.072 | What Funding Strategy? 2008: 5000
|  |  |  | Manual controls | 1978 | 8 | 425 | 25 | 3 | 20% | 2 |  | 92% | 17 | 476 | 1 | 1 |  | 2 | 50% | 5 | 2 | 5 | 7 | CBM | 0% | 2500 | 2008 | 2379.536 | What Funding Strategy? 2008: 2500
Land & Improvemnts.
|  |  |  | Land | 1950 | 10 | 630 | 300 | 1 | 0% | 244 |  | 18.67% | 2.1 | 117.6 | 1 | 1 |  | 4 | 0% | 2 | 1 | 2 | 1 | CBM | 0% | 0 | 2250 | 0
|  |  |  | Access Road | 1963 | 1 | 12500 | 75 | 5 | 0% | 32 |  | 57.33% | 166.6667 | 7166.6667 | 1 | 1 |  | 4 | 0% | 6 | 1 | 6 | 2 | CBM | 0% | 8500 | 2038 | 3857.0497
|  |  |  | Landscaping | 2000 | 1 | 595 | 75 | 4 | 0% | 69 |  | 8% | 7.9333 | 47.6 | 1 | 1 |  | 3 | 0% | 1 | 1 | 1 | 7 | CBM | 0% | 3500 | 2075 | 636.9735
|  |  |  | Security fence | 1963 | 1 | 1360 | 75 | 4 | 0% | 32 |  | 57.33% | 18.1333 | 779.7333 | 1 | 1 |  | 2 | 0% | 6 | 3 | 18 | 5 | CBM | 25% | 8000 | 2038 | 3630.1644
Sub Structure
|  |  |  | Cassion Outer | 1963 | 1 | 30600 | 75 | 3 | 0% | 32 |  | 57.33% | 408 | 17544 | 1 | 1 |  | 3 | 0% | 6 | 4 | 24 | 2 | CBM | 0% | 180000 | 2038 | 81678.6992
|  |  |  | Upper Floor | 1963 | 1 | 4250 | 75 | 3 | 0% | 32 |  | 57.33% | 56.6667 | 2436.6667 | 1 | 1 |  | 3 | 0% | 6 | 4 | 24 | 2 | CBM | 0% | 25000 | 2038 | 11344.2638
|  |  |  | Dry well | 1963 | 1 | 6800 | 75 | 3 | 0% | 32 |  | 57.33% | 90.6667 | 3898.6667 | 1 | 1 |  | 3 | 0% | 6 | 4 | 24 | 2 | CBM | 0% | 40000 | 2038 | 18150.822
|  |  |  | Landings and Stairs | 1963 | 9 | 4250 | 60 | 3 | 0% | 17 |  | 71.67% | 70.8333 | 3045.8333 | 2 | 2 |  | 2 | 0% | 7 | 4 | 28 | 2 | CBM | 0% | 25000 | 2023 | 16429.8764 | What Funding Strategy? 2023: 25000
|  |  |  | Wet Well | 1963 | 1 | 5100 | 75 | 2 | 0% | 32 |  | 57.33% | 68 | 2924 | 1 | 1 |  | 3 | 0% | 6 | 4 | 24 | 2 | CBM | 0% | 30000 | 2038 | 13613.1165
|  |  |  | Shaped floor | 1963 | 1 | 850 | 75 | 3 | 0% | 32 |  | 57.33% | 11.3333 | 487.3333 | 1 | 1 |  | 3 | 0% | 6 | 3 | 18 | 2 | CBM | 0% | 5000 | 2038 | 2268.8528
|  |  |  | Sump pump | 1963 | 4 | 595 | 40 | 3 | 0% | -3 | 1 | 97.5% | 14.875 | 639.625 | 3 | 3 |  | 2 | 0% | 10 | 4 | 40 | 8 | CBM | 25% | 3500 | 2007 | 3414.6341 | What Funding Strategy? 2007: 3500
|  |  | Pumps | [14 empty] | peak 2100cfm
|  |  |  | Drive shafts | 2006 | 6 | 12560 | 35 | 1 | 0% | 35 |  | 0% | 358.8571 | 0 | 2 | 1 |  | 2 | TBD | 10 | TBD | #VALUE! | TBD | TBD | TBD | 35000 | 2041 | 14747.9873
|  |  |  | Pumps | 2006 | 4 | 29750 | 40 | 1 | 0% | 40 |  | 0% | 743.75 | 0 | 3 | 3 |  | 2 | TBD | 10 | TBD | #VALUE! | TBD | TBD | TBD | 35000 | 2046 | 13035.0718
|  |  |  | Motors | 2006 | 6 | 32500 | 35 | 1 | 0% | 35 |  | 0% | 928.5714 | 0 | 4 | 5 |  | 2 | TBD | 10 | TBD | #VALUE! | TBD | TBD | TBD | 35000 | 2041 | 14747.9873
Electrics
|  |  |  | Meters & Breakers | 1963 | 7 | 1275 | 35 | 4 | 0% | -8 | 1 | 97.14% | 36.4286 | 1566.4286 | 2 | 2 |  | 2 | 0% | 10 | 5 | 50 | 8 | CBM | 25% | 7500 | 2007 | 7317.0732 | What Funding Strategy? 2007: 7500
|  |  |  | Switchboard | 1963 | 7 | 2705 | 35 | 4 | 0% | -8 | 1 | 97.14% | 77.2857 | 3323.2857 | 2 | 2 |  | 2 | 0% | 10 | 5 | 50 | 8 | CBM | 25% | 34000 | 2007 | 33170.7317 | What Funding Strategy? 2007: 34000
|  |  |  | Pump Starters | 1963 | 7 | 1445 | 35 | 5 | 0% | -8 | 1 | 97.14% | 41.2857 | 1775.2857 | 2 | 2 |  | 2 | 0% | 10 | 3 | 30 | 7 | CBM | 25% | 8500 | 2007 | 8292.6829 | What Funding Strategy? 2007: 8500
|  |  |  | Emergency connect. | 2006 | 7 | 765 | 35 | 0 | 0% | 35 |  | 0% | 21.8571 | 0 | 2 | 2 |  | 2 | 0% | 1 | 3 | 3 | 8 | CBM | 0% | 4500 | 2041 | 1896.1698
|  |  |  | Alarms / General L& P. | 1963 | 7 | 595 | 35 | 4 | 0% | -8 | 1 | 97.14% | 17 | 731 | 2 | 2 |  | 2 | 0% | 10 | 3 | 30 | 8 | CBM | 25% | 3500 | 2007 | 3414.6341 | What Funding Strategy? 2007: 3500
Force Main
|  |  |  | Pipes | 1963 | 2 | 2380 | 60 | 4 | 0% | 17 |  | 71.67% | 39.6667 | 1705.6667 | 1 | 1 |  | 2 | 0% | 7 | 5 | 35 | 5 | PM | 50% | 14000 | 2023 | 9200.7308 | What Funding Strategy? 2023: 14000
|  |  |  | Valves(check& gate) | 1978 | 5 | 1105 | 30 | 5 | -10% | -1 | 1 | 96.67% | 36.8333 | 1031.3333 | 1 | 1 |  | 2 | 0% | 10 | 4 | 40 | 7 | CBM | 50% | 6500 | 2007 | 6341.4634 | What Funding Strategy? 2007: 6500
Superstructure
|  |  |  | Walls | 1963 | 9 | 3400 | 60 | 3 | 0% | 17 |  | 71.67% | 56.6667 | 2436.6667 | 2 | 2 |  | 3 | 0% | 7 | 2 | 14 | 5 | CBM | 0% | 20000 | 2023 | 13143.9011 | What Funding Strategy? 2023: 20000
|  |  |  | Roof | 1963 | 9 | 1445 | 60 | 5 | 0% | 17 |  | 71.67% | 24.0833 | 1035.5833 | 2 | 2 |  | 3 | 0% | 7 | 3 | 21 | 6 | CBM | 0% | 8500 | 2023 | 5586.158 | What Funding Strategy? 2023: 8500
|  |  |  | Roller door | 1963 | 9 | 408 | 60 | 4 | 0% | 17 |  | 71.67% | 6.8 | 292.4 | 2 | 2 |  | 2 | 0% | 7 | 2 | 14 | 7 | CBM | 0% | 2400 | 2023 | 1577.2681 | What Funding Strategy? 2023: 2400
|  |  |  | Gantry Crane | 1963 | 9 | 2040 | 60 | 4 | 0% | 17 |  | 71.67% | 34 | 1462 | 2 | 2 |  | 2 | 0% | 7 | 2 | 14 | 5 | CBM | 0% | 12000 | 2023 | 7886.3407 | What Funding Strategy? 2023: 12000
[7 empty] | 171520 | [6 empty] | 3735.9774 | 63971.7917 | [10 empty] | Renewal | 567700 |  | 305543.823 | 0 | 63500 | 7500 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 2600 | 0 | 0 | 0 | 0 | 0 | 0 | 81900 | 0 | 0
[26 empty] | Replace | 510000 |  |  | What Funding Strategy? 2006: 100018.2247
[30 empty] | 5000.9112 | 5000.9112 | 5000.9112 | 5000.9112 | 5000.9112 | 5000.9112 | 5000.9112 | 5000.9112 | 5000.9112 | 5000.9112 | 5000.9112 | 5000.9112 | 5000.9112 | 5000.9112 | 5000.9112 | 5000.9112 | 5000.9112 | 5000.9112 | 5000.9112 | 5000.9112
[30 empty] | 3735.9774 | 3735.9774 | 3735.9774 | 3735.9774 | 3735.9774 | 3735.9774 | 3735.9774 | 3735.9774 | 3735.9774 | 3735.9774 | 3735.9774 | 3735.9774 | 3735.9774 | 3735.9774 | 3735.9774 | 3735.9774 | 3735.9774 | 3735.9774 | 3735.9774 | 3735.9774
Note on F8: Installed Date: Set the date you believe the asset was first put into service. Don't b e too concerned about this as it doesn't matter a lot. Eventually .. It is just used to get us started
Note on G8: Asset Classes: 1 Civil 2 Pressure Pipework 3 Sewers 4 Pumps 5 Valves 6 Motors 7 Electrical 8 Controls 9 Building Assets 10 Land
Note on H8: Original Cost: In this case, these costs were estimated using current renewal/replacement costs deflated back to year of acquisition using a construction CPI.
Note on I8: Estimated Effective Life: (This is just a starting point) Effective Lives (Years) Asset Type Average Effective Lives Civil Structures 75 Pressure Pipe work 60 Sewers – Gravity Pipe work. 100 Mechanical 40 Electrical Motors (large) 35 Other Electrical 30 Controls 25 Building Assets 60
Note on L8: Residual Physical Life: This is done by following the chart below and shown on sheet B at the bottom of the spreadsheet. This is for a guide only… We want your expert group to really try and judge the condition and the residual physical life. You need to do this realistically ..and HONESTLY. Try not to be pessimistic .. Use the chart to understand the residual lives that we found to be correct after 15 years of doing this ..so use them to help justify the figures you adopt Effective Lives (Years) Condition Rating / Residual Life Asset Type Average Effective Lives 1 2 3 4 5 Civil Structures 75 75 60 45 30 15 Pressure Pipe work 60 60 48 36 24 12 Sewers – Gravity Pipe work. 100 100 80 60 40 20 Mechanical 40 40 32 24 16 8 Electrical Motors (large) 35 35 28 21 14 7 Other Electrical 30 30 24 18 12 6 Controls 25 25 20 15 10 5 Building Assets 60 60 48 36 24 12
Note on N8: % Asset Comsumed (Physical): This is calculated by the spreadsheet taking the effective life that you have identified for the individual components from a condition perspective.. (see next step documents for optimising your verification of these valued judgements ('delphi group')) ..
Note on O8: Annual Depreciation: Straight-line depreciation is used here. More accurate "exponential" curves should be considered.
Note on P8: Accumulated Depreciaition: The sum of each year's depreciation expense since installation of the asset - "what we have expensed to date"
Note on U8: Redundancy: Make allowance for the Level of Redundancy .Reduce PoF by: 50% Backup 50% 100% Backup 90% 200% Secondary Backup 98%
Note on V8: Probability of Failure (PoF): This is calculted by the software. It is just the % effective life consumed (Column J) being used as a number equal to this divided by 10,, just to give a quick figure …This is then modified by the back up that we have for some assets & components.
Note on W9: Consequence of Failure (CoF): CoF Rating Description % Affected Level 1 Minor Component Failure 0-50% Child Asset 2 Major Component Failure 50-100% Child Asset 3 Major Asset 0-50% Asset 4 Major asset 50-100% Asset 5 Multiple Asset Failure 0-50% Facility /Sub-System 6 Major Facilty Failure 50-100% Facility /Sub-System 7 Minor Sanitory System Failure 20-40% Total System 8 Medium System failure 40-60% Total System 10 Intermediate System Failure 60-75% Total System 15 Significant system Failure 75-90% Total System 20 Total System Failure 90-100% Total System
Note on X8: Business Risk Exposure (BRE): This column is calculated by the spreadsheet .. It multiplies the probability of failure (% of life consumed) by the consequence of failure you have determined for each component.
Note on Y9: Renewal Strategy: 1- Staus quo 2 Increase Maintenance 3 Operate differently 4 Repair only 5 Refurbish or rehabilitate 6 Replace with similar asset 7 Replace with improved asset 8 Reduce the cause of failure 9 Use demand management 10 Pay rebate to customers 11 Reduce the level of service 12 Construct a new asset
Note on Z8: Maintenance Tactics PM - Preventivie CBM - Condition based UBM - Condition based RTF/CM- Run to Failure/Corrective
Note on AA9: Future Maintenance Change (%): 1 Status Quo 100% 2 Slightly higher 125% 3 Considerably higher 150% 4 Significantly Higher 200% 5 Reduce Slightly 75% 6 Reduce moderately 50% 7 Reduced significantly 25%
Note on AB8: Cost of Renewal Option: For this column you need to use your best valued judgement. Prepare cost estimates in current $ and only for what will be accomplished during the "planning timeframe" of the analysis (in this example, 20 years). Use the best information you can get including : engineering estimators, manufacturers & agents & your knowledgeable staff & construction contractors ( ask them for a price)
Note on AC8: Recommended Renewal Date: This is calculated by the spreadsheet, setting the year based on your 'residual economic life' (see Column T)

## A - Class & Condition
A-1 | Effective Lives (Years)
Class | Asset Type | Exp Life
1 | Civil | 75
2 | Pressure Pipework | 60
3 | Sewers | 100
4 | Pumps | 40
5 | Valves | 30
6 | Motors | 35
7 | Electrical | 35
8 | Controls | 25
9 | Building Assets | 60
10 | Land | 300
A-1 | Condition Assessment
Condition Rating | Description | Maintenance Level | Description
1 | New or Excellent Condition | Normal PM
2
3 | Minor Defects Only | Normal PM, Minor CM
4
5 | Moderate Deterioration | Normal PM, Major CM
6
7 | Significant Deterioration | Major repair, rehabilitate
8
9 | Virtually Unserviceable | Rehab unlikely
10 | Unserviceable | Replace
A-2 | Performance
Performance Rating | Description
1 | Exceeds / Meets all Performance Targets
2 | Minor Performance Deficiencies
3 | Considerable Performance Deficiencies
4 | Major Performance Deficiencies
5 | Does not meet any Performance Targets
A-3 | Reliability
Reliability Rating | Description | Failure Timing
1 | As Specified by Manufacturer | Never
2 | Random Breakdown | Every 20 Years
3 | Occasional Breakdown | Every 5 Years
4 | Periodic Breakdown | Every 2 Years
5 | Continuous Breakdown | = 1 year

## B - Cond-Resid Lives
B-1 Conditon - Residual Life Factors |  | Condition/Residual Life
| Effective Lives | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
| Civil | 0.9 | 0.8 | 0.7 | 0.6 | 0.5 | 0.4 | 0.3 | 0.2 | 0.1 | 0
| Pressure Pipework | 0.9 | 0.8 | 0.7 | 0.6 | 0.5 | 0.4 | 0.3 | 0.2 | 0.1 | 0
| Sewers | 0.9 | 0.8 | 0.7 | 0.6 | 0.5 | 0.4 | 0.3 | 0.2 | 0.1 | 0
| Pumps | 0.9 | 0.8 | 0.7 | 0.6 | 0.5 | 0.4 | 0.3 | 0.2 | 0.1 | 0
| Valves | 0.9 | 0.8 | 0.7 | 0.6 | 0.5 | 0.4 | 0.3 | 0.2 | 0.1 | 0
| Motors | 0.9 | 0.8 | 0.7 | 0.6 | 0.5 | 0.4 | 0.3 | 0.2 | 0.1 | 0
| Electrical | 0.9 | 0.8 | 0.7 | 0.6 | 0.5 | 0.4 | 0.3 | 0.2 | 0.1 | 0
| Controls | 0.9 | 0.8 | 0.7 | 0.6 | 0.5 | 0.4 | 0.3 | 0.2 | 0.1 | 0
| Building Assets | 0.9 | 0.8 | 0.7 | 0.6 | 0.5 | 0.4 | 0.3 | 0.2 | 0.1 | 0
Land | bar: Condition/Residual Life 1 to Condition/Residual Life 10
B-2 Condition Based Effective Lives |  | Condition/Residual Life 1: Condition/Residual Life
| Effective Lives | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
| Civil | 67.5 | 60 | 52.5 | 45 | 37.5 | 30 | 22.5 | 15 | 7.5 | 0
| Pressure Pipework | 54 | 48 | 42 | 36 | 30 | 24 | 18 | 12 | 6 | 0
| Sewers | 90 | 80 | 70 | 60 | 50 | 40 | 30 | 20 | 10 | 0
| Pumps | 36 | 32 | 28 | 24 | 20 | 16 | 12 | 8 | 4 | 0
| Valves | 27 | 24 | 21 | 18 | 15 | 12 | 9 | 6 | 3 | 0
| Motors | 31.5 | 28 | 24.5 | 21 | 17.5 | 14 | 10.5 | 7 | 3.5 | 0
| Electrical | 31.5 | 28 | 24.5 | 21 | 17.5 | 14 | 10.5 | 7 | 3.5 | 0
| Controls | 22.5 | 20 | 17.5 | 15 | 12.5 | 10 | 7.5 | 5 | 2.5 | 0
| Building Assets | 54 | 48 | 42 | 36 | 30 | 24 | 18 | 12 | 6 | 0
| Land | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
B-3 Design LifeAdjustment Factors |  | Condition/Residual Life 1: IMPACT RATING FACTORS
| Factor | Condition/Residual Life 1: 1; Condition/Residual Life 2: 2; Condition/Residual Life 3: 3; Condition/Residual Life 4: 4; Condition/Residual Life 5: 5
| DESIGN STANDARDS | Condition/Residual Life 1: 10%; Condition/Residual Life 2: 5%; Condition/Residual Life 3: 0%; Condition/Residual Life 4: -5%; Condition/Residual Life 5: -10%
| CONSTRUCTION QUALITY | Condition/Residual Life 1: 10%; Condition/Residual Life 2: 5%; Condition/Residual Life 3: 0%; Condition/Residual Life 4: -5%; Condition/Residual Life 5: -10%
| MATERIAL QUALITY | Condition/Residual Life 1: 10%; Condition/Residual Life 2: 5%; Condition/Residual Life 3: 0%; Condition/Residual Life 4: -5%; Condition/Residual Life 5: -10%
| OPERATIONAL HISTORY | Condition/Residual Life 1: 10%; Condition/Residual Life 2: 5%; Condition/Residual Life 3: 0%; Condition/Residual Life 4: -5%; Condition/Residual Life 5: -10%
| MAINTENANCE HISTORY | Condition/Residual Life 1: 10%; Condition/Residual Life 2: 5%; Condition/Residual Life 3: 0%; Condition/Residual Life 4: -5%; Condition/Residual Life 5: -10%
| OPERATING ENVIRONMENT | Condition/Residual Life 1: 10%; Condition/Residual Life 2: 5%; Condition/Residual Life 3: 0%; Condition/Residual Life 4: -5%; Condition/Residual Life 5: -10%
| EXTERNAL STRESSES | Condition/Residual Life 1: 10%; Condition/Residual Life 2: 5%; Condition/Residual Life 3: 0%; Condition/Residual Life 4: -5%; Condition/Residual Life 5: -10%

## C - Consequence of Failure
C-1 Consequence of Failure
CoF Rating | Description | % Affected | Level
1 | Minor Component Failure | 0-25% | Asset
2 | Major Component Failure | 25-50% | Asset
3 | Major Asset | 0-25% | Asset
4 | Multiple Asset Failure | 25-50% | Facility / Sub-System
5 | Major Facilty Failure | 50-100% | Facility
6 | Minor Sanitory System Failure | 20-40% | Total System
7 | Medium | 40-60% | Total System
8 | Intermediate | 60-80% | Total System
9 | Significant | 80-90% | Total System
10 | Total | 90-100% | Total System

## D - Probabilty of Failure
D-1 Probability of Failure
% of Effective Life Consumed | PoF Rating
0% | 1
10% | 2
20% | 3
30% | 4
40% | 5
50% | 6
60% | 7
70% | 8
80% | 9
90% | 10
D-2 Don't Forget Redundancy!
Level of Redundancy | Reduce PoF by:
50% Backup | 50%
100% Backup | 90%
200% Secondary Backup | 98%

## E - Renewal Strategies
E-1 Renewal Strategies
Option | Description | Type
1 | Do nothing | Non-Capital
2 | Continue with Status Quo | Non-Capital
3 | Maintain differently | Non-Capital
4 | Operate differently | Non-Capital
5 | Repair | Capital
6 | Refurbish/rehabilitate | Capital
7 | Replace asset with similar | Capital
8 | Replace with improved asset | Capital
9 | Reduce Levels of Service | Non-Asset