## Sheet1
UV Treatment
UV Sensor Correction Factor (CF) Worksheet
PWS Name:
Facility Name:
PWSID:
Facility ID:
Reporting Period:
Reactor Number:
Date | Duty Sensor Number | Duty Sensor Operating Time | Reference Sensor Serial Number | Duty Sensor Reading1 | Reference Sensor Reading1 | Sensor Correction Factor ([A]/[B]-0.2)
(hr)
|  |  |  | [A] | [B]
1If three duty sensor and reference sensor readings are taken, the mean of the readings can be used. |  |  |  |  | Selected UV Sensor CF2:
2UV Sensor CF should be based on the calibration ratios for the failed sensors and should use the maximum ratio. The CF is reactor specific.
where:
SDuty is the duty UV sensor reading
SRef is the reference UV sensor reading
𝐶𝑎𝑙𝑖𝑏𝑟𝑎𝑡𝑖𝑜𝑛 𝑅𝑎𝑡𝑖𝑜= 𝑆_𝐷𝑢𝑡𝑦⁄𝑆_𝑅𝑒𝑓
𝑆𝑒𝑛𝑠𝑜𝑟 𝐶𝑜𝑟𝑟𝑒𝑐𝑡𝑖𝑜𝑛 𝐹𝑎𝑐𝑡𝑜𝑟= 𝑆_𝐷𝑢𝑡𝑦⁄𝑆_𝑅𝑒𝑓 − 0.2
where:
SDuty is the duty UV sensor reading
SRef is the reference UV sensor reading
State Logo