## Summary
Key Parameters | Results
Combined Data Set SCC List | 50100802
Does the SCC contain more than 15 sources? | Yes
Pollutant | Cadmium
Units | LB
Activity | TONS DRIED SLUDGE FED
Factor Quality Rating | Moderately Representative
Number of individual test data values used to calculate the emissions factor | 6
Number of individual test data values excluded from the calculation | 2
Composite Test Rating | 75.21
Control Device Configuration | AFTERBURNER,SCRUBBER,VENTURI SCRUBBER
AFTERBURNER,TRAY SCRUBBER,VENTURI SCRUBBER
AFTERBURNER,VENTURI SCRUBBER
New Candidate Factor Value | 0.000397

## Data Included
Individual Test Data Value | Individual Test Method | Individual Test Data Units | Individual Test Data Activity | Individual Test Rating | Detection Limit Flag | Year of Test | Facility Name | Control_1 | Control_2 | Control_3 | Control_4 | Control_5 | Test City | Test State | ERT Project Data Set | Submission_ID
0.000237 | Method 29 | LB | TONS DRIED SLUDGE FED | 75 | DLL | 2015 | MCES - Seneca Wastewater Treatment Plant | SCRUBBER | SCRUBBER | VENTURI SCRUBBER | VENTURI SCRUBBER | SCRUBBER | Eagan | MN | PDS | 80124740
0.000318 | Method 29 | LB | TONS DRIED SLUDGE FED | 78.5 | DLL | 2015 | Anchorage Water and Wastewater Utility (AWWU) | VENTURI SCRUBBER |  |  |  |  | Anchorage | AK | PDS | 80123866
0.00041 | Method 29 | LB | TONS DRIED SLUDGE FED | 74 | ADL | 2016 | MCES - Seneca Wastewater Treatment Plant | AFTERBURNER | SCRUBBER | SCRUBBER | VENTURI SCRUBBER |  | Eagan | MN | PDS | 80245743
0.000454 | Method 29 | LB | TONS DRIED SLUDGE FED | 75 | ADL | 2017 | Blue River Wastewater Treatment Plant | AFTERBURNER | VENTURI SCRUBBER | VENTURI SCRUBBER |  |  | Kansas City | MO | PDS | 80272499
0.00046 | Method 29 | LB | TONS DRIED SLUDGE FED | 75 | DLL | 2019 | Blue River Wastewater Treatment Plant | AFTERBURNER | VENTURI SCRUBBER | TRAY SCRUBBER |  |  | Kansas City | MO | PDS | 80410495
0.000504 | Method 29 | LB | TONS DRIED SLUDGE FED | 74 | ADL | 2016 | MCES - Seneca Wastewater Treatment Plant | AFTERBURNER | SCRUBBER | SCRUBBER | VENTURI SCRUBBER |  | Eagan | MN | PDS | 80174548

## Data Excluded
Reason for Exclusion | Individual Test Data Value | Individual Test Method | Individual Test Data Units | Individual Test Data Activity | Individual Test Rating | Detection Limit Flag | Year of Test | Facility Name | Control_1 | Control_2 | Test City | Test State | ERT Project Data Set | Submission_ID
Data value is an outlier. | 0.00205 | Method 29 | LB | TONS DRIED SLUDGE FED | 75 | ADL | 2016 | Erie Waste Water Treatment Plant | VENTURI SCRUBBER |  | Erie | PA | PDS | 80135251
Data value is an outlier. | 7.47e-05 | Method 29 | LB | TONS DRIED SLUDGE FED | 25 | ADL | 2016 | Blue River Wastewater Treatment Plant | AFTERBURNER | VENTURI SCRUBBER | Kansas City | MO | PDS | 80162371