EPA Region 8 Seasonal Start-up Checklist

For Public Water Systems in Wyoming or on Tribal Lands in EPA Region 8

If your public water system (PWS) is open to the public only part of the year, it is considered a seasonal system. Under the Revised Total Coliform Rule (RTCR), you are required to complete the following steps and submit this form to our office prior to serving water to the public for the season. You will be in violation of the RTCR and subject to enforcement action if you serve water to the public before completing these start-up procedures and submitting this form to our office.

Wyoming and EPA R8 Tribal water systems can submit this checklist to:

RTCR Manager

8WD-SDR

1595 Wynkoop Street

Denver, CO  80202

Or fax at: 303-312-7517 or email at: R8DWU@epa.gov

PWS Name: ___________________________________________________________________

PWS ID number: _______________________________________________________________

Today’s Date: _________________________________________________________________

Date water system opens to the public*: ___________________________________________

Estimated closure date for the season**: ___________________________________________

Is your system open to the public year-round with a portion that closes seasonally? _______

Unless otherwise noted as optional, all actions must be completed. If an action does not apply or you do not have a specified piece of equipment, mark “N/A”. If you need more room to answer a question, please use an additional sheet or reference the question number and add more information on page 4. If your system has more than one water source and more than one distribution system, please complete the table at the end of the form specifying when each well/distribution system will open/closed and when you plan to complete the startup procedures on each well/distribution system. You are required to submit this form to EPA BEFORE you start serving water to the public EVERY YEAR. Even if the water system remains pressurized throughout the year, if your system is not considered a public water system for part of the year (total coliform samples are not required year-round), this Seasonal Start-up Checklist is required. Please let EPA know via email when the system stops serving water to the public.

*Sampling requirements may change based on the schedule you put in the Checklist. Check Drinking Water Watch (https://sdwisdww.epa.gov/DWWR8WY/) for the most up to date sampling requirements.

**This date will be used as the seasonal shutdown date. If you write that the PWS closes on September 1, 2025, then EPA will expect a September sample result. If the system actually closes on August 15, 2025, let EPA know of the early closure so that an adjustment can be made to the sampling schedule, and the system will not receive a monitoring violation.

| Action | Completed? | Comments |
| --- | --- | --- |
| - Inspect each source- - Wells - Is each well sealed and intact? Are all required gaskets and screens undamaged and properly installed? Are all bolts present and tight? Are there any openings that could allow in animals, insects, stagnant or other water? - Spring(s) - Are there any breaches or openings that could allow in contamination? Has deep rooted vegetation been removed? Is your spring area fenced or protected from stock or wildlife? - Intake(s) - Any repairs needed? Complete any repairs prior to opening. If more time for repairs is needed, be sure to contact our office first. |  |  |
| - Does your system have any treatment? List all treatment. - Ensure that chemical feeds are functioning properly, you have fresh disinfectant, and conduct UV maintenance (if necessary). Include the disinfectant residual on your “special” sample result so that you know the chemical feed is working. - If you have any cartridge filters on your system (i.e., reverse osmosis or sediment filters) be sure to check the user manual to see if it is time to change the filter. Please indicate if filter(s) changed. Complete any repairs prior to opening. If more time for repairs is needed, be sure to contact our office first. |  |  |
| - Inspect any storage or pressure tanks. List the storage tanks. - Are there any openings or repairs needed? _________ - Are vents and overflows intact and properly fitted with #24 mesh screen? ________ - Are access penetrations gasketed and sealed? _______ - Are all valves operational? __________ - When was/were the storage tank(s) last cleaned? _______ - What were the conditions of the storage tank when last cleaned? ______________________________________ - For each storage tank, please describe the latest cleaning or inspection procedures in the comment section. Complete any repairs prior to opening. If more time for repairs is needed, be sure to contact our office first. Failure to describe the most recent storage tank cleaning or inspection procedure may lead to a significant deficiency during the next sanitary survey. |  |  |
| - Flush the distribution system You must flush your system to rid your distribution system of stagnant water, even if it remains pressurized during the off-season. We recommend disinfecting and flushing as it is more effective and will kill any bacteria that may have accumulated. Be sure to use a chlorine solution approved for drinking water. a) Recommended: Add disinfectant at proper dosage. Fill the system then turn on faucets to get disinfected water throughout your entire distribution. Shut the water off and let sit 24 hours. Prevent anyone using this water during this time as it would contain high levels of disinfectant. b) Required: Flush the stagnant or disinfected water out of the system. Be sure to keep chlorinated water away from septic systems and surface water bodies such as lakes, streams and ponds. |  |  |
| - Flush out your tanks (if applicable). Ensure stagnant or disinfected water is removed and all valves are operational. |  |  |
| - Inspect your pipes (distribution system). - Any leaks noted? Does the system hold pressure with all taps closed? Complete any repairs prior to opening. If more time for repairs is needed, be sure to contact our office first. |  |  |
| - When the above steps are completed, collect a bacteriological sample and mark it as “special” (not routine or repeat), and send to the lab for analysis. Be sure EPA gets a copy of these results as well. This sample can serve as a double check to ensure your system is fully operational and ready for the season. Samples labeled as “special” do not count for compliance. Not collecting the “special” sample is considered not completing this form and may result in a violation. This sample does not count as your “routine” sample for the month. If you serve water to the public the same month you do your seasonal start-up you must collect both a “special” sample and a “routine” sample to meet compliance. |  |  |
| - Was your system required to complete a Level 1 or Level 2 Assessment last year? Did you complete all the required corrective actions before filling out the Seasonal Startup Checklist this year? |  |  |

If you need further instruction on disinfection practices, you can consult the Wyoming Association of Rural Water Systems (WARWS) at 307-436-8636 or Midwest Assistance Program, Inc. (MAP) at (307) 941-0990. If in Indian country, consult Megan Falk (MT) at Falk.megan@epa.gov or Colby Brakke (ND, SD) at Brakke.colby@epa.gov or Motaz Zarooq (CO, UT) at Zarooq.motaz@epa.gov. Any time you have a positive total coliform sample, be sure to refer to: https://www.epa.gov/region8-waterops/addressing-total-coliform-positive-or-ecoli-positive-sample-results-epa-region-8 for the required steps. If you have any other questions please contact Jamie Harris, the RTCR Manager at Harris.Jamie@epa.gov or 303-312-6072.

Additional Comments:

Certification of Completion:

I hereby certify that the information in this form is the truth and each start-up procedure listed above was completed before water was delivered to my customers.

Name (Printed) ____________________________________________________________________

Signature __________________________________	Date _______________________________

Phone Number _____________________________	Email _______________________________

Complete the following table if:

- Your seasonal system has more than one source serving more than one distribution system.

- Your seasonal system distribution system(s) open or close during different months (i.e., WL01 – Dist 1 opens in May and WL03 - Dist 3 opens in June).

| Well Name (i.e., WL0x) | Distribution System Name (i.e., DS0x) | Planned Startup Activity (use additional space if necessary) | Startup Date (if different than other sources) | Shutdown Date (if different than other sources) | Date Special Sample Collected |
| --- | --- | --- | --- | --- | --- |
| WL01 (EXAMPLE) | Dist 1 | Dist 1 opens to the public in May. In April we flushed WL01 to waste and shock chlorinated Dist 1 for 24 hours and then flushed the system. Special samples were TC-. | 05/02/2025 | 09/30/2025 | 04/29/2025 |
| WL03 (EXAMPLE) | Dist 3 | Dist 3 opens to the public in June. In May we will flush WL03 to waste and shock chlorinate Dist 3 for 24 hours and then flush the system. Special samples will be collected in May. | 06/07/2025 | 10/30/2025 | 05/28/2025 |

Additional Comments: