| EPA Region 8 Drinking Water Unit Finished Water Storage Tank Checklist: Overflow For either a Tank Inspection/Cleaning Report or an Unknown Integrity Significant Deficiency Fill out one checklist per storage tank & submit labeled photos of each tank component with this form. - Inspection/Cleaning Checklist: Submit labeled photos of each tank component inspected. - Unknown Integrity Checklist: Submit labeled photos of each tank component inspected. |  |  |  |
| --- | --- | --- | --- |
| PWS Name: | PWS ID: |  |  |
| Tank Name: | Tank ID: |  |  |
| Proposed Cleaning/Inspection Date: | Actual Cleaning/Inspection Date: |  |  |
| Name of Person Filling Out Form: | Title of Person Filling Out Form: |  |  |
| I certify that this information is complete & accurate: |  | Date: |  |

| Inspector Qualifications: fill out regardless of which type of Checklist you are completing (answers to questions in this section should be “yes”) |  |
| --- | --- |
| Name & contact information of inspector (if water system personnel) or inspection company: |  |
| - Yes ☐ No | Has the inspector completed confined space training? |
| - Yes ☐ No | Did the inspector have a confined space entry permit? |

| Overall Tank Condition |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Significant Deficiency |  |  | Required Correction | Proposed Completion Date | Actual Completion Date |
| - Yes | - No | Are there issues with the tank foundation? | If “Yes”, what repairs does tank inspector recommend? |  |  |
| - Yes | - No | Does the tank appear structurally sound? | If “No”, what repairs does the tank inspector recommend? |  |  |
| - Yes | - No | Are there tank unprotected openings (breaches, leaks, daylight coming through tank in spots, etc) | If “Yes”, explain type of breach & how it will be repaired. |  |  |
| - Yes | - No | Is there corrosion developing in or on the tank? | If “Yes”, explain where the corrosion is & how it will be repaired. |  |  |

| Unknown Integrity/Tank Inspection Checklist: Overflow |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Significant Deficiency |  |  | Required Correction | Proposed Completion Date | Actual Completion Date |
| - Yes ☐ No |  | Does the tank have an overflow separate from the vent? | If “No”, explain deficiency & how it will be corrected: |  |  |
| - Yes | - No | Does the tank overflow exit the tank below the tank vent? | If “No”, explain deficiency & how it will be corrected: |  |  |
| - Yes | - No | Is the overflow accessible for inspection? | If “No”, explain deficiency & how it will be corrected: |  |  |
| - Yes | - No | Is it equipped with #24-mesh non-corrodible screen OR is it a duckbill valve OR a sealed flapper valve with a screen inside (EPA recommends #24-mesh)? | If “No”, explain deficiency & how it will be corrected: |  |  |
| - Yes ☐ No ☐ NA (“NA” only applies if not using a duckbill or flapper valve) |  | Using a duckbill or flapper valve? Date of last inspection of duckbill valve OR flapper valve with a screen inside: | If not known, state when it will next be inspected. |  |  |
|  |  | If using a flapper valve, what is the screen size inside it? |  |  |  |
| - Yes ☐ No ☐ NA (“NA” only applies if answering question below “Yes” or “No”) |  | Does overflow discharge 12-24 inches above an inlet structure, splash plate or riprap? | If “No”, modify overflow to provide for an appropriate discharge height & discharge material. |  |  |
|  |  | What is discharge height & material? |  |  |  |

| - Yes ☐ No ☐ NA (“NA” only applies if answering question above “Yes” or “No”) | Does the overflow have an air gap of 3 or more pipe diameters above any storm or sanitary sewer or drain entrance? | If “No”, explain deficiency & how it will be corrected: |  |  |
| --- | --- | --- | --- | --- |
| - Yes ☐ No | Is the discharge dry? Is any water that exits the overflow able to flow rapidly & freely away to avoid ponding? | If “No”, explain deficiency & how it will be corrected: |  |  |
| - Yes ☐ No | Is there a blockage, a too-small overflow, a level control malfunction, or other issue that causes overflow through the hatch or vent, or continuous overflow? Overflow structure capacity should at least equal maximum fill rate. | If “Yes”, explain what is causing the problem & how it will be repaired: |  |  |
| - Yes ☐ No ☐ NA (“NA” only applies if tank is not in a properly constructed building) | If tank is in a properly constructed building, is the overflow designed such that an overflow event will not damage electrical or other vulnerable components in the building through splashing or flooding? | If “No”, explain deficiency & how it will be corrected: |  |  |
| - Yes ☐ No | Is the overflow discharge point visible? | If “No”, EPA recommends moving it to a place where it is visible to allow inspection & emergency overflow event detection. |  |  |
| - Yes ☐ No ☐ NA (“NA” only applies if tank is not in a properly constructed building) | If tank is in a properly constructed building, does the overflow discharge to an inside floor drain or through piping to outside? | If “No”, explain deficiency & how it will be corrected: |  |  |