| EPA Region 8 Drinking Water Unit Finished Water Storage Tank Checklist: Rooftop For either a Tank Inspection/Cleaning Report or an Unknown Integrity Significant Deficiency Fill out one checklist per storage tank & submit labeled photos of each tank component with this form. - Inspection/Cleaning Checklist: Submit labeled photos of each tank component inspected. - Unknown Integrity Checklist: Submit labeled photos of each tank component inspected. |  |  |  |
| --- | --- | --- | --- |
| PWS Name: | PWS ID: |  |  |
| Tank Name: | Tank ID: |  |  |
| Proposed Cleaning/Inspection Date: | Actual Cleaning/Inspection Date: |  |  |
| Name of Person Filling Out Form: | Title of Person Filling Out Form: |  |  |
| I certify that this information is complete & accurate: |  | Date: |  |

| Inspector Qualifications: fill out regardless of which type of Checklist you are completing (answers to questions in this section should be “yes”) |  |
| --- | --- |
| Name & contact information of inspector (if water system personnel) or inspection company: |  |
| - Yes ☐ No | Has the inspector completed confined space training? |
| - Yes ☐ No | Did the inspector have a confined space entry permit? |

| Overall Tank Condition |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Significant Deficiency |  |  | Required Correction | Proposed Completion Date | Actual Completion Date |
| - Yes | - No | Are there issues with the tank foundation? | If “Yes”, what repairs does tank inspector recommend? |  |  |
| - Yes | - No | Does the tank appear structurally sound? | If “No”, what repairs does the tank inspector recommend? |  |  |
| - Yes | - No | Are there tank unprotected openings (breaches, leaks, daylight coming through tank in spots, etc) | If “Yes”, explain type of breach & how it will be repaired. |  |  |
| - Yes | - No | Is there corrosion developing in or on the tank? | If “Yes”, explain where the corrosion is & how it will be repaired. |  |  |

| Unknown Integrity/Tank Inspection Checklist: Air Vent |  |  |  |  |
| --- | --- | --- | --- | --- |
| Significant Deficiency |  | Required Correction | Proposed Completion Date | Actual Completion Date |
| - Yes ☐ No | Does the tank have a vent separate from the overflow? | If “No”, explain how it will be corrected: |  |  |
| - Yes ☐ No | Does the tank vent exit the tank above the overflow? | If “No”, explain how it will be corrected: |  |  |
| - Yes ☐ No | Is the vent covered with #24-mesh non-corrodible screen? Mesh Size: | If “No”, explain deficiency & how it will be corrected: |  |  |
| - Yes ☐ No ☐ NA (“NA” only if tank has a non-downturned vent) | Downturned vent: Is the vent ≥ 24” (outdoor tank) or 8” (indoor tank) above the nearest horizontal surface/roof? | If “No”, reconfigure vent to provide proper air gap. |  |  |
| - Yes ☐ No ☐ NA (“NA” only if tank has a downturned vent) | Non-downturned vent (not allowed on buried tanks): Does vent have a solid cover that terminates at its base? | If “No”, explain deficiency & how it will be corrected: |  |  |
| - Yes ☐ No ☐ NA (“NA” only if tank has a downturned vent) | Non-downturned vent (not allowed on buried tanks): Is screen ≥ 8” above the nearest horizontal surface/roof? What is screen height? | If “No”, explain deficiency & how it will be corrected: |  |  |

| Unknown Integrity/Tank Inspection Checklist: Access Hatch |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Significant Deficiency |  |  | Required Correction | Proposed Completion Date | Actual Completion Date |
| - Yes | - No | Is hatch ≥ 4” above nearest horizontal surface/roof (not required for above-ground indoor tanks)? What is the height? | If “No”, the hatch should be raised to the appropriate height above the nearest horizontal surface/roof. |  |  |
| - Yes | - No | For outdoor tanks, is hatch ≥ 24” above natural ground surface (sum of roof height above ground + at least 4” hatch height above nearest horizontal surface/roof)? Height above nearest horizontal surface/roof? | If “No”, raise the hatch to the appropriate height above the natural ground surface. |  |  |
| - Yes ☐ No ☐ NA (“NA” only applies if answering the below question “Yes” or “No”) |  | Does hatch have a shoebox lid with a 2” rim overlap (not required if using another approved lid type)? | If “No”, install a properly designed lid & have it approved by EPA. |  |  |
| - Yes ☐ No ☐ NA (“NA” only applies if answering the above question “Yes” or “No”) |  | If lid is not shoebox-style, is it an approved watertight lid type with a neoprene rubber gasket? Describe lid type: | If “No”, install a properly designed lid & have it approved by EPA. |  |  |
| - Yes | - No | Is the hatch lid watertight & sealed with a neoprene rubber gasket? | If “No”, investigate & repair the seal lack. |  |  |
| - Yes | - No | Is the hatch locked, or in a secured area or locked building? | If “No”, equip the hatch with a lock. |  |  |