## Total and 5- and 25-year
Measure Number | Description | Current kg/year | Predicted kg/yr | Change kg/yr | Years Measure complete during 2025-2030 | kg 2025-2030 | kg 2025-2050 | Annual metric tons | Total metric tons 2025-2030 | Total metric tons 2025-2050 | TOTAL EPA Funding Request | Cost/ Emission reduction 2025-2030 | Cost/ Emission reduction 2025-2050
Measure 1 | Seward Seawater Heat Pump | 80051.951 | 16562.4773 | 63489.4737 | 4 | 253957.8947 | 1523747.3684 | 63.4895 | 253.9579 | 1523.7474
Measure 2 | Troth Yeddha' Campus ULT Freezers | 504868 | 77894 | 426974 | 4 | 1707896 | 10247376 | 426.974 | 1707.896 | 10247.376
Measure 3 | Troth Yeddha' Campus Lighting | 342775.7632 | 214622.8032 | 128152.96 | 3 | 384458.88 | 2947518.08 | 128.153 | 384.4589 | 2947.5181
Measure 4 | Kodiak Ventilation | 337623 | 265178 | 72445 | 3.5 | 253557.5 | 1702457.5 | 72.445 | 253.5575 | 1702.4575
Measure 5 | Kuskokwim Lights and Motors | 88301 | 25229 | 63072 | 3 | 189216 | 1450656 | 63.072 | 189.216 | 1450.656
Measure 6 | Eielson | 37642.7298 | 18821.3649 | 18821.3649 | 4 | 75285.4596 | 451712.7574 | 18.8214 | 75.2855 | 451.7128
| Patty | 217791.7155 | 108895.8578 | 108895.8578 | 3 | 326687.5733 | 2504604.7284 | 108.8959 | 326.6876 | 2504.6047
| Bunnell | 283539.8879 | 141769.9439 | 141769.9439 | 2 | 283539.8879 | 3118938.7667 | 141.7699 | 283.5399 | 3118.9388
| Troth Yeddha' Campus Building Envelopes Subtotal | 538974.3332 | 269487.1666 | 269487.1666 |  | 685512.9207 | 6075256.2525 | 269.4872 | 685.5129 | 6075.2563
Measure 7 | Rasmuson Hall Boiler | 935601.6334 | 850075.7713 | 85525.8621 | 5 | 427629.3103 | 2138146.5517 | 85.5259 | 427.6293 | 2138.1466
Measure 8 | Microturbine CHP | 2205179.7958 | 2038803.1416 | 166376.6543 | 5 | 831883.2713 | 4159416.3566 | 166.3767 | 831.8833 | 4159.4164
TOTAL |  | 5033375.4766 | 3757852.36 | 1275523.1166 |  | 4734111.7771 | 30244574.1092 | 1275.5231 | 4734.1118 | 30244.5741
COSTS | [10 empty] | 33592654 | 7095.8726 | 1110.7002

## Measure 1
Measure 1: Seward Marine Center Seawater Heat Pump
| Gallons of Diesel Heating Fuel used per year | CO2 emission in kg/year*** | CO2 emission in metric tons/year
Current heating fuel usage* | 7859 | 80083.21 | 80.0832
Projected heating fuel usage** | 1626 | 16568.94 | 16.5689
Reduction | 6233 | 63514.27 | 63.5143
*Based on Seward Marine Center purchasing records.
**Based on the proportional reduction in the use of heating fuel, 79%, experienced by the Alaska SeaLife Center (ASLC)
after they installed a similar heating system in 2012. ASLC is located immediately adjacent to the Seward Marine Center.
***Calculated using the EIA crbon dioxide coefficient for diesel and home heating fuel, 10.19 kg CO2 per gallon, and the net heating value of diesel fuel, 128,450 Btu/gallon.
https://www.eia.gov/environment/emissions/co2_vol_mass.php

## Measure 2
Measure 2. Replace Inefficient Ultra Low Temperature Freezers.
|  | Power consumption, kWh per day per freezer* | Power consumption, kWh per year per 38 freezers** | Total CO2 emission in kg/year*** | CO2 emission in metric tons/year
Current Freezers | Mechanical, -80 C chest freezer, 27 cubic feet | 35 | 485450 | 504868 | 504.868
New Freezers | Mechanical, -80 C chest freezer, 27 cubic feet | 5.4 | 74898 | 77893.92 | 77.8939
Reduction |  | 29.6 | 410552 | 426974.08 | 426.9741
*Power consumption was reported in “Research and Academic Sample Preservation”, which has been uploaded as an optional appendix.
This document was uploaded as an optional attachment in the "other attachments" section of the application package.
**Assumes based on the list price and funding requested that at least 38 freezers will be purchased.
***Calculated using an estimate from the EIA table "U.S. electricity net generation and resulting CO2 emissions by fuel in 2022", which shows 2.3 pounds (1.04kg)
of CO2 emitted per kWh generated. https://www.eia.gov/tools/faqs/faq.php?id=74&t=11
UAF power plant actuals were about 3.0 lb CO2 per kWh in 2023, so using the EIA value is conservative.

## Measure 3
Measure. Pathways and Parking Lots LED Lighting Conversion
| Number of lights | Non-LED average wattage | LED average wattage | Wattage difference per light | Total wattage difference for all lights | Annual average daily hours of operation | Non-LED average kWh*/year | LED average kWh** | kWh difference | Total CO2 emission in kg/year** | Total CO2 emission in kg/year** | Total CO2 emission reduction in kg/year** | Total CO2 emission reduction in metric tons/year
Ski trail flood lights**** | 83 | 250 | 160 | 90 | 7470 | 7.49 | 56727.3875 | 36305.528 | 20421.8595 | 58996.483 | 37757.7491 | 21238.7339 | 21.2387
Other flood lights | 80 | 250 | 160 | 90 | 7200 | 11.51 | 84023 | 53774.72 | 30248.28 | 87383.92 | 55925.7088 | 31458.2112 | 31.4582
Shoebox lights | 122 | 200 | 150 | 50 | 6100 | 11.51 | 102508.06 | 76881.045 | 25627.015 | 106608.3824 | 79956.2868 | 26652.0956 | 26.6521
Canopy lights | 3 | 150 | 40 | 110 | 330 | 11.51 | 1890.5175 | 504.138 | 1386.3795 | 1966.1382 | 524.3035 | 1441.8347 | 1.4418
Bollard lights | 38 | 150 | 40 | 110 | 4180 | 11.51 | 23946.555 | 6385.748 | 17560.807 | 24904.4172 | 6641.1779 | 18263.2393 | 18.2632
Gold-pan lights | 90 | 150 | 80 | 70 | 6300 | 11.51 | 56715.525 | 30248.28 | 26467.245 | 58984.146 | 31458.2112 | 27525.9348 | 27.5259
Metal halide lights | 6 | 150 | 90 | 60 | 360 | 11.51 | 3781.035 | 2268.621 | 1512.414 | 3932.2764 | 2359.3658 | 1572.9106 | 1.5729
TOTAL | 422 | [5 empty] | 329592.08 | 206368.08 | 123224 | 342775.7632 | 214622.8032 | 128152.96 | 128.153
*Non-LED (current) consumption in kWh/day is based on of lamp manufacturer specifications and data on hours of operation by UA facilities staff
and checked against metering data. The several lighting circuits on campus are metered and controlled centrally.
**LED consumption in kWhr/day is based on manufacturer data and hours of operation, using the same hours as for current lamps.
***Calculated using the EIA table "U.S. electricity net generation and resulting CO2 emissions by fuel in 2022", which shows 2.3 pounds (1.04 kg)
of CO2 emitted per kWh generated from coal. https://www.eia.gov/tools/faqs/faq.php?id=74&t=11
UAF power plant actuals were about 3.0 lb CO2 per kWh in 2023, so using the EIA value is conservative.
****Winter use only.

## Measure 4
Measure 4: Kodiak Laboratory Ventilation Upgrade
| MBTU/year* | CO2 emission in kg/year** | CO2 emission in metric tons/year
Current energy loss due to ventilation | 4255.9 | 337622.5847 | 337.6226
Energy loss due to ventilation after renovation is complete | 3342.7 | 265177.9914 | 265.178
Reduction | 913.2 | 72444.5932 | 72.4446
*The ventilation energy loss reduction is included in a 2010 Schematic Design Report by the Bell Design Group.
This document was uploaded as an optional attachment in the "other attachments" section of the application package.
**Calculated using the EIA crbon dioxide coefficient for diesel and home heating fuel, 10.19 kg CO2 per gallon, and the net heating value of diesel fuel, 128,450 Btu/gallon.
https://www.eia.gov/environment/emissions/co2_vol_mass.php

## Measure 5
Measure 5.Kuskokwim Campus Lighting Conversion to LED and Motor Replacement*
|  | Watts | Number of Tubes | Hours of Operation** | kWh/day | kg CO2/year** | Metric tons CO2/year
Current lights | T8 fluorescent | 28 | 800 | 10 | 224 | 88300.8 | 88.3008
New lights | LED | 10 | 800 | 8 | 64 | 25228.8 | 25.2288
Reduction |  |  |  | 2 | 160 | 63072 | 63.072
*CO2 emission reduction is calculated based on the lighting only and so is a conservative estimate. We have no systematic information on the energy consumption.
of the motors. Low wattage LEDs used for replacements because of the very high power cost.
**Hours of operation were reduced because of the new controls.
***Calculated using the EIA table "U.S. electricity net generation and resulting CO2 emissions by fuel in 2022", which shows 2.38 pounds (1.08 kg)
of CO2 emitted per kWh generated from petroleum. https://www.eia.gov/tools/faqs/faq.php?id=74&t=11
The Bethel power plant has diesel engine generators.

## Measure 6
Measure 6. Exterior Wall Replacements to Reduce Heat Loss.
| Year 1 | Year 2 | Year 3 | Average | Estimated loss through envelope (%)*** | Envelope loss of CO2 in kg/year | Reduction in envelope loss due to curtain wall replacement @ 50%, kg of CO2/year***
Eielson Building steam use*
Total in pounds/year | 1753472 | 1789062 | 1648159 | 1730231 | 35
CO2 in kg/year** | 108995.3103 | 111207.5744 | 102449.0848 | 107550.6565 | 35 | 37642.7298 | 18821.3649
Patty Center steam use*
Total in pounds/year | 9818621 | 9746880 | 10466594 | 10010698.3333 | 35
CO2 in kg/year** | 610322.6302 | 605863.2305 | 650600.4437 | 622262.1015 | 35 | 217791.7355 | 108895.8678
Bunnell Building steam use*
Total in pounds/year | 13393365 | 12994055 | 12710927 | 13032782.3333 | 35
CO2 in kg/year** | 832527.6792 | 807706.6856 | 790107.5313 | 810113.9654 | 35 | 283539.8879 | 141769.9439
TOTAL CO2 in kg/year | [5 empty] | 538974.3532 | 269487.1766
TOTAL in metric tons/year | [5 empty] | 538.9744 | 269.4872
*Steam use is monitored via a meter for each building.
**Calculated from the carbon content of coal (0.268 lbs. C per lb. coal)and the results of UAF Power Plant efficiency testing
The efficiency testing result was 137 lb. of CO2 emitted per 1000 lbs. of steam.
***Most of the heat loss from a typical UAF building is due to ventilation, which must meet code requirements.
Quantitative heat loss studies have not been done for these buildings, but since the studied buildings are better insulated, this is a conservative assumption.
Further, the envelope heat loss reduction is expected to be better than 50%, so this is also a conservative assumption.

## Measure 7
Measure 7: Rasmuson Hall Boiler Replacement*
Boiler Model, Type | Natural Gas Consumption/year (ccf)** | Heating Capacity (MMBtu) | CO2 Emissions lb/year*** | CO2 Emissions kg/year | CO2 Emissions metric tons/year
Weil McClain 1188 non-condensing | 176245 | 17624 | 2062008 | 935575.3176 | 935.5753
Aerco BMK 3000 (condensing) | 160134 | 16013 | 1873521 | 850054.9002 | 850.0549
Reduction | 16111 | 1611 | 188487 | 85520.4174 | 85.5204
*The information presented in the first three columns of the table is from a contractor report, "University of Alaska Anchorage, Boiler Replacement Upgrades,
Greenhouse Gas Emissions Reduction Analysis." This document was uploaded as an optional attachment in the "other attachments" section of the application package.
**AKWarm software (https://www.analysisnorth.com/AkWarm/AkWarm2downloadPublic.html) was used to calculate the natural gas consumption from
manufacturer information about the two boilers and the design data for Rasmuson Hall.
***The EIA ratio of 117 lbs. of CO2 per million Btu was used to calculate CO2 emissions. https://www.eia.gov/energyexplained/natural-gas/natural-gas-and-the-environment.php

## Measure 8
Measure 8: Conoco Phillips Integrated Science Building Combined Heat and Power (CHP) Plant*
| Utility Power/year | Natural Gas/year | Equivalent Btu Energy Load (Power) (MMBtu/year)** | Equivalent Heating Capacity (Gas) (MMBtu/year) | Total MMBtu/year | CO2 Emissions (lbs/year) | CO2 Emissions (metric tons/year) | CO2 Emissions (metric tons/year)
Existing Energy Consumption | 3876100 | 133524 | 27520.31 | 14020 | 41540.31 | 4860216.27 | 2205179.7958 | 2205.1798
Energy Consumption with CHP | 2129320 | 221790 | 15118.172 | 23288 | 38406.172 | 4493522.124 | 2038803.1416 | 2038.8031
Change | 1746780 | -88266 | 12402.138 | -9268 | 3134.138 | 366694.146 | 166376.6543 | 166.3767
*The information presented in the first five columns of the table is from a contractor report, "University of Alaska Anchorage, ConocoPhillips Integrated Science Building,
Combined Heat and Power Upgrades, Greenhouse Gas Emissions Reduction Analysis." This document was uploaded as an optional attachment in the "other attachments" section of the application package.
**The ratio 0.0071 MMBtu/kWh was used.
***The EIA ratio of 117 lbs. of CO2 per million Btu was used to calculate CO2 emissions. https://www.eia.gov/energyexplained/natural-gas/natural-gas-and-the-environment.php