## KPI Overview (hidden)
Clinton National Airport
KPI Overview - Data Sources
|  | Category Type | Description | Internal Notes | Source File Name | Baseline UoM
| Environmental | Electrical Consumption | Terminal | Entergy Account 8599857 | LIT Terminal Electric 2021-2022.pdf | kWh
|  | Electrical Consumption | Parking Deck | Entergy Account 3488731 | LIT Parking Deck Electric 2021-2022.pdf | kWh
|  | Natural Gas Consumption |  |  | NG Utility Data.xlsx
|  | Water Consumption | Terminal | Account #20176280 and Account #20180454 | LIT Terminal Water 0846_001.pdf
|  | Waste | Landfill |  |  | lbs
|  | Waste | Paper |  |  | lbs
|  | Waste | Bottles |  |  | lbs
|  | Waste | Water Bottles Saved |  |  | #
|  | Waste | Liquid Diverted (liquid collection stations) |  |  | gal
|  | Fuel Usage | Gasoline |  |  | gal
|  | Fuel Usage | Diesel |  |  | gal
|  | Fuel Usage | Jet Fuel |  |  | gal
|  | Fugitive GHG Emissions | Refrigerant Leaks
|  | Deicing | Aircraft Deicing/Anti Icing Fluid Used |  |  | gal
|  | Deicing | Pavement Deicers |  |  | gal
|  | Noise | Number of people within DNL 65 | is there a number to call or a website link to complain if needed?
|  | Noise | Number of noise related complaints
|  | Noise | Number of complainants
|  | Stormwater Sampling | # of samples completed during reporting year
|  | Stormwater Sampling | # of samples above benchmark
|  | SPCC Compliance | # of significant spills
| Social | Customer Appreciation Events?
Health & Wellness Clinics?
|  | Facebook Reach | (likes/comments/shares) per post
|  | Direct Jobs Provided |  |  | Annual Comprehensive Financial Report; Page 90 | #
|  | Employee Compensation | Salaries & Benefits |  | Annual Comprehensive Financial Report; Page 37 | USD $
|  | Wifi Availability | Is there a way to measure airport Wifi usage to have as a metric? # of people using, agreeing to terms of use?
|  | Donations to Local Charities |  |  |  | USD $
Blood drives hosted
Exhibits of local artists?
|  | Employee Retention | Average years of work, retirements, quit/dismissal, new hire, promotion OR % employed more that 5 yrs etc.
Donations of clothing from lost and found
| Economic | Total Passengers (in 000s) |  |  | Annual Comprehensive Financial Report; Page 28 | #
|  | Total Revenue |  |  | Annual Comprehensive Financial Report; Page 34 | USD $
|  | Total Operating Costs |  |  | Annual Comprehensive Financial Report; Page 37 | USD $
GHG Emissions - Other Asks
Make/Model of aircraft using airport
Ground Support Equipment - what equipment is airport owned/controlled versus tenant?
Diesel Generators for back up power?
Fleet Vehicles (passenger transport, maintenance, etc.) for airport
Fire fighting equipment

## Guide (hidden)
Clinton National Airport CUP Project
Grant Funding Assistance
Geothermal CUP project calculations are shown in GREEN tabs
Traditional CUP project, with new energy efficient equipment, calculations are shown in BLUE tabs
Airport baseline energy usage data is shown on YELLOW tabs.

## Questions (hidden)
Questions
When will geothermal project be implemented? | Drill well field by end of 2024. Have switch out of equipment and heat pump working by 2026.
When will terminal expansion take place? | Terminal Expansion: Being construction in March of 2026. 2 Phases of project. 75% space = arrival haul. 25% "terminal commons". Look at the phases of design
What is the change in square footage? | Suzanne sent example in chat during meeting.
Can we continue to use the same HVAC savings estimates (100% natural gas, 25% electricity)? | Yes
Is the draft predesign report from Dec 2023 still the most current report? | Yes.

## CUP Geothermal-New
Clinton National Airport CUP Project
Energy Savings from Geothermal System
Geothermal Project Estimated Terminal HVAC Savings
System | Natural Gas | Electricity
Geothermal Project HVAC Savings | 100% | 25%
1Estimated Energy Savings based on meeting with Airport on 2024-01-08
Geothermal Estimated Electricity Savings
| 2019 Terminal Electricity2 Usage (kWh) | HVAC Electricity Usage Compared with Overall Terminal Electricity Usage3 | 2019 Estimated Electricity for Terminal HVAC (kWh) | HVAC Electricity Savings | Anticipated Electricity Savings (kwh/year) | GHG Emission Rate4 (kg CO2e/kWh) | Anticipated GHG Savings (kg CO2e/year)
Project Electricity Savings | 10564488 | 75% | 7923366 | 25% | 1980841.5 | 0.54437 | 1078319.8146
2Electricity Usage for Airport Terminal, Entergy Account 8599847, provided by Janet Hicks of Entergy on 2022-12-15
3Estimated HVAC Electricity consumption compared to overall terminal consumption provided by Tony Robeson of TME Bernhard on 1-25-2023
4US EPA eGRID 2019 Subregion Output Emission Rates. 2021-02-23. https://www.epa.gov/egrid/summary-data. Non-baseload output emission rate. Calculated CO2e savings using CH4 and N2O GWP from AR5.
Geothermal Estimated Natural Gas Savings
| 2019 Terminal Natural Gas5 Usage (MMBtu) | HVAC Natural Gas Usage Compared with Overall Terminal Natural Gas Usage6 | 2019 Estimated Natural Gas usage for Terminal HVAC (MMBtu) | Natural Gas Savings from HVAC | Anticipated Natural Gas Savings (MMBtu/year) | GHG Emission Rate7 (kg CO2e/MMBtu) | Anticipated GHG Savings (kg CO2e/year)
Project Natural Gas Savings | 28986 | 85% | 24638.1 | 100% | 24638.1 | 53.1145 | 1308640.3624
5Natural Gas Usage for Airport Terminal provided by Bernhard TMP: Quarterly Natural Gas Management Report for LR Airport Main Terminal. This natural gas usage is limited to the terminal usage and excludes natural gas usage at the Airport Maintenance Facility (AMF) and airfield vault generator.
6Estimated HVAC Natural Gas consumption compared to overall terminal consumption.
7US EPA Center for Corporate Climate Leadership. GHG Emission Factors Hub. Last Updated September 12, 2023.Natural Gas Stationary Combustion GHG Factor. Calculated CO2e savings using CH4 and N2O GWP from AR5.
Geothermal Estimated Change in GHG Fugitive Emissions (kg of CO2e)
| Year 1 | Year 2 | Year 3 | Year 4 | Year 5
Fugitive Emissions | 108204.3716 | -324613.1148 | -324613.1148 | -324613.1148 | -324613.1148
8Scope 1 fugitive emission calculations are based on the decommissioning of Chiller #1, #2, and #3 as they will be replaced by geothermal. There is an anticipated spike in emissions in year 1 when the units are retired but a subsequent reduction in GHG emissions with this units no longer having annual operating losses.
See 'Fugitve YoY Savings' Reductions worksheets for supporting documentation.
CUP Estimated Near Term GHG Emissions (kg CO2e)
| 2019 Baseline9 | Year 1 | Year 2 | Year 3 | Year 4 | Year 5
GHG Emissions: Business as Usual | 7973563.9224 | 8196498.5239 | 7948063.1212 | 7712049.4886 | 8362674.8441 | 8121829.9523
GHG Emissions: Geothermal | -- | 5649535.9502 | 5025593.7126 | 4844025.1989 | 5021292.2121 | 4839938.7735
Annual GHG Savings | -- | 2546962.5737 | 2922469.4086 | 2868024.2898 | 3341382.632 | 3281891.1788
GHG Reduction from 2019 Baseline |  | 29.15% | 36.97% | 39.25% | 37.03% | 39.3%
9Scope 1 and Scope 2 GHG emissions owned or under operational control of the Clinton National Airport. Detailed breakdown of emissions are provided on the "2019 Baseline" worksheet. All factor use global warming potentials (GWP) from AR5.
See GHG Project Future Savings worksheets for anticipated GHG savings to 2050 and details regarding assumptions for various scenarios.
Geothermal Project Cost per GHG Savings
|  | Geothermal Project Cost10 | Cumulative GHG Savings (kg CO2e) | Cumulative GHG Savings (mt CO2e) | Cost per GHG Reductions (USD/mt CO2e)
Cumulative GHG Savings from 2025-2030 |  | 24374000 | 14960730.0829 | 14960.7301 | 1629.1986
Cumulative GHG Savings from 2025-2050 |  |  | 70488424.9637 | 70488.425 | 345.7873
10Clinton National Airport Central Utility Plant & Utility Relocation Predesign Draft, 1 December 2023, Geotherm CUP w/New Concourse before incentives (IRA credit, VALE grant, etc.); Pg. 37.
CUP Estimated Overall Energy Savings
Electricity Savings (kwh) | Natural Gas Savings (MMBtu) | Energy Conversion kwh/MMBtu | Natural Gas Savings (kwh) | Energy Savings (kwh) | 2019 Airport Energy Usage11 (kWh) | Overall Energy Savings (percent)
1980841.5 | 24638.1 | 293.0711 | 7220714.3298 | 9201555.8298 | 26077889.9942 | 35.28%
11Energy usage for Clinton National Airport calculated in the Sustainability Management Plan prepared by Harbor.
COBRA Results: Summary of Health Effects
COBRA Scenario Discount Rates | Monetary Value (dollars, annual)
| Low | High
3% Discount Rate | 61647 | 139099
7% Discount Rate | 55020 | 124043
See COBRA and AVERT worksheets for supporting documentation.

## GHG Projected Future Savings
Clinton National Airport CUP Project
Projected GHG Future Savings
Estimated GHG Emissions (kg CO2e) with Geothermal Implementation in 2026
Year | Year | Business as Usual | Geothermal Project | GHG Savings per Year | Cumulative GHG Savings | 2019 Baseline | Geothermal Project Reduction from 2019 Baseline
2019 Baseline |  | 7973563.9224 | 7973563.9224 | -- | -- | 7973563.9224 | 0%
Not yet started | 2020 |  |  | -- | -- | 7973563.9224
Not yet started | 2021 |  |  | -- | -- | 7973563.9224
Not yet started | 2022 |  |  | -- | -- | 7973563.9224
Not yet started | 2023 |  |  | -- | -- | 7973563.9224
Not yet started | 2024 |  |  | -- | -- | 7973563.9224
-- | 2025 | 7827023.7759 | 7827023.7759 | -- | -- | 7973563.9224 | 1.838%
Year 1 | 2026 | 8196498.5239 | 5649535.9502 | 2546962.5737 | 2546962.5737 | 7973563.9224 | 29.15%
Year 2 | 2027 | 7948063.1212 | 5025593.7126 | 2922469.4086 | 5469431.9823 | 7973563.9224 | 36.97%
Year 3 | 2028 | 7712049.4886 | 4844025.1989 | 2868024.2898 | 8337456.2721 | 7973563.9224 | 39.25%
Year 4 | 2029 | 8362674.8441 | 5021292.2121 | 3341382.632 | 11678838.9041 | 7973563.9224 | 37.03%
Year 5 | 2030 | 8121829.9523 | 4839938.7735 | 3281891.1788 | 14960730.0829 | 7973563.9224 | 39.3%
Year 6 | 2031 | 7893027.3051 | 4667653.0068 | 3225374.2984 | 18186104.3813 | 7973563.9224 | 41.46%
Year 7 | 2032 | 7675664.7903 | 4503981.5284 | 3171683.2619 | 21357787.6432 | 7973563.9224 | 43.51%
Year 8 | 2033 | 7469170.4012 | 4348493.6239 | 3120676.7773 | 24478464.4205 | 7973563.9224 | 45.46%
Year 9 | 2034 | 7273000.7316 | 4200780.1147 | 3072220.6169 | 27550685.0374 | 7973563.9224 | 47.32%
Year 10 | 2035 | 7086639.5454 | 4060452.2809 | 3026187.2645 | 30576872.3019 | 7973563.9224 | 49.08%
Year 11 | 2036 | 6909596.4185 | 3927140.8388 | 2982455.5797 | 33559327.8816 | 7973563.9224 | 50.75%
Year 12 | 2037 | 6657309.9628 | 3737172.0338 | 2920137.929 | 36479465.8106 | 7973563.9224 | 53.13%
Year 13 | 2038 | 6423944.9912 | 3561450.8892 | 2862494.102 | 39341959.9126 | 7973563.9224 | 55.33%
Year 14 | 2039 | 6208082.3925 | 3398908.8304 | 2809173.562 | 42151133.4746 | 7973563.9224 | 57.37%
Year 15 | 2040 | 6008409.4887 | 3248557.4261 | 2759852.0626 | 44910985.5372 | 7973563.9224 | 59.26%
Year 16 | 2041 | 5823712.0527 | 3109482.3771 | 2714229.6756 | 47625215.2128 | 7973563.9224 | 61% |  | 2019 Electricity Breakdown (kWh)
Year 17 | 2042 | 5652866.9243 | 2980837.9567 | 2672028.9676 | 50297244.1804 | 7973563.9224 | 62.62% |  | 2951668 | Non-Terminal Electricity Usage
Year 18 | 2043 | 5494835.1806 | 2861841.8679 | 2632993.3127 | 52930237.4932 | 7973563.9224 | 64.11% |  | 10564488 | Terminal Electricity Usage
Year 19 | 2044 | 5348655.8177 | 2751770.4857 | 2596885.332 | 55527122.8252 | 7973563.9224 | 65.49% |  | 13516156 | Total Electricity Usage
Year 20 | 2045 | 5213439.907 | 2649954.4572 | 2563485.4498 | 58090608.2749 | 7973563.9224 | 66.77%
Year 21 | 2046 | 5088365.1896 | 2555774.6309 | 2532590.5588 | 60623198.8337 | 7973563.9224 | 67.95% |  | 2019 Natural Gas Breakdown (MMBtu)
Year 22 | 2047 | 4972671.076 | 2468658.2915 | 2504012.7845 | 63127211.6182 | 7973563.9224 | 69.04% |  | 2523.0366 | Non-Terminal Gas Usage
Year 23 | 2048 | 4865654.0209 | 2388075.6775 | 2477578.3434 | 65604789.9617 | 7973563.9224 | 70.05% |  | 28986 | Terminal Natural Gas Usage
Year 24 | 2049 | 4766663.245 | 2313536.7597 | 2453126.4854 | 68057916.447 | 7973563.9224 | 70.98% |  | 31509.0366 | Total Natural Gas Usage
Year 25 | 2050 | 4675096.7773 | 2244588.2606 | 2430508.5166 | 70488424.9637 | 7973563.9224 | 71.85%
Scenario 1: Business as Usual (BAU) Scenario (kg CO2e)
Year | Year | Natural Gas | Propane | Diesel | Gasoline |  | Fugitive Emissions | Electricity (LB) | Total GHG Emissions | YOY Scope 2 LB GHG EF Reduction (in %) | Predicted Electricity (LB) Emission Factor (kg CO2e/kWh) | Terminal Electricity Usage (kwh) | Total Airport Electricity Usage (kwh) | Terminal Natural Gas Usage (MMBtu) | Total Airport Natural Gas Usage
2019 Baseline |  | 1673586.7245 | 2009.2835 | 531164.8994 | 293619.3206 |  | 527096.6882 | 4946087.0061 | 7973563.9224 | -- | 0.36594 | 10564488 | 13516156 | 28986 | 31509.0366
Not yet started | 2020 | [6 empty] | 4921356.571 |  | 0.5% | 0.36411 | 10564488 | 13516156 | 28986 | 31509.0366
Not yet started | 2021 | [6 empty] | 4896749.7882 |  | 0.5% | 0.36229 | 10564488 | 13516156 | 28986 | 31509.0366
Not yet started | 2022 | [6 empty] | 4872266.0392 |  | 0.5% | 0.36048 | 10564488 | 13516156 | 28986 | 31509.0366
Not yet started | 2023 | [6 empty] | 4847904.709 |  | 0.5% | 0.35867 | 10564488 | 13516156 | 28986 | 31509.0366
Not yet started | 2024 | [6 empty] | 4823665.1855 |  | 0.5% | 0.35688 | 10564488 | 13516156 | 28986 | 31509.0366
-- | 2025 | 1673586.7245 | 2009.2835 | 531164.8994 | 293619.3206 |  | 527096.6882 | 4799546.8596 | 7827023.7759 | 0.5% | 0.3551 | 10564488 | 13516156 | 28986 | 31509.0366
Year 1 | 2026 | 1873900.2783 | 2009.2835 | 531164.8994 | 293619.3206 |  | 527096.6882 | 4968708.0538 | 8196498.5239 | 5% | 0.33734 | 11777317.4732 | 14728985.4732 | 32757.3535 | 35280.3901
Year 2 | 2027 | 1873900.2783 | 2009.2835 | 531164.8994 | 293619.3206 |  | 527096.6882 | 4720272.6511 | 7948063.1212 | 5% | 0.32048 | 11777317.4732 | 14728985.4732 | 32757.3535 | 35280.3901
Year 3 | 2028 | 1873900.2783 | 2009.2835 | 531164.8994 | 293619.3206 |  | 527096.6882 | 4484259.0186 | 7712049.4886 | 5% | 0.30445 | 11777317.4732 | 14728985.4732 | 32757.3535 | 35280.3901
Year 4 | 2029 | 2191886.8166 | 2009.2835 | 531164.8994 | 293619.3206 |  | 527096.6882 | 4816897.8357 | 8362674.8441 | 5% | 0.28923 | 13702616.2781 | 16654284.2781 | 38744.1657 | 41267.2023
Year 5 | 2030 | 2191886.8166 | 2009.2835 | 531164.8994 | 293619.3206 |  | 527096.6882 | 4576052.944 | 8121829.9523 | 5% | 0.27477 | 13702616.2781 | 16654284.2781 | 38744.1657 | 41267.2023
Year 6 | 2031 | 2191886.8166 | 2009.2835 | 531164.8994 | 293619.3206 |  | 527096.6882 | 4347250.2968 | 7893027.3051 | 5% | 0.26103 | 13702616.2781 | 16654284.2781 | 38744.1657 | 41267.2023
Year 7 | 2032 | 2191886.8166 | 2009.2835 | 531164.8994 | 293619.3206 |  | 527096.6882 | 4129887.7819 | 7675664.7903 | 5% | 0.24798 | 13702616.2781 | 16654284.2781 | 38744.1657 | 41267.2023
Year 8 | 2033 | 2191886.8166 | 2009.2835 | 531164.8994 | 293619.3206 |  | 527096.6882 | 3923393.3928 | 7469170.4012 | 5% | 0.23558 | 13702616.2781 | 16654284.2781 | 38744.1657 | 41267.2023
Year 9 | 2034 | 2191886.8166 | 2009.2835 | 531164.8994 | 293619.3206 |  | 527096.6882 | 3727223.7232 | 7273000.7316 | 5% | 0.2238 | 13702616.2781 | 16654284.2781 | 38744.1657 | 41267.2023
Year 10 | 2035 | 2191886.8166 | 2009.2835 | 531164.8994 | 293619.3206 |  | 527096.6882 | 3540862.537 | 7086639.5454 | 5% | 0.21261 | 13702616.2781 | 16654284.2781 | 38744.1657 | 41267.2023
Year 11 | 2036 | 2191886.8166 | 2009.2835 | 531164.8994 | 293619.3206 |  | 527096.6882 | 3363819.4102 | 6909596.4185 | 5% | 0.20198 | 13702616.2781 | 16654284.2781 | 38744.1657 | 41267.2023
Year 12 | 2037 | 2191886.8166 | 2009.2835 | 531164.8994 | 293619.3206 |  | 527096.6882 | 3111532.9544 | 6657309.9628 | 7.5% | 0.18683 | 13702616.2781 | 16654284.2781 | 38744.1657 | 41267.2023
Year 13 | 2038 | 2191886.8166 | 2009.2835 | 531164.8994 | 293619.3206 |  | 527096.6882 | 2878167.9828 | 6423944.9912 | 7.5% | 0.17282 | 13702616.2781 | 16654284.2781 | 38744.1657 | 41267.2023
Year 14 | 2039 | 2191886.8166 | 2009.2835 | 531164.8994 | 293619.3206 |  | 527096.6882 | 2662305.3841 | 6208082.3925 | 7.5% | 0.15986 | 13702616.2781 | 16654284.2781 | 38744.1657 | 41267.2023
Year 15 | 2040 | 2191886.8166 | 2009.2835 | 531164.8994 | 293619.3206 |  | 527096.6882 | 2462632.4803 | 6008409.4887 | 7.5% | 0.14787 | 13702616.2781 | 16654284.2781 | 38744.1657 | 41267.2023
Year 16 | 2041 | 2191886.8166 | 2009.2835 | 531164.8994 | 293619.3206 |  | 527096.6882 | 2277935.0443 | 5823712.0527 | 7.5% | 0.13678 | 13702616.2781 | 16654284.2781 | 38744.1657 | 41267.2023
Year 17 | 2042 | 2191886.8166 | 2009.2835 | 531164.8994 | 293619.3206 |  | 527096.6882 | 2107089.916 | 5652866.9243 | 7.5% | 0.12652 | 13702616.2781 | 16654284.2781 | 38744.1657 | 41267.2023
Year 18 | 2043 | 2191886.8166 | 2009.2835 | 531164.8994 | 293619.3206 |  | 527096.6882 | 1949058.1723 | 5494835.1806 | 7.5% | 0.11703 | 13702616.2781 | 16654284.2781 | 38744.1657 | 41267.2023
Year 19 | 2044 | 2191886.8166 | 2009.2835 | 531164.8994 | 293619.3206 |  | 527096.6882 | 1802878.8093 | 5348655.8177 | 7.5% | 0.10825 | 13702616.2781 | 16654284.2781 | 38744.1657 | 41267.2023
Year 20 | 2045 | 2191886.8166 | 2009.2835 | 531164.8994 | 293619.3206 |  | 527096.6882 | 1667662.8986 | 5213439.907 | 7.5% | 0.10013 | 13702616.2781 | 16654284.2781 | 38744.1657 | 41267.2023
Year 21 | 2046 | 2191886.8166 | 2009.2835 | 531164.8994 | 293619.3206 |  | 527096.6882 | 1542588.1812 | 5088365.1896 | 7.5% | 0.092624 | 13702616.2781 | 16654284.2781 | 38744.1657 | 41267.2023
Year 22 | 2047 | 2191886.8166 | 2009.2835 | 531164.8994 | 293619.3206 |  | 527096.6882 | 1426894.0677 | 4972671.076 | 7.5% | 0.085677 | 13702616.2781 | 16654284.2781 | 38744.1657 | 41267.2023
Year 23 | 2048 | 2191886.8166 | 2009.2835 | 531164.8994 | 293619.3206 |  | 527096.6882 | 1319877.0126 | 4865654.0209 | 7.5% | 0.079252 | 13702616.2781 | 16654284.2781 | 38744.1657 | 41267.2023
Year 24 | 2049 | 2191886.8166 | 2009.2835 | 531164.8994 | 293619.3206 |  | 527096.6882 | 1220886.2366 | 4766663.245 | 7.5% | 0.073308 | 13702616.2781 | 16654284.2781 | 38744.1657 | 41267.2023
Year 25 | 2050 | 2191886.8166 | 2009.2835 | 531164.8994 | 293619.3206 |  | 527096.6882 | 1129319.7689 | 4675096.7773 | 7.5% | 0.06781 | 13702616.2781 | 16654284.2781 | 38744.1657 | 41267.2023
The BAU scenario assume HVAC energy usage is proportional to square footage of conditioned space (terminal). BAU scenario includes an increase in electricity and natural gas consumption associated with planned terminal expansion. In addition, this scenario include a "greening" of grid electricity where the GHG emission factor for electricity decreases over time.
Scenario 2: Geothermal Implementation in 2026 | [16 empty] | Projected GHG Emissions Savings (kg Co2e)
Year | Year | Natural Gas | Propane | Diesel | Gasoline |  | Fugitive Emissions | Electricity (LB) | Total GHG Emissions | YOY Scope 2 LB GHG EF Reduction (in %) | Non-Baseload LB Scope 2 GHG EF (kg CO2e/kWh) | BAU Terminal HVAC Electricity Usage (kwh) | Terminal HVAC Electricity Saving with Geothermal (%) | Terminal HVAC Electricity Saving with Geothermal (kWh) | BAU Terminal HVAC Natural Gas Usage (MMBtu) | Terminal HVAC Natural Gas Saving with Geothermal (%) | Natural Gas | CFC/HCFC Fugitives | Electricity (LB)
2019 Baseline |  | 1673586.7245 | 2009.2835 | 531164.8994 | 293619.3206 |  | 527096.6882 | 4946087.0061 | 7973563.9224 | -- | 0.54437 | 7923366 | 0% | 0 | 24638.1 | 0% | 1308640.3624 |  | 0
Not yet started | 2020 | [6 empty] | 4921356.571 |  | 0.5% | 0.54165 | 7923366 | 0% | 0 | 24638.1 | 0% |  |  | 0
Not yet started | 2021 | [6 empty] | 4896749.7882 |  | 0.5% | 0.53894 | 7923366 | 0% | 0 | 24638.1 | 0% |  |  | 0
Not yet started | 2022 | [6 empty] | 4872266.0392 |  | 0.5% | 0.53625 | 7923366 | 0% | 0 | 24638.1 | 0% |  |  | 0
Not yet started | 2023 | [6 empty] | 4847904.709 |  | 0.5% | 0.53357 | 7923366 | 0% | 0 | 24638.1 | 0% |  |  | 0
Not yet started | 2024 | [6 empty] | 4823665.1855 |  | 0.5% | 0.5309 | 7923366 | 0% | 0 | 24638.1 | 0% |  |  | 0
-- | 2025 | 1673586.7245 | 2009.2835 | 531164.8994 | 293619.3206 |  | 527096.6882 | 4799546.8596 | 7827023.7759 | 0.5% | 0.52825 | 7923366 | 0% | 0 | 24638.1 | 0% | 0 | 0 | 0
Year 1 | 2026 | 364946.362 | 2009.2835 | 531164.8994 | 293619.3206 |  | 635301.0598 | 3822495.0247 | 5649535.9502 | 5% | 0.50183 | 9136195.4732 | 25% | 2284048.8683 | 28409.4535 | 100% | 1508953.9162 | -108204.3716 | 1146213.0291
Year 2 | 2027 | 364946.362 | 2009.2835 | 531164.8994 | 293619.3206 |  | 202483.5734 | 3631370.2735 | 5025593.7126 | 5% | 0.47674 | 9136195.4732 | 25% | 2284048.8683 | 28409.4535 | 100% | 1508953.9162 | 324613.1148 | 1088902.3776
Year 3 | 2028 | 364946.362 | 2009.2835 | 531164.8994 | 293619.3206 |  | 202483.5734 | 3449801.7598 | 4844025.1989 | 5% | 0.45291 | 9136195.4732 | 25% | 2284048.8683 | 28409.4535 | 100% | 1508953.9162 | 324613.1148 | 1034457.2587
Year 4 | 2029 | 364946.362 | 2009.2835 | 531164.8994 | 293619.3206 |  | 202483.5734 | 3627068.7731 | 5021292.2121 | 5% | 0.43026 | 11061494.2781 | 25% | 2765373.5695 | 34396.2657 | 100% | 1826940.4545 | 324613.1148 | 1189829.0627
Year 5 | 2030 | 364946.362 | 2009.2835 | 531164.8994 | 293619.3206 |  | 202483.5734 | 3445715.3344 | 4839938.7735 | 5% | 0.40875 | 11061494.2781 | 25% | 2765373.5695 | 34396.2657 | 100% | 1826940.4545 | 324613.1148 | 1130337.6095
Year 6 | 2031 | 364946.362 | 2009.2835 | 531164.8994 | 293619.3206 |  | 202483.5734 | 3273429.5677 | 4667653.0068 | 5% | 0.38831 | 11061494.2781 | 25% | 2765373.5695 | 34396.2657 | 100% | 1826940.4545 | 324613.1148 | 1073820.729
Year 7 | 2032 | 364946.362 | 2009.2835 | 531164.8994 | 293619.3206 |  | 202483.5734 | 3109758.0893 | 4503981.5284 | 5% | 0.36889 | 11061494.2781 | 25% | 2765373.5695 | 34396.2657 | 100% | 1826940.4545 | 324613.1148 | 1020129.6926
Year 8 | 2033 | 364946.362 | 2009.2835 | 531164.8994 | 293619.3206 |  | 202483.5734 | 2954270.1849 | 4348493.6239 | 5% | 0.35045 | 11061494.2781 | 25% | 2765373.5695 | 34396.2657 | 100% | 1826940.4545 | 324613.1148 | 969123.208
Year 9 | 2034 | 364946.362 | 2009.2835 | 531164.8994 | 293619.3206 |  | 202483.5734 | 2806556.6756 | 4200780.1147 | 5% | 0.33293 | 11061494.2781 | 25% | 2765373.5695 | 34396.2657 | 100% | 1826940.4545 | 324613.1148 | 920667.0476
Year 10 | 2035 | 364946.362 | 2009.2835 | 531164.8994 | 293619.3206 |  | 202483.5734 | 2666228.8418 | 4060452.2809 | 5% | 0.31628 | 11061494.2781 | 25% | 2765373.5695 | 34396.2657 | 100% | 1826940.4545 | 324613.1148 | 874633.6952
Year 11 | 2036 | 364946.362 | 2009.2835 | 531164.8994 | 293619.3206 |  | 202483.5734 | 2532917.3997 | 3927140.8388 | 5% | 0.30047 | 11061494.2781 | 25% | 2765373.5695 | 34396.2657 | 100% | 1826940.4545 | 324613.1148 | 830902.0104
Year 12 | 2037 | 364946.362 | 2009.2835 | 531164.8994 | 293619.3206 |  | 202483.5734 | 2342948.5948 | 3737172.0338 | 7.5% | 0.27793 | 11061494.2781 | 25% | 2765373.5695 | 34396.2657 | 100% | 1826940.4545 | 324613.1148 | 768584.3596
Year 13 | 2038 | 364946.362 | 2009.2835 | 531164.8994 | 293619.3206 |  | 202483.5734 | 2167227.4502 | 3561450.8892 | 7.5% | 0.25709 | 11061494.2781 | 25% | 2765373.5695 | 34396.2657 | 100% | 1826940.4545 | 324613.1148 | 710940.5327
Year 14 | 2039 | 364946.362 | 2009.2835 | 531164.8994 | 293619.3206 |  | 202483.5734 | 2004685.3914 | 3398908.8304 | 7.5% | 0.23781 | 11061494.2781 | 25% | 2765373.5695 | 34396.2657 | 100% | 1826940.4545 | 324613.1148 | 657619.9927
Year 15 | 2040 | 364946.362 | 2009.2835 | 531164.8994 | 293619.3206 |  | 202483.5734 | 1854333.987 | 3248557.4261 | 7.5% | 0.21997 | 11061494.2781 | 25% | 2765373.5695 | 34396.2657 | 100% | 1826940.4545 | 324613.1148 | 608298.4933
Year 16 | 2041 | 364946.362 | 2009.2835 | 531164.8994 | 293619.3206 |  | 202483.5734 | 1715258.938 | 3109482.3771 | 7.5% | 0.20347 | 11061494.2781 | 25% | 2765373.5695 | 34396.2657 | 100% | 1826940.4545 | 324613.1148 | 562676.1063
Year 17 | 2042 | 364946.362 | 2009.2835 | 531164.8994 | 293619.3206 |  | 202483.5734 | 1586614.5177 | 2980837.9567 | 7.5% | 0.18821 | 11061494.2781 | 25% | 2765373.5695 | 34396.2657 | 100% | 1826940.4545 | 324613.1148 | 520475.3983
Year 18 | 2043 | 364946.362 | 2009.2835 | 531164.8994 | 293619.3206 |  | 202483.5734 | 1467618.4288 | 2861841.8679 | 7.5% | 0.1741 | 11061494.2781 | 25% | 2765373.5695 | 34396.2657 | 100% | 1826940.4545 | 324613.1148 | 481439.7434
Year 19 | 2044 | 364946.362 | 2009.2835 | 531164.8994 | 293619.3206 |  | 202483.5734 | 1357547.0467 | 2751770.4857 | 7.5% | 0.16104 | 11061494.2781 | 25% | 2765373.5695 | 34396.2657 | 100% | 1826940.4545 | 324613.1148 | 445331.7627
Year 20 | 2045 | 364946.362 | 2009.2835 | 531164.8994 | 293619.3206 |  | 202483.5734 | 1255731.0182 | 2649954.4572 | 7.5% | 0.14896 | 11061494.2781 | 25% | 2765373.5695 | 34396.2657 | 100% | 1826940.4545 | 324613.1148 | 411931.8805
Year 21 | 2046 | 364946.362 | 2009.2835 | 531164.8994 | 293619.3206 |  | 202483.5734 | 1161551.1918 | 2555774.6309 | 7.5% | 0.13779 | 11061494.2781 | 25% | 2765373.5695 | 34396.2657 | 100% | 1826940.4545 | 324613.1148 | 381036.9894
Year 22 | 2047 | 364946.362 | 2009.2835 | 531164.8994 | 293619.3206 |  | 202483.5734 | 1074434.8524 | 2468658.2915 | 7.5% | 0.12745 | 11061494.2781 | 25% | 2765373.5695 | 34396.2657 | 100% | 1826940.4545 | 324613.1148 | 352459.2152
Year 23 | 2048 | 364946.362 | 2009.2835 | 531164.8994 | 293619.3206 |  | 202483.5734 | 993852.2385 | 2388075.6775 | 7.5% | 0.1179 | 11061494.2781 | 25% | 2765373.5695 | 34396.2657 | 100% | 1826940.4545 | 324613.1148 | 326024.7741
Year 24 | 2049 | 364946.362 | 2009.2835 | 531164.8994 | 293619.3206 |  | 202483.5734 | 919313.3206 | 2313536.7597 | 7.5% | 0.10905 | 11061494.2781 | 25% | 2765373.5695 | 34396.2657 | 100% | 1826940.4545 | 324613.1148 | 301572.916
Year 25 | 2050 | 364946.362 | 2009.2835 | 531164.8994 | 293619.3206 |  | 202483.5734 | 850364.8216 | 2244588.2606 | 7.5% | 0.10087 | 11061494.2781 | 25% | 2765373.5695 | 34396.2657 | 100% | 1826940.4545 | 324613.1148 | 278954.9473
The geothermal scenario has the same assumption as the BAU scenario but also include an estimated reduction of 100% for terminal natural gas HVAC usage and a reduction of 25% for terminal electricity HVAC usage. GHG savings from electricity savings are calculated using the non baseload emission factor for grid electricity.

## Projected Terminal Area (SF)
Clinton National Airport
Terminal Area
Terminal Area with Planned Expansion
| Terminal Area (sf) | Year | Description
| 291370 | 2024 | Current Airport Terminal1
| 335970 | 2026-2028 | with Arrivals Haul
| 406770 | 2028-2030 | with Terminal Commons
1Table 1-11 of Airport Master Plan; Terminal Building Space Allocation
Arrivals Haul Planned Development
| Year | Area | Level | Description | Area (sf)
| 2026-2028 | Arrivals Haul | Level 1 | Public Claim Area | 28800
|  | Arrivals Haul | Level 1 | Office and Circulation Area | 7200
|  | Arrivals Haul | Level 1 | Secure Baggage Lay-Down Area | 15000
|  | Arrivals Haul | Level 2 | Office/Support and Public Area | 24600
|  |  |  | Total New Area: | 75600
|  |  |  | Existing Baggage Claim Demo Area | 31000
|  |  |  | Net Change | 44600
Terminal Commons Planned Development
| Year | Area | Level | Description | Area (sf)
| 2028-2030 | Terminal Commons | Level 1 | Terminal Commons Level 1 | 36400
|  | Terminal Commons | Level 2 | Terminal Commons Level 2 | 34400
|  |  |  | Total New Area: | 70800
|  |  |  | Demo Area | 0
|  |  |  | Net Change | 70800
Predicted Change in Terminal Energy Usage with Change in Terminal Square Footage
| Year | Year | Square Footage (sf) | Terminal HVAC Electricity Usage (kwh) | Terminal HVAC Natural Gas Usage (MMBtu) | Terminal Non-HVAC Electricity Consumption (kwh) | Non-HVAC Natural Gas Consumption (MMBtu) | Terminal Electricity Usage (kwh) | Terminal Natural Gas Usage (MMBtu) | Change in Terminal Electricity Usage (percent from baseline) | Change in Terminal Natural Gas Usage (percent from baseline)
| 2019 Baseline |  | 291370 | 7923366 | 24638.1 | 2641122 | 4347.9 | 10564488 | 28986 | 100% | 100%
| Not yet started | 2020 | 291370 | 7923366 | 24638.1 | 2641122 | 4347.9 | 10564488 | 28986 | 100% | 100%
| Not yet started | 2021 | 291370 | 7923366 | 24638.1 | 2641122 | 4347.9 | 10564488 | 28986 | 100% | 100%
| Not yet started | 2022 | 291370 | 7923366 | 24638.1 | 2641122 | 4347.9 | 10564488 | 28986 | 100% | 100%
| Not yet started | 2023 | 291370 | 7923366 | 24638.1 | 2641122 | 4347.9 | 10564488 | 28986 | 100% | 100%
| Not yet started | 2024 | 291370 | 7923366 | 24638.1 | 2641122 | 4347.9 | 10564488 | 28986 | 100% | 100%
| -- | 2025 | 291370 | 7923366 | 24638.1 | 2641122 | 4347.9 | 10564488 | 28986 | 100% | 100%
| Year 1 | 2026 | 335970 | 9136195.4732 | 28409.4535 | 2641122 | 4347.9 | 11777317.4732 | 32757.3535 | 111.5% | 113%
| Year 2 | 2027 | 335970 | 9136195.4732 | 28409.4535 | 2641122 | 4347.9 | 11777317.4732 | 32757.3535 | 111.5% | 113%
| Year 3 | 2028 | 335970 | 9136195.4732 | 28409.4535 | 2641122 | 4347.9 | 11777317.4732 | 32757.3535 | 111.5% | 113%
| Year 4 | 2029 | 406770 | 11061494.2781 | 34396.2657 | 2641122 | 4347.9 | 13702616.2781 | 38744.1657 | 129.7% | 133.7%
| Year 5 | 2030 | 406770 | 11061494.2781 | 34396.2657 | 2641122 | 4347.9 | 13702616.2781 | 38744.1657 | 129.7% | 133.7%
| Year 6 | 2031 | 406770 | 11061494.2781 | 34396.2657 | 2641122 | 4347.9 | 13702616.2781 | 38744.1657 | 129.7% | 133.7%
| Year 7 | 2032 | 406770 | 11061494.2781 | 34396.2657 | 2641122 | 4347.9 | 13702616.2781 | 38744.1657 | 129.7% | 133.7%
| Year 8 | 2033 | 406770 | 11061494.2781 | 34396.2657 | 2641122 | 4347.9 | 13702616.2781 | 38744.1657 | 129.7% | 133.7%
| Year 9 | 2034 | 406770 | 11061494.2781 | 34396.2657 | 2641122 | 4347.9 | 13702616.2781 | 38744.1657 | 129.7% | 133.7%
| Year 10 | 2035 | 406770 | 11061494.2781 | 34396.2657 | 2641122 | 4347.9 | 13702616.2781 | 38744.1657 | 129.7% | 133.7%
| Year 11 | 2036 | 406770 | 11061494.2781 | 34396.2657 | 2641122 | 4347.9 | 13702616.2781 | 38744.1657 | 129.7% | 133.7%
| Year 12 | 2037 | 406770 | 11061494.2781 | 34396.2657 | 2641122 | 4347.9 | 13702616.2781 | 38744.1657 | 129.7% | 133.7%
| Year 13 | 2038 | 406770 | 11061494.2781 | 34396.2657 | 2641122 | 4347.9 | 13702616.2781 | 38744.1657 | 129.7% | 133.7%
| Year 14 | 2039 | 406770 | 11061494.2781 | 34396.2657 | 2641122 | 4347.9 | 13702616.2781 | 38744.1657 | 129.7% | 133.7%
| Year 15 | 2040 | 406770 | 11061494.2781 | 34396.2657 | 2641122 | 4347.9 | 13702616.2781 | 38744.1657 | 129.7% | 133.7%
| Year 16 | 2041 | 406770 | 11061494.2781 | 34396.2657 | 2641122 | 4347.9 | 13702616.2781 | 38744.1657 | 129.7% | 133.7%
| Year 17 | 2042 | 406770 | 11061494.2781 | 34396.2657 | 2641122 | 4347.9 | 13702616.2781 | 38744.1657 | 129.7% | 133.7%
| Year 18 | 2043 | 406770 | 11061494.2781 | 34396.2657 | 2641122 | 4347.9 | 13702616.2781 | 38744.1657 | 129.7% | 133.7%
| Year 19 | 2044 | 406770 | 11061494.2781 | 34396.2657 | 2641122 | 4347.9 | 13702616.2781 | 38744.1657 | 129.7% | 133.7%
| Year 20 | 2045 | 406770 | 11061494.2781 | 34396.2657 | 2641122 | 4347.9 | 13702616.2781 | 38744.1657 | 129.7% | 133.7%
| Year 21 | 2046 | 406770 | 11061494.2781 | 34396.2657 | 2641122 | 4347.9 | 13702616.2781 | 38744.1657 | 129.7% | 133.7%
| Year 22 | 2047 | 406770 | 11061494.2781 | 34396.2657 | 2641122 | 4347.9 | 13702616.2781 | 38744.1657 | 129.7% | 133.7%
| Year 23 | 2048 | 406770 | 11061494.2781 | 34396.2657 | 2641122 | 4347.9 | 13702616.2781 | 38744.1657 | 129.7% | 133.7%
| Year 24 | 2049 | 406770 | 11061494.2781 | 34396.2657 | 2641122 | 4347.9 | 13702616.2781 | 38744.1657 | 129.7% | 133.7%
| Year 25 | 2050 | 406770 | 11061494.2781 | 34396.2657 | 2641122 | 4347.9 | 13702616.2781 | 38744.1657 | 129.7% | 133.7%

## 2019 Baseline
Clinton National Airport CUP Project
2019 Baseline GHG Emissions
2019 Usage Data
|  | Natural Gas | Propane | Diesel | Gasoline | Electricity
|  | MMBtu | Gal | Gal | Gal | kWh
|  | 31509.0366 | 350 | 51858 | 33321 | 13516156
Emission Factors (kg CO2e per unit)
|  | Natural Gas | Propane | Diesel | Gasoline | Electricity (MB) | Electricity (LB)
|  | MMBtu | Gal | Gal | Gal | kWh | kWh
|  | 53.1145 | 5.7408 | 10.2427 | 8.8118 | 0.36671 | 0.36594
GHG Emission (kg CO2e)
|  | Natural Gas | Propane | Diesel | Gasoline | Electricity (MB) | Electricity (LB) | Fugitive Emissions
|  | kg CO2e | kg CO2e | kg CO2e | kg CO2e | kg CO2e | kg CO2e | kg CO2e
|  | 1673586.7245 | 2009.2835 | 531164.8994 | 293619.3206 | 4956467.9135 | 4946087.0061 | 527096.6882
[7 empty] | Market-Based GHG Emissions (kg CO2e): | 7983944.8298
[7 empty] | Location-Based GHG Emission (kg CO2e): | 7973563.9224
GHG Emission Factor & References
| Grid Electricity Emission Factors | Total Output Emission Factors
|  | CO2 Factor | CH4 Factor | N2O Factor | CH4 GWP (AR5) | N2O GWP (AR5) | lb CO2e per MWh | kg CO2e per kWh
| eGRID Subregion Name | (lb / MWh) | (lb / MWh) | (lb / MWh)
| SRMV Location-Based1 | 806.755 | 0.043 | 0.006 | 28 | 265 | 806.7578 | 0.36594
| SRMV Market-Based2 | 808.4482 | 0.04309 | 0.0060126 | 28 | 265 | 808.451 | 0.36671
1US EPA eGRID 2019 Subregion Output Emission Rates. 2021-02-23. https://www.epa.gov/egrid/summary-data
2US EPA eGRID 2019 Subregion Output Emission Rates. 2021-02-23 https://www.epa.gov/egrid/summary-data adjusted per Green-E 2021 Residual Grid Emission Rates. 2021-04-14. https://www.green-e.org/2021-residual-mix
Non-Baseload Emission Factors
| Grid Electricity Emission Factors | CO2 Factor | CH4 Factor | N2O Factor | CH4 GWP (AR5) | N2O GWP (AR5) | lb CO2e per MWh | kg CO2e per kWh
|  | (lb / MWh) | (lb / MWh) | (lb / MWh)
| SRMV Location-Based3 | 1200.137 | 0.068 | 0.01 | 28 | 265 | 1200.1416 | 0.54437
3US EPA eGRID 2019 Subregion Output Emission Rates. 2021-02-23. https://www.epa.gov/egrid/summary-data. Non-Baseload Factor used to estimate GHG emissions reductions on the grid from changes in electricity use.
| Stationary Combustion GHG Factors4 | kg CO2 per gallon | g CH4 per gallon | g N2O per gallon | CH4 GWP (AR5) | N2O GWP (AR5) | kg CO2e per gallon
| Distillate Fuel Oil No. 2 | 10.21 | 0.41 | 0.08 | 28 | 265 | 10.2427
| Motor Gasoline | 8.78 | 0.38 | 0.08 | 28 | 265 | 8.8118
| Propane | 5.72 | 0.27 | 0.05 | 28 | 265 | 5.7408
4US EPA Center for Corporate Climate Leadership. GHG Emission Factors Hub. Last Updated September 12, 2023. Stationary Combustion GHG Factors. Calculated CO2e savings using CH4 and N2O GWP from AR5.
| Stationary Combustion GHG Factors5 | kg CO2 per mmBtu | g CH4 per mmBtu | g N2O per mmBtu | CH4 GWP (AR5) | N2O GWP (AR5) | kg CO2e per MMBtu
| Natural Gas | 53.06 | 1 | 0.1 | 28 | 265 | 53.1145
5US EPA Center for Corporate Climate Leadership. GHG Emission Factors Hub. Last Updated September 12, 2023. Stationary Combustion GHG Factors. Calculated CO2e savings using CH4 and N2O GWP from AR5.

## Emission Factors Hub (hidden)
Emission Factors for Greenhouse Gas Inventories
Last Modified: 12 September 2023
Blue text indicates an update from the 2022 version of this document.
Typically, greenhouse gas emissions are reported in units of carbon dioxide equivalent (CO2e). Gases are converted to CO2e by multiplying by their global warming potential (GWP). The emission factors listed in this document have not been converted to CO2e. To do so, multiply the emissions by the corresponding GWP listed in the table below.
|  | Gas | 100-Year GWP
|  | CH4 | 25
|  | N2O | 298
Source: Intergovernmental Panel on Climate Change (IPCC), Fourth Assessment Report (AR4), 2007. See the source note to Table 11 for further explanation.
Table 1 | Stationary Combustion
| Fuel Type | Heat Content (HHV) | CO2 Factor | CH4 Factor | N2O Factor | CO2 Factor | CH4 Factor | N2O Factor
|  | mmBtu per short ton | kg CO2 per mmBtu | g CH4 per mmBtu | g N2O per mmBtu | kg CO2 per short ton | g CH4 per short ton | g N2O per short ton
Coal and Coke
| Anthracite Coal | 25.09 | 103.69 | 11 | 1.6 | 2602 | 276 | 40
| Bituminous Coal | 24.93 | 93.28 | 11 | 1.6 | 2325 | 274 | 40
| Sub-bituminous Coal | 17.25 | 97.17 | 11 | 1.6 | 1676 | 190 | 28
| Lignite Coal | 14.21 | 97.72 | 11 | 1.6 | 1389 | 156 | 23
| Mixed (Commercial Sector) | 21.39 | 94.27 | 11 | 1.6 | 2016 | 235 | 34
| Mixed (Electric Power Sector) | 19.73 | 95.52 | 11 | 1.6 | 1885 | 217 | 32
| Mixed (Industrial Coking) | 26.28 | 93.9 | 11 | 1.6 | 2468 | 289 | 42
| Mixed (Industrial Sector) | 22.35 | 94.67 | 11 | 1.6 | 2116 | 246 | 36
| Coal Coke | 24.8 | 113.67 | 11 | 1.6 | 2819 | 273 | 40
Other Fuels - Solid
| Municipal Solid Waste | 9.95 | 90.7 | 32 | 4.2 | 902 | 318 | 42
| Petroleum Coke (Solid) | 30 | 102.41 | 32 | 4.2 | 3072 | 960 | 126
| Plastics | 38 | 75 | 32 | 4.2 | 2850 | 1216 | 160
| Tires | 28 | 85.97 | 32 | 4.2 | 2407 | 896 | 118
Biomass Fuels - Solid
| Agricultural Byproducts | 8.25 | 118.17 | 32 | 4.2 | 975 | 264 | 35
| Peat | 8 | 111.84 | 32 | 4.2 | 895 | 256 | 34
| Solid Byproducts | 10.39 | 105.51 | 32 | 4.2 | 1096 | 332 | 44 | HARBOR CALCULATIONS IN GREEN
| Wood and Wood Residuals | 17.48 | 93.8 | 7.2 | 3.6 | 1640 | 126 | 63
|  | mmBtu per scf | kg CO2 per mmBtu | g CH4 per mmBtu | g N2O per mmBtu | kg CO2 per scf | g CH4 per scf | g N2O per scf
| Natural Gas | [8 empty] | kg CO2e per mmBtu
| Natural Gas | 0.001026 | 53.06 | 1 | 0.1 | 0.05444 | 0.00103 | 0.0001 | Natural Gas | 53.1148
Other Fuels - Gaseous
| Blast Furnace Gas | 9.2e-05 | 274.32 | 0.022 | 0.1 | 0.02524 | 2e-06 | 9e-06
| Coke Oven Gas | 0.000599 | 46.85 | 0.48 | 0.1 | 0.02806 | 0.000288 | 6e-05
| Fuel Gas | 0.001388 | 59 | 3 | 0.6 | 0.08189 | 0.004164 | 0.000833
| Propane Gas | 0.002516 | 61.46 | 3 | 0.6 | 0.15463 | 0.007548 | 0.00151
Biomass Fuels - Gaseous
| Landfill Gas | 0.000485 | 52.07 | 3.2 | 0.63 | 0.025254 | 0.001552 | 0.000306
| Other Biomass Gases | 0.000655 | 52.07 | 3.2 | 0.63 | 0.034106 | 0.002096 | 0.000413
|  | mmBtu per gallon | kg CO2 per mmBtu | g CH4 per mmBtu | g N2O per mmBtu | kg CO2 per gallon | g CH4 per gallon | g N2O per gallon
Petroleum Products
| Asphalt and Road Oil | 0.158 | 75.36 | 3 | 0.6 | 11.91 | 0.47 | 0.09
| Aviation Gasoline | 0.12 | 69.25 | 3 | 0.6 | 8.31 | 0.36 | 0.07
| Butane | 0.103 | 64.77 | 3 | 0.6 | 6.67 | 0.31 | 0.06
| Butylene | 0.105 | 68.72 | 3 | 0.6 | 7.22 | 0.32 | 0.06
| Crude Oil | 0.138 | 74.54 | 3 | 0.6 | 10.29 | 0.41 | 0.08
| Distillate Fuel Oil No. 1 | 0.139 | 73.25 | 3 | 0.6 | 10.18 | 0.42 | 0.08
| Distillate Fuel Oil No. 2 | 0.138 | 73.96 | 3 | 0.6 | 10.21 | 0.41 | 0.08
| Distillate Fuel Oil No. 4 | 0.146 | 75.04 | 3 | 0.6 | 10.96 | 0.44 | 0.09
| Ethane | 0.068 | 59.6 | 3 | 0.6 | 4.05 | 0.2 | 0.04
| Ethylene | 0.058 | 65.96 | 3 | 0.6 | 3.83 | 0.17 | 0.03
| Heavy Gas Oils | 0.148 | 74.92 | 3 | 0.6 | 11.09 | 0.44 | 0.09
| Isobutane | 0.099 | 64.94 | 3 | 0.6 | 6.43 | 0.3 | 0.06
| Isobutylene | 0.103 | 68.86 | 3 | 0.6 | 7.09 | 0.31 | 0.06
| Kerosene | 0.135 | 75.2 | 3 | 0.6 | 10.15 | 0.41 | 0.08
| Kerosene-Type Jet Fuel | 0.135 | 72.22 | 3 | 0.6 | 9.75 | 0.41 | 0.08
| Liquefied Petroleum Gases (LPG) | 0.092 | 61.71 | 3 | 0.6 | 5.68 | 0.28 | 0.06
| Lubricants | 0.144 | 74.27 | 3 | 0.6 | 10.69 | 0.43 | 0.09
| Motor Gasoline | 0.125 | 70.22 | 3 | 0.6 | 8.78 | 0.38 | 0.08
| Naphtha (<401 deg F) | 0.125 | 68.02 | 3 | 0.6 | 8.5 | 0.38 | 0.08
| Natural Gasoline | 0.11 | 66.88 | 3 | 0.6 | 7.36 | 0.33 | 0.07
| Other Oil (>401 deg F) | 0.139 | 76.22 | 3 | 0.6 | 10.59 | 0.42 | 0.08
| Pentanes Plus | 0.11 | 70.02 | 3 | 0.6 | 7.7 | 0.33 | 0.07
| Petrochemical Feedstocks | 0.125 | 71.02 | 3 | 0.6 | 8.88 | 0.38 | 0.08
| Propane | 0.091 | 62.87 | 3 | 0.6 | 5.72 | 0.27 | 0.05
| Propylene | 0.091 | 67.77 | 3 | 0.6 | 6.17 | 0.27 | 0.05
| Residual Fuel Oil No. 5 | 0.14 | 72.93 | 3 | 0.6 | 10.21 | 0.42 | 0.08
| Residual Fuel Oil No. 6 | 0.15 | 75.1 | 3 | 0.6 | 11.27 | 0.45 | 0.09
| Special Naphtha | 0.125 | 72.34 | 3 | 0.6 | 9.04 | 0.38 | 0.08
| Unfinished Oils | 0.139 | 74.54 | 3 | 0.6 | 10.36 | 0.42 | 0.08
| Used Oil | 0.138 | 74 | 3 | 0.6 | 10.21 | 0.41 | 0.08
Biomass Fuels - Liquid
| Biodiesel (100%) | 0.128 | 73.84 | 1.1 | 0.11 | 9.45 | 0.14 | 0.01
| Ethanol (100%) | 0.084 | 68.44 | 1.1 | 0.11 | 5.75 | 0.09 | 0.01
| Rendered Animal Fat | 0.125 | 71.06 | 1.1 | 0.11 | 8.88 | 0.14 | 0.01
| Vegetable Oil | 0.12 | 81.55 | 1.1 | 0.11 | 9.79 | 0.13 | 0.01
Biomass Fuels - Kraft Pulping Liquor, by Wood Furnish
| North American Softwood |  | 94.4 | 1.9 | 0.42
| North American Hardwood |  | 93.7 | 1.9 | 0.42
| Bagasse |  | 95.5 | 1.9 | 0.42
| Bamboo |  | 93.7 | 1.9 | 0.42
| Straw |  | 95.1 | 1.9 | 0.42
Source:
Federal Register EPA; 40 CFR Part 98; e-CFR, (see link below). Table C-1 and Table C-2 (78 FR 71950, Nov. 29, 2013, as amended at 81 FR 89252, Dec. 9, 2016), Table AA-1 (78 FR 71965, Nov. 29, 2013).
https://www.ecfr.gov/current/title-40/chapter-I/subchapter-C/part-98
Notes:
Emission factors are per unit of heat content using higher heating values (HHV). If heat content is available from the fuel supplier, it is preferable to use that value. If not, default heat contents are provided.
The factors represented in the table above represent combustion emissions only (tank-to-wheel) and do not represent upstream emissions or well-to-wheel emissions.
Table 2 | Mobile Combustion CO2
| Fuel Type | kg CO2 per unit | Unit
| Aviation Gasoline | 8.31 | gallon
| Biodiesel (100%) | 9.45 | gallon
| Compressed Natural Gas (CNG) | 0.05444 | scf
| Diesel Fuel | 10.21 | gallon
| Ethanol (100%) | 5.75 | gallon
| Kerosene-Type Jet Fuel | 9.75 | gallon
| Liquefied Natural Gas (LNG) | 4.5 | gallon
| Liquefied Petroleum Gases (LPG) | 5.68 | gallon
| Motor Gasoline | 8.78 | gallon
| Residual Fuel Oil | 11.27 | gallon
Source:
Federal Register EPA; 40 CFR Part 98; e-CFR, (see link below). Table C-1 (78 FR 71950, Nov. 29, 2013, as amended at 81 FR 89252, Dec. 9, 2016)
https://www.ecfr.gov/current/title-40/chapter-I/subchapter-C/part-98
Notes:
LNG: The factor was developed based on the CO2 factor for Natural Gas factor and LNG fuel density from GREET1_2022.xlsx Model, Argonne National Laboratory (Fuel_Specs worksheet).
The factors represented in the table above represent combustion emissions only (tank-to-wheel) and do not represent upstream emissions or well-to-wheel emissions.
Table 3 | Mobile Combustion CH4 and N2O for On-Road Gasoline Vehicles
| Vehicle Type | Year | CH4 Factor (g / mile) | N2O Factor (g / mile)
| Gasoline Passenger Cars | 1973-1974 | 0.1696 | 0.0197
|  | 1975 | 0.1423 | 0.0443
|  | 1976-1977 | 0.1406 | 0.0458
|  | 1978-1979 | 0.1389 | 0.0473
|  | 1980 | 0.1326 | 0.0499
|  | 1981 | 0.0802 | 0.0626
|  | 1982 | 0.0795 | 0.0627
|  | 1983 | 0.0782 | 0.063
|  | 1984-1993 | 0.0704 | 0.0647
|  | 1994 | 0.0617 | 0.0603
|  | 1995 | 0.0531 | 0.056
|  | 1996 | 0.0434 | 0.0503
|  | 1997 | 0.0337 | 0.0446
|  | 1998 | 0.024 | 0.0389
|  | 1999 | 0.0215 | 0.0355
|  | 2000 | 0.0175 | 0.0304
|  | 2001 | 0.0105 | 0.0212
|  | 2002 | 0.0102 | 0.0207
|  | 2003 | 0.0095 | 0.0181
|  | 2004 | 0.0078 | 0.0085
|  | 2005 | 0.0075 | 0.0067
|  | 2006 | 0.0076 | 0.0075
|  | 2007 | 0.0072 | 0.0052
|  | 2008 | 0.0072 | 0.0049
|  | 2009 | 0.0071 | 0.0046
|  | 2010 | 0.0071 | 0.0046
|  | 2011 | 0.0071 | 0.0046
|  | 2012 | 0.0071 | 0.0046
|  | 2013 | 0.0071 | 0.0046
|  | 2014 | 0.0071 | 0.0046
|  | 2015 | 0.0068 | 0.0042
|  | 2016 | 0.0065 | 0.0038
|  | 2017 | 0.0054 | 0.0018
|  | 2018 | 0.0052 | 0.0016
|  | 2019 | 0.0051 | 0.0015
|  | 2020 | 0.005 | 0.0014
| Gasoline Light-Duty Trucks | 1973-1974 | 0.1908 | 0.0218
| (Vans, Pickup Trucks, SUVs) | 1975 | 0.1634 | 0.0513
|  | 1976 | 0.1594 | 0.0555
|  | 1977-1978 | 0.1614 | 0.0534
|  | 1979-1980 | 0.1594 | 0.0555
|  | 1981 | 0.1479 | 0.066
|  | 1982 | 0.1442 | 0.0681
|  | 1983 | 0.1368 | 0.0722
|  | 1984 | 0.1294 | 0.0764
|  | 1985 | 0.122 | 0.0806
|  | 1986 | 0.1146 | 0.0848
|  | 1987-1993 | 0.0813 | 0.1035
|  | 1994 | 0.0646 | 0.0982
|  | 1995 | 0.0517 | 0.0908
|  | 1996 | 0.0452 | 0.0871
|  | 1997 | 0.0452 | 0.0871
|  | 1998 | 0.0412 | 0.0787
|  | 1999 | 0.0333 | 0.0618
|  | 2000 | 0.034 | 0.0631
|  | 2001 | 0.0221 | 0.0379
|  | 2002 | 0.0242 | 0.0424
|  | 2003 | 0.0221 | 0.0373
|  | 2004 | 0.0115 | 0.0088
|  | 2005 | 0.0105 | 0.0064
|  | 2006 | 0.0108 | 0.008
|  | 2007 | 0.0103 | 0.0061
|  | 2008 | 0.0095 | 0.0036
|  | 2009 | 0.0095 | 0.0036
|  | 2010 | 0.0095 | 0.0035
|  | 2011 | 0.0096 | 0.0034
|  | 2012 | 0.0096 | 0.0033
|  | 2013 | 0.0095 | 0.0035
|  | 2014 | 0.0095 | 0.0033
|  | 2015 | 0.0094 | 0.0031
|  | 2016 | 0.0091 | 0.0029
|  | 2017 | 0.0084 | 0.0018
|  | 2018 | 0.0081 | 0.0015
|  | 2019 | 0.008 | 0.0013
|  | 2020 | 0.0079 | 0.0012
| Gasoline Heavy-Duty Vehicles | ≤1980 | 0.4604 | 0.0497
|  | 1981-1984 | 0.4492 | 0.0538
|  | 1985-1986 | 0.409 | 0.0515
|  | 1987 | 0.3675 | 0.0849
|  | 1988-1989 | 0.3492 | 0.0933
|  | 1990-1995 | 0.3246 | 0.1142
|  | 1996 | 0.1278 | 0.168
|  | 1997 | 0.0924 | 0.1726
|  | 1998 | 0.0655 | 0.175
|  | 1999 | 0.0648 | 0.1724
|  | 2000 | 0.063 | 0.166
|  | 2001 | 0.0577 | 0.1468
|  | 2002 | 0.0634 | 0.1673
|  | 2003 | 0.0602 | 0.1553
|  | 2004 | 0.0298 | 0.0164
|  | 2005 | 0.0297 | 0.0083
|  | 2006 | 0.0299 | 0.0241
|  | 2007 | 0.0322 | 0.0015
|  | 2008 | 0.034 | 0.0015
|  | 2009 | 0.0339 | 0.0015
|  | 2010 | 0.032 | 0.0015
|  | 2011 | 0.0304 | 0.0015
|  | 2012 | 0.0313 | 0.0015
|  | 2013 | 0.0313 | 0.0015
|  | 2014 | 0.0315 | 0.0015
|  | 2015 | 0.0332 | 0.0021
|  | 2016 | 0.0321 | 0.0061
|  | 2017 | 0.0329 | 0.0084
|  | 2018 | 0.0326 | 0.0082
|  | 2019 | 0.033 | 0.0091
|  | 2020 | 0.0328 | 0.0098
| Gasoline Motorcycles | 1960-1995 | 0.007 | 0.0083
|  | 1996-2005 | 0 | 0
|  | 2006-2020 | 0.007 | 0.0083
Source: EPA (2022) Inventory of U.S. Greenhouse Gas Emissions and Sinks: 1990-2020 (Annexes). All values are calculated from Tables A-84 through A-88.
Notes: Emission factor updates due to a methodology change. The factors represented in the table above represent combustion emissions only (tank-to-wheel) and do not represent upstream emissions or well-to-wheel emissions.
Table 4 | Mobile Combustion CH4 and N2O for On-Road Diesel and Alternative Fuel Vehicles
| Vehicle Type | Fuel Type | Vehicle Year | CH4 Factor (g / mile) | N2O Factor (g / mile)
| Passenger Cars | Diesel | 1960-1982 | 0.0006 | 0.0012
|  |  | 1983-2006 | 0.0005 | 0.001
|  |  | 2007-2020 | 0.0302 | 0.0192
| Light-Duty Trucks | Diesel | 1960-1982 | 0.0011 | 0.0017
|  |  | 1983-2006 | 0.0009 | 0.0014
|  |  | 2007-2020 | 0.029 | 0.0214
| Medium- and Heavy-Duty Vehicles | Diesel | 1960-2006 | 0.0051 | 0.0048
|  |  | 2007-2020 | 0.0095 | 0.0431
| Light-Duty Cars | Methanol |  | 0.015 | 0.004
|  | Ethanol |  | 0.015 | 0.004
|  | CNG |  | 0.146 | 0.004
|  | LPG |  | 0.015 | 0.004
|  | Biodiesel |  | 0.03 | 0.019
| Light-Duty Trucks | Ethanol |  | 0.016 | 0.005
|  | CNG |  | 0.158 | 0.005
|  | LPG |  | 0.016 | 0.005
|  | LNG |  | 0.158 | 0.005
|  | Biodiesel |  | 0.029 | 0.021
| Medium-Duty Trucks | CNG |  | 1.829 | 0.001
|  | LPG |  | 0.009 | 0.018
|  | LNG |  | 1.829 | 0.001
|  | Biodiesel |  | 0.009 | 0.043
| Heavy-Duty Trucks | Methanol |  | 0.075 | 0.028
|  | Ethanol |  | 0.075 | 0.028
|  | CNG |  | 0.921 | 0
|  | LPG |  | 0.003 | 0.007
|  | LNG |  | 0.921 | 0
|  | Biodiesel |  | 0.009 | 0.043
| Buses | Methanol |  | 0.102 | 0.047
|  | Ethanol |  | 0.102 | 0.047
|  | CNG |  | 2.787 | 0.001
|  | LPG |  | 0.01 | 0.011
|  | LNG |  | 2.787 | 0.001
|  | Biodiesel |  | 0.009 | 0.043
Source: EPA (2022) Inventory of U.S. Greenhouse Gas Emissions and Sinks: 1990-2020 (Annexes). All values are calculated from Tables A-88 through A-90.
https://www.epa.gov/ghgemissions/inventory-us-greenhouse-gas-emissions-and-sinks
Notes: Emission factor updates due to a methodology change. The factors represented in the table above represent combustion emissions only (tank-to-wheel) and do not represent upstream emissions or well-to-wheel emissions.
Table 5 | Mobile Combustion CH4 and N2O for Non-Road Vehicles
| Vehicle Type | Fuel Type | CH4 Factor (g / gallon) | N2O Factor (g / gallon)
| Ships and Boats | Residual Fuel Oil | 1.11 | 0.32
|  | Gasoline (2 stroke) | 4.61 | 0.08
|  | Gasoline (4 stroke) | 2.25 | 0.01
|  | Diesel | 6.41 | 0.17
| Locomotives | Diesel | 0.8 | 0.26
| Aircraft | Jet Fuel | 0 | 0.3
|  | Aviation Gasoline | 7.06 | 0.11
| Agricultural EquipmentA | Gasoline (2 stroke) | 6.92 | 0.47
|  | Gasoline (4 stroke) | 1.93 | 1.2
|  | Gasoline Off-Road Trucks | 1.93 | 1.2
|  | Diesel Equipment | 1.27 | 1.07
|  | Diesel Off-Road Trucks | 0.91 | 0.56
|  | LPG | 0.33 | 0.94
| Construction/Mining EquipmentB | Gasoline (2 stroke) | 7.98 | 0.12
|  | Gasoline (4 stroke) | 2.85 | 1.47
|  | Gasoline Off-Road Trucks | 2.85 | 1.48
|  | Diesel Equipment | 1.01 | 0.94
|  | Diesel Off-Road Trucks | 0.91 | 0.56
|  | LPG | 0.59 | 0.5
| Lawn and Garden Equipment | Gasoline (2 stroke) | 7.28 | 0.31
|  | Gasoline (4 stroke) | 2.99 | 1.49
|  | Diesel | 0.67 | 0.49
|  | LPG | 0.41 | 0.63
| Airport Equipment | Gasoline | 1.03 | 1.07
|  | Diesel | 1.88 | 1.16
|  | LPG | 0.35 | 0.89
| Industrial/Commercial Equipment | Gasoline (2 stroke) | 7.12 | 0.5
|  | Gasoline (4 stroke) | 2.74 | 1.54
|  | Diesel | 0.41 | 0.6
|  | LPG | 0.45 | 0.64
| Logging Equipment | Gasoline (2 stroke) | 9.68 | 0
|  | Gasoline (4 stroke) | 3.24 | 2.05
|  | Diesel | 0.48 | 1.27
| Railroad Equipment | Gasoline | 3.24 | 1.81
|  | Diesel | 0.38 | 0.95
|  | LPG | 1.99 | 0.01
| Recreational Equipment | Gasoline (2 stroke) | 17.61 | 0.11
|  | Gasoline (4 stroke) | 2.87 | 1.5
|  | Diesel | 0.73 | 0.66
|  | LPG | 0.43 | 0.6
Source: EPA (2022) Inventory of U.S. Greenhouse Gas Emissions and Sinks: 1990-2020 (Annexes). All values are calculated from Tables A-91 through A-92.
https://www.epa.gov/ghgemissions/inventory-us-greenhouse-gas-emissions-and-sinks
Notes: Emission factor updates due to a methodology change. The factors represented in the table above represent combustion emissions only (tank-to-wheel) and do not represent upstream emissions or well-to-wheel emissions. A Includes equipment, such as tractors and combines, as well as fuel consumption from trucks that are used off-road in agriculture. B Includes equipment, such as cranes, dumpers, and excavators, as well as fuel consumption from trucks that are used off-road in construction.
Table 6 | Electricity
|  |  | Total Output Emission Factors |  |  | Non-Baseload Emission Factors
| eGRID Subregion Acronym | eGRID Subregion Name | CO2 Factor | CH4 Factor | N2O Factor | CO2 Factor | CH4 Factor | N2O Factor
|  |  | (lb / MWh) | (lb / MWh) | (lb / MWh) | (lb / MWh) | (lb / MWh) | (lb / MWh)
| AKGD | AKGD (ASCC Alaska Grid) | 1067.7 | 0.091 | 0.012 | 1229.6 | 0.12 | 0.016
| AKMS | AKMS (ASCC Miscellaneous) | 485.2 | 0.025 | 0.004 | 1531.3 | 0.066 | 0.012
| AZNM | AZNM (WECC Southwest) | 819.7 | 0.052 | 0.007 | 1227.6 | 0.067 | 0.009 | lbs to kgs
| CAMX | CAMX (WECC California) | 531.7 | 0.031 | 0.004 | 1047.5 | 0.049 | 0.006 | 0.45359
| ERCT | ERCT (ERCOT All) | 813.6 | 0.054 | 0.008 | 1177.4 | 0.065 | 0.009
| FRCC | FRCC (FRCC All) | 832.9 | 0.053 | 0.007 | 1016.5 | 0.054 | 0.007
| HIMS | HIMS (HICC Miscellaneous) | 1134.4 | 0.135 | 0.021 | 1649.4 | 0.176 | 0.027
| HIOA | HIOA (HICC Oahu) | 1633.1 | 0.176 | 0.027 | 1784 | 0.172 | 0.027
| MROE | MROE (MRO East) | 1582.1 | 0.148 | 0.022 | 1555.9 | 0.133 | 0.019
| MROW | MROW (MRO West) | 995.8 | 0.107 | 0.015 | 1808.3 | 0.183 | 0.026
| NEWE | NEWE (NPCC New England) | 539.4 | 0.072 | 0.009 | 900.5 | 0.073 | 0.009 | Total Output Emission Factors (Location Based Approach)
| NWPP | NWPP (WECC Northwest) | 634.6 | 0.058 | 0.008 | 1545.7 | 0.139 | 0.02 |  | lb CO2e per MWh | lb CO2e per kWh | kg CO2e per kWh
| NYCW | NYCW (NPCC NYC/Westchester) | 816.8 | 0.019 | 0.002 | 930.8 | 0.02 | 0.002 | SRMV | 775.488 | 0.77549 | 0.35176
| NYLI | NYLI (NPCC Long Island) | 1210.9 | 0.126 | 0.016 | 1317.3 | 0.04 | 0.005
| NYUP | NYUP (NPCC Upstate NY) | 233.1 | 0.015 | 0.002 | 880.7 | 0.047 | 0.006
| PRMS | PRMS (Puerto Rico Miscellaneous) | 1558 | 0.081 | 0.013 | 1618.1 | 0.06 | 0.011 | Total Non-Baseload Emission Factors (Location Based Approach)
| RFCE | RFCE (RFC East) | 672.8 | 0.049 | 0.007 | 1357.3 | 0.106 | 0.015 |  | lb CO2e per MWh | lb CO2e per kWh | kg CO2e per kWh
| RFCM | RFCM (RFC Michigan) | 1214.1 | 0.115 | 0.016 | 1717 | 0.16 | 0.023 | SRMV | 1181.332 | 1.1813 | 0.53584
| RFCW | RFCW (RFC West) | 1046.1 | 0.095 | 0.014 | 1798.8 | 0.172 | 0.025
| RMPA | RMPA (WECC Rockies) | 1158.9 | 0.109 | 0.016 | 1614.2 | 0.128 | 0.018 | Total Output Emission Factors (Market Based using eGRID 2020 data)
| SPNO | SPNO (SPP North) | 991.7 | 0.108 | 0.016 | 1926.2 | 0.204 | 0.029 |  | LB kg CO2e per kWh | % Difference | MB kg CO2e per kWh
| SPSO | SPSO (SPP South) | 1031.6 | 0.08 | 0.012 | 1584.6 | 0.116 | 0.017 | SRMV (SERC Mississippi Valley) | 0.35176 | 0.034% | 0.35187
| SRMV | SRMV (SERC Mississippi Valley) | 772.7 | 0.04 | 0.006 | 1177 | 0.066 | 0.009
| SRMW | SRMW (SERC Midwest) | 1543 | 0.171 | 0.025 | 1763.2 | 0.179 | 0.026
| SRSO | SRSO (SERC South) | 891.9 | 0.067 | 0.01 | 1384.6 | 0.101 | 0.015
| SRTV | SRTV (SERC Tennessee Valley) | 931.6 | 0.087 | 0.013 | 1636.2 | 0.151 | 0.022
| SRVC | SRVC (SERC Virginia/Carolina) | 639.7 | 0.052 | 0.007 | 1357 | 0.116 | 0.016
| US Average | US Average | 852.3 | 0.071 | 0.01 | 1410 | 0.11 | 0.016
Source: EPA eGRID2021, February 2023 (Table 1. Subregion Output Emission Rates)
https://www.epa.gov/egrid/download-data
Notes:
Total output emission factors can be used as default factors for estimating GHG emissions from electricity use when developing a carbon footprint or emissions inventory. Annual non-baseload output emission factors should not be used when developing a carbon footprint or emissions inventory, but can be used to estimate GHG emissions reductions on the grid from changes in electricity use. For technical information, reference the EPA's eGRID Technical Guide
https://www.epa.gov/system/files/documents/2023-01/eGRID2021_technical_guide.pdf
The factors represented in the table above represent combustion emissions only (tank-to-wheel) and do not represent upstream emissions or well-to-wheel emissions.
Table 7 | Steam and Heat
|  | CO2 Factor (kg / mmBtu) | CH4 Factor (g / mmBtu) | N2O Factor (g / mmBtu)
| Steam and Heat | 66.33 | 1.25 | 0.125
Notes:
Emission factors are per mmBtu of steam or heat purchased. These factors assume natural gas fuel is used to generate steam or heat at 80 percent thermal efficiency.
The factors represented in the table above represent combustion emissions only (tank-to-wheel) and do not represent upstream emissions or well-to-wheel emissions.
Scope 3 Emission Factors
Scope 3 emission factors provided below are aligned with the Greenhouse Gas Protocol Technical Guidance for Calculating Scope 3 Emissions, version 1.0 (Scope 3 Calculation Guidance). Where applicable, the specific calculation method is referenced. Refer to the Scope 3 Calculation Guidance for more information (http://www.ghgprotocol.org/scope-3-technical-calculation-guidance)
Table 8 | Scope 3 Category 4: Upstream Transportation and Distribution and Category 9: Downstream Transportation and Distribution
These factors are intended for use in the distance-based method defined in the Scope 3 Calculation Guidance. If fuel data are available, then the fuel-based method should be used, with factors from Tables 2 through 5.
| Vehicle Type | CO2 Factor (kg / unit) | CH4 Factor (g / unit) | N2O Factor (g / unit) | Units
| Medium- and Heavy-Duty Truck | 1.387 | 0.013 | 0.038 | vehicle-mile
| Passenger Car A | 0.313 | 0.008 | 0.007 | vehicle-mile
| Light-Duty Truck B | 0.467 | 0.013 | 0.012 | vehicle-mile
| Medium- and Heavy-Duty TruckC | 0.17 | 0.0016 | 0.0047 | ton-mile
| Rail | 0.021 | 0.0016 | 0.0005 | ton-mile
| Waterborne Craft | 0.044 | 0.0254 | 0.0011 | ton-mile
| Aircraft | 0.698 | 0 | 0.0215 | ton-mile
Source: CO2, CH4, and N2O emissions data for road vehicles are from Table 2-13 of the EPA (2022) Inventory of U.S. Greenhouse Gas Emissions and Sinks: 1990-2020. Vehicle-miles and passenger-miles data for road vehicles are from Table VM-1 of the Federal Highway Administration Highway Statistics 2020. CO2e emissions data for non-road vehicles are based on Table A-107 of the EPA (2022) Inventory of U.S. Greenhouse Gas Emissions and Sinks: 1990-2020, which are distributed into CO2, CH4, and N2O emissions based on fuel/vehicle emission factors. Freight ton-mile data are from Table 1-50 of the Bureau of Transportation Statistics, National Transportation Statistics for 2021 (2020 data).
Notes: Vehicle-mile factors are appropriate to use when the entire vehicle is dedicated to transporting the reporting company's product. Ton-mile factors are appropriate when the vehicle is shared with products from other companies. The factors represented in the table above represent combustion emissions only (tank-to-wheel) and do not represent upstream emissions or well-to-wheel emissions. A Passenger car: includes passenger cars, minivans, SUVs, and small pickup trucks (vehicles with wheelbase less than 121 inches). B Light-duty truck: includes full-size pickup trucks, full-size vans, and extended-length SUVs (vehicles with wheelbase greater than 121 inches). C Medium- and Heavy-Duty Truck: includes Combination Trucks and single frame trucks that have 2-Axles and at least 6 tires or a gross vehicle weight rating exceeding 10,000 lbs.
Table 9 | Scope 3 Category 5: Waste Generated in Operations and Category 12: End-of-Life Treatment of Sold Products
These factors are intended for use in the waste-type-specific method or the average-data method defined in the Scope 3 Calculation Guidance for category 5 and category 12. Choose the appropriate material and disposal method from the table below. For the average-data method, use one of the mixed material types, such as mixed MSW.
Metric Tons CO2e / Short Ton Material
| Material | RecycledA | LandfilledB | CombustedC | CompostedD | Anaerobically Digested (Dry Digestate with Curing) | Anaerobically Digested (Wet Digestate with Curing)
| Aluminum Cans | 0.06 | 0.02 | 0.01 | NA | NA | NA
| Aluminum Ingot | 0.04 | 0.02 | 0.01 | NA | NA | NA
| Steel Cans | 0.32 | 0.02 | 0.01 | NA | NA | NA
| Copper Wire | 0.18 | 0.02 | 0.01 | NA | NA | NA
| Glass | 0.05 | 0.02 | 0.01 | NA | NA | NA
| HDPE | 0.21 | 0.02 | 2.8 | NA | NA | NA
| LDPE | NA | 0.02 | 2.8 | NA | NA | NA
| PET | 0.23 | 0.02 | 2.05 | NA | NA | NA
| LLDPE | NA | 0.02 | 2.8 | NA | NA | NA
| PP | NA | 0.02 | 2.8 | NA | NA | NA
| PS | NA | 0.02 | 3.02 | NA | NA | NA
| PVC | NA | 0.02 | 1.26 | NA | NA | NA
| PLA | NA | 0.02 | 0.01 | 0.17 | NA | NA
| Corrugated Containers | 0.11 | 0.9 | 0.05 | NA | NA | NA
| Magazines/Third-class mail | 0.02 | 0.42 | 0.05 | NA | NA | NA
| Newspaper | 0.02 | 0.35 | 0.05 | NA | NA | NA
| Office Paper | 0.02 | 1.25 | 0.05 | NA | NA | NA
| Phonebooks | 0.04 | 0.35 | 0.05 | NA | NA | NA
| Textbooks | 0.04 | 1.25 | 0.05 | NA | NA | NA
| Dimensional Lumber | 0.09 | 0.17 | 0.05 | NA | NA | NA
| Medium-density Fiberboard | 0.15 | 0.07 | 0.05 | NA | NA | NA
| Food Waste (non-meat) | NA | 0.58 | 0.05 | 0.15 | 0.14 | 0.11
| Food Waste (meat only) | NA | 0.58 | 0.05 | NA | 0.14 | 0.11
| Beef | NA | 0.58 | 0.05 | 0.15 | 0.14 | 0.11
| Poultry | NA | 0.58 | 0.05 | 0.15 | 0.14 | 0.11
| Grains | NA | 0.58 | 0.05 | 0.15 | 0.14 | 0.11
| Bread | NA | 0.58 | 0.05 | 0.15 | 0.14 | 0.11
| Fruits and Vegetables | NA | 0.58 | 0.05 | 0.15 | 0.14 | 0.11
| Dairy Products | NA | 0.58 | 0.05 | 0.15 | 0.14 | 0.11
| Yard Trimmings | NA | 0.33 | 0.05 | 0.19 | 0.11 | NA
| Grass | NA | 0.26 | 0.05 | 0.19 | 0.09 | NA
| Leaves | NA | 0.26 | 0.05 | 0.19 | 0.13 | NA
| Branches | NA | 0.53 | 0.05 | 0.19 | 0.16 | NA
| Mixed Paper (general) | 0.07 | 0.8 | 0.05 | NA | NA | NA
| Mixed Paper (primarily residential) | 0.07 | 0.77 | 0.05 | NA | NA | NA
| Mixed Paper (primarily from offices) | 0.03 | 0.75 | 0.05 | NA | NA | NA
| Mixed Metals | 0.23 | 0.02 | 0.01 | NA | NA | NA
| Mixed Plastics | 0.22 | 0.02 | 2.34 | NA | NA | NA
| Mixed Recyclables | 0.09 | 0.68 | 0.11 | NA | NA | NA
| Food Waste | NA | 0.58 | 0.05 | 0.15 | NA | NA
| Mixed Organics | NA | 0.48 | 0.05 | 0.17 | NA | NA
| Mixed MSW | NA | 0.52 | 0.43 | NA | NA | NA
| Carpet | NA | 0.02 | 1.68 | NA | NA | NA
| Desktop CPUs | NA | 0.02 | 0.4 | NA | NA | NA
| Portable Electronic Devices | NA | 0.02 | 0.89 | NA | NA | NA
| Flat-panel Displays | NA | 0.02 | 0.74 | NA | NA | NA
| CRT Displays | NA | 0.02 | 0.64 | NA | NA | NA
| Electronic Peripherals | NA | 0.02 | 2.23 | NA | NA | NA
| Hard-copy Devices | NA | 0.02 | 1.92 | NA | NA | NA
| Mixed Electronics | NA | 0.02 | 0.87 | NA | NA | NA
| Clay Bricks | NA | 0.02 | NA | NA | NA | NA
| Concrete | 0.01 | 0.02 | NA | NA | NA | NA
| Fly Ash | 0.01 | 0.02 | NA | NA | NA | NA
| Tires | 0.1 | 0.02 | 2.21 | NA | NA | NA
| Asphalt Concrete | 0 | 0.02 | NA | NA | NA | NA
| Asphalt Shingles | 0.03 | 0.02 | 0.7 | NA | NA | NA
| Drywall | NA | 0.02 | NA | NA | NA | NA
| Fiberglass Insulation | 0.05 | 0.02 | NA | NA | NA | NA
| Vinyl Flooring | NA | 0.02 | 0.29 | NA | NA | NA
| Wood Flooring | NA | 0.18 | 0.08 | NA | NA | NA
Source: EPA, Office of Resource Conservation and Recovery (February 2016) Documentation for Greenhouse Gas Emission and Energy Factors used in the Waste Reduction Model (WARM). Factors from tables provided in the Management Practices Chapters and Background Chapters. WARM Version 15, November 2020 Update. Additional data provided by EPA, WARM-15 Background Data.
Notes: These factors do not include any avoided emissions impact from any of the disposal methods. All the factors presented here include transportation emissions, which are optional in the Scope 3 Calculation Guidance, with an assumed average distance traveled to the processing facility. AR4 GWPs are used to convert all waste emission factors into CO2e. A Recycling emissions include transport to recycling facility and sorting of recycled materials at material recovery facility. B Landfilling emissions include transport to landfill, equipment use at landfill and fugitive landfill CH4 emissions. Landfill CH4 is based on typical landfill gas collection practices and average landfill moisture conditions. C Combustion emissions include transport to combustion facility and combustion-related non-biogenic CO2 and N2O D Composting emissions include transport to composting facility, equipment use at composting facility and CH4 and N2O emissions during composting.
Table 10 | Scope 3 Category 6: Business Travel and Category 7: Employee Commuting
These factors are intended for use in the distance-based method defined in the Scope 3 Calculation Guidance. If fuel data are available, then the fuel-based method should be used, with factors from Tables 2 through 5.
| Vehicle Type | CO2 Factor (kg / unit) | CH4 Factor (g / unit) | N2O Factor (g / unit) | Units
| Passenger Car A | 0.313 | 0.008 | 0.007 | vehicle-mile
| Light-Duty Truck B | 0.467 | 0.013 | 0.012 | vehicle-mile
| Motorcycle | 0.178 | 0.111 | 0.019 | vehicle-mile
| Intercity Rail - Northeast Corridor C | 0.058 | 0.0055 | 0.0007 | passenger-mile
| Intercity Rail - Other Routes C | 0.15 | 0.0117 | 0.0038 | passenger-mile
| Intercity Rail - National Average C | 0.113 | 0.0092 | 0.0026 | passenger-mile
| Commuter Rail D | 0.135 | 0.0109 | 0.0027 | passenger-mile
| Transit Rail (i.e. Subway, Tram) E | 0.096 | 0.008 | 0.0011 | passenger-mile
| Bus | 0.055 | 0.0063 | 0.0011 | passenger-mile
| Air Travel - Short Haul (< 300 miles) | 0.207 | 0.0064 | 0.0066 | passenger-mile
| Air Travel - Medium Haul (>= 300 miles, < 2300 miles) | 0.129 | 0.0006 | 0.0041 | passenger-mile
| Air Travel - Long Haul (>= 2300 miles) | 0.163 | 0.0006 | 0.0052 | passenger-mile
Source: CO2, CH4, and N2O emissions data for highway vehicles are from Table 2-13 of the EPA (2022) Inventory of U.S. Greenhouse Gas Emissions and Sinks: 1990–2020. Vehicle-miles and passenger-miles data for highway vehicles are from Table VM-1 of the Federal Highway Administration Highway Statistics 2020. Fuel consumption data and passenger-miles data for rail are from Tables A.14 to A.16 and C.9 to C.11 of the Transportation Energy Data Book: Edition 40. Fuel consumption was converted to emissions by using fuel and electricity emission factors presented in the tables above. Intercity Rail factors from communication with Amtrak, March 2020. These are based on 2019 values. Air Travel factors from 2022 Guidelines to Defra / DECC's GHG Conversion Factors for Company Reporting. Version 2.0 June 2022.
Notes: The factors represented in the table above represent combustion emissions only (tank-to-wheel) and do not represent upstream emissions or well-to-wheel emissions. CH4 and N2O emission factor updates for motorcycle and bus due to a methodology change. A Passenger car: includes passenger cars, minivans, SUVs, and small pickup trucks (vehicles with wheelbase less than 121 inches). B Light-duty truck: includes full-size pickup trucks, full-size vans, and extended-length SUVs (vehicles with wheelbase greater than 121 inches). C Intercity rail: Amtrak long-distance rail between major cities. Northeast Corridor extends from Boston to Washington D.C. Other Routes are all routes outside the Northeast Corridor. D Commuter rail: rail service between a central city and adjacent suburbs (also called regional rail or suburban rail). E Transit rail: rail typically within an urban center, such as subways, elevated railways, metropolitan railways (metro), streetcars, trolley cars, and tramways.
Global Warming Potentials
Table 11 | Global Warming Potentials (GWPs)
| Gas | 100-Year GWP
| CO2 | 1
| CH4 | 25
| N2O | 298
| HFC-23 | 14800
| HFC-32 | 675
| HFC-41 | 92
| HFC-125 | 3500
| HFC-134 | 1100
| HFC-134a | 1430
| HFC-143 | 353
| HFC-143a | 4470
| HFC-152 | 53
| HFC-152a | 124
| HFC-161 | 12
| HFC-227ea | 3220
| HFC-236cb | 1340
| HFC-236ea | 1370
| HFC-236fa | 9810
| HFC-245ca | 693
| HFC-245fa | 1030
| HFC-365mfc | 794
| HFC-43-10mee | 1640
| SF6 | 22800
| NF3 | 17200
| CF4 | 7390
| C2F6 | 12200
| C3F8 | 8830
| c-C4F8 | 10300
| C4F10 | 8860
| C5F12 | 9160
| C6F14 | 9300
| C10F18 | >7,500
Source: 100-year GWPs from IPCC Fourth Assessment Report (AR4), 2007. IPCC AR4 was published in 2007 and is among the most current and comprehensive peer-reviewed assessments of climate change. AR4 provides revised GWPs of several GHGs relative to the values provided in previous assessment reports, following advances in scientific knowledge on the radiative efficiencies and atmospheric lifetimes of these GHGs and of CO2. Factors in the 2023 Emission Factors update are based on AR4 GWPs, but EPA recognizes that Fifth Assessment Report (AR5) GWPs have been published and used in the Draft Inventory of U.S. Greenhouse Gas Emissions and Sinks: 1990-2021 report (published February 2023). However, this 2023 Emission Factors Hub and the GHG Reporting Program continue to use AR4 GWPs. EPA plans to incorporate AR5 GWPs into the 2024 Emission Factors Hub update.
Table 12 | Global Warming Potentials (GWPs) for Blended Refrigerants
| ASHRAE # | 100-year GWP | Blend Composition
| R-401A | 16 | 53% HCFC-22 , 34% HCFC-124 , 13% HFC-152a
| R-401B | 14 | 61% HCFC-22 , 28% HCFC-124 , 11% HFC-152a
| R-401C | 19 | 33% HCFC-22 , 52% HCFC-124 , 15% HFC-152a
| R-402A | 2100 | 38% HCFC-22 , 6% HFC-125 , 2% propane
| R-402B | 1330 | 60% HCFC-22 , 38% HFC-125 , 2% propane
| R-403B | 3444 | 56% HCFC-22 , 39% PFC-218 , 5% propane
| R-404A | 3922 | 44% HFC-125 , 4% HFC-134a , 52% HFC 143a
| R-406A | 0 | 55% HCFC-22 , 41% HCFC-142b , 4% isobutane
| R-407A | 2107 | 20% HFC-32 , 40% HFC-125 , 40% HFC-134a
| R-407B | 2804 | 10% HFC-32 , 70% HFC-125 , 20% HFC-134a
| R-407C | 1774 | 23% HFC-32 , 25% HFC-125 , 52% HFC-134a
| R-407D | 1627 | 15% HFC-32 , 15% HFC-125 , 70% HFC-134a
| R-407E | 1552 | 25% HFC-32 , 15% HFC-125 , 60% HFC-134a
| R-408A | 2301 | 47% HCFC-22 , 7% HFC-125 , 46% HFC 143a
| R-409A | 0 | 60% HCFC-22 , 25% HCFC-124 , 15% HCFC-142b
| R-410A | 2088 | 50% HFC-32 , 50% HFC-125
| R-410B | 2229 | 45% HFC-32 , 55% HFC-125
| R-411A | 14 | 87.5% HCFC-22 , 11 HFC-152a , 1.5% propylene
| R-411B | 4 | 94% HCFC-22 , 3% HFC-152a , 3% propylene
| R-413A | 2053 | 88% HFC-134a , 9% PFC-218 , 3% isobutane
| R-414A | 0 | 51% HCFC-22 , 28.5% HCFC-124 , 16.5% HCFC-142b
| R-414B | 0 | 5% HCFC-22 , 39% HCFC-124 , 9.5% HCFC-142b
| R-417A | 2346 | 46.6% HFC-125 , 5% HFC-134a , 3.4% butane
| R-422A | 3143 | 85.1% HFC-125 , 11.5% HFC-134a , 3.4% isobutane
| R-422D | 2729 | 65.1% HFC-125 , 31.5% HFC-134a , 3.4% isobutane
| R-423A | 2280 | 47.5% HFC-227ea , 52.5% HFC-134a
| R-424A | 2440 | 50.5% HFC-125 , 47% HFC-134a , 2.5% butane/pentane
| R-426A | 1508 | 5.1% HFC-125 , 93% HFC-134a , 1.9% butane/pentane
| R-428A | 3607 | 77.5% HFC-125 , 2% HFC-143a , 1.9% isobutane
| R-434A | 3245 | 63.2% HFC-125 , 16% HFC-134a , 18% HFC-143a , 2.8% isobutane
| R-500 | 32 | 73.8% CFC-12 , 26.2% HFC-152a , 48.8% HCFC-22
| R-502 | 0 | 48.8% HCFC-22 , 51.2% CFC-115
| R-504 | 325 | 48.2% HFC-32 , 51.8% CFC-115
| R-507 | 3985 | 5% HFC-125 , 5% HFC143a
| R-508A | 13214 | 39% HFC-23 , 61% PFC-116
| R-508B | 13396 | 46% HFC-23 , 54% PFC-116
Source: 100-year GWPs from IPCC Fourth Assessment Report (AR4), 2007. See the source note to Table 11 for further explanation. GWPs of blended refrigerants are based on their HFC and PFC constituents, which are based on data from http://www.epa.gov/ozone/snap/refrigerants/refblend.html.

## CUP Geothermal-Original (hidden)
Clinton National Airport CUP Project
Energy Savings from Geothermal System
Geothermal Project Estimated Terminal HVAC Savings
System | Natural Gas | Electricity
Geothermal Project HVAC Savings | 100% | 25%
1Estimated Energy Savings based on meeting with Airport on 2024-01-08
Geothermal Estimated Electricity Savings
| 2019 Terminal Electricity2 Usage (kWh) | Electricity Savings | HVAC Electricity Usage Compared with Overall Terminal Electricity Usage3 | Anticipated Electricity Savings (kwh/year) | GHG Emission Rate4 (kg CO2e/kWh) | Anticipated GHG Savings (kg CO2e/year)
Project Electricity Savings | 10564488 | 25% | 75% | 1980841.5 | 0.53584 | 1061419.5459
2Electricity Usage for Airport Terminal, Entergy Account 8599847, provided by Janet Hicks of Entergy on 2022-12-15
3Estimated HVAC Electricity consumption compared to overall terminal consumption provided by Tony Robeson of TME Bernhard on 1-25-2023
4US EPA Center for Corporate Climate Leadership. GHG Emission Factors Hub. Last Updated September 12, 2023. eGRID2021 Non-baseload emission factor for SRMV region.
Geothermal Estimated Natural Gas Savings
System | 2019 Terminal Natural Gas5 Usage (MMBtu) | Natural Gas Savings from HVAC | HVAC Natural Gas Usage Compared with Overall Terminal Natural Gas Usage6 | Anticipated Natural Gas Savings (MMBtu/year) | GHG Emission Rate7 (kg CO2e/MMBtu) | Anticipated GHG Savings (kg CO2e/year)
Project Natural Gas Savings | 28986 | 100% | 85% | 24638.1 | 53.1148 | 1308647.7539
5Natural Gas Usage for Airport Terminal provided by Bernhard TMP: Quarterly Natural Gas Management Report for LR Airport Main Terminal. This natural gas usage is limited to the terminal usage and excludes natural gas usage at the Airport Maintenance Facility (AMF) and airfield vault generator.
6Estimated HVAC Natural Gas consumption compared to overall terminal consumption.
7US EPA Center for Corporate Climate Leadership. GHG Emission Factors Hub. Last Updated September 12, 2023.Natural Gas Stationary Combustion GHG Factor.
CUP Estimated Overall GHG Savings
Overall GHG Annual Savings (kg CO2e) | Overall GHG Annual Savings (mt CO2e) | 2019 Airport GHG Footprint8 (mt CO2e) | Overall GHG Annual Savings (percent)
2370067.2997 | 2370.0673 | 7589 | 31.23%
8Scope 1 and Scope 2 GHG emissions owned or under operational control of the Clinton National Airport calculated in the Sustainability Management Plan prepared by Harbor using the location based approach.
CUP Estimated Overall Energy Savings
Electricity Savings (kwh) | Natural Gas Savings (MMBtu) | Energy Conversion kwh/MMBtu | Natural Gas Savings (kwh) | Energy Savings (kwh) | 2019 Airport Energy Usage9 (kWh) | Overall Energy Savings (percent)
1980841.5 | 24638.1 | 293.0711 | 7220714.3298 | 9201555.8298 | 26077889.9942 | 35.28%
9Energy usage for Clinton National Airport calculated in the Sustainability Management Plan prepared by Harbor.
COBRA Results: Summary of Health Effects
COBRA Scenario Discount Rates | Monetary Value (dollars, annual)
| Low | High
3% Discount Rate | 61647 | 139099
7% Discount Rate | 55020 | 124043
See COBRA and AVERT worksheets for supporting documentation.

## COBRA Geothermal
Clinton National Airport CUP Project
Energy Savings from Geothermal System
CO-Benefits Risk Assessment Health Impacts Screening and Mapping Tool (COBRA)
Electricity Savings: AVERT Air Pollution Reduction in Power Sector
Region | Electricity Savings (kwh/yr):
Midwest Region | 1980841.5
AVERT RESULTS:
| Original | Post Change | Change | Emission Reduction (tons) for COBRA input
Generation (MWh) | 489984320 | 489982190 | -2130
Total Emissions from Fossil Generation Fleet
SO2 (lb) | 633025640 | 633023130 | -2500 | -1.25
NOX (lb) | 456101410 | 456099440 | -1970 | -0.985
Ozone season NOX (lb) | 188317820 | 188317030 | -790 | -0.395
CO2 (tons) | 411246730 | 411245070 | -1660 | -1660
PM2.5 (lb) | 43376700 | 43376500 | -200 | -0.1
VOCs (lb) | 13900830 | 13900770 | -60 | -0.03
NH3 (lb) | 10422480 | 10422420 | -60 | -0.03
Natural Gas Savings: Air Pollution Reduction from Natural Gas
Natural Gas Savings (MMBtu/yr) | Natural Gas Energy Conversion MMBtu/106 scf | Natural Gas Savings (106scf/yr)
24638.1 | 1026 | 24.0137
AP-42
Pollutant | Emission Rate (lb/106 scf) | Source | Emission Reduction (lb) | Emission Reduction (tons) for COBRA input
SO2 | 0.6 | EPA AP 42 Table 1.4-2 | 14.4082 | 0.0072041
NOX | 100 | EPA AP 42 Table 1.4-1 | 2401.3743 | 1.2007
CO | 84 | EPA AP 42 Table 1.4-1 | 2017.1544 | 1.0086
CO2 | 120000 | EPA AP 42 Table 1.4-2 | 2881649.1228 | 1440.8246
PM2.5 | 7.6 | EPA AP 42 Table 1.4-2 | 182.5044 | 0.091252
VOCs | 5.5 | EPA AP 42 Table 1.4-2 | 132.0756 | 0.066038
COBRA Scenario: Emissions Reductions from Electricity and Natural Gas Savings
COBRA Results: Summary of Health Effects Results with 3% Discount Rate
COBRA Results: Summary of Health Effects Results with 7% Discount Rate

## AVERT Geothermal
Clinton National Airport CUP Project
Energy Savings from Geothermal System
AVoided Emissions and geneRation Tool (AVERT)
AVERT INPUTS:
| AVERT Region: | Midwest Region
| Electricity Savings (kwh/yr): | 1980841.5
AVERT RESULTS:
|  | Original | Post Change | Change
| Generation (MWh) | 489984320 | 489982190 | -2130
Total Emissions from Fossil Generation Fleet
| SO2 (lb) | 633025640 | 633023130 | -2500
| NOX (lb) | 456101410 | 456099440 | -1970
| Ozone season NOX (lb) | 188317820 | 188317030 | -790
| CO2 (tons) | 411246730 | 411245070 | -1660
| PM2.5 (lb) | 43376700 | 43376500 | -200
| VOCs (lb) | 13900830 | 13900770 | -60
| NH3 (lb) | 10422480 | 10422420 | -60
| AVERT-derived Emission Rates: | Average Fossil |  | Marginal Fossil
| SO2 (lb/MWh) | 1.292 |  | 1.174
| NOX (lb/MWh) | 0.931 |  | 0.925
| Ozone season NOX (lb/MWh) | 0.834 |  | 0.878
| CO2 (tons/MWh) | 0.839 |  | 0.778
| PM2.5 (lb/MWh) | 0.089 |  | 0.093
| VOCs (lb/MWh) | 0.028 |  | 0.03
| NH3 (lb/MWh) | 0.021 |  | 0.027

## Fugitives YoY Savings
CO2e Losses (kgs) from Refrigerant Leaks
| Year 1 | Year 2 | Year 3 | Year 4 | Year 5 | Year 6 | Total 6 Years:
Business As Usual; No Change in Equipment | 527096.6882 | 527096.6882 | 527096.6882 | 527096.6882 | 527096.6882 | 527096.6882 | 3162580.1294
Geothermal Project; Retire Chillers #1, #2, #3 | 635301.0598 | 202483.5734 | 202483.5734 | 202483.5734 | 202483.5734 | 202483.5734 | 1647718.927
Change in Fugitive Emissions | 108204.3716 | -324613.1148 | -324613.1148 | -324613.1148 | -324613.1148 | -324613.1148 | -1514861.2024
[6 empty] | CO2e Savings (kg) over 6 years: | 1514861.2024
[6 empty] | Annual Average CO2e Savings (kg) over 6 years: | 252476.8671
Original GHG Savings Estimate:
CUP Estimated Overall GHG Savings
Overall GHG Annual Savings (kg CO2e) | Overall GHG Annual Savings (mt CO2e) | 2019 Airport GHG Footprint8 (mt CO2e) | Overall GHG Annual Savings (percent)
2370067.2997 | 2370.0673 | 7589 | 31.23%
Updated GHG Savings Estimate with reduction in Scope 1 fugitive emissions:
CUP Estimated Overall GHG Savings
Overall GHG Annual Savings (kg CO2e) | Overall GHG Annual Savings (mt CO2e) | 2019 Airport GHG Footprint8 (mt CO2e) | Overall GHG Annual Savings (percent)
2622544.1668 | 2622.5442 | 7589 | 34.56%

## Fugitives - BAU
GHG Fugitive Emissions from Refrigerant Loss
Equipment List provided by Keith Shinnall on 2023-01-05
[6 empty] | Equipment Activity Counts | [17 empty] | EPA Leak Rates (% of capacity) |  |  | Estimated Refrigerant Losses (lbs)
[6 empty] | Year 1 |  |  | Year 2 |  |  | Year 3 |  |  | Year 4 |  |  | Year 5 |  |  | Year 6 | [5 empty] | Year 1 |  |  | Year 2 |  |  | Year 3 |  |  | Year 4 |  |  | Year 5 |  |  | Year 6
Description | Application | Application | Initial Charge (lbs) | Refrigerant | Date MFG | Installed | Operating | Disposed | Installed | Operating | Disposed | Installed | Operating | Disposed | Installed | Operating | Disposed | Installed | Operating | Disposed | Installed | Operating | Disposed | Installed | Operating | Disposed | Installed | Operating | Disposed | Installed | Operating | Disposed | Installed | Operating | Disposed | Installed | Operating | Disposed | Installed | Operating | Disposed | Installed | Operating | Disposed
PCA JB1; JBT/JetAire; XPC6013-113-17-40; SER # 64970 | 7 - Residential and Commercial A/C, including Heat Pumps | A/C | 60 | R407C | 2016-09-01 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1% | 10% | 16% | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 6 | 0
PCA JB2; JBT/JetAire; XPC4500-111-12-40; SER # 61015 | 7 - Residential and Commercial A/C, including Heat Pumps | A/C | 48 | R22 | 2000-11-01 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1% | 10% | 16% | 0 | 4.8 | 0 | 0 | 4.8 | 0 | 0 | 4.8 | 0 | 0 | 4.8 | 0 | 0 | 4.8 | 0 | 0 | 4.8 | 0
PCA JB3; JBT/JetAire; XPC6013-113-17-40; SER # 64971 | 7 - Residential and Commercial A/C, including Heat Pumps | A/C | 60 | R407C | 2016-09-01 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1% | 10% | 16% | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 6 | 0
PCA JB5; JBT/JetAire; XPC6013-113-17-40; SER # 64972 | 7 - Residential and Commercial A/C, including Heat Pumps | A/C | 60 | R407C | 2016-12-01 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1% | 10% | 16% | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 6 | 0
PCA JB6; JBT/JetAire; SJ-115-4; SER # 65958 | 7 - Residential and Commercial A/C, including Heat Pumps | A/C | 57 | R410a | 2020-08-01 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1% | 10% | 16% | 0 | 5.7 | 0 | 0 | 5.7 | 0 | 0 | 5.7 | 0 | 0 | 5.7 | 0 | 0 | 5.7 | 0 | 0 | 5.7 | 0
PCA JB7; JBT/JetAire; XPC6013-113-17-40; SER # 64973 | 7 - Residential and Commercial A/C, including Heat Pumps | A/C | 60 | R407C | 2016-12-01 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1% | 10% | 16% | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 6 | 0
PCA JB8; JBT/JetAire; XPC6013-113-17-40; SER # 64974 | 7 - Residential and Commercial A/C, including Heat Pumps | A/C | 60 | R407C | 2016-12-01 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1% | 10% | 16% | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 6 | 0
PCA JB9; JBT/JetAire; SJ-115-4; SER # 65959 | 7 - Residential and Commercial A/C, including Heat Pumps | A/C | 57 | R410a | 2020-05-01 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1% | 10% | 16% | 0 | 5.7 | 0 | 0 | 5.7 | 0 | 0 | 5.7 | 0 | 0 | 5.7 | 0 | 0 | 5.7 | 0 | 0 | 5.7 | 0
PCA JB12; JBT/JetAire; SJ-115-4; SER # 65960 | 7 - Residential and Commercial A/C, including Heat Pumps | A/C | 57 | R410a | 2020-08-01 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1% | 10% | 16% | 0 | 5.7 | 0 | 0 | 5.7 | 0 | 0 | 5.7 | 0 | 0 | 5.7 | 0 | 0 | 5.7 | 0 | 0 | 5.7 | 0
Chiller #1; Daikin; WME0501SBSNA; SER # STNU181200176 | 6 - Chillers | Chiller | 1154 | R134a | 1905-07-11 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1% | 15% | 5% | 0 | 173.1 | 0 | 0 | 173.1 | 0 | 0 | 173.1 | 0 | 0 | 173.1 | 0 | 0 | 173.1 | 0 | 0 | 173.1 | 0
Chiller #2; McQuay; WS0087-BBABR; SER # STNU120500101 | 6 - Chillers | Chiller | 1402 | R134a | 1905-07-04 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1% | 15% | 5% | 0 | 210.3 | 0 | 0 | 210.3 | 0 | 0 | 210.3 | 0 | 0 | 210.3 | 0 | 0 | 210.3 | 0 | 0 | 210.3 | 0
Chiller #3; McQuay; WSC087-BAAAM; SER # STNU030300246 | 6 - Chillers | Chiller | 1114 | R134a | 1905-06-25 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1% | 15% | 5% | 0 | 167.1 | 0 | 0 | 167.1 | 0 | 0 | 167.1 | 0 | 0 | 167.1 | 0 | 0 | 167.1 | 0 | 0 | 167.1 | 0
Chiller Parking Deck; Daikin; WMC250DCN-ER0B; SER # STNU140700048 | 6 - Chillers | Chiller | 702 | R134a | 1905-07-06 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1% | 15% | 5% | 0 | 105.3 | 0 | 0 | 105.3 | 0 | 0 | 105.3 | 0 | 0 | 105.3 | 0 | 0 | 105.3 | 0 | 0 | 105.3 | 0
Chiller ABP; Daikin; AGZ226ETSEMN00; SER # STNU170500022 | 6 - Chillers | Chiller | 440 | R410a | 1905-07-09 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1% | 15% | 5% | 0 | 66 | 0 | 0 | 66 | 0 | 0 | 66 | 0 | 0 | 66 | 0 | 0 | 66 | 0 | 0 | 66 | 0
RTU Building 100; Daikin; MPS061ELYS6; SER # FBOU200201073 | 7 - Residential and Commercial A/C, including Heat Pumps | A/C | 95 | R410a | 1905-07-12 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1% | 10% | 16% | 0 | 9.5 | 0 | 0 | 9.5 | 0 | 0 | 9.5 | 0 | 0 | 9.5 | 0 | 0 | 9.5 | 0 | 0 | 9.5 | 0
RTU 1; Carrier; 48TCED08A501; SER # 3907G30612 | 7 - Residential and Commercial A/C, including Heat Pumps | A/C | 17 | R410a | 1905-06-29 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1% | 10% | 16% | 0 | 1.7 | 0 | 0 | 1.7 | 0 | 0 | 1.7 | 0 | 0 | 1.7 | 0 | 0 | 1.7 | 0 | 0 | 1.7 | 0
RTU 2; Carrier; 48TCED08A2A5A0A0; SER # 3510G20595 | 7 - Residential and Commercial A/C, including Heat Pumps | A/C | 17 | R410a | 1905-07-02 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1% | 10% | 16% | 0 | 1.7 | 0 | 0 | 1.7 | 0 | 0 | 1.7 | 0 | 0 | 1.7 | 0 | 0 | 1.7 | 0 | 0 | 1.7 | 0
RTU 3; Rheem; RKMA-048CK10E; SER # 2A5654DAAF30019917 | 7 - Residential and Commercial A/C, including Heat Pumps | A/C | 19 | R22 | 1905-06-23 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1% | 10% | 16% | 0 | 1.9 | 0 | 0 | 1.9 | 0 | 0 | 1.9 | 0 | 0 | 1.9 | 0 | 0 | 1.9 | 0 | 0 | 1.9 | 0
RTU 4; Rudd; Faded; SER # Faded | 7 - Residential and Commercial A/C, including Heat Pumps | A/C | 19.375 | R410a | -- | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1% | 10% | 16% | 0 | 1.9375 | 0 | 0 | 1.9375 | 0 | 0 | 1.9375 | 0 | 0 | 1.9375 | 0 | 0 | 1.9375 | 0 | 0 | 1.9375 | 0
RTU 5; Rudd; RKKL-A060CK10E; SER # 2G7503ADAAF371106278 | 7 - Residential and Commercial A/C, including Heat Pumps | A/C | 21 | R410a | 1905-07-03 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1% | 10% | 16% | 0 | 2.1 | 0 | 0 | 2.1 | 0 | 0 | 2.1 | 0 | 0 | 2.1 | 0 | 0 | 2.1 | 0 | 0 | 2.1 | 0
RTU 6; Rudd; RKNN-A048CK10E; SER # F281601283 | 7 - Residential and Commercial A/C, including Heat Pumps | A/C | 17 | R410a | 1905-07-08 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1% | 10% | 16% | 0 | 1.7 | 0 | 0 | 1.7 | 0 | 0 | 1.7 | 0 | 0 | 1.7 | 0 | 0 | 1.7 | 0 | 0 | 1.7 | 0
RTU 7; Carrier; 48TME006-A-501; SER # 4407G20158 | 7 - Residential and Commercial A/C, including Heat Pumps | A/C | 19 | R22 | 1905-06-29 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1% | 10% | 16% | 0 | 1.9 | 0 | 0 | 1.9 | 0 | 0 | 1.9 | 0 | 0 | 1.9 | 0 | 0 | 1.9 | 0 | 0 | 1.9 | 0
RTU 8; Rudd; RKKL-B090CL15E; SER # 2N829ADAAF181202954 | 7 - Residential and Commercial A/C, including Heat Pumps | A/C | 28 | R410a | 1905-07-04 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1% | 10% | 16% | 0 | 2.8 | 0 | 0 | 2.8 | 0 | 0 | 2.8 | 0 | 0 | 2.8 | 0 | 0 | 2.8 | 0 | 0 | 2.8 | 0
RTU 9; Rheem; Faded; SER # Faded | 7 - Residential and Commercial A/C, including Heat Pumps | A/C | 19.375 | R410a | -- | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1% | 10% | 16% | 0 | 1.9375 | 0 | 0 | 1.9375 | 0 | 0 | 1.9375 | 0 | 0 | 1.9375 | 0 | 0 | 1.9375 | 0 | 0 | 1.9375 | 0
RTU 10; Rudd; RKNLA048CK10E; SER # 2G7502ADAAF48120 | 7 - Residential and Commercial A/C, including Heat Pumps | A/C | 17 | R410a | 1905-07-04 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1% | 10% | 16% | 0 | 1.7 | 0 | 0 | 1.7 | 0 | 0 | 1.7 | 0 | 0 | 1.7 | 0 | 0 | 1.7 | 0 | 0 | 1.7 | 0
East Vault WPAC-2; Bard; TGOS1DB155SMXE; SER # 386K193679345-02 | 7 - Residential and Commercial A/C, including Heat Pumps | A/C | 12.43 | R410a | 1905-07-13 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1% | 10% | 16% | 0 | 1.243 | 0 | 0 | 1.243 | 0 | 0 | 1.243 | 0 | 0 | 1.243 | 0 | 0 | 1.243 | 0 | 0 | 1.243 | 0
East Vault WPAC-1; Bard; TGOS1DB155SMXE; SER # Faded | 7 - Residential and Commercial A/C, including Heat Pumps | A/C | 12.43 | R410a | 1905-07-13 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1% | 10% | 16% | 0 | 1.243 | 0 | 0 | 1.243 | 0 | 0 | 1.243 | 0 | 0 | 1.243 | 0 | 0 | 1.243 | 0 | 0 | 1.243 | 0
West Vault; Diakin; DCC120XXX4WMML; SER # 386K193679345-02 | 7 - Residential and Commercial A/C, including Heat Pumps | A/C | 35 | R410a | 1905-07-12 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1% | 10% | 16% | 0 | 3.5 | 0 | 0 | 3.5 | 0 | 0 | 3.5 | 0 | 0 | 3.5 | 0 | 0 | 3.5 | 0 | 0 | 3.5 | 0
West Vault; Diakin; DCC120XXX4WMML; SER # 386K193679344-02 | 7 - Residential and Commercial A/C, including Heat Pumps | A/C | 35 | R410a | 1905-07-12 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1% | 10% | 16% | 0 | 3.5 | 0 | 0 | 3.5 | 0 | 0 | 3.5 | 0 | 0 | 3.5 | 0 | 0 | 3.5 | 0 | 0 | 3.5 | 0
West Vault; Bard; TGOS1DB155SMXE; SER # ? | 7 - Residential and Commercial A/C, including Heat Pumps | A/C | 12.5 | R410a | 1905-07-12 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1% | 10% | 16% | 0 | 1.25 | 0 | 0 | 1.25 | 0 | 0 | 1.25 | 0 | 0 | 1.25 | 0 | 0 | 1.25 | 0 | 0 | 1.25 | 0
Civil Air Patrol RTU 1; Rudd; RKKB-A240CL30E; SER # 2D6611ADAF34050699 | 7 - Residential and Commercial A/C, including Heat Pumps | A/C | 14 | R22 | 1905-06-27 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1% | 10% | 16% | 0 | 1.4 | 0 | 0 | 1.4 | 0 | 0 | 1.4 | 0 | 0 | 1.4 | 0 | 0 | 1.4 | 0 | 0 | 1.4 | 0
Civil Air Patrol RTU 2; Carrier; 48TJE012-611; SER # Faded | 7 - Residential and Commercial A/C, including Heat Pumps | A/C | 23.3333 | R22 | -- | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1% | 10% | 16% | 0 | 2.3333 | 0 | 0 | 2.3333 | 0 | 0 | 2.3333 | 0 | 0 | 2.3333 | 0 | 0 | 2.3333 | 0 | 0 | 2.3333 | 0
Civil Air Patrol RTU 3; Rudd; RKKA-A060CK10E; SER # 2G5643ADAAF20080 | 7 - Residential and Commercial A/C, including Heat Pumps | A/C | 29 | R22 | 1905-06-30 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1% | 10% | 16% | 0 | 2.9 | 0 | 0 | 2.9 | 0 | 0 | 2.9 | 0 | 0 | 2.9 | 0 | 0 | 2.9 | 0 | 0 | 2.9 | 0
Civil Air Patrol RTU 4; Mammoth; R6GDX60C120E; SER # R6F150665475 | 7 - Residential and Commercial A/C, including Heat Pumps | A/C | 27 | R410a | 1905-06-28 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1% | 10% | 16% | 0 | 2.7 | 0 | 0 | 2.7 | 0 | 0 | 2.7 | 0 | 0 | 2.7 | 0 | 0 | 2.7 | 0 | 0 | 2.7 | 0
AC = Residential and Commercial A/C, including Heat Pumps | [22 empty] | GWP (AR5) |  |  |  | Year 1 |  |  | Year 2 |  |  | Year 3 |  |  | Year 4 |  |  | Year 5 |  |  | Year 6
[20 empty] | Losses (lbs) per Refrigerant Type |  |  | R407C |  | 1624 |  | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 30 | 0
[23 empty] | R22 |  | 1760 |  | 0 | 15.2333 | 0 | 0 | 15.2333 | 0 | 0 | 15.2333 | 0 | 0 | 15.2333 | 0 | 0 | 15.2333 | 0 | 0 | 15.2333 | 0
[23 empty] | R410a |  | 1924 |  | 0 | 121.611 | 0 | 0 | 121.611 | 0 | 0 | 121.611 | 0 | 0 | 121.611 | 0 | 0 | 121.611 | 0 | 0 | 121.611 | 0
[23 empty] | R134a |  | 1300 |  | 0 | 655.8 | 0 | 0 | 655.8 | 0 | 0 | 655.8 | 0 | 0 | 655.8 | 0 | 0 | 655.8 | 0 | 0 | 655.8 | 0
[20 empty] | CO2e Losses (Lbs) per Refrigerant Type |  |  |  | R407C |  |  | 0 | 48720 | 0 | 0 | 48720 | 0 | 0 | 48720 | 0 | 0 | 48720 | 0 | 0 | 48720 | 0 | 0 | 48720 | 0
[24 empty] | R22 |  |  | 0 | 26810.6667 | 0 | 0 | 26810.6667 | 0 | 0 | 26810.6667 | 0 | 0 | 26810.6667 | 0 | 0 | 26810.6667 | 0 | 0 | 26810.6667 | 0
[24 empty] | R410a |  |  | 0 | 233979.564 | 0 | 0 | 233979.564 | 0 | 0 | 233979.564 | 0 | 0 | 233979.564 | 0 | 0 | 233979.564 | 0 | 0 | 233979.564 | 0
[24 empty] | R134a |  |  | 0 | 852540 | 0 | 0 | 852540 | 0 | 0 | 852540 | 0 | 0 | 852540 | 0 | 0 | 852540 | 0 | 0 | 852540 | 0
[20 empty] | CO2e Losses (kgs) per Refrigerant Type |  |  |  | R407C |  |  | 0 | 22099.0022 | 0 | 0 | 22099.0022 | 0 | 0 | 22099.0022 | 0 | 0 | 22099.0022 | 0 | 0 | 22099.0022 | 0 | 0 | 22099.0022 | 0
[24 empty] | R22 |  |  | 0 | 12161.1039 | 0 | 0 | 12161.1039 | 0 | 0 | 12161.1039 | 0 | 0 | 12161.1039 | 0 | 0 | 12161.1039 | 0 | 0 | 12161.1039 | 0
[24 empty] | R410a |  |  | 0 | 106131.2584 | 0 | 0 | 106131.2584 | 0 | 0 | 106131.2584 | 0 | 0 | 106131.2584 | 0 | 0 | 106131.2584 | 0 | 0 | 106131.2584 | 0
[24 empty] | R134a |  |  | 0 | 386705.3237 | 0 | 0 | 386705.3237 | 0 | 0 | 386705.3237 | 0 | 0 | 386705.3237 | 0 | 0 | 386705.3237 | 0 | 0 | 386705.3237 | 0
[20 empty] | CO2e Losses (kgs) from Refrigerant Leaks | [6 empty] | Year 1 |  |  | Year 2 |  |  | Year 3 |  |  | Year 4 |  |  | Year 5 |  |  | Year 6 |  |  | Total 6 Years:
[27 empty] | 527096.6882 |  |  | 527096.6882 |  |  | 527096.6882 |  |  | 527096.6882 |  |  | 527096.6882 |  |  | 527096.6882 |  |  | 3162580.1294

## Fugitives - Geothermal
GHG Fugitive Emissions from Refrigerant Loss
Equipment List provided by Keith Shinnall on 2023-01-05
[6 empty] | Equipment Activity Counts | [17 empty] | EPA Leak Rates (% of capacity) |  |  | Estimated Refrigerant Losses (lbs)
[6 empty] | Year 1 |  |  | Year 2 |  |  | Year 3 |  |  | Year 4 |  |  | Year 5 |  |  | Year 6 | [5 empty] | Year 1 |  |  | Year 2 |  |  | Year 3 |  |  | Year 4 |  |  | Year 5 |  |  | Year 6
Description | Application | Application | Initial Charge (lbs) | Refrigerant | Date MFG | Installed | Operating | Disposed | Installed | Operating | Disposed | Installed | Operating | Disposed | Installed | Operating | Disposed | Installed | Operating | Disposed | Installed | Operating | Disposed | Installed | Operating | Disposed | Installed | Operating | Disposed | Installed | Operating | Disposed | Installed | Operating | Disposed | Installed | Operating | Disposed | Installed | Operating | Disposed | Installed | Operating | Disposed
PCA JB1; JBT/JetAire; XPC6013-113-17-40; SER # 64970 | 7 - Residential and Commercial A/C, including Heat Pumps | A/C | 60 | R407C | 2016-09-01 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1% | 10% | 16% | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 6 | 0
PCA JB2; JBT/JetAire; XPC4500-111-12-40; SER # 61015 | 7 - Residential and Commercial A/C, including Heat Pumps | A/C | 48 | R22 | 2000-11-01 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1% | 10% | 16% | 0 | 4.8 | 0 | 0 | 4.8 | 0 | 0 | 4.8 | 0 | 0 | 4.8 | 0 | 0 | 4.8 | 0 | 0 | 4.8 | 0
PCA JB3; JBT/JetAire; XPC6013-113-17-40; SER # 64971 | 7 - Residential and Commercial A/C, including Heat Pumps | A/C | 60 | R407C | 2016-09-01 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1% | 10% | 16% | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 6 | 0
PCA JB5; JBT/JetAire; XPC6013-113-17-40; SER # 64972 | 7 - Residential and Commercial A/C, including Heat Pumps | A/C | 60 | R407C | 2016-12-01 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1% | 10% | 16% | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 6 | 0
PCA JB6; JBT/JetAire; SJ-115-4; SER # 65958 | 7 - Residential and Commercial A/C, including Heat Pumps | A/C | 57 | R410a | 2020-08-01 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1% | 10% | 16% | 0 | 5.7 | 0 | 0 | 5.7 | 0 | 0 | 5.7 | 0 | 0 | 5.7 | 0 | 0 | 5.7 | 0 | 0 | 5.7 | 0
PCA JB7; JBT/JetAire; XPC6013-113-17-40; SER # 64973 | 7 - Residential and Commercial A/C, including Heat Pumps | A/C | 60 | R407C | 2016-12-01 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1% | 10% | 16% | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 6 | 0
PCA JB8; JBT/JetAire; XPC6013-113-17-40; SER # 64974 | 7 - Residential and Commercial A/C, including Heat Pumps | A/C | 60 | R407C | 2016-12-01 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1% | 10% | 16% | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 6 | 0
PCA JB9; JBT/JetAire; SJ-115-4; SER # 65959 | 7 - Residential and Commercial A/C, including Heat Pumps | A/C | 57 | R410a | 2020-05-01 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1% | 10% | 16% | 0 | 5.7 | 0 | 0 | 5.7 | 0 | 0 | 5.7 | 0 | 0 | 5.7 | 0 | 0 | 5.7 | 0 | 0 | 5.7 | 0
PCA JB12; JBT/JetAire; SJ-115-4; SER # 65960 | 7 - Residential and Commercial A/C, including Heat Pumps | A/C | 57 | R410a | 2020-08-01 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1% | 10% | 16% | 0 | 5.7 | 0 | 0 | 5.7 | 0 | 0 | 5.7 | 0 | 0 | 5.7 | 0 | 0 | 5.7 | 0 | 0 | 5.7 | 0
Chiller #1; Daikin; WME0501SBSNA; SER # STNU181200176 | 6 - Chillers | Chiller | 1154 | R134a | 1905-07-11 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1% | 15% | 5% | 0 | 173.1 | 57.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chiller #2; McQuay; WS0087-BBABR; SER # STNU120500101 | 6 - Chillers | Chiller | 1402 | R134a | 1905-07-04 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1% | 15% | 5% | 0 | 210.3 | 70.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chiller #3; McQuay; WSC087-BAAAM; SER # STNU030300246 | 6 - Chillers | Chiller | 1114 | R134a | 1905-06-25 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1% | 15% | 5% | 0 | 167.1 | 55.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chiller Parking Deck; Daikin; WMC250DCN-ER0B; SER # STNU140700048 | 6 - Chillers | Chiller | 702 | R134a | 1905-07-06 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1% | 15% | 5% | 0 | 105.3 | 0 | 0 | 105.3 | 0 | 0 | 105.3 | 0 | 0 | 105.3 | 0 | 0 | 105.3 | 0 | 0 | 105.3 | 0
Chiller ABP; Daikin; AGZ226ETSEMN00; SER # STNU170500022 | 6 - Chillers | Chiller | 440 | R410a | 1905-07-09 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1% | 15% | 5% | 0 | 66 | 0 | 0 | 66 | 0 | 0 | 66 | 0 | 0 | 66 | 0 | 0 | 66 | 0 | 0 | 66 | 0
RTU Building 100; Daikin; MPS061ELYS6; SER # FBOU200201073 | 7 - Residential and Commercial A/C, including Heat Pumps | A/C | 95 | R410a | 1905-07-12 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1% | 10% | 16% | 0 | 9.5 | 0 | 0 | 9.5 | 0 | 0 | 9.5 | 0 | 0 | 9.5 | 0 | 0 | 9.5 | 0 | 0 | 9.5 | 0
RTU 1; Carrier; 48TCED08A501; SER # 3907G30612 | 7 - Residential and Commercial A/C, including Heat Pumps | A/C | 17 | R410a | 1905-06-29 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1% | 10% | 16% | 0 | 1.7 | 0 | 0 | 1.7 | 0 | 0 | 1.7 | 0 | 0 | 1.7 | 0 | 0 | 1.7 | 0 | 0 | 1.7 | 0
RTU 2; Carrier; 48TCED08A2A5A0A0; SER # 3510G20595 | 7 - Residential and Commercial A/C, including Heat Pumps | A/C | 17 | R410a | 1905-07-02 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1% | 10% | 16% | 0 | 1.7 | 0 | 0 | 1.7 | 0 | 0 | 1.7 | 0 | 0 | 1.7 | 0 | 0 | 1.7 | 0 | 0 | 1.7 | 0
RTU 3; Rheem; RKMA-048CK10E; SER # 2A5654DAAF30019917 | 7 - Residential and Commercial A/C, including Heat Pumps | A/C | 19 | R22 | 1905-06-23 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1% | 10% | 16% | 0 | 1.9 | 0 | 0 | 1.9 | 0 | 0 | 1.9 | 0 | 0 | 1.9 | 0 | 0 | 1.9 | 0 | 0 | 1.9 | 0
RTU 4; Rudd; Faded; SER # Faded | 7 - Residential and Commercial A/C, including Heat Pumps | A/C | 19.375 | R410a | -- | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1% | 10% | 16% | 0 | 1.9375 | 0 | 0 | 1.9375 | 0 | 0 | 1.9375 | 0 | 0 | 1.9375 | 0 | 0 | 1.9375 | 0 | 0 | 1.9375 | 0
RTU 5; Rudd; RKKL-A060CK10E; SER # 2G7503ADAAF371106278 | 7 - Residential and Commercial A/C, including Heat Pumps | A/C | 21 | R410a | 1905-07-03 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1% | 10% | 16% | 0 | 2.1 | 0 | 0 | 2.1 | 0 | 0 | 2.1 | 0 | 0 | 2.1 | 0 | 0 | 2.1 | 0 | 0 | 2.1 | 0
RTU 6; Rudd; RKNN-A048CK10E; SER # F281601283 | 7 - Residential and Commercial A/C, including Heat Pumps | A/C | 17 | R410a | 1905-07-08 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1% | 10% | 16% | 0 | 1.7 | 0 | 0 | 1.7 | 0 | 0 | 1.7 | 0 | 0 | 1.7 | 0 | 0 | 1.7 | 0 | 0 | 1.7 | 0
RTU 7; Carrier; 48TME006-A-501; SER # 4407G20158 | 7 - Residential and Commercial A/C, including Heat Pumps | A/C | 19 | R22 | 1905-06-29 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1% | 10% | 16% | 0 | 1.9 | 0 | 0 | 1.9 | 0 | 0 | 1.9 | 0 | 0 | 1.9 | 0 | 0 | 1.9 | 0 | 0 | 1.9 | 0
RTU 8; Rudd; RKKL-B090CL15E; SER # 2N829ADAAF181202954 | 7 - Residential and Commercial A/C, including Heat Pumps | A/C | 28 | R410a | 1905-07-04 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1% | 10% | 16% | 0 | 2.8 | 0 | 0 | 2.8 | 0 | 0 | 2.8 | 0 | 0 | 2.8 | 0 | 0 | 2.8 | 0 | 0 | 2.8 | 0
RTU 9; Rheem; Faded; SER # Faded | 7 - Residential and Commercial A/C, including Heat Pumps | A/C | 19.375 | R410a | -- | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1% | 10% | 16% | 0 | 1.9375 | 0 | 0 | 1.9375 | 0 | 0 | 1.9375 | 0 | 0 | 1.9375 | 0 | 0 | 1.9375 | 0 | 0 | 1.9375 | 0
RTU 10; Rudd; RKNLA048CK10E; SER # 2G7502ADAAF48120 | 7 - Residential and Commercial A/C, including Heat Pumps | A/C | 17 | R410a | 1905-07-04 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1% | 10% | 16% | 0 | 1.7 | 0 | 0 | 1.7 | 0 | 0 | 1.7 | 0 | 0 | 1.7 | 0 | 0 | 1.7 | 0 | 0 | 1.7 | 0
East Vault WPAC-2; Bard; TGOS1DB155SMXE; SER # 386K193679345-02 | 7 - Residential and Commercial A/C, including Heat Pumps | A/C | 12.43 | R410a | 1905-07-13 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1% | 10% | 16% | 0 | 1.243 | 0 | 0 | 1.243 | 0 | 0 | 1.243 | 0 | 0 | 1.243 | 0 | 0 | 1.243 | 0 | 0 | 1.243 | 0
East Vault WPAC-1; Bard; TGOS1DB155SMXE; SER # Faded | 7 - Residential and Commercial A/C, including Heat Pumps | A/C | 12.43 | R410a | 1905-07-13 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1% | 10% | 16% | 0 | 1.243 | 0 | 0 | 1.243 | 0 | 0 | 1.243 | 0 | 0 | 1.243 | 0 | 0 | 1.243 | 0 | 0 | 1.243 | 0
West Vault; Diakin; DCC120XXX4WMML; SER # 386K193679345-02 | 7 - Residential and Commercial A/C, including Heat Pumps | A/C | 35 | R410a | 1905-07-12 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1% | 10% | 16% | 0 | 3.5 | 0 | 0 | 3.5 | 0 | 0 | 3.5 | 0 | 0 | 3.5 | 0 | 0 | 3.5 | 0 | 0 | 3.5 | 0
West Vault; Diakin; DCC120XXX4WMML; SER # 386K193679344-02 | 7 - Residential and Commercial A/C, including Heat Pumps | A/C | 35 | R410a | 1905-07-12 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1% | 10% | 16% | 0 | 3.5 | 0 | 0 | 3.5 | 0 | 0 | 3.5 | 0 | 0 | 3.5 | 0 | 0 | 3.5 | 0 | 0 | 3.5 | 0
West Vault; Bard; TGOS1DB155SMXE; SER # ? | 7 - Residential and Commercial A/C, including Heat Pumps | A/C | 12.5 | R410a | 1905-07-12 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1% | 10% | 16% | 0 | 1.25 | 0 | 0 | 1.25 | 0 | 0 | 1.25 | 0 | 0 | 1.25 | 0 | 0 | 1.25 | 0 | 0 | 1.25 | 0
Civil Air Patrol RTU 1; Rudd; RKKB-A240CL30E; SER # 2D6611ADAF34050699 | 7 - Residential and Commercial A/C, including Heat Pumps | A/C | 14 | R22 | 1905-06-27 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1% | 10% | 16% | 0 | 1.4 | 0 | 0 | 1.4 | 0 | 0 | 1.4 | 0 | 0 | 1.4 | 0 | 0 | 1.4 | 0 | 0 | 1.4 | 0
Civil Air Patrol RTU 2; Carrier; 48TJE012-611; SER # Faded | 7 - Residential and Commercial A/C, including Heat Pumps | A/C | 23.3333 | R22 | -- | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1% | 10% | 16% | 0 | 2.3333 | 0 | 0 | 2.3333 | 0 | 0 | 2.3333 | 0 | 0 | 2.3333 | 0 | 0 | 2.3333 | 0 | 0 | 2.3333 | 0
Civil Air Patrol RTU 3; Rudd; RKKA-A060CK10E; SER # 2G5643ADAAF20080 | 7 - Residential and Commercial A/C, including Heat Pumps | A/C | 29 | R22 | 1905-06-30 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1% | 10% | 16% | 0 | 2.9 | 0 | 0 | 2.9 | 0 | 0 | 2.9 | 0 | 0 | 2.9 | 0 | 0 | 2.9 | 0 | 0 | 2.9 | 0
Civil Air Patrol RTU 4; Mammoth; R6GDX60C120E; SER # R6F150665475 | 7 - Residential and Commercial A/C, including Heat Pumps | A/C | 27 | R410a | 1905-06-28 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1% | 10% | 16% | 0 | 2.7 | 0 | 0 | 2.7 | 0 | 0 | 2.7 | 0 | 0 | 2.7 | 0 | 0 | 2.7 | 0 | 0 | 2.7 | 0
AC = Residential and Commercial A/C, including Heat Pumps | [22 empty] | GWP (AR5) |  |  |  | Year 1 |  |  | Year 2 |  |  | Year 3 |  |  | Year 4 |  |  | Year 5 |  |  | Year 6
[20 empty] | Losses (lbs) per Refrigerant Type |  |  | R407C |  | 1624 |  | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 30 | 0
[23 empty] | R22 |  | 1760 |  | 0 | 15.2333 | 0 | 0 | 15.2333 | 0 | 0 | 15.2333 | 0 | 0 | 15.2333 | 0 | 0 | 15.2333 | 0 | 0 | 15.2333 | 0
[23 empty] | R410a |  | 1924 |  | 0 | 121.611 | 0 | 0 | 121.611 | 0 | 0 | 121.611 | 0 | 0 | 121.611 | 0 | 0 | 121.611 | 0 | 0 | 121.611 | 0
[23 empty] | R134a |  | 1300 |  | 0 | 655.8 | 183.5 | 0 | 105.3 | 0 | 0 | 105.3 | 0 | 0 | 105.3 | 0 | 0 | 105.3 | 0 | 0 | 105.3 | 0
[20 empty] | CO2e Losses (Lbs) per Refrigerant Type |  |  |  | R407C |  |  | 0 | 48720 | 0 | 0 | 48720 | 0 | 0 | 48720 | 0 | 0 | 48720 | 0 | 0 | 48720 | 0 | 0 | 48720 | 0
[24 empty] | R22 |  |  | 0 | 26810.6667 | 0 | 0 | 26810.6667 | 0 | 0 | 26810.6667 | 0 | 0 | 26810.6667 | 0 | 0 | 26810.6667 | 0 | 0 | 26810.6667 | 0
[24 empty] | R410a |  |  | 0 | 233979.564 | 0 | 0 | 233979.564 | 0 | 0 | 233979.564 | 0 | 0 | 233979.564 | 0 | 0 | 233979.564 | 0 | 0 | 233979.564 | 0
[24 empty] | R134a |  |  | 0 | 852540 | 238550 | 0 | 136890 | 0 | 0 | 136890 | 0 | 0 | 136890 | 0 | 0 | 136890 | 0 | 0 | 136890 | 0
[20 empty] | CO2e Losses (kgs) per Refrigerant Type |  |  |  | R407C |  |  | 0 | 22099.0022 | 0 | 0 | 22099.0022 | 0 | 0 | 22099.0022 | 0 | 0 | 22099.0022 | 0 | 0 | 22099.0022 | 0 | 0 | 22099.0022 | 0
[24 empty] | R22 |  |  | 0 | 12161.1039 | 0 | 0 | 12161.1039 | 0 | 0 | 12161.1039 | 0 | 0 | 12161.1039 | 0 | 0 | 12161.1039 | 0 | 0 | 12161.1039 | 0
[24 empty] | R410a |  |  | 0 | 106131.2584 | 0 | 0 | 106131.2584 | 0 | 0 | 106131.2584 | 0 | 0 | 106131.2584 | 0 | 0 | 106131.2584 | 0 | 0 | 106131.2584 | 0
[24 empty] | R134a |  |  | 0 | 386705.3237 | 108204.3716 | 0 | 62092.2089 | 0 | 0 | 62092.2089 | 0 | 0 | 62092.2089 | 0 | 0 | 62092.2089 | 0 | 0 | 62092.2089 | 0
[20 empty] | CO2e Losses (kgs) from Refrigerant Leaks | [6 empty] | Year 1 |  |  | Year 2 |  |  | Year 3 |  |  | Year 4 |  |  | Year 5 |  |  | Year 6 |  |  | Total 6 Years:
[27 empty] | 635301.0598 |  |  | 202483.5734 |  |  | 202483.5734 |  |  | 202483.5734 |  |  | 202483.5734 |  |  | 202483.5734 |  |  | 1647718.927

## CUP EE Equipment (hidden)
Clinton National Airport CUP Project
Energy Savings from New Energy Efficient Equipment
CUP Project Estimated Energy Savings
System | Natural Gas | Electricity
Heat Pump Chiller Heater | 10% | 10%
Heat Pump Heaters | 10% | 0%
Building Automation System | 10% | 10%
CUP Project Total Savings: | 30% | 20%
1Estimated Energy Savings provided by Tony Robeson of TME Bernhard on 1-25-2023
CUP Estimated Energy Savings
| 2019 Terminal Electricity2 Usage (kWh) | Electricity Savings | HVAC Electricity Usage Compared with Overall Terminal Electricity Usage3 | Anticipated Electricity Savings (kwh/year) | GHG Emission Rate4 (kg CO2e/kWh) | Anticipated GHG Savings (kg CO2e/year)
Project Electricity Savings | 10564488 | 20% | 75% | 1584673.2 | 0.53584 | 849135.6367
2Electricity Usage for Airport Terminal, Entergy Account 8599847, provided by Janet Hicks of Entergy on 2022-12-15
3Estimated HVAC Electricity consumption compared to overall terminal consumption provided by Tony Robeson of TME Bernhard on 1-25-2023
4US EPA Center for Corporate Climate Leadership. GHG Emission Factors Hub. Last Updated September 12, 2023. eGRID2020 Non-baseload emission factor for SRMV region.
CUP Estimated Natural Gas Savings
System | 2019 Terminal Natural Gas5 Usage (MMBtu) | Natural Gas Savings | HVAC Natural Gas Usage Compared with Overall Terminal Natural Gas Usage6 | Anticipated Natural Gas Savings (MMBtu/year) | GHG Emission Rate7 (kg CO2e/MMBtu) | Anticipated GHG Savings (kg CO2e/year)
Project Natural Gas Savings | 28986 | 30% | 85% | 7391.43 | 53.1148 | 392594.3262
5Natural Gas Usage for Airport Terminal provided by Bernhard TMP: Quarterly Natural Gas Management Report for LR Airport Main Terminal. This natural gas usage is limited to the terminal usage and excludes natural gas usage at the Airport Maintenance Facility (AMF) and airfield vault generator.
6Estimated HVAC Natural Gas consumption compared to overall terminal consumption.
7US EPA Center for Corporate Climate Leadership. GHG Emission Factors Hub. Last Updated April 1, 2022. Natural Gas Stationary Combustion GHG Factor.
CUP Estimated Overall GHG Savings
Overall GHG Annual Savings (kg CO2e) | Overall GHG Annual Savings (mt CO2e) | 2019 Airport GHG Footprint8 (mt CO2e) | Overall GHG Annual Savings (percent)
1241729.9629 | 1241.73 | 7589 | 16.36%
8Scope 1 and Scope 2 GHG emissions owned or under operational control of the Clinton National Airport calculated in the Sustainability Management Plan prepared by Harbor using the location based approach.
CUP Estimated Overall Energy Savings
Electricity Savings (kwh) | Natural Gas Savings (MMBtu) | Energy Conversion kwh/MMBtu | Natural Gas Savings (kwh) | Energy Savings (kwh) | 2019 Airport Energy Usage9 (kWh) | Overall Energy Savings (percent)
1584673.2 | 7391.43 | 293.0711 | 2166214.2989 | 3750887.4989 | 26077889.9942 | 14.38%
9Energy usage for Clinton National Airport calculated in the Sustainability Management Plan prepared by Harbor.
COBRA Results: Summary of Health Effects
COBRA Scenario Discount Rates | Monetary Value (dollars, annual)
| Low | High
3% Discount Rate | 39518 | 89171
7% Discount Rate | 35270 | 79519
See COBRA and AVERT worksheets for supporting documentation.

## COBRA EE Equipment (hidden)
Clinton National Airport CUP Project
Energy Savings from New Energy Efficient Equipment
CO-Benefits Risk Assessment Health Impacts Screening and Mapping Tool (COBRA)
Electricity Savings: AVERT Air Pollution Reduction in Power Sector
Region | Electricity Savings (kwh/yr):
Midwest Region | 1584673.2
AVERT RESULTS:
| Original | Post Change | Change | Emission Reduction (tons) for COBRA input
Generation (MWh) | 489984320 | 489982610 | -1710
Total Emissions from Fossil Generation Fleet
SO2 (lb) | 633025640 | 633023630 | -2000 | -1
NOX (lb) | 456101410 | 456099830 | -1580 | -0.79
Ozone season NOX (lb) | 188317820 | 188317190 | -630 | -0.315
CO2 (tons) | 411246730 | 411245400 | -1330 | -1330
PM2.5 (lb) | 43376700 | 43376540 | -160 | -0.08
VOCs (lb) | 13900830 | 13900780 | -50 | -0.025
NH3 (lb) | 10422480 | 10422430 | -50 | -0.025
Natural Gas Savings: Air Pollution Reduction from Natural Gas
Natural Gas Savings (MMBtu/yr) | Natural Gas Energy Conversion MMBtu/106 scf | Natural Gas Savings (106scf/yr)
7391.43 | 1026 | 7.2041
AP-42
Pollutant | Emission Rate (lb/106 scf) | Source | Emission Reduction (lb) | Emission Reduction (tons) for COBRA input
SO2 | 0.6 | EPA AP 42 Table 1.4-2 | 4.3225 | 0.0021612
NOX | 100 | EPA AP 42 Table 1.4-1 | 720.4123 | 0.36021
CO | 84 | EPA AP 42 Table 1.4-1 | 605.1463 | 0.30257
CO2 | 120000 | EPA AP 42 Table 1.4-2 | 864494.7368 | 432.2474
PM2.5 | 7.6 | EPA AP 42 Table 1.4-2 | 54.7513 | 0.027376
VOCs | 5.5 | EPA AP 42 Table 1.4-2 | 39.6227 | 0.019811
COBRA Scenario: Emissions Reductions from Electricity and Natural Gas Savings
COBRA Results: Summary of Health Effects Results with 3% Discount Rate
COBRA Results: Summary of Health Effects Results with 7% Discount Rate

## AVERT EE Equipment (hidden)
Clinton National Airport CUP Project
Energy Savings from New Energy Efficient Equipment
AVoided Emissions and geneRation Tool (AVERT)
AVERT INPUTS:
| AVERT Region: | Midwest Region
| Electricity Savings (kwh/yr): | 1584673.2
AVERT RESULTS:
|  | Original | Post Change | Change
| Generation (MWh) | 489984320 | 489982610 | -1710
Total Emissions from Fossil Generation Fleet
| SO2 (lb) | 633025640 | 633023630 | -2000
| NOX (lb) | 456101410 | 456099830 | -1580
| Ozone season NOX (lb) | 188317820 | 188317190 | -630
| CO2 (tons) | 411246730 | 411245400 | -1330
| PM2.5 (lb) | 43376700 | 43376540 | -160
| VOCs (lb) | 13900830 | 13900780 | -50
| NH3 (lb) | 10422480 | 10422430 | -50
| AVERT-derived Emission Rates: | Average Fossil |  | Marginal Fossil
| SO2 (lb/MWh) | 1.292 |  | 1.174
| NOX (lb/MWh) | 0.931 |  | 0.925
| Ozone season NOX (lb/MWh) | 0.834 |  | 0.878
| CO2 (tons/MWh) | 0.839 |  | 0.778
| PM2.5 (lb/MWh) | 0.089 |  | 0.093
| VOCs (lb/MWh) | 0.028 |  | 0.03
| NH3 (lb/MWh) | 0.021 |  | 0.027

## OLD Electricity-Terminal (hidden)
Account #8599847
TERMINAL
Reporting Month | Service To | Days | kWh | Billed kW | Billed kVA/kVAR | Electric Fuel Charges | Electric Non-Fuel Charges | Electric Monthly Charges | Monthly $/kWh | Billed CCF | Gas Fuel Charges | Gas Non-Fuel Charges | Gas Monthly Charges | Monthly $/CCF | Mailed Date | Invoice
2021-04-30 | 2021-04-30 | 30 | 650952 | 1196 | 0 | 6242.63 | 20876.17 | 27118.8 | 0.04166 | 0 | 0 | 0 | 0 | ---- | 2021-05-07 | 2023156882
2021-05-31 | 2021-05-31 | 31 | 768960 | 1415 | 0 | 7374.33 | 32383.58 | 39757.91 | 0.0517 | 0 | 0 | 0 | 0 | ---- | 2021-06-10 | 2023339441
2021-06-30 | 2021-06-30 | 30 | 934488 | 1689 | 0 | 8961.74 | 36971.02 | 45932.76 | 0.04915 | 0 | 0 | 0 | 0 | ---- | 2021-07-09 | 2023490010
2021-07-31 | 2021-07-31 | 31 | 986760 | 1710 | 0 | 9463.03 | 38556.94 | 48019.97 | 0.04866 | 0 | 0 | 0 | 0 | ---- | 2021-08-10 | 2023650043
2021-08-31 | 2021-08-31 | 31 | 992304 | 1698 | 0 | 9516.2 | 34934.33 | 44450.53 | 0.0448 | 0 | 0 | 0 | 0 | ---- | 2021-09-09 | 2023821229
2021-09-30 | 2021-09-30 | 30 | 883008 | 1582 | 0 | 8468.05 | 24015.83 | 32483.88 | 0.03679 | 0 | 0 | 0 | 0 | ---- | 2021-10-08 | 2023950760
2021-10-31 | 2021-10-31 | 31 | 822816 | 1520 | 0 | 7890.81 | 22834.21 | 30725.02 | 0.03734 | 0 | 0 | 0 | 0 | ---- | 2021-11-09 | 2024105772
2021-11-30 | 2021-11-30 | 30 | 710352 | 1384 | 0 | 6812.28 | 19825.65 | 26637.93 | 0.0375 | 0 | 0 | 0 | 0 | ---- | 2021-12-16 | 2024268151
2021-12-31 | 2021-12-31 | 31 | 757872 | 1348 | 0 | 7267.99 | 19466.72 | 26734.71 | 0.03528 | 0 | 0 | 0 | 0 | ---- | 2022-01-13 | 2024339605
2022-01-31 | 2022-01-31 | 31 | 737280 | 1371 | 0 | 7070.52 | 19262.63 | 26333.15 | 0.03572 | 0 | 0 | 0 | 0 | ---- | 2022-02-16 | 2024438232
2022-02-28 | 2022-02-28 | 28 | 665208 | 1344 | 0 | 6379.34 | 18073.29 | 24452.63 | 0.03676 | 0 | 0 | 0 | 0 | ---- | 2022-03-18 | 2024600357
2022-03-31 | 2022-03-31 | 31 | 730152 | 1382 | 0 | 11967.19 | 19519.99 | 31487.18 | 0.04312 | 0 | 0 | 0 | 0 | ---- | 2022-04-11 | 2024683931
2022-04-30 | 2022-04-30 | 30 | 696096 | 1386 | 0 | 11409.01 | 19342.77 | 30751.78 | 0.04418 | 0 | 0 | 0 | 0 | ---- | 2022-05-06 | 2024743591
2022-05-31 | 2022-05-31 | 31 | 846576 | 1697 | 0 | 13875.38 | 29660.17 | 43535.55 | 0.05143 | 0 | 0 | 0 | 0 | ---- | 2022-06-08 | 2024932142
2022-06-30 | 2022-06-30 | 30 | 913896 | 1869 | 0 | 14978.75 | 32051.65 | 47030.4 | 0.05146 | 0 | 0 | 0 | 0 | ---- | 2022-07-07 | 2024989718
2022-07-31 | 2022-07-31 | 31 | 998640 | 1829 | 0 | 16367.71 | 59304.81 | 75672.52 | 0.07578 | 0 | 0 | 0 | 0 | ---- | 2022-08-10 | 2025060660
2022-08-31 | 2022-08-31 | 31 | 985176 | 1723 | 0 | 16147.03 | 32584.21 | 48731.24 | 0.04946 | 0 | 0 | 0 | 0 | ---- | 2022-09-08 | 2025126015

## OLD Electricity-ParkingDeck (hidden)
Account #3488731
PARKING DECK
Reporting Month | Service To | Days | kWh | Billed kW | Billed kVA/kVAR | Electric Fuel Charges | Electric Non-Fuel Charges | Electric Monthly Charges | Monthly $/kWh | Billed CCF | Gas Fuel Charges | Gas Non-Fuel Charges | Gas Monthly Charges | Monthly $/CCF | Mailed Date | Invoice
2021-04-30 | 2021-04-30 | 30 | 127400 | 255 | 0 | 1221.77 | 4329 | 5550.77 | 0.04357 | 0 | 0 | 0 | 0 | ---- | 2021-05-07 | 2023156857
2021-05-31 | 2021-05-31 | 31 | 150800 | 268 | 0 | 1446.17 | 6225.09 | 7671.26 | 0.05087 | 0 | 0 | 0 | 0 | ---- | 2021-06-10 | 2023339209
2021-06-30 | 2021-06-30 | 30 | 163400 | 307 | 0 | 1567.01 | 6865.86 | 8432.87 | 0.05161 | 0 | 0 | 0 | 0 | ---- | 2021-07-13 | 2023511598
2021-07-31 | 2021-07-31 | 31 | 171800 | 303 | 0 | 1647.56 | 7043.51 | 8691.07 | 0.05059 | 0 | 0 | 0 | 0 | ---- | 2021-08-10 | 2023649585
2021-08-31 | 2021-08-31 | 31 | 172600 | 284 | 0 | 1655.23 | 6244.23 | 7899.46 | 0.04577 | 0 | 0 | 0 | 0 | ---- | 2021-09-09 | 2023821134
2021-09-30 | 2021-09-30 | 30 | 148200 | 312 | 0 | 1421.24 | 4759.86 | 6181.1 | 0.04171 | 0 | 0 | 0 | 0 | ---- | 2021-10-08 | 2023950647
2021-10-31 | 2021-10-31 | 31 | 149600 | 268 | 0 | 1434.66 | 4345.52 | 5780.18 | 0.03864 | 0 | 0 | 0 | 0 | ---- | 2021-11-10 | 2024110291
2021-11-30 | 2021-11-30 | 30 | 130200 | 256 | 0 | 1248.62 | 3933.3 | 5181.92 | 0.0398 | 0 | 0 | 0 | 0 | ---- | 2021-12-09 | 2024242387
2021-12-31 | 2021-12-31 | 31 | 138600 | 263 | 0 | 1329.17 | 3976.67 | 5305.84 | 0.03828 | 0 | 0 | 0 | 0 | ---- | 2022-01-13 | 2024340759
2022-01-31 | 2022-01-31 | 31 | 128400 | 257 | 0 | 1231.36 | 3762.74 | 4994.1 | 0.03889 | 0 | 0 | 0 | 0 | ---- | 2022-02-11 | 2024429890
2022-02-28 | 2022-02-28 | 28 | 121400 | 261 | 0 | 1164.23 | 3687.07 | 4851.3 | 0.03996 | 0 | 0 | 0 | 0 | ---- | 2022-03-18 | 2024600114
2022-03-31 | 2022-03-31 | 31 | 128000 | 257 | 0 | 2097.92 | 3809.11 | 5907.03 | 0.04615 | 0 | 0 | 0 | 0 | ---- | 2022-04-11 | 2024683882
2022-04-30 | 2022-04-30 | 30 | 118600 | 253 | 0 | 1943.85 | 3642.15 | 5586 | 0.0471 | 0 | 0 | 0 | 0 | ---- | 2022-05-06 | 2024743566
2022-05-31 | 2022-05-31 | 31 | 139000 | 268 | 0 | 2278.21 | 5101.77 | 7379.98 | 0.05309 | 0 | 0 | 0 | 0 | ---- | 2022-06-09 | 2024934151
2022-06-30 | 2022-06-30 | 30 | 146600 | 321 | 0 | 2402.77 | 5603.08 | 8005.85 | 0.05461 | 0 | 0 | 0 | 0 | ---- | 2022-07-07 | 2024989662
2022-07-31 | 2022-07-31 | 31 | 160800 | 295 | 0 | 2635.51 | 10952.44 | 13587.95 | 0.0845 | 0 | 0 | 0 | 0 | ---- | 2022-08-11 | 2025064935
2022-08-31 | 2022-08-31 | 31 | 163600 | 284 | 0 | 2681.4 | 5712.53 | 8393.93 | 0.05131 | 0 | 0 | 0 | 0 | ---- | 2022-09-09 | 2025129020

## Refrigerant Leak Rates
Refrigerant Leak Rates
Source: US EPA. Greenhouse Gas Inventory Guidance: Direct Fugitive Emissions from Refrigeration, Air Conditioning, Fire Suppression, and Industrial Gases. November 2014. Accessed 2023-01-13 at https://www.epa.gov/sites/default/files/2015-07/documents/fugitiveemissions.pdf
|  |  | Refrigerant | GWP (AR4)
|  |  | R407C | 1774
|  |  | R22 | 1760
|  |  | R410a | 2088
|  |  | R134a | 1300
Application | DEFINITION (added by Harbor per IPCC, Special Report SROC04/SROC5) | Capacity (kg) Range | Assembly | Operating Emissions | Remaining Refrigerant at Disposal | Recovery Rate | End of Life
|  |  | % of initial charge | % of initial charge | % of capacity | % of remaining | % of initial charge
1 - Domestic Refrigeration | Used for food storage in dwelling units and non-commercial areas, such as offices. | 0.05-0.5 | 1% | 0.5% | 80% | 70% | 24%
2 - Stand-Alone Commercial Applications | Systems where all the components are integrated: wine coolers, beer coolers, ice cream freezers, beverage vending machines and all kinds of standalone display cases. | 0.2-6.0 | 3% | 15% | 80% | 70% | 24%
3 - Medium and Large Commercial Refrigeration | Categorized by whether refrigerant evaporation occurs in the coolers, or whether a low temperature secondary heat transfer fluid (HTF) that is cooled centrally is circulated in a closed loop to the display cabinets and cold stores. | 50-2,000 | 3% | 35% | 100% | 70% | 30%
4 - Transport Refrigeration | Refrigeration systems for transporting chilled or frozen goods. | 3.0-8.0 | 1% | 50% | 50% | 70% | 15%
5 - Industrial Refrigeration | Refrigerating systems used for food processing and cold storage are based on vapour compression systems of the direct type, with the refrigerant distributed to heat exchangers in the space or apparatus to be refrigerated. Such systems are generally custom-made and erected on site. | 10-10,000 | 3% | 25% | 100% | 90% | 10%
6 - Chillers | Comfort air conditioning in large commercial buildings is often provided by water chillers connected to an air handling and distribution system. Chillers cool water or a water/antifreeze mixture which is then pumped through a heat exchanger in an air handler or fan-coil unit to cool and dehumidify the air. | 10-2,000 | 1% | 15% | 100% | 95% | 5%
7 - Residential and Commercial A/C, including Heat Pumps | Comfort air conditioning provided through small, stationary residential and commercial air conditioning units. | 0.5-100 | 1% | 10% | 80% | 80% | 16%
8- Mobile Air Conditioning | Mobile air-conditioning systems used in passenger cars, truck cabins, buses, and trains. | 0.5-1.5 | 0.5% | 20% | 50% | 50% | 25%
AC = Residential and Commercial A/C, including Heat Pumps

## Natural Gas
Natural Gas Consumption
Monthly Natural Gas Consumption
Reporting Month | LR Airport Main Terminal | AMF | AMF | Airfield Vault Generator | Airfield Vault Generator | Total | Natural Gas MMBtu/CCF
| MMBtu | CCF | MMBtu | CCF | MMBtu | MMBtu | 0.1026
Source: | Data provided by Berhard TMP: Quarterly Natural Gas Management Report for LR Airport Main Terminal | Data provided by Randy Ellison on 2023-02-09. | conversion to MMBtu | Data provided by Randy Ellison on 2023-02-09. | conversion to MMBtu
2019-01-01 | 4121 | 3627 | 372.1302 |  | 0 | 4493.1302
2019-02-01 | 3158 | 5301 | 543.8826 |  | 0 | 3701.8826
2019-03-01 | 2999 | 5064 | 519.5664 | 47 | 4.8222 | 3523.3886
2019-04-01 | 2160 | 1978 | 202.9428 | 231 | 23.7006 | 2386.6434
2019-05-01 | 1776 | 303 | 31.0878 | 55 | 5.643 | 1812.7308
2019-06-01 | 1203 | 88 | 9.0288 | 70 | 7.182 | 1219.2108
2019-07-01 | 1330 | 69 | 7.0794 | 61 | 6.2586 | 1343.338
2019-08-01 | 1443 | 76 | 7.7976 | 87 | 8.9262 | 1459.7238
2019-09-01 | 1425 | 65 | 6.669 | 30 | 3.078 | 1434.747
2019-10-01 | 2095 | 613 | 62.8938 | 99 | 10.1574 | 2168.0512
2019-11-01 | 3299 | 2922 | 299.7972 | 121 | 12.4146 | 3611.2118
2019-12-01 | 3977 | 3402 | 349.0452 | 282 | 28.9332 | 4354.9784
2020-01-01 | 4012 | 4484 | 460.0584 | 372 | 38.1672 | 4510.2256
2020-02-01 | 3814 | 5357 | 549.6282 | 786 | 80.6436 | 4444.2718
2020-03-01 | 2879 | 9079 | 931.5054 | 125 | 12.825 | 3823.3304
2020-04-01 | 2244 | 4462 | 457.8012 | 171 | 17.5446 | 2719.3458
2020-05-01 | 1720 | 2359 | 242.0334 | 47 | 4.8222 | 1966.8556
2020-06-01 | 1387 | 647 | 66.3822 | 58 | 5.9508 | 1459.333
2020-07-01 | 1519 | 67 | 6.8742 | 40 | 4.104 | 1529.9782
2020-08-01 | 1616 | 67 | 6.8742 | 40 | 4.104 | 1626.9782
2020-09-01 | 1723 | 72 | 7.3872 | 62 | 6.3612 | 1736.7484
2020-10-01 | 2017 | 790 | 81.054 | 71 | 7.2846 | 2105.3386
2020-11-01 | 2349 | 766 | 78.5916 | 50 | 5.13 | 2432.7216
2020-12-01 | 3789 | 7355 | 754.623 | 165 | 16.929 | 4560.552
2021-01-01 | 3965 | 7699 | 789.9174 | 96 | 9.8496 | 4764.767
2021-02-01 | 4235 | 6150 | 630.99 | 65 | 6.669 | 4872.659
2021-03-01 | 2573 | 7781 | 798.3306 | 565 | 57.969 | 3429.2996
2021-04-01 | 2088 | 3401 | 348.9426 | 69 | 7.0794 | 2444.022
2021-05-01 | 1610 | 2297 | 235.6722 | 50 | 5.13 | 1850.8022
2021-06-01 | 1447 | 539 | 55.3014 | 30 | 3.078 | 1505.3794
2021-07-01 | 1353 | 156 | 16.0056 | 116 | 11.9016 | 1380.9072
2021-08-01 | 1370 | 54 | 5.5404 | 40 | 4.104 | 1379.6444
2021-09-01 | 1383 | 59 | 6.0534 | 33 | 3.3858 | 1392.4392
2021-10-01 | 1740 | 128 | 13.1328 | 82 | 8.4132 | 1761.546
2021-11-01 | 3087 | 1266 | 129.8916 | 41 | 4.2066 | 3221.0982
2021-12-01 | 2990 | 6094 | 625.2444 | 69 | 7.0794 | 3622.3238
2022-01-01 | 4268 | 2982 | 305.9532 | 403 | 41.3478 | 4615.301
2022-02-01 | 3615 | 7757 | 795.8682 | 157 | 16.1082 | 4426.9764
2022-03-01 | 3192 | 5229 | 536.4954 | 87 | 8.9262 | 3737.4216
2022-04-01 | 2419 | 4302 | 441.3852 | 88 | 9.0288 | 2869.414
2022-05-01 | 2065 | 2528 | 259.3728 | 76 | 7.7976 | 2332.1704
2022-06-01 | 1967 | 96 | 9.8496 | 59 | 6.0534 | 1982.903
2022-07-01 | 1397 | 54 | 5.5404 | 69 | 7.0794 | 1409.6198
2022-08-01 | 1601 | 62 | 6.3612 | 79 | 8.1054 | 1615.4666
2022-09-01 | 1624 | 58 | 5.9508 | 58 | 5.9508 | 1635.9016
2022-10-01 |  | 63 | 6.4638 | 55 | 5.643 | 12.1068
2022-11-01 |  | 475 | 48.735 | 42 | 4.3092 | 53.0442
2022-12-01 |  | 3099 | 317.9574 | 270 | 27.702 | 345.6594
2019 TOTAL | 28986 |  | 2411.9208 |  | 111.1158 | 31509.0366
2020 TOTAL | 29069 |  | 3642.813 |  | 203.8662 | 32915.6792
2021 TOTAL | 27841 |  | 3655.0224 |  | 128.8656 | 31624.888
2022 YTD TOTAL | 22148 |  | 2421.9756 |  | 120.3498 | 24690.3254

## Electricity
Electricity Consumption (kWh)
Data provided by Janet Hicks of Entergy on 2022-12-15
|  | Account # | 100786938 | 100980036 | 111736849 | 172407595 | 3488731 | 44445559 | 56826605 | 6924724 | 8599318 | 8599706 | 8599847 | 8600025 | 8610362 | 8610644 | 92029362
|  | Include? | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
|  | Long Description | CARGO ACCT | OLD FAA TOWER SITE | AIRFIELD MAINTENANCE FACILITY | LRMAC | PARKING DECK | LR MUNICIPAL AIRPORT | LR MUNICIPAL AIRPORT | L R MUNICIPAL AIRPORT | LR MUNICIPAL AIRPORT | LR MUNICIPAL AIRPORT | LR MUNICIPAL AIRPORT | LR MUNICIPAL AIRPORT | LR MUNICIPAL AIRPORT | LR MUNICIPAL AIRPORT | LR MUNICIPAL AIRPORT
|  | Medium Description | LR MUNICIPAL AIRPORT | LR MUNICIPAL AIRPORT | CLINTON NATIONAL AIRPORT | CLINTON NATIONAL AIRPORT | LR MUNICIPAL AIRPORT PARKING DECK | LR MUNICIPAL AIRPORT | LR MUNICIPAL AIRPORT | L R MUNICIPAL AIRPORT | LR MUNICIPAL AIRPORT | LR MUNICIPAL AIRPORT | LR MUNICIPAL AIRPORT | LR MUNICIPAL AIRPORT | LR MUNICIPAL AIRPORT | LR MUNICIPAL AIRPORT | LR MUNICIPAL AIRPORT
|  | Address | 1000 TEMPLE ST | AMF TOWER | 1 AIRPORT RD NEW MAINTENANCE BLDG | 2201 CRISP DR | 1 AIRPORT RD | WATER FEATURE AIRPORT DR | 1701 BOND AVE | EAST AIRFIELD ELECTRICAL VAULT | 1 AIRPORT RD GSE PARKING PAD | 4200 E 35TH ST | ADAMS FLD AIRPORT BUS ACCT | WEST AIRFIELD ELECTRICAL VAULT | E 38TH E OF HWY 365 | E 41ST E OF HWY 365 | 4300 33RD ST | TOTALS
1 | 2019 | 2019-01-01 | 1127 | 960 | 37680 | 0 | 154400 | 3280 | 3007 | 11800 | 1920 | 7 | 764280 | 32560 | 7 | 9 | 0 | 1011037
2 | 2019 | 2019-02-01 | 1138 | 800 | 34560 | 0 | 138200 | 3120 | 2478 | 11000 | 1680 | 5 | 770616 | 26800 | 7 | 9 | 0 | 990413
3 | 2019 | 2019-03-01 | 1075 | 800 | 43520 | 0 | 142600 | 5120 | 2704 | 13800 | 1680 | 5 | 754776 | 31680 | 6 | 9 | 0 | 997775
4 | 2019 | 2019-04-01 | 682 | 880 | 34000 | 0 | 191000 | 5120 | 2203 | 11800 | 1440 | 6 | 1186416 | 24880 | 6 | 8 | 0 | 1458441
5 | 2019 | 2019-05-01 | 590 | 800 | 34000 | 0 | 152400 | 5600 | 2113 | 11000 | 1440 | 5 | 831600 | 25760 | 5 | 5 | 0 | 1065318
6 | 2019 | 2019-06-01 | 608 | 880 | 42000 | 0 | 158200 | 6560 | 2214 | 12400 | 1360 | 4 | 882288 | 26400 | 7 | 6 | 0 | 1132927
7 | 2019 | 2019-07-01 | 680 | 880 | 45200 | 0 | 179200 | 6880 | 2102 | 12200 | 1200 | 6 | 1073160 | 26160 | 9 | 6 | 0 | 1347683
8 | 2019 | 2019-08-01 | 612 | 800 | 52000 | 0 | 171200 | 6960 | 2299 | 13800 | 1360 | 5 | 1064448 | 29200 | 8 | 6 | 0 | 1342698
9 | 2019 | 2019-09-01 | 741 | 240 | 39040 | 0 | 165200 | 5120 | 2062 | 11800 | 1280 | 5 | 1036728 | 24720 | 7 | 5 | 0 | 1286948
10 | 2019 | 2019-10-01 | 450 | 160 | 31680 | 0 | 142400 | 5040 | 2225 | 10200 | 1440 | 5 | 797544 | 25040 | 7 | 5 | 0 | 1016196
11 | 2019 | 2019-11-01 | 798 | 240 | 31040 | 0 | 138800 | 3760 | 2092 | 10200 | 1440 | 4 | 701712 | 23680 | 9 | 6 | 0 | 913781
12 | 2019 | 2019-12-01 | 908 | 160 | 42320 | 0 | 155200 | 5280 | 2572 | 13400 | 1840 | 5 | 700920 | 30320 | 9 | 5 | 0 | 952939
1 | 2020 | 2020-01-01 | 975 | 240 | 42160 | 0 | 147400 | 5600 | 2522 | 13600 | 1840 | 6 | 712008 | 28320 | 10 | 7 | 0 | 954688
2 | 2020 | 2020-02-01 | 1035 | 160 | 41840 | 0 | 133200 | 5200 | 2155 | 4400 | 1520 | 6 | 623304 | 24640 | 9 | 6 | 0 | 837475
3 | 2020 | 2020-03-01 | 842 | 240 | 51280 | 0 | 140400 | 5280 | 2424 | 3400 | 1760 | 5 | 677952 | 28320 | 9 | 5 | 0 | 911917
4 | 2020 | 2020-04-01 | 595 | 160 | 45280 | 0 | 132400 | 5200 | 1794 | 8800 | 1440 | 5 | 586872 | 24480 | 7 | 6 | 0 | 807039
5 | 2020 | 2020-05-01 | 570 | 240 | 37200 | 0 | 145400 | 5680 | 1838 | 9400 | 1200 | 5 | 662112 | 22480 | 7 | 5 | 0 | 886137
6 | 2020 | 2020-06-01 | 491 | 240 | 38960 | 0 | 150000 | 5280 | 1842 | 9400 | 1200 | 5 | 779328 | 24240 | 7 | 6 | 0 | 1010999
7 | 2020 | 2020-07-01 | 642 | 160 | 44240 | 0 | 167800 | 6000 | 1653 | 10600 | 1200 | 6 | 948024 | 27840 | 7 | 6 | 0 | 1208178
8 | 2020 | 2020-08-01 | 579 | 240 | 36080 | 0 | 162600 | 5680 | 1569 | 9400 | 1200 | 4 | 933768 | 25920 | 6 | 5 | 0 | 1177051
9 | 2020 | 2020-09-01 | 530 | 160 | 37760 | 329 | 148800 | 5840 | 1712 | 10600 | 1440 | 0 | 825264 | 28080 | 6 | 5 | 0 | 1060526
10 | 2020 | 2020-10-01 | 491 | 240 | 30320 | 1024 | 134000 | 5760 | 1721 | 10600 | 1520 | 0 | 750024 | 27360 | 8 | 2 | 0 | 963070
11 | 2020 | 2020-11-01 | 677 | 160 | 35760 | 989 | 124000 | 5360 | 1761 | 11800 | 1760 | 0 | 676368 | 28400 | 8 | 0 | 0 | 887043
12 | 2020 | 2020-12-01 | 961 | 240 | 37120 | 1099 | 135400 | 5200 | 1724 | 11400 | 1760 | 0 | 718344 | 26480 | 9 | 1 | 4 | 939742
1 | 2021 | 2021-01-01 | 1304 | 160 | 42480 | 1278 | 137400 | 5600 | 1980 | 12400 | 2000 | 0 | 718344 | 30160 | 9 | 1 | 5 | 953121
2 | 2021 | 2021-02-01 | 1384 | 240 | 41600 | 1111 | 117000 | 5040 | 1765 | 11200 | 1680 | 0 | 624096 | 28320 | 9 | 0 | 4 | 833449
3 | 2021 | 2021-03-01 | 759 | 160 | 36800 | 1118 | 127400 | 4880 | 1547 | 10800 | 1600 | 0 | 651816 | 24160 | 9 | 0 | 4 | 861053
4 | 2021 | 2021-04-01 | 520 | 160 | 27040 | 917 | 127400 | 4320 | 1163 | 8600 | 1200 | 0 | 649440 | 20080 | 7 | 0 | 4 | 840851
5 | 2021 | 2021-05-01 | 522 | 160 | 33920 | 858 | 150800 | 5280 | 918 | 10200 | 1520 | 0 | 767448 | 24000 | 7 | 0 | 3 | 995636
6 | 2021 | 2021-06-01 | 508 | 160 | 35280 | 997 | 163400 | 3520 | 810 | 10400 | 1280 | 0 | 932976 | 20880 | 7 | 0 | 0 | 1170218
7 | 2021 | 2021-07-01 | 637 | 160 | 39200 | 828 | 171800 | 3520 | 949 | 10800 | 1360 | 0 | 985248 | 19360 | 7 | 0 | 4 | 1233873
8 | 2021 | 2021-08-01 | 670 | 560 | 36640 | 786 | 172600 | 5440 | 904 | 10000 | 1200 | 0 | 990792 | 15600 | 6 | 0 | 3 | 1235201
9 | 2021 | 2021-09-01 | 636 | 2080 | 36320 | 871 | 148200 | 5280 | 802 | 10600 | 1440 | 0 | 881496 | 17280 | 7 | 0 | 3 | 1105015
10 | 2021 | 2021-10-01 | 539 | 2560 | 35520 | 919 | 149600 | 5200 | 654 | 11200 | 1600 | 0 | 821304 | 16880 | 7 | 0 | 4 | 1045987
11 | 2021 | 2021-11-01 | 839 | 960 | 35760 | 1088 | 130200 | 5440 | 679 | 10600 | 1680 | 0 | 708840 | 16240 | 3 | 0 | 4 | 912333
12 | 2021 | 2021-12-01 | 1032 | 880 | 37200 | 1173 | 138600 | 4880 | 719 | 11200 | 1840 | 0 | 756360 | 16800 | 5 | 0 | 5 | 970694
1 | 2022 | 2022-01-01 | 1592 | 1200 | 41840 | 1315 | 128400 | 5520 | 812 | 14400 | 2000 | 0 | 735768 | 22640 | 3 | 0 | 3 | 955493
2 | 2022 | 2022-02-01 | 1445 | 1120 | 37680 | 1048 | 121400 | 4320 | 672 | 11000 | 1680 | 0 | 663696 | 18320 | 2 | 0 | 4 | 862387
3 | 2022 | 2022-03-01 | 1271 | 960 | 37360 | 1047 | 128000 | 4640 | 676 | 11200 | 1680 | 0 | 728640 | 15840 | 3 | 0 | 4 | 931321
4 | 2022 | 2022-04-01 | 853 | 880 | 33840 | 1001 | 118600 | 4240 | 597 | 9000 | 1440 | 0 | 694584 | 14240 | 2 | 0 | 4 | 879281
5 | 2022 | 2022-05-01 | 627 | 1040 | 32720 | 858 | 139000 | 4320 | 563 | 9400 | 1280 | 0 | 845064 | 17200 | 2 | 0 | 3 | 1052077
6 | 2022 | 2022-06-01 | 645 | 2320 | 38720 | 909 | 146600 | 5280 | 659 | 11400 | 1280 | 0 | 912384 | 20800 | 3 | 0 | 3 | 1141003
7 | 2022 | 2022-07-01 | 718 | 3360 | 38000 | 768 | 160800 | 4880 | 763 | 10200 | 1280 | 0 | 997128 | 21280 | 3 | 0 | 3 | 1239183
8 | 2022 | 2022-08-01 | 614 | 2320 | 37280 | 806 | 163600 | 4720 | 608 | 10200 | 1280 | 0 | 983664 | 25840 | 2 | 0 | 3 | 1230937
9 | 2022 | 2022-09-01 | 614 | 2000 | 38320 | 895 | 141400 | 6080 | 643 | 11000 | 1520 | 0 | 850608 | 28640 | 3 | 0 | 4 | 1081727
10 | 2022 | 2022-10-01 | 713 | 1120 | 32240 | 1016 | 130800 | 5200 | 667 | 9800 | 1680 | 0 | 761112 | 28080 | 2 | 0 | 4 | 972434
11 | 2022 | 2022-11-01 | 958 | 240 | 30560 | 1042 | 124200 | 4720 | 638 | 10600 | 1680 | 0 | 723096 | 24320 | 3 | 0 | 4 | 922061
0
|  | 2019 TOTAL | 9409 | 7600 | 467040 | 0 | 1888800 | 61840 | 28071 | 143400 | 18080 | 62 | 10564488 | 327200 | 87 | 79 | 0
|  | 2020 TOTAL | 8388 | 2480 | 478000 | 3441 | 1721400 | 66080 | 22715 | 113400 | 17840 | 42 | 8893368 | 316560 | 93 | 54 | 4
|  | 2021 TOTAL | 9350 | 8240 | 437760 | 11944 | 1734400 | 58400 | 12890 | 128000 | 18400 | 0 | 9488160 | 249760 | 83 | 1 | 43
|  | 2022 YTD TOTAL | 10050 | 16560 | 398560 | 10705 | 1502800 | 53920 | 7298 | 118200 | 16800 | 0 | 8895744 | 237200 | 28 | 0 | 39
|  | 2019 TOTAL | 13516156
|  | 2020 TOTAL | 11643865
|  | 2021 TOTAL | 12157431
|  | 2022 YTD TOTAL | 11267904

## Electricity-ALL (hidden)
Electricity Consumption (kWh)
Data provided by Janet Hicks of Entergy on 2022-12-15
|  | Account # | 100786938 | 100980036 | 101820892 | 105193676 | 111736849 | 112406467 | 112426515 | 112426572 | 112426671 | 112426705 | 116997776 | 118465178 | 13595699 | 13595749 | 161084611 | 179977467 | 172407595 | 3488731 | 3493889 | 3923216 | 44445559 | 56826605 | 6924724 | 69755742 | 8567455 | 8567588 | 8599318 | 8599706 | 8599847 | 8600025 | 8600108 | 8610362 | 8610644 | 9183112 | 92029362
|  | Include? | Yes | Yes | No | No | Yes | No | No | No | No | No | No | No | No | No | No | No | Yes | Yes | No | No | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes
|  | Long Description | CARGO ACCT | OLD FAA TOWER SITE | LR MUNICIPAL AIRPORT | LR MUNICIPAL AIRPORT | AIRFIELD MAINTENANCE FACILITY | CLINTON NATIONAL AIRPORT | CLINTON NATIONAL AIRPORT | CLINTON NATIONAL AIRPORT | CLINTON NATIONAL AIRPORT | CLINTON NATIONAL AIRPORT | AIR CARGO 2, STE., 4A | CLINTON NATIONAL AIRPORT | LR MUNICIPAL AIRPORT | LR MUNICIPAL AIRPORT | CLINTON NATIONAL AIRPORT | CLINTON NATIONAL AIRPORT | LRMAC | PARKING DECK | LR MUNICIPAL AIRPORT | L R MUN AIRPORT | LR MUNICIPAL AIRPORT | LR MUNICIPAL AIRPORT | L R MUNICIPAL AIRPORT | DTFASW-08-U-00005 | L R MUN AIRPORT | L R MUN AIRPORT | LR MUNICIPAL AIRPORT | LR MUNICIPAL AIRPORT | LR MUNICIPAL AIRPORT | LR MUNICIPAL AIRPORT | LR MUNICIPAL AIRPORT | LR MUNICIPAL AIRPORT | LR MUNICIPAL AIRPORT | RTR DTFA07-02-U-03105 | LR MUNICIPAL AIRPORT
|  | Medium Description | LR MUNICIPAL AIRPORT | LR MUNICIPAL AIRPORT | LR MUNICIPAL AIRPORT | LR MUNICIPAL AIRPORT | CLINTON NATIONAL AIRPORT | CLINTON NATIONAL AIRPORT | CLINTON NATIONAL AIRPORT | CLINTON NATIONAL AIRPORT | CLINTON NATIONAL AIRPORT | CLINTON NATIONAL AIRPORT | CLINTON NATIONAL AIRPORT | CLINTON NATIONAL AIRPORT | LR MUNICIPAL AIRPORT | LR MUNICIPAL AIRPORT | CLINTON NATIONAL AIRPORT | CLINTON NATIONAL AIRPORT | CLINTON NATIONAL AIRPORT | LR MUNICIPAL AIRPORT PARKING DECK | LR MUNICIPAL AIRPORT | L R MUN AIRPORT | LR MUNICIPAL AIRPORT | LR MUNICIPAL AIRPORT | L R MUNICIPAL AIRPORT | FAA | L R MUN AIRPORT | L R MUN AIRPORT | LR MUNICIPAL AIRPORT | LR MUNICIPAL AIRPORT | LR MUNICIPAL AIRPORT | LR MUNICIPAL AIRPORT | LR MUNICIPAL AIRPORT | LR MUNICIPAL AIRPORT | LR MUNICIPAL AIRPORT | FAA LITTLE ROCK SSC | LR MUNICIPAL AIRPORT
|  | Address | 1000 TEMPLE ST | AMF TOWER | 1000 TEMPLE ST E 10TH EXIT 10 | 1100 TEMPLE ST | 1 AIRPORT RD NEW MAINTENANCE BLDG | 2400 DAVID GRUNDFEST JR DR | 2400 DAVID GRUNDFEST JR DR | 2400 DAVID GRUNDFEST JR DR | 2400 DAVID GRUNDFEST JR DR | 2400 DAVID GRUNDFEST JR DR | 1100 TEMPLE ST | 3301 E ROOSEVELT RD | AIR CARGO 3 | AIR CARGO 2 | 1100 HARRINGTON AVE | 1100 TEMPLE ST | 2201 CRISP DR | 1 AIRPORT RD | 1701 BOND AVE | L R AIRPORT | WATER FEATURE AIRPORT DR | 1701 BOND AVE | EAST AIRFIELD ELECTRICAL VAULT | 5016 E ROOSEVELT RD | E 10TH H ST EXIT 2 | E 10TH ST EXIT 8 | 1 AIRPORT RD GSE PARKING PAD | 4200 E 35TH ST | ADAMS FLD AIRPORT BUS ACCT | WEST AIRFIELD ELECTRICAL VAULT | ARFF STATION 22 | E 38TH E OF HWY 365 | E 41ST E OF HWY 365 | 2601 GRUNDFEST DR | 4300 33RD ST
1 | 2019 | 2019-01-01 | 1127 | 960 | 72 | 157 | 37680 | 20560 | 86800 | 78400 | 11840 | 81000 | 979 | 160 | 668 | 792 | 0 | 0 | 0 | 154400 | 7440 | 3202 | 3280 | 3007 | 11800 | 17030 | 5439 | 915 | 1920 | 7 | 764280 | 32560 | 7600 | 7 | 9 | 2926 | 0
2 | 2019 | 2019-02-01 | 1138 | 800 | 222 | 139 | 34560 | 18000 | 79200 | 77400 | 10880 | 60000 | 861 | 133 | 635 | 748 | 0 | 0 | 0 | 138200 | 7440 | 2806 | 3120 | 2478 | 11000 | 16254 | 4710 | 891 | 1680 | 5 | 770616 | 26800 | 6600 | 7 | 9 | 2776 | 0
3 | 2019 | 2019-03-01 | 1075 | 800 | 220 | 237 | 43520 | 18640 | 76400 | 65400 | 12640 | 72600 | 830 | 136 | 712 | 803 | 0 | 0 | 0 | 142600 | 8320 | 2612 | 5120 | 2704 | 13800 | 17287 | 4437 | 897 | 1680 | 5 | 754776 | 31680 | 8200 | 6 | 9 | 3077 | 0
4 | 2019 | 2019-04-01 | 682 | 880 | 112 | 219 | 34000 | 23840 | 66000 | 42600 | 9120 | 68400 | 787 | 120 | 534 | 699 | 101 | 0 | 0 | 191000 | 8640 | 2455 | 5120 | 2203 | 11800 | 16700 | 3427 | 834 | 1440 | 6 | 1186416 | 24880 | 7200 | 6 | 8 | 2622 | 0
5 | 2019 | 2019-05-01 | 590 | 800 | 81 | 87 | 34000 | 24800 | 67200 | 49800 | 9360 | 84000 | 1021 | 105 | 485 | 674 | 270 | 0 | 0 | 152400 | 9120 | 2237 | 5600 | 2113 | 11000 | 16783 | 3024 | 1052 | 1440 | 5 | 831600 | 25760 | 7400 | 5 | 5 | 3022 | 0
6 | 2019 | 2019-06-01 | 608 | 880 | 57 | 87 | 42000 | 34320 | 76400 | 56800 | 4480 | 111000 | 1087 | 109 | 503 | 697 | 312 | 0 | 0 | 158200 | 15520 | 2205 | 6560 | 2214 | 12400 | 20193 | 2994 | 1854 | 1360 | 4 | 882288 | 26400 | 9000 | 7 | 6 | 3608 | 0
7 | 2019 | 2019-07-01 | 680 | 880 | 276 | 66 | 45200 | 48720 | 77200 | 41400 | 1360 | 123000 | 1467 | 102 | 503 | 662 | 296 | 0 | 0 | 179200 | 17760 | 1921 | 6880 | 2102 | 12200 | 18171 | 2902 | 2337 | 1200 | 6 | 1073160 | 26160 | 9800 | 9 | 6 | 2986 | 0
8 | 2019 | 2019-08-01 | 612 | 800 | 136 | 59 | 52000 | 17200 | 80800 | 41200 | 1440 | 143400 | 1303 | 119 | 445 | 593 | 350 | 0 | 0 | 171200 | 18960 | 1832 | 6960 | 2299 | 13800 | 20679 | 2650 | 2082 | 1360 | 5 | 1064448 | 29200 | 10800 | 8 | 6 | 4264 | 0
9 | 2019 | 2019-09-01 | 741 | 240 | 309 | 71 | 39040 | 35360 | 69200 | 38200 | 1280 | 126600 | 1259 | 106 | 539 | 710 | 301 | 0 | 0 | 165200 | 18640 | 2507 | 5120 | 2062 | 11800 | 18434 | 3572 | 2444 | 1280 | 5 | 1036728 | 24720 | 8400 | 7 | 5 | 3472 | 0
10 | 2019 | 2019-10-01 | 450 | 160 | 224 | 41 | 31680 | 29920 | 67600 | 47800 | 1200 | 91200 | 659 | 113 | 323 | 521 | 229 | 0 | 0 | 142400 | 10960 | 2260 | 5040 | 2225 | 10200 | 15946 | 2707 | 1180 | 1440 | 5 | 797544 | 25040 | 7800 | 7 | 5 | 3137 | 0
11 | 2019 | 2019-11-01 | 798 | 240 | 709 | 17 | 31040 | 15440 | 64000 | 40400 | 8320 | 63600 | 814 | 131 | 557 | 756 | 295 | 0 | 0 | 138800 | 7600 | 2356 | 3760 | 2092 | 10200 | 16257 | 4125 | 737 | 1440 | 4 | 701712 | 23680 | 5800 | 9 | 6 | 2287 | 0
12 | 2019 | 2019-12-01 | 908 | 160 | 366 | 50 | 42320 | 22160 | 79600 | 44400 | 18640 | 151800 | 1090 | 153 | 177 | 831 | 261 | 0 | 0 | 155200 | 7920 | 2937 | 5280 | 2572 | 13400 | 16039 | 4733 | 951 | 1840 | 5 | 700920 | 30320 | 7400 | 9 | 5 | 2655 | 0
1 | 2020 | 2020-01-01 | 975 | 240 | 114 | 58 | 42160 | 30000 | 88400 | 43800 | 18160 | 169800 | 1198 | 149 | 190 | 847 | 302 | 0 | 0 | 147400 | 8640 | 3012 | 5600 | 2522 | 13600 | 19478 | 4812 | 854 | 1840 | 6 | 712008 | 28320 | 7400 | 10 | 7 | 2588 | 0
2 | 2020 | 2020-02-01 | 1035 | 160 | 487 | 58 | 41840 | 24480 | 93600 | 39400 | 16240 | 52200 | 910 | 135 | 442 | 777 | 333 | 0 | 0 | 133200 | 8720 | 2669 | 5200 | 2155 | 4400 | 15775 | 4645 | 896 | 1520 | 6 | 623304 | 24640 | 7200 | 9 | 6 | 2430 | 0
3 | 2020 | 2020-03-01 | 842 | 240 | 298 | 51 | 51280 | 32480 | 101600 | 48400 | 16160 | 72000 | 1067 | 127 | 323 | 833 | 258 | 0 | 0 | 140400 | 8000 | 2685 | 5280 | 2424 | 3400 | 17906 | 4571 | 901 | 1760 | 5 | 677952 | 28320 | 8400 | 9 | 5 | 2402 | 0
4 | 2020 | 2020-04-01 | 595 | 160 | 71 | 18 | 45280 | 23120 | 69600 | 39400 | 7040 | 100200 | 715 | 94 | 375 | 1400 | 221 | 0 | 0 | 132400 | 6000 | 2182 | 5200 | 1794 | 8800 | 16684 | 3249 | 741 | 1440 | 5 | 586872 | 24480 | 7800 | 7 | 6 | 2622 | 0
5 | 2020 | 2020-05-01 | 570 | 240 | 82 | 14 | 37200 | 29760 | 81200 | 37600 | 1600 | 121200 | 483 | 68 | 744 | 977 | 228 | 0 | 0 | 145400 | 6800 | 1940 | 5680 | 1838 | 9400 | 16024 | 3271 | 1056 | 1200 | 5 | 662112 | 22480 | 7400 | 7 | 5 | 2203 | 0
6 | 2020 | 2020-06-01 | 491 | 240 | 70 | 15 | 38960 | 36560 | 73200 | 58600 | 1840 | 118800 | 757 | 72 | 895 | 652 | 261 | 0 | 0 | 150000 | 10560 | 2010 | 5280 | 1842 | 9400 | 19581 | 2677 | 1584 | 1200 | 5 | 779328 | 24240 | 9000 | 7 | 6 | 2003 | 0
7 | 2020 | 2020-07-01 | 642 | 160 | 425 | 15 | 44240 | 47440 | 77600 | 23400 | 2080 | 140400 | 1094 | 71 | 1000 | 682 | 662 | 0 | 0 | 167800 | 16560 | 1963 | 6000 | 1653 | 10600 | 17255 | 2881 | 2319 | 1200 | 6 | 948024 | 27840 | 10400 | 7 | 6 | 2390 | 0
8 | 2020 | 2020-08-01 | 579 | 240 | 482 | 14 | 36080 | 41040 | 58000 | 39000 | 2080 | 109200 | 1083 | 41 | 761 | 604 | 1802 | 0 | 0 | 162600 | 16640 | 1801 | 5680 | 1569 | 9400 | 18389 | 2754 | 2099 | 1200 | 4 | 933768 | 25920 | 9400 | 6 | 5 | 2394 | 0
9 | 2020 | 2020-09-01 | 530 | 160 | 585 | 14 | 37760 | 41120 | 82400 | 49800 | 1840 | 111600 | 999 | 61 | 480 | 619 | 1048 | 0 | 329 | 148800 | 14880 | 2054 | 5840 | 1712 | 10600 | 20537 | 3242 | 1750 | 1440 | 0 | 825264 | 28080 | 9400 | 6 | 5 | 2332 | 0
10 | 2020 | 2020-10-01 | 491 | 240 | 579 | 16 | 30320 | 30240 | 68000 | 41800 | 1840 | 84000 | 510 | 68 | 484 | 693 | 2567 | 0 | 1024 | 134000 | 10880 | 2247 | 5760 | 1721 | 10600 | 17044 | 3585 | 847 | 1520 | 0 | 750024 | 27360 | 8200 | 8 | 2 | 2596 | 0
11 | 2020 | 2020-11-01 | 677 | 160 | 404 | 30 | 35760 | 27520 | 72800 | 36000 | 1600 | 74400 | 589 | 81 | 526 | 743 | 3654 | 0 | 989 | 124000 | 7120 | 2517 | 5360 | 1761 | 11800 | 17160 | 4307 | 673 | 1760 | 0 | 676368 | 28400 | 8400 | 8 | 0 | 2968 | 0
12 | 2020 | 2020-12-01 | 961 | 240 | 78 | 62 | 37120 | 22720 | 73600 | 39200 | 7200 | 59400 | 1094 | 83 | 924 | 792 | 3365 | 0 | 1099 | 135400 | 6800 | 2563 | 5200 | 1724 | 11400 | 16682 | 4651 | 738 | 1760 | 0 | 718344 | 26480 | 7600 | 9 | 1 | 2788 | 4
1 | 2021 | 2021-01-01 | 1304 | 160 | 89 | 86 | 42480 | 23680 | 88000 | 89600 | 22560 | 76200 | 1417 | 93 | 1154 | 882 | 925 | 0 | 1278 | 137400 | 7200 | 2895 | 5600 | 1980 | 12400 | 19162 | 5612 | 952 | 2000 | 0 | 718344 | 30160 | 9000 | 9 | 1 | 3617 | 5
2 | 2021 | 2021-02-01 | 1384 | 240 | 80 | 78 | 41600 | 22400 | 81200 | 86400 | 16240 | 51600 | 1158 | 468 | 844 | 737 | 1028 | 0 | 1111 | 117000 | 6960 | 2448 | 5040 | 1765 | 11200 | 17747 | 5538 | 918 | 1680 | 0 | 624096 | 28320 | 8200 | 9 | 0 | 3833 | 4
3 | 2021 | 2021-03-01 | 759 | 160 | 77 | 53 | 36800 | 24400 | 70800 | 71800 | 16160 | 63000 | 854 | 1099 | 480 | 680 | 586 | 0 | 1118 | 127400 | 6480 | 2171 | 4880 | 1547 | 10800 | 16828 | 4149 | 727 | 1600 | 0 | 651816 | 24160 | 7800 | 9 | 0 | 2382 | 4
4 | 2021 | 2021-04-01 | 520 | 160 | 74 | 20 | 27040 | 23040 | 68400 | 60400 | 7040 | 64800 | 528 | 1088 | 455 | 606 | 529 | 0 | 917 | 127400 | 6080 | 1744 | 4320 | 1163 | 8600 | 15917 | 3006 | 611 | 1200 | 0 | 649440 | 20080 | 6000 | 7 | 0 | 2313 | 4
5 | 2021 | 2021-05-01 | 522 | 160 | 29 | 20 | 33920 | 30000 | 84800 | 52400 | 19200 | 86400 | 629 | 736 | 869 | 740 | 947 | 0 | 858 | 150800 | 7200 | 2039 | 5280 | 918 | 10200 | 18396 | 3522 | 866 | 1520 | 0 | 767448 | 24000 | 8200 | 7 | 0 | 2625 | 3
6 | 2021 | 2021-06-01 | 508 | 160 | 43 | 42 | 35280 | 34800 | 75200 | 54600 | 4400 | 100800 | 1056 | 796 | 867 | 676 | 2040 | 0 | 997 | 163400 | 14000 | 1836 | 3520 | 810 | 10400 | 18494 | 3014 | 1482 | 1280 | 0 | 932976 | 20880 | 9800 | 7 | 0 | 3191 | 0
7 | 2021 | 2021-07-01 | 637 | 160 | 264 | 85 | 39200 | 43840 | 83600 | 42000 | 2320 | 118200 | 1178 | 578 | 879 | 657 | 3474 | 0 | 828 | 171800 | 17440 | 1791 | 3520 | 949 | 10800 | 19176 | 2846 | 1939 | 1360 | 0 | 985248 | 19360 | 11200 | 7 | 0 | 3283 | 4
8 | 2021 | 2021-08-01 | 670 | 560 | 448 | 81 | 36640 | 42240 | 68800 | 45200 | 1840 | 108000 | 1222 | 542 | 436 | 638 | 3830 | 0 | 786 | 172600 | 17600 | 1997 | 5440 | 904 | 10000 | 18634 | 3056 | 2117 | 1200 | 0 | 990792 | 15600 | 11200 | 6 | 0 | 3655 | 3
9 | 2021 | 2021-09-01 | 636 | 2080 | 555 | 81 | 36320 | 40000 | 77200 | 38000 | 2000 | 103200 | 1188 | 555 | 529 | 649 | 3678 | 333 | 871 | 148200 | 16320 | 2161 | 5280 | 802 | 10600 | 18444 | 3371 | 1861 | 1440 | 0 | 881496 | 17280 | 10400 | 7 | 0 | 3286 | 3
10 | 2021 | 2021-10-01 | 539 | 2560 | 324 | 86 | 35520 | 31920 | 93200 | 40200 | 2800 | 91200 | 729 | 780 | 964 | 687 | 1999 | 189 | 919 | 149600 | 12080 | 2472 | 5200 | 654 | 11200 | 18251 | 3796 | 1132 | 1600 | 0 | 821304 | 16880 | 10200 | 7 | 0 | 2886 | 4
11 | 2021 | 2021-11-01 | 839 | 960 | 196 | 107 | 35760 | 22240 | 89200 | 46800 | 8400 | 66600 | 827 | 1020 | 1157 | 694 | 849 | 320 | 1088 | 130200 | 7440 | 2613 | 5440 | 679 | 10600 | 16862 | 4168 | 664 | 1680 | 0 | 708840 | 16240 | 8800 | 3 | 0 | 2529 | 4
12 | 2021 | 2021-12-01 | 1032 | 880 | 258 | 124 | 37200 | 24400 | 75600 | 51600 | 7600 | 63600 | 925 | 1072 | 1194 | 695 | 646 | 369 | 1173 | 138600 | 6800 | 2753 | 4880 | 719 | 11200 | 17039 | 4583 | 682 | 1840 | 0 | 756360 | 16800 | 8200 | 5 | 0 | 2527 | 5
1 | 2022 | 2022-01-01 | 1592 | 1200 | 385 | 151 | 41840 | 24880 | 78400 | 67000 | 0 | 66000 | 1096 | 1214 | 1565 | 784 | 792 | 31 | 1315 | 128400 | 7280 | 3171 | 5520 | 812 | 14400 | 19488 | 5002 | 849 | 2000 | 0 | 735768 | 22640 | 9400 | 3 | 0 | 2927 | 3
2 | 2022 | 2022-02-01 | 1445 | 1120 | 338 | 141 | 37680 | 20720 | 68800 | 65000 | 9200 | 48000 | 1092 | 955 | 1092 | 680 | 867 | 28 | 1048 | 121400 | 6560 | 2554 | 4320 | 672 | 11000 | 16619 | 4502 | 814 | 1680 | 0 | 663696 | 18320 | 8200 | 2 | 0 | 2603 | 4
3 | 2022 | 2022-03-01 | 1271 | 960 | 220 | 135 | 37360 | 23680 | 73600 | 65600 | 37440 | 56400 | 973 | 992 | 909 | 689 | 905 | 63 | 1047 | 128000 | 7200 | 2544 | 4640 | 676 | 11200 | 17570 | 4022 | 776 | 1680 | 0 | 728640 | 15840 | 8600 | 3 | 0 | 2556 | 4
4 | 2022 | 2022-04-01 | 853 | 880 | 203 | 102 | 33840 | 23760 | 70000 | 48400 | 15840 | 57600 | 782 | 859 | 653 | 635 | 853 | 182 | 1001 | 118600 | 7520 | 2181 | 4240 | 597 | 9000 | 16544 | 3380 | 667 | 1440 | 0 | 694584 | 14240 | 7800 | 2 | 0 | 2498 | 4
5 | 2022 | 2022-05-01 | 627 | 1040 | 80 | 81 | 32720 | 32240 | 67200 | 42800 | 8720 | 81600 | 816 | 713 | 565 | 619 | 1682 | 108 | 858 | 139000 | 10720 | 1983 | 4320 | 563 | 9400 | 17263 | 3003 | 1077 | 1280 | 0 | 845064 | 17200 | 9000 | 2 | 0 | 2615 | 3
6 | 2022 | 2022-06-01 | 645 | 2320 | 78 | 91 | 38720 | 41840 | 86000 | 46600 | 6960 | 115200 | 999 | 638 | 779 | 687 | 2978 | 108 | 909 | 146600 | 16800 | 2103 | 5280 | 659 | 11400 | 19724 | 3103 | 1820 | 1280 | 0 | 912384 | 20800 | 12200 | 3 | 0 | 3203 | 3
7 | 2022 | 2022-07-01 | 718 | 3360 | 77 | 80 | 38000 | 43600 | 82400 | 51400 | 6880 | 130200 | 1286 | 850 | 473 | 589 | 4413 | 125 | 768 | 160800 | 21280 | 1846 | 4880 | 763 | 10200 | 18158 | 2798 | 2330 | 1280 | 0 | 997128 | 21280 | 12800 | 3 | 0 | 3169 | 3
8 | 2022 | 2022-08-01 | 614 | 2320 | 110 | 77 | 37280 | 41040 | 72400 | 44000 | 5760 | 92400 | 1147 | 829 | 472 | 584 | 3557 | 107 | 806 | 163600 | 18240 | 1965 | 4720 | 608 | 10200 | 18612 | 2935 | 2149 | 1280 | 0 | 983664 | 25840 | 12600 | 2 | 0 | 2929 | 3
9 | 2022 | 2022-09-01 | 614 | 2000 | 218 | 101 | 38320 | 39600 | 79600 | 45000 | 7280 | 104400 | 1186 | 811 | 550 | 662 | 2859 | 169 | 895 | 141400 | 15360 | 2387 | 6080 | 643 | 11000 | 19518 | 3576 | 1716 | 1520 | 0 | 850608 | 28640 | 11400 | 3 | 0 | 3125 | 4
10 | 2022 | 2022-10-01 | 713 | 1120 | 146 | 86 | 32240 | 31120 | 70800 | 43600 | 11840 | 70200 | 807 | 597 | 484 | 638 | 1626 | 33 | 1016 | 130800 | 12960 | 2441 | 5200 | 667 | 9800 | 17763 | 3732 | 1059 | 1680 | 0 | 761112 | 28080 | 9600 | 2 | 0 | 2772 | 4
11 | 2022 | 2022-11-01 | 958 | 240 | 309 | 85 | 30560 | 26000 | 69200 | 45600 | 10320 | 55800 | 814 | 646 | 479 | 629 | 737 | 37 | 1042 | 124200 | 8480 | 2517 | 4720 | 638 | 10600 | 16753 | 3992 | 690 | 1680 | 0 | 723096 | 24320 | 9000 | 3 | 0 | 2388 | 4
|  | 2019 TOTAL | 9409 | 7600 | 2784 | 1230 | 467040 | 308960 | 890400 | 623800 | 90560 | 1176600 | 12157 | 1487 | 6081 | 8486 | 2415 | 0 | 0 | 1888800 | 138320 | 29330 | 61840 | 28071 | 143400 | 209773 | 44720 | 16174 | 18080 | 62 | 10564488 | 327200 | 96000 | 87 | 79 | 36832 | 0
|  | 2020 TOTAL | 8388 | 2480 | 3675 | 365 | 478000 | 386480 | 940000 | 496400 | 77680 | 1213200 | 10499 | 1050 | 7144 | 9619 | 14701 | 0 | 3441 | 1721400 | 121600 | 27643 | 66080 | 22715 | 113400 | 212515 | 44645 | 14458 | 17840 | 42 | 8893368 | 316560 | 100600 | 93 | 54 | 29716 | 4
|  | 2021 TOTAL | 9350 | 8240 | 2437 | 863 | 437760 | 362960 | 956000 | 679000 | 110560 | 993600 | 11711 | 8827 | 9828 | 8341 | 20531 | 1211 | 11944 | 1734400 | 125600 | 26920 | 58400 | 12890 | 128000 | 214950 | 46661 | 13951 | 18400 | 0 | 9488160 | 249760 | 109000 | 83 | 1 | 36127 | 43
|  | 2022 YTD TOTAL | 10050 | 16560 | 2164 | 1130 | 398560 | 348480 | 818400 | 565000 | 120240 | 877800 | 10998 | 9104 | 8021 | 7196 | 21269 | 991 | 10705 | 1502800 | 132400 | 25692 | 53920 | 7298 | 118200 | 198012 | 40045 | 13947 | 16800 | 0 | 8895744 | 237200 | 110600 | 28 | 0 | 30785 | 39
|  | 2019 IWH INCLUDED | 9409 | 7600 | 0 | 0 | 467040 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1888800 | 0 | 0 | 61840 | 28071 | 143400 | 0 | 0 | 0 | 18080 | 62 | 10564488 | 327200 | 0 | 87 | 79 | 0 | 0
|  | TOTAL KWH INCLUDED | 13516156
|  | TOTAL KWH | 17212265
|  | % Included | 78.53%

## Entergy Account List (hidden)
Entergy Account List
Column J completed by Randy Ellison on 2023-01-04
| Contract Account | Long description | Business Partner | Medium description | Full Address | City 1 | State | Device Number | INCLUDE?
(AKA: Under Airport Operational Control)
1 | 100786938 | CARGO ACCT | 7261767 | LR MUNICIPAL AIRPORT | 1000 TEMPLE ST | LITTLE ROCK | AR | AM11240448 | Yes
2 | 100980036 | OLD FAA TOWER SITE | 7261767 | LR MUNICIPAL AIRPORT | AMF TOWER | LITTLE ROCK | AR | AM10267075 | Yes
3 | 101820892 | LR MUNICIPAL AIRPORT | 7261767 | LR MUNICIPAL AIRPORT | 1000 TEMPLE ST E 10TH EXIT 10 | LITTLE ROCK | AR | AM11240452 | No
4 | 105193676 | LR MUNICIPAL AIRPORT | 7261767 | LR MUNICIPAL AIRPORT | 1100 TEMPLE ST | LITTLE ROCK | AR | AM11440588 | No
5 | 111736849 | AIRFIELD MAINTENANCE FACILITY | 7685506 | CLINTON NATIONAL AIRPORT | 1 AIRPORT RD NEW MAINTENANCE BLDG | LITTLE ROCK | AR | AM10101707 | Yes
6 | 112406467 | CLINTON NATIONAL AIRPORT | 7685506 | CLINTON NATIONAL AIRPORT | 2400 DAVID GRUNDFEST JR DR | LITTLE ROCK | AR | AM10101712 | No
7 | 112426515 | CLINTON NATIONAL AIRPORT | 7685506 | CLINTON NATIONAL AIRPORT | 2400 DAVID GRUNDFEST JR DR | LITTLE ROCK | AR | AM10100643 | No
8 | 112426572 | CLINTON NATIONAL AIRPORT | 7685506 | CLINTON NATIONAL AIRPORT | 2400 DAVID GRUNDFEST JR DR | LITTLE ROCK | AR | AM12154875 | No
9 | 112426671 | CLINTON NATIONAL AIRPORT | 7685506 | CLINTON NATIONAL AIRPORT | 2400 DAVID GRUNDFEST JR DR | LITTLE ROCK | AR | AM12828084 | No
10 | 112426705 | CLINTON NATIONAL AIRPORT | 7685506 | CLINTON NATIONAL AIRPORT | 2400 DAVID GRUNDFEST JR DR | LITTLE ROCK | AR | AM10100644 | No
11 | 116997776 | AIR CARGO 2, STE., 4A | 7685506 | CLINTON NATIONAL AIRPORT | 1100 TEMPLE ST | LITTLE ROCK | AR | AM10346881 | No
12 | 118465178 | CLINTON NATIONAL AIRPORT | 7685506 | CLINTON NATIONAL AIRPORT | 3301 E ROOSEVELT RD | LITTLE ROCK | AR | AM11240470 | No
13 | 13595699 | LR MUNICIPAL AIRPORT | 1575252 | LR MUNICIPAL AIRPORT | AIR CARGO 3 | LITTLE ROCK | AR | AM11445022 | No
14 | 13595749 | LR MUNICIPAL AIRPORT | 1575255 | LR MUNICIPAL AIRPORT | AIR CARGO 2 | LITTLE ROCK | AR | AM11240469 | No
15 | 161084611 | CLINTON NATIONAL AIRPORT | 7685506 | CLINTON NATIONAL AIRPORT | 1100 HARRINGTON AVE | LITTLE ROCK | AR | AM12148214 | No
16 | 179977467 | CLINTON NATIONAL AIRPORT | 7685506 | CLINTON NATIONAL AIRPORT | 1100 TEMPLE ST | LITTLE ROCK | AR | AM12866819 | No
17 | 172407595 | LRMAC | 7685506 | CLINTON NATIONAL AIRPORT | 2201 CRISP DR | LITTLE ROCK | AR | AM11738426 | Yes
18 | 3488731 | PARKING DECK | 513127 | LR MUNICIPAL AIRPORT PARKING DECK | 1 AIRPORT RD | LITTLE ROCK | AR | 3687260 | Yes
19 | 3493889 | LR MUNICIPAL AIRPORT | 493955 | LR MUNICIPAL AIRPORT | 1701 BOND AVE | LITTLE ROCK | AR | AM12157094 | No
20 | 3923216 | L R MUN AIRPORT | 301023 | L R MUN AIRPORT | L R AIRPORT | LITTLE ROCK | AR | AM11445023 | No
21 | 44445559 | LR MUNICIPAL AIRPORT | 660458 | LR MUNICIPAL AIRPORT | WATER FEATURE AIRPORT DR | LITTLE ROCK | AR | AM10101713 | Yes
22 | 56826605 | LR MUNICIPAL AIRPORT | 493955 | LR MUNICIPAL AIRPORT | 1701 BOND AVE | LITTLE ROCK | AR | AM10022554 | Yes
23 | 6924724 | L R MUNICIPAL AIRPORT | 691815 | L R MUNICIPAL AIRPORT | EAST AIRFIELD ELECTRICAL VAULT | LITTLE ROCK | AR | AM10101710 | Yes
24 | 69755742 | DTFASW-08-U-00005 | 6082426 | FAA | 5016 E ROOSEVELT RD | LITTLE ROCK | AR | AM11727600 | No
25 | 8567455 | L R MUN AIRPORT | 653653 | L R MUN AIRPORT | E 10TH H ST EXIT 2 | LITTLE ROCK | AR | AM11240449 | No
26 | 8567588 | L R MUN AIRPORT | 653653 | L R MUN AIRPORT | E 10TH ST EXIT 8 | LITTLE ROCK | AR | AM10346882 | No
27 | 8599318 | LR MUNICIPAL AIRPORT | 660458 | LR MUNICIPAL AIRPORT | 1 AIRPORT RD GSE PARKING PAD | LITTLE ROCK | AR | AM10101708 | Yes
28 | 8599706 | LR MUNICIPAL AIRPORT | 660458 | LR MUNICIPAL AIRPORT | 4200 E 35TH ST | LITTLE ROCK | AR | AM11646583 | Yes
29 | 8599847 | LR MUNICIPAL AIRPORT | 660458 | LR MUNICIPAL AIRPORT | ADAMS FLD AIRPORT BUS ACCT | LITTLE ROCK | AR | 7857472 | Yes
30 | 8600025 | LR MUNICIPAL AIRPORT | 660458 | LR MUNICIPAL AIRPORT | WEST AIRFIELD ELECTRICAL VAULT | LITTLE ROCK | AR | AM10101965 | Yes
31 | 8600108 | LR MUNICIPAL AIRPORT | 660458 | LR MUNICIPAL AIRPORT | ARFF STATION 22 | LITTLE ROCK | AR | AM10101709 | No
32 | 8610362 | LR MUNICIPAL AIRPORT | 660458 | LR MUNICIPAL AIRPORT | E 38TH E OF HWY 365 | LITTLE ROCK | AR | 3328300 | Yes
33 | 8610644 | LR MUNICIPAL AIRPORT | 660458 | LR MUNICIPAL AIRPORT | E 41ST E OF HWY 365 | COLLEGE STATION | AR | AM11728381 | Yes
34 | 9183112 | RTR DTFA07-02-U-03105 | 171972 | FAA LITTLE ROCK SSC | 2601 GRUNDFEST DR | LITTLE ROCK | AR | AM11647109 | No
35 | 92029362 | LR MUNICIPAL AIRPORT | 660458 | LR MUNICIPAL AIRPORT | 4300 33RD ST | LITTLE ROCK | AR | AM14176317 | Yes