## GHG (LP FULL) (hidden)
Lincoln Park - Every Building Connects
MNPower Renewable Reduction % |  | 5% | 52.49% | 60.5% | 57.59% | 57.69% | 59.74% | 61.79% | 63.85% | 65.9% | 67.95% | 70% | 73% | 76% | 79% | 82% | 85% | 88% | 91% | 94% | 97% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Year |  | 2005 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
MNPower Metric Tons per MWh |  | 0.962 | 0.457 | 0.38 | 0.408 | 0.407 | 0.38727 | 0.36753 | 0.3478 | 0.32807 | 0.30833 | 0.2886 | 0.25974 | 0.23088 | 0.20202 | 0.17316 | 0.1443 | 0.11544 | 0.08658 | 0.05772 | 0.02886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Baseline LP Energy | MMBtu |  |  | 124000 | 124000 | 124000 | 124000 | 124000 | 124000 | 124000 | 124000 | 124000 | 124000 | 124000 | 124000 | 124000 | 124000 | 124000 | 124000 | 124000 | 124000 | 124000 | 124000 | 124000 | 124000 | 124000 | 124000 | 124000 | 124000 | 124000 | 124000 | 124000
Assumed Connected Enegy | MMBtu |  |  | 124000 | 124000 | 124000 | 124000 | 124000 | 124000 | 124000 | 124000 | 124000 | 124000 | 124000 | 124000 | 124000 | 124000 | 124000 | 124000 | 124000 | 124000 | 124000 | 124000 | 124000 | 124000 | 124000 | 124000 | 124000 | 124000 | 124000 | 124000 | 124000
Building Energy | MMBtu |  |  | 99200 | 99200 | 99200 | 99200 | 99200 | 99200 | 99200 | 99200 | 99200 | 99200 | 99200 | 99200 | 99200 | 99200 | 99200 | 99200 | 99200 | 99200 | 99200 | 99200 | 99200 | 99200 | 99200 | 99200 | 99200 | 99200 | 99200 | 99200 | 99200
HP Electricity | MWh |  |  | 6922.3469 | 6922.3469 | 6922.3469 | 6922.3469 | 6922.3469 | 6922.3469 | 6922.3469 | 6922.3469 | 6922.3469 | 6922.3469 | 6922.3469 | 6922.3469 | 6922.3469 | 6922.3469 | 6922.3469 | 6922.3469 | 6922.3469 | 6922.3469 | 6922.3469 | 6922.3469 | 6922.3469 | 6922.3469 | 6922.3469 | 6922.3469 | 6922.3469 | 6922.3469 | 6922.3469 | 6922.3469 | 6922.3469
District System Operational | % |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Natural Gas Metric Tons CO2 | Metric Tons CO2 |  |  | 6582.5771 | 6582.5771 | 6582.5771 | 6582.5771 | 6582.5771 | 6582.5771 | 6582.5771 | 6582.5771 | 6582.5771 | 6582.5771 | 6582.5771 | 6582.5771 | 6582.5771 | 6582.5771 | 6582.5771 | 6582.5771 | 6582.5771 | 6582.5771 | 6582.5771 | 6582.5771 | 6582.5771 | 6582.5771 | 6582.5771 | 6582.5771 | 6582.5771 | 6582.5771 | 6582.5771 | 6582.5771 | 6582.5771
District System HP Metric Tons CO2 | Metric Tons CO2 |  |  | 6582.5771 | 6582.5771 | 6582.5771 | 6582.5771 | 6582.5771 | 6582.5771 | 2270.9913 | 2134.3903 | 1997.7893 | 1798.0104 | 1598.2315 | 1398.4525 | 1198.6736 | 998.8947 | 799.1157 | 599.3368 | 399.5579 | 199.7789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
District System Pumping | Metric Tons CO2 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 162.7211 | 152.9333 | 143.1456 | 128.831 | 114.5165 | 100.2019 | 85.8874 | 71.5728 | 57.2582 | 42.9437 | 28.6291 | 14.3146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual CO2 Percent Reduction | % |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 63.03% | 65.25% | 67.48% | 70.73% | 73.98% | 77.23% | 80.49% | 83.74% | 86.99% | 90.24% | 93.5% | 96.75% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Annual CO2 Reduction | Metric Tons CO2 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 4148.8648 | 4295.2535 | 4441.6422 | 4655.7357 | 4869.8292 | 5083.9227 | 5298.0162 | 5512.1097 | 5726.2032 | 5940.2967 | 6154.3901 | 6368.4836 | 6582.5771 | 6582.5771 | 6582.5771 | 6582.5771 | 6582.5771 | 6582.5771 | 6582.5771 | 6582.5771 | 6582.5771 | 6582.5771 | 6582.5771
Notes:
Furnace/Boiler Eff | 80%
Connected Load (NG offset) | 100%
Heat Pump COP | 4.2
Natural Gas lbs CO2/MMBtu | 117
Hydronic Pumps kWh/MMBtu | 5
https://allete.blob.core.windows.net/allete/Documents/Sustainability/ALE-Sustainability-Report.pdf
https://mn.gov/commerce/news/?id=17-563384#:~:text=The%20bill%20establishes%20a%20standard,for%20all%20electric%20utilities%20by
Cumulative CO2 Emissions from 2025 to 2030 (Metric Tons)
Lnkn Prk Natural Gas Consumption | 39495.4628
District System w/ Heat Pumps | 26609.7023
Emissions Avoided | 12885.7605
Percent Reduction | 32.63%
Cumulative CO2 Emissions from 2025 to 2050 (Metric Tons)
Lnkn Prk Natural Gas Consumption | 171147.0054
District System w/ Heat Pumps | 36243.9094
Emissions Avoided | 134903.096
Percent Reduction | 78.82%

## GHG (LP BASE)
Lincoln Park - Probable Connections
MNPower Renewable Reduction % |  | 5% | 52.49% | 60.5% | 57.59% | 57.69% | 59.74% | 61.79% | 63.85% | 65.9% | 67.95% | 70% | 73% | 76% | 79% | 82% | 85% | 88% | 91% | 94% | 97% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Year |  | 2005 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
MNPower Metric Tons per MWh |  | 0.962 | 0.457 | 0.38 | 0.408 | 0.407 | 0.38727 | 0.36753 | 0.3478 | 0.32807 | 0.30833 | 0.2886 | 0.25974 | 0.23088 | 0.20202 | 0.17316 | 0.1443 | 0.11544 | 0.08658 | 0.05772 | 0.02886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Baseline LP Energy | MMBtu |  |  | 124000 | 124000 | 124000 | 124000 | 124000 | 124000 | 124000 | 124000 | 124000 | 124000 | 124000 | 124000 | 124000 | 124000 | 124000 | 124000 | 124000 | 124000 | 124000 | 124000 | 124000 | 124000 | 124000 | 124000 | 124000 | 124000 | 124000 | 124000 | 124000
Assumed Connected Enegy | MMBtu |  |  | 62000 | 62000 | 62000 | 62000 | 62000 | 62000 | 62000 | 62000 | 62000 | 62000 | 62000 | 62000 | 62000 | 62000 | 62000 | 62000 | 62000 | 62000 | 62000 | 62000 | 62000 | 62000 | 62000 | 62000 | 62000 | 62000 | 62000 | 62000 | 62000
Building Energy | MMBtu |  |  | 49600 | 49600 | 49600 | 49600 | 49600 | 49600 | 49600 | 49600 | 49600 | 49600 | 49600 | 49600 | 49600 | 49600 | 49600 | 49600 | 49600 | 49600 | 49600 | 49600 | 49600 | 49600 | 49600 | 49600 | 49600 | 49600 | 49600 | 49600 | 49600
HP Electricity | MWh |  |  | 3461.1734 | 3461.1734 | 3461.1734 | 3461.1734 | 3461.1734 | 3461.1734 | 3461.1734 | 3461.1734 | 3461.1734 | 3461.1734 | 3461.1734 | 3461.1734 | 3461.1734 | 3461.1734 | 3461.1734 | 3461.1734 | 3461.1734 | 3461.1734 | 3461.1734 | 3461.1734 | 3461.1734 | 3461.1734 | 3461.1734 | 3461.1734 | 3461.1734 | 3461.1734 | 3461.1734 | 3461.1734 | 3461.1734
District System Operational | % |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Natural Gas Metric Tons CO2 | Metric Tons CO2 |  |  | 3291.2886 | 3291.2886 | 3291.2886 | 3291.2886 | 3291.2886 | 3291.2886 | 3291.2886 | 3291.2886 | 3291.2886 | 3291.2886 | 3291.2886 | 3291.2886 | 3291.2886 | 3291.2886 | 3291.2886 | 3291.2886 | 3291.2886 | 3291.2886 | 3291.2886 | 3291.2886 | 3291.2886 | 3291.2886 | 3291.2886 | 3291.2886 | 3291.2886 | 3291.2886 | 3291.2886 | 3291.2886 | 3291.2886
District System HP Metric Tons CO2 | Metric Tons CO2 |  |  | 3291.2886 | 3291.2886 | 3291.2886 | 3291.2886 | 3291.2886 | 3291.2886 | 1135.4956 | 1067.1951 | 998.8947 | 899.0052 | 799.1157 | 699.2263 | 599.3368 | 499.4473 | 399.5579 | 299.6684 | 199.7789 | 99.8895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
District System Pumping | Metric Tons CO2 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 81.3605 | 76.4667 | 71.5728 | 64.4155 | 57.2582 | 50.101 | 42.9437 | 35.7864 | 28.6291 | 21.4718 | 14.3146 | 7.1573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual CO2 Percent Reduction | % |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 63.03% | 65.25% | 67.48% | 70.73% | 73.98% | 77.23% | 80.49% | 83.74% | 86.99% | 90.24% | 93.5% | 96.75% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Annual CO2 Reduction | Metric Tons CO2 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2074.4324 | 2147.6268 | 2220.8211 | 2327.8679 | 2434.9146 | 2541.9613 | 2649.0081 | 2756.0548 | 2863.1016 | 2970.1483 | 3077.1951 | 3184.2418 | 3291.2886 | 3291.2886 | 3291.2886 | 3291.2886 | 3291.2886 | 3291.2886 | 3291.2886 | 3291.2886 | 3291.2886 | 3291.2886 | 3291.2886
Notes:
Furnace/Boiler Eff | 80%
Connected Load (NG offset) | 50%
Heat Pump COP | 4.2
Natural Gas lbs CO2/MMBtu | 117
Hydronic Pumps kWh/MMBtu | 5
https://allete.blob.core.windows.net/allete/Documents/Sustainability/ALE-Sustainability-Report.pdf
https://mn.gov/commerce/news/?id=17-563384#:~:text=The%20bill%20establishes%20a%20standard,for%20all%20electric%20utilities%20by
Cumulative CO2 Emissions from 2025 to 2030 (Metric Tons)
Lnkn Prk Natural Gas Consumption | 19747.7314 | 2022: lower number because system does not come online until 2028
District System w/ Heat Pumps | 13304.8511
Emissions Avoided | 6442.8803
Percent Reduction | 32.63%
Cumulative CO2 Emissions from 2025 to 2050 (Metric Tons)
Lnkn Prk Natural Gas Consumption | 85573.5027
District System w/ Heat Pumps | 18121.9547
Emissions Avoided | 67451.548
Percent Reduction | 78.82%

## GHG (DES FULL) (hidden)
DES - Full Downtown HW Load
MNPower Renewable Reduction % |  | 5% | 52.49% | 60.5% | 57.59% | 57.69% | 59.74% | 61.79% | 63.85% | 65.9% | 67.95% | 70% | 73% | 76% | 79% | 82% | 85% | 88% | 91% | 94% | 97% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Year |  | 2005 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
MNPower Metric Tons per MWh |  | 0.962 | 0.457 | 0.38 | 0.408 | 0.407 | 0.38727 | 0.36753 | 0.3478 | 0.32807 | 0.30833 | 0.2886 | 0.25974 | 0.23088 | 0.20202 | 0.17316 | 0.1443 | 0.11544 | 0.08658 | 0.05772 | 0.02886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DES HW Customer Metering | MMBtu |  |  | 85000 | 85000 | 85000 | 85000 | 85000 | 85000 | 85000 | 85000 | 85000 | 85000 | 85000 | 85000 | 85000 | 85000 | 85000 | 85000 | 85000 | 85000 | 85000 | 85000 | 85000 | 85000 | 85000 | 85000 | 85000 | 85000 | 85000 | 85000 | 85000
DES HW Generation Nat Gas Input | MMBtu |  |  | 106250 | 106250 | 106250 | 106250 | 106250 | 106250 | 106250 | 106250 | 106250 | 106250 | 106250 | 106250 | 106250 | 106250 | 106250 | 106250 | 106250 | 106250 | 106250 | 106250 | 106250 | 106250 | 106250 | 106250 | 106250 | 106250 | 106250 | 106250 | 106250
CO2 Emissions | Metric Tons |  |  | 6203.2186 | 6203.2186 | 6203.2186 | 6203.2186 | 6203.2186 | 6203.2186 | 6203.2186 | 6203.2186 | 6203.2186 | 6203.2186 | 6203.2186 | 6203.2186 | 6203.2186 | 6203.2186 | 6203.2186 | 6203.2186 | 6203.2186 | 6203.2186 | 6203.2186 | 6203.2186 | 6203.2186 | 6203.2186 | 6203.2186 | 6203.2186 | 6203.2186 | 6203.2186 | 6203.2186 | 6203.2186 | 6203.2186
DES HP | MWh |  |  | 5931.4464 | 5931.4464 | 5931.4464 | 5931.4464 | 5931.4464 | 5931.4464 | 5931.4464 | 5931.4464 | 5931.4464 | 5931.4464 | 5931.4464 | 5931.4464 | 5931.4464 | 5931.4464 | 5931.4464 | 5931.4464 | 5931.4464 | 5931.4464 | 5931.4464 | 5931.4464 | 5931.4464 | 5931.4464 | 5931.4464 | 5931.4464 | 5931.4464 | 5931.4464 | 5931.4464 | 5931.4464 | 5931.4464
DES Pumping | MWh |  |  | 425 | 425 | 425 | 425 | 425 | 425 | 425 | 425 | 425 | 425 | 425 | 425 | 425 | 425 | 425 | 425 | 425 | 425 | 425 | 425 | 425 | 425 | 425 | 425 | 425 | 425 | 425 | 425 | 425
District System Operational | % |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
DES HP CO2 Emissions | Metric Tons |  |  | 6203.2186 | 6203.2186 | 6203.2186 | 6203.2186 | 6203.2186 | 6203.2186 | 2085.3382 | 1959.9043 | 1834.4704 | 1651.0234 | 1467.5764 | 1284.1293 | 1100.6823 | 917.2352 | 733.7882 | 550.3411 | 366.8941 | 183.447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual CO2 Percent Reduction | % |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 66.38% | 68.41% | 70.43% | 73.38% | 76.34% | 79.3% | 82.26% | 85.21% | 88.17% | 91.13% | 94.09% | 97.04% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Annual CO2 Reduction | Metric Tons CO2 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 4117.8804 | 4243.3142 | 4368.7481 | 4552.1952 | 4735.6422 | 4919.0893 | 5102.5363 | 5285.9833 | 5469.4304 | 5652.8774 | 5836.3245 | 6019.7715 | 6203.2186 | 6203.2186 | 6203.2186 | 6203.2186 | 6203.2186 | 6203.2186 | 6203.2186 | 6203.2186 | 6203.2186 | 6203.2186 | 6203.2186
Notes:
Natural Gas lbs CO2/MMBtu | 117
Hydronic Pumps kWh/MMBtu | 5
DES Boiler/HW Efficiency | 80%
DES HP COP | 4.2
https://allete.blob.core.windows.net/allete/Documents/Sustainability/ALE-Sustainability-Report.pdf
https://mn.gov/commerce/news/?id=17-563384#:~:text=The%20bill%20establishes%20a%20standard,for%20all%20electric%20utilities%20by
DES Cumulative CO2 Emissions from 2025 to 2030 (Metric Tons)
DES Natural Gas Consumption | 37219.3114
DES w/ Heat Pumps | 24489.3686
Emissions Avoided | 12729.9427
Percent Reduction | 34.2%
DES Cumulative CO2 Emissions from 2025 to 2050 (Metric Tons)
DES Natural Gas Consumption | 161283.6826
DES w/ Heat Pumps | 32744.4856
Emissions Avoided | 128539.197
Percent Reduction | 79.7%

## GHG (DES BASE)
DES - Base Downtown HW Load
MNPower Renewable Reduction % |  | 5% | 52.49% | 60.5% | 57.59% | 57.69% | 59.74% | 61.79% | 63.85% | 65.9% | 67.95% | 70% | 73% | 76% | 79% | 82% | 85% | 88% | 91% | 94% | 97% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Year |  | 2005 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
MNPower Metric Tons per MWh |  | 0.962 | 0.457 | 0.38 | 0.408 | 0.407 | 0.38727 | 0.36753 | 0.3478 | 0.32807 | 0.30833 | 0.2886 | 0.25974 | 0.23088 | 0.20202 | 0.17316 | 0.1443 | 0.11544 | 0.08658 | 0.05772 | 0.02886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DES HW Customer Metering | MMBtu |  |  | 53500 | 53500 | 53500 | 53500 | 53500 | 53500 | 53500 | 53500 | 53500 | 53500 | 53500 | 53500 | 53500 | 53500 | 53500 | 53500 | 53500 | 53500 | 53500 | 53500 | 53500 | 53500 | 53500 | 53500 | 53500 | 53500 | 53500 | 53500 | 53500
DES Steam Water Makeup | MMBtu |  |  | 26700 | 26700 | 26700 | 26700 | 26700 | 26700 | 26700 | 26700 | 26700 | 26700 | 26700 | 26700 | 26700 | 26700 | 26700 | 26700 | 26700 | 26700 | 26700 | 26700 | 26700 | 26700 | 26700 | 26700 | 26700 | 26700 | 26700 | 26700 | 26700
DES HW Generation Nat Gas Input | MMBtu |  |  | 100250 | 100250 | 100250 | 100250 | 100250 | 100250 | 100250 | 100250 | 100250 | 100250 | 100250 | 100250 | 100250 | 100250 | 100250 | 100250 | 100250 | 100250 | 100250 | 100250 | 100250 | 100250 | 100250 | 100250 | 100250 | 100250 | 100250 | 100250 | 100250
CO2 Emissions | Metric Tons |  |  | 5321.8013 | 5321.8013 | 5321.8013 | 5321.8013 | 5321.8013 | 5321.8013 | 5321.8013 | 5321.8013 | 5321.8013 | 5321.8013 | 5321.8013 | 5321.8013 | 5321.8013 | 5321.8013 | 5321.8013 | 5321.8013 | 5321.8013 | 5321.8013 | 5321.8013 | 5321.8013 | 5321.8013 | 5321.8013 | 5321.8013 | 5321.8013 | 5321.8013 | 5321.8013 | 5321.8013 | 5321.8013 | 5321.8013
DES HP | MWh |  |  | 5596.4942 | 5596.4942 | 5596.4942 | 5596.4942 | 5596.4942 | 5596.4942 | 5596.4942 | 5596.4942 | 5596.4942 | 5596.4942 | 5596.4942 | 5596.4942 | 5596.4942 | 5596.4942 | 5596.4942 | 5596.4942 | 5596.4942 | 5596.4942 | 5596.4942 | 5596.4942 | 5596.4942 | 5596.4942 | 5596.4942 | 5596.4942 | 5596.4942 | 5596.4942 | 5596.4942 | 5596.4942 | 5596.4942
DES Pumping | MWh |  |  | 401 | 401 | 401 | 401 | 401 | 401 | 401 | 401 | 401 | 401 | 401 | 401 | 401 | 401 | 401 | 401 | 401 | 401 | 401 | 401 | 401 | 401 | 401 | 401 | 401 | 401 | 401 | 401 | 401
District System Operational | % |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
DES HP CO2 Emissions | Metric Tons |  |  | 5321.8013 | 5321.8013 | 5321.8013 | 5321.8013 | 5321.8013 | 5321.8013 | 1967.5779 | 1849.2274 | 1730.8768 | 1557.7891 | 1384.7015 | 1211.6138 | 1038.5261 | 865.4384 | 692.3507 | 519.263 | 346.1754 | 173.0877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual CO2 Percent Reduction | % |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 63.03% | 65.25% | 67.48% | 70.73% | 73.98% | 77.23% | 80.49% | 83.74% | 86.99% | 90.24% | 93.5% | 96.75% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Annual CO2 Reduction | Metric Tons CO2 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 3354.2234 | 3472.5739 | 3590.9245 | 3764.0121 | 3937.0998 | 4110.1875 | 4283.2752 | 4456.3629 | 4629.4505 | 4802.5382 | 4975.6259 | 5148.7136 | 5321.8013 | 5321.8013 | 5321.8013 | 5321.8013 | 5321.8013 | 5321.8013 | 5321.8013 | 5321.8013 | 5321.8013 | 5321.8013 | 5321.8013
Notes:
Natural Gas lbs CO2/MMBtu | 117
Hydronic Pumps kWh/MMBtu | 5
DES Boiler/HW Efficiency | 80%
DES HP COP | 4.2
https://allete.blob.core.windows.net/allete/Documents/Sustainability/ALE-Sustainability-Report.pdf
https://mn.gov/commerce/news/?id=17-563384#:~:text=The%20bill%20establishes%20a%20standard,for%20all%20electric%20utilities%20by
DES Cumulative CO2 Emissions Avoided from 2025 to 2030 (Metric Tons)
DES Natural Gas Consumption | 31930.8076 | 2025: 37219.3114
DES w/ Heat Pumps | 21513.0859 | 2024: Emissions Avoided; 2025: 10417.7217
Emissions Avoided | 10417.7217 | 2025: 26801.5897
Percent Reduction | 32.63% | 2025: 27.99%
DES Cumulative CO2 Emissions Avoided from 2025 to 2050 (Metric Tons)
DES Natural Gas Consumption | 138366.833 | 2025: 161283.6826
DES w/ Heat Pumps | 29302.0316 | 2024: Emissions Avoided; 2025: 109064.8014
Emissions Avoided | 109064.8014 | 2025: 52218.8812
Percent Reduction | 78.82% | 2025: 67.62%

## Make Up Water Preheat
2023 | Sewer Lbs | Cust ccf | Cust Usage | Sewer Cust | Sewer Costs | Water Bill | Water Usage (ccf) | Coverage | gallons | Hours | Average GPM | Average MMBtu/hr | MMBtu | Metric Tons CO2 | MMBtu | Metric Tons CO2 | HDD | HDD Adj. | HDD Adj. MMBtu | HDD Adj. Metric Tons CO2
January | 17859709 | 2863.723 | 41.35% | 83 | 7322.48 | 29030.11 | 6926 | 25.22% | 4662583.2 | 744 | 104.4485 | 5.2224 | 4856.8575 | 257.7552 | 4860.743 | 257.9614 | 1464 | 7.342% | 356.8647 | 18.9389
February | 19283866 | 3092.0801 | 41.35% | 83 | 7906.39 | 31304.63 | 7477 | 25.26% | 5033516.4 | 672 | 124.8392 | 6.242 | 5243.2463 | 278.261 | 5247.4408 | 278.4836 | 1370 | 13.29% | 697.4447 | 37.0136
March | 26334546 | 4222.6246 | 60.97% | 81 | 10797.16 | 29967.23 | 6926 | 36.03% | 4662583.2 | 744 | 104.4485 | 5.2224 | 4856.8575 | 257.7552 | 4860.743 | 257.9614 | 1294 | 18.1% | 879.856 | 46.6943
April | 20905337 | 3352.0756 | 43.21% | 81 | 8571.19 | 33427.17 | 7757 | 25.64% | 5222012.4 | 720 | 120.8799 | 6.044 | 5439.5963 | 288.6814 | 5443.9479 | 288.9123 | 870 | 100% | 5443.9479 | 288.9123
May | 17655320 | 2830.9502 | 51.95% | 81 | 7238.68 | 23588.17 | 5449 | 30.69% | 3668266.8 | 744 | 82.1744 | 4.1087 | 3821.1112 | 202.7878 | 3824.1681 | 202.95 | 339 | 100% | 3824.1681 | 202.95
June | 9003624 | 1443.6901 | 31.74% | 81 | 3691.49 | 19761.19 | 4549 | 18.68% | 3062386.8 | 720 | 70.8886 | 3.5444 | 3189.9863 | 169.2938 | 3192.5382 | 169.4292 | 101 | 100% | 3192.5382 | 169.4292
July | 11568300 | 1854.9242 | 53.86% | 81 | 4743 | 15030.45 | 3444 | 31.56% | 2318500.8 | 744 | 51.9377 | 2.5969 | 2415.105 | 128.1705 | 2417.0371 | 128.2731 | 49 | 100% | 2417.0371 | 128.2731
August | 9632609 | 1544.545 | 40.73% | 81 | 3949.37 | 16553.97 | 3792 | 23.86% | 2552774.4 | 744 | 57.1858 | 2.8593 | 2659.14 | 141.1215 | 2661.2673 | 141.2344 | 50 | 100% | 2661.2673 | 141.2344
September | 7063783 | 1132.6454 | 28.65% | 81 | 2896.15 | 17244.57 | 3954 | 16.79% | 2661832.8 | 720 | 61.6165 | 3.0808 | 2772.7425 | 147.1505 | 2774.9607 | 147.2682 | 307 | 100% | 2774.9607 | 147.2682
October | 16125185 | 2585.6 | 58.88% | 82 | 6611.33 | 19107.51 | 4391 | 34.6% | 2956021.2 | 744 | 66.2191 | 3.311 | 3079.1887 | 163.4137 | 3081.6521 | 163.5444 | 661 | 100% | 3081.6521 | 163.5444
November | 22759166 | 3649.3287 | 55.49% | 83 | 9848.76 | 28424.44 | 6576 | 34.65% | 4426963.2 | 720 | 102.476 | 5.1238 | 4611.42 | 244.7298 | 4615.1091 | 244.9256 | 1105 | 30.06% | 1387.4537 | 73.6327
December | 18605732 | 2983.3444 | 44.95% | 83 | 7628.35 | 28712.81 | 6637 | 26.57% | 4468028.4 | 744 | 100.0902 | 5.0045 | 4654.1962 | 246.9999 | 4657.9196 | 247.1975 | 1580 | 0% | 0 | 0
[9 empty] | Total |  |  |  | 47599.4475 | 2526.1203 | 47637.5271 | 2528.1412 |  |  | 26717.1905 | 1417.8912
2022 | Sewer Lbs | Cust ccf | Cust Usage | Sewer Cust | Sewer Costs | Water Bill | Water Usage (ccf) | Coverage | gallons | Hours | Average GPM | Average MMBtu/hr | MMBtu | Metric Tons CO2 | MMBtu | Metric Tons CO2 | HDD | HDD Adj. | HDD Adj. MMBtu | HDD Adj. Metric Tons CO2
January | 24352313 | 3904.7825 | 39.75% | 86 | 11070.99 | 40012.01 | 9824 | 27.67% | 6613516.8 | 744 | 148.1523 | 7.4076 | 6889.08 | 365.606 | 6894.5913 | 365.8985 | 1860 | 0% | 0 | 0
February | 21024026 | 3371.1069 | 39.69% | 86 | 10071.54 | 34591.85 | 8493 | 29.12% | 5717487.6 | 672 | 141.8028 | 7.0901 | 5955.7163 | 316.0721 | 5960.4808 | 316.3249 | 1653 | 11.13% | 663.3438 | 35.2039
March | 20355763 | 3263.9539 | 48.58% | 85 | 10073.28 | 30562 | 6719 | 32.96% | 4523230.8 | 744 | 101.3269 | 5.0663 | 4711.6988 | 250.0516 | 4715.4681 | 250.2516 | 1260 | 32.26% | 1521.1187 | 80.7263
April | 15639492 | 2507.7214 | 34.08% | 85 | 8355.19 | 29523.67 | 7359 | 28.3% | 4954078.8 | 720 | 114.6778 | 5.7339 | 5160.4987 | 273.8696 | 5164.6271 | 274.0887 | 931 | 100% | 5164.6271 | 274.0887
May | 11170455 | 1791.1316 | 36.24% | 85 | 6751.36 | 30059.16 | 4942 | 22.46% | 3326954.4 | 744 | 74.5285 | 3.7264 | 3465.5775 | 183.9195 | 3468.35 | 184.0666 | 380 | 100% | 3468.35 | 184.0666
June | 7421907 | 1190.069 | 30.16% | 85 | 4565.89 | 24092.88 | 3946 | 18.95% | 2656447.2 | 720 | 61.4918 | 3.0746 | 2767.1325 | 146.8527 | 2769.3462 | 146.9702 | 169 | 100% | 2769.3462 | 146.9702
July | 5652949 | 906.4246 | 23.25% | 84 | 3650.79 | 5699.73 | 3899 | 64.05% | 2624806.8 | 744 | 58.7994 | 2.94 | 2734.1738 | 145.1036 | 2736.3611 | 145.2197 | 31 | 100% | 2736.3611 | 145.2197
August | 7642261 | 1225.4018 | 35.52% | 85 | 4033.69 | 13185.78 | 3450 | 30.59% | 2322540 | 744 | 52.0282 | 2.6014 | 2419.3125 | 128.3938 | 2421.2479 | 128.4965 | 37 | 100% | 2421.2479 | 128.4965
September | 5891267 | 944.6378 | 26.47% | 84 | 3394.09 | 14569.06 | 3569 | 23.3% | 2402650.8 | 720 | 55.6169 | 2.7808 | 2502.7613 | 132.8225 | 2504.7635 | 132.9287 | 215 | 100% | 2504.7635 | 132.9287
October | 9863016 | 1581.4897 | 36.84% | 84 | 4983.56 | 17437.78 | 4293 | 28.58% | 2890047.6 | 744 | 64.7412 | 3.2371 | 3010.4663 | 159.7666 | 3012.8746 | 159.8944 | 578 | 100% | 3012.8746 | 159.8944
November | 14996260 | 2404.582 | 37.17% | 84 | 7450.22 | 26055.7 | 6469 | 28.59% | 4354930.8 | 720 | 100.8086 | 5.0404 | 4536.3862 | 240.7477 | 4540.0154 | 240.9403 | 1027 | 44.78% | 2033.2434 | 107.905
December | 23396844 | 3751.5774 | 49.62% | 84 | 11144.15 | 30381.39 | 7561 | 36.68% | 5090065.2 | 744 | 114.0248 | 5.7012 | 5302.1512 | 281.3871 | 5306.393 | 281.6122 | 1582 | 14.95% | 793.106 | 42.0904
[9 empty] | Total |  |  |  | 49454.955 | 2624.5928 | 49494.519 | 2626.6925 |  |  | 27088.3825 | 1437.5905
Notes:
[9 empty] | Steam Makeup (HW Removed) |  | 90%
[9 empty] | Raise makeup water temperature by |  | 100 | °F
[9 empty] | Boiler Eff |  | 80%
[9 empty] | Lbs CO2 per MMBtu |  | 117

## Summary
Metric Tons of CO2 Avoided
CPRG Time Period
| 2025-2030 | 2025-2050 | GSF | Tons Carbon Avoided per kSF
Lincoln Park - Connectable Load | 6442.8803 | 67451.548 | 1027362 | 6.2713
Lincoln Park - Full Load | 12885.7605 | 134903.096 | 2290137 | 5.6266
DES HW Baseload | 10417.7217 | 109064.8014 | 3652100 | 2.8525
DES HW Full | 12729.9427 | 128539.197 | 3652100 | 3.4857
DuluthWWHR- Lincoln Park Connectable + DES Baseload | 16860.602 | 176516.3495 | 4679462 | 3.6031 | * Basis of DuluthWWHR Application
Lincoln Park Full + DES Full | 25615.7033 | 263442.2931 | 5942237 | 4.3108
Metric Tons of CO2 Avoided
CPRG Time Period
| 2025-2030 | 2025-2050
Lincoln Park Connectable Load | 6400 | 67000
Lincoln Park Connectable + DES Baseload | 16900 | 177000 | * Basis of DuluthWWHR Application
*includes preheat
Impact of Schedule Shift on Metric Tons of CO2 Avoided
| Operational 2027 |  | Operational 2028 |  | Operational 2029
| CPRG Time Period |  | CPRG Time Period |  | CPRG Time Period
| 2025-2030 | 2025-2050 | 2025-2030 | 2025-2050 | 2025-2030 | 2025-2050
Lincoln Park Connectable Load | 8400 | 69000 | 6400 | 67000 | 4400 | 65000
Lincoln Park Connectable + DES Baseload | 22200 | 156000 | 16900 | 177000 | 11600 | 171700
| 31.25% | 2.985% | 0% | 0% | -31.25% | -2.985%
| Operational 2027 |  | Operational 2028 |  | Operational 2029
| Lincoln Park Connectable Load | Lincoln Park Connectable + DES Baseload | Lincoln Park Connectable Load | Lincoln Park Connectable + DES Baseload | Lincoln Park Connectable Load | Lincoln Park Connectable + DES Baseload
2025-2030 | 8400 | 22200 | 6400 | 16900 | 4400 | 11600
2030-2050 | 60600 | 133800 | 60600 | 160100 | 60600 | 160100
2025-2030 | 31.25% | 31.36% | 0% | 0% | -31.25% | -31.36%
2030-2050 | 2.985% | -11.86% | 0% | 0% | -2.985% | -2.994%
| 69000 | 156000 | 67000 | 177000 | 65000 | 172000