## Summary
| Year | Biogas Used for the Plant (therms) | Electricity Generated from the Plant for On-site Use (kWh) | Electricity Generated from the Plant Supplied to the Grid (kWh) | GHG Reductions (MT CO2e)
| 2025 | 0 | 0 | 0 | 0 | Assumptions:
| 2026 | 0 | 0 | 0 | 0 | Total CHP Capacity (2x1.2 MW)
Start Up | 2027 | 1303272.1182 | 15278688.3726 | 0 | -4924.9937 | Biogas to CHP over time (increasing biosolids, increasing HSW)
| 2028 | 1333972.8 | 15638602.5791 | 0 | -5613.6702 | Grid CI decreases over time in line with 2022 Scoping Plan (85% reduce in GHG emissions by 2045 vs. 1990 baseline)
| 2029 | 1333972.8 | 15638602.5791 | 0 | -5509.8658 | HSW ramp up in Year 1
| 2030 | 1333972.8 | 15638602.5791 | 0 | -5406.0614
| 2031 | 1333972.8 | 15638602.5791 | 0 | -5245.332
| 2032 | 1333972.8 | 15638602.5791 | 0 | -5084.6026
| 2033 | 1333972.8 | 15638602.5791 | 0 | -4923.8733
| 2034 | 1333972.8 | 15638602.5791 | 0 | -4763.1439
| 2035 | 1333972.8 | 15638602.5791 | 0 | -4602.4145
| 2036 | 1333972.8 | 15638602.5791 | 0 | -4441.6851
| 2037 | 1333972.8 | 15638602.5791 | 0 | -4280.9558
| 2038 | 1333972.8 | 15638602.5791 | 0 | -4120.2264
| 2039 | 1333972.8 | 15638602.5791 | 0 | -3959.497
| 2040 | 1400198.4 | 16414987.1043 | 0 | -3541.3353
| 2041 | 1400198.4 | 16414987.1043 | 0 | -3372.6264
| 2042 | 1400198.4 | 16414987.1043 | 0 | -3203.9176
| 2043 | 1400198.4 | 16414987.1043 | 0 | -3035.2087
| 2044 | 1400198.4 | 16414987.1043 | 0 | -2866.4999
| 2045 | 1400198.4 | 16414987.1043 | 0 | -2697.791
| 2046 | 1400198.4 | 16414987.1043 | 0 | -2697.791
| 2047 | 1400198.4 | 16414987.1043 | 0 | -2697.791
| 2048 | 1400198.4 | 16414987.1043 | 0 | -2697.791
| 2049 | 1400198.4 | 16414987.1043 | 0 | -2697.791
| 2050 | 1586260.8 | 18596257.9132 | 0 | -2329.3598

## GHG_Calculations
|  | Assumptions |  | Value | Unit | Source/Basis
|  | Diverting Food Waste From Landfills | % Dilution of Food Waste | 50% |  | Design basis
|  |  | GHG Emissions from Food Waste to Landfill | 0.25585 | MTCO2E/wet ton | EPA WARM (see separate model inputs)
|  | CHP GHG Emission Calculations | CO2 Emission Factor | 110 | lb/mmbtu | EPA AP-42 Table 3.2-2
|  |  | CH4 Emission Factor | 0 | lb/mmbtu | EPA AP-42 Table 3.2-2
|  |  | NO2 Emission Factor | 0 | lb/mmbtu | EPA AP-42 Table 3.2-2
|  |  | Maximum Daily Hours | 24 | hr | Design basis
|  |  | % of Max Operating Load | 90% |  | Design basis
|  |  | Annual Hours | 7884 | hr | Calculation
|  |  | Biogas heat value | 600 | BTU/ft3 | Wastewater Engineering: Treatment and Reuse (Metcalf & Eddy 2003)
|  |  | 1560 kW Engine Rated Capacity | 13.3074 | mmbtu/hr | Calculation
|  |  | 1200 kW Engine Rated Capacity | 10.2364 | mmbtu/hr | Calculation
|  | Plant Power Consumption | CHP Electrical Efficiency | 40% |  | Vendor Spec
|  | Boiler Emissions | Number of Digesters | 3 |  | Design basis
|  |  | Heat Demand per Digesters | 1.6 | MMBTU/hr | Package #1 Design basis
|  |  | Heat Demand per Digesters | 23360000 | ft3/yr | Calculation
|  |  | Boiler CO2e Emission Factor | 52.33 | kg CO2e/mmbtu | Emission factors for Greenhouse Gas Inventories, Stationary Combustion Emission Factors, USEPA 2015 IPCC Fifth Assessment Report, 2014 (AR5)
|  |  | Boiler CO2e Emission Factor | 115.3876 | lb CO2e/mmbtu | Calculation
|  |  | % of Running with CHPs Installed | 10% |  | Design basis
Year | Diverting Food Waste From Landfills |  |  | CHP GHG Emission Calculations | [8 empty] | Plant Power Consumption |  |  | Boiler Emissions |  | GHG Reductions
| HSW Feed | Food Waste Diverted from Landfill to Digester | Total GHG Emissions from Baseline MSW Generation and Management | Biogas Produced | Biogas Heat Value | 1200kW CHPs | 1560kW CHPs | Max Rated Capacity | CO2 Emissions | CH4 Emissions | N20 Emissions | Total CO2e Emissions | Electricity Generated from the Plant for On-site Use | Grid CI (from SANDAG) | Total GHG Emissions from SDG&E Power Consumption | GHG Emissions from Boiler without CHPs installed | GHG Emissions from Boiler with CHPs installed | MT CO2e/yr
| wet ton/day | wet tons/day | MTCOe/yr | scfm | mmbtu/hr | # | # | mmbtu/hr | ton/yr | ton/yr | ton/yr | MT CO2e/yr | kWh | lb CO2e/MWh | MT CO2e/yr | MT CO2e/yr | MT CO2e/yr
2027 | 131.4175 | 65.7087 | 6136.1944 | 413.2649 | 14.8775 | 2 | 0 | 18.4256 | 6451.197 | 0 | 0 | 5851.2357 | 15278688.3726 | 383.8444 | 2659.7002 | 2200.3718 | 220.0372 | -4924.9937
2028 | 150 | 75 | 7003.8571 | 423 | 15.228 | 2 | 0 | 18.4256 | 6603.1654 | 0 | 0 | 5989.071 | 15638602.5791 | 369.2083 | 2618.5494 | 2200.3718 | 220.0372 | -5613.6702
2029 | 150 | 75 | 7003.8571 | 423 | 15.228 | 2 | 0 | 18.4256 | 6603.1654 | 0 | 0 | 5989.071 | 15638602.5791 | 354.5721 | 2514.745 | 2200.3718 | 220.0372 | -5509.8658
2030 | 150 | 75 | 7003.8571 | 423 | 15.228 | 2 | 0 | 18.4256 | 6603.1654 | 0 | 0 | 5989.071 | 15638602.5791 | 339.936 | 2410.9406 | 2200.3718 | 220.0372 | -5406.0614
2031 | 150 | 75 | 7003.8571 | 423 | 15.228 | 2 | 0 | 18.4256 | 6603.1654 | 0 | 0 | 5989.071 | 15638602.5791 | 317.2736 | 2250.2112 | 2200.3718 | 220.0372 | -5245.332
2032 | 150 | 75 | 7003.8571 | 423 | 15.228 | 2 | 0 | 18.4256 | 6603.1654 | 0 | 0 | 5989.071 | 15638602.5791 | 294.6112 | 2089.4818 | 2200.3718 | 220.0372 | -5084.6026
2033 | 150 | 75 | 7003.8571 | 423 | 15.228 | 2 | 0 | 18.4256 | 6603.1654 | 0 | 0 | 5989.071 | 15638602.5791 | 271.9488 | 1928.7525 | 2200.3718 | 220.0372 | -4923.8733
2034 | 150 | 75 | 7003.8571 | 423 | 15.228 | 2 | 0 | 18.4256 | 6603.1654 | 0 | 0 | 5989.071 | 15638602.5791 | 249.2864 | 1768.0231 | 2200.3718 | 220.0372 | -4763.1439
2035 | 150 | 75 | 7003.8571 | 423 | 15.228 | 2 | 0 | 18.4256 | 6603.1654 | 0 | 0 | 5989.071 | 15638602.5791 | 226.624 | 1607.2937 | 2200.3718 | 220.0372 | -4602.4145
2036 | 150 | 75 | 7003.8571 | 423 | 15.228 | 2 | 0 | 18.4256 | 6603.1654 | 0 | 0 | 5989.071 | 15638602.5791 | 203.9616 | 1446.5644 | 2200.3718 | 220.0372 | -4441.6851
2037 | 150 | 75 | 7003.8571 | 423 | 15.228 | 2 | 0 | 18.4256 | 6603.1654 | 0 | 0 | 5989.071 | 15638602.5791 | 181.2992 | 1285.835 | 2200.3718 | 220.0372 | -4280.9558
2038 | 150 | 75 | 7003.8571 | 423 | 15.228 | 2 | 0 | 18.4256 | 6603.1654 | 0 | 0 | 5989.071 | 15638602.5791 | 158.6368 | 1125.1056 | 2200.3718 | 220.0372 | -4120.2264
2039 | 150 | 75 | 7003.8571 | 423 | 15.228 | 2 | 0 | 18.4256 | 6603.1654 | 0 | 0 | 5989.071 | 15638602.5791 | 135.9744 | 964.3762 | 2200.3718 | 220.0372 | -3959.497
2040 | 150 | 75 | 7003.8571 | 444 | 15.984 | 2 | 0 | 18.4256 | 6930.9821 | 0 | 0 | 6286.4007 | 16414987.1043 | 113.312 | 843.5442 | 2200.3718 | 220.0372 | -3541.3353
2041 | 150 | 75 | 7003.8571 | 444 | 15.984 | 2 | 0 | 18.4256 | 6930.9821 | 0 | 0 | 6286.4007 | 16414987.1043 | 90.6496 | 674.8354 | 2200.3718 | 220.0372 | -3372.6264
2042 | 150 | 75 | 7003.8571 | 444 | 15.984 | 2 | 0 | 18.4256 | 6930.9821 | 0 | 0 | 6286.4007 | 16414987.1043 | 67.9872 | 506.1265 | 2200.3718 | 220.0372 | -3203.9176
2043 | 150 | 75 | 7003.8571 | 444 | 15.984 | 2 | 0 | 18.4256 | 6930.9821 | 0 | 0 | 6286.4007 | 16414987.1043 | 45.3248 | 337.4177 | 2200.3718 | 220.0372 | -3035.2087
2044 | 150 | 75 | 7003.8571 | 444 | 15.984 | 2 | 0 | 18.4256 | 6930.9821 | 0 | 0 | 6286.4007 | 16414987.1043 | 22.6624 | 168.7088 | 2200.3718 | 220.0372 | -2866.4999
2045 | 150 | 75 | 7003.8571 | 444 | 15.984 | 2 | 0 | 18.4256 | 6930.9821 | 0 | 0 | 6286.4007 | 16414987.1043 | 0 | 0 | 2200.3718 | 220.0372 | -2697.791
2046 | 150 | 75 | 7003.8571 | 444 | 15.984 | 2 | 0 | 18.4256 | 6930.9821 | 0 | 0 | 6286.4007 | 16414987.1043 | 0 | 0 | 2200.3718 | 220.0372 | -2697.791
2047 | 150 | 75 | 7003.8571 | 444 | 15.984 | 2 | 0 | 18.4256 | 6930.9821 | 0 | 0 | 6286.4007 | 16414987.1043 | 0 | 0 | 2200.3718 | 220.0372 | -2697.791
2048 | 150 | 75 | 7003.8571 | 444 | 15.984 | 2 | 0 | 18.4256 | 6930.9821 | 0 | 0 | 6286.4007 | 16414987.1043 | 0 | 0 | 2200.3718 | 220.0372 | -2697.791
2049 | 150 | 75 | 7003.8571 | 444 | 15.984 | 2 | 0 | 18.4256 | 6930.9821 | 0 | 0 | 6286.4007 | 16414987.1043 | 0 | 0 | 2200.3718 | 220.0372 | -2697.791
2050 | 160 | 80 | 7470.7809 | 503 | 18.108 | 2 | 0 | 18.4256 | 7851.991 | 0 | 0 | 7121.7558 | 18596257.9132 | 0 | 0 | 2200.3718 | 220.0372 | -2329.3598

## CZ10
San Diego Region Electricity Emission Rate
Year | lbs CO2e/MWh | Renewable/Zero Carbon Content | Interpolation-lbs CO2e/MWh | Interpolation- MT CO2e/MWh
2021 | 471.6617 | 44.5% | 471.6617 | 0.21394
2022 |  | 46.22% | 457.0251 | 0.2073
2023 |  | 47.94% | 442.3889 | 0.20066
2024 |  | 49.67% | 427.7528 | 0.19403
2025 |  | 51.39% | 413.1167 | 0.18739
2026 |  | 53.11% | 398.4805 | 0.18075
2027 |  | 54.83% | 383.8444 | 0.17411
2028 |  | 56.56% | 369.2083 | 0.16747
2029 |  | 58.28% | 354.5721 | 0.16083
2030 |  | 60% | 339.936 | 0.15419
2031 |  | 62.67% | 317.2736 | 0.14391
2032 |  | 65.33% | 294.6112 | 0.13363
2033 |  | 68% | 271.9488 | 0.12335
2034 |  | 70.67% | 249.2864 | 0.11307
2035 |  | 73.33% | 226.624 | 0.10279
2036 |  | 76% | 203.9616 | 0.092515
2037 |  | 78.67% | 181.2992 | 0.082236
2038 |  | 81.33% | 158.6368 | 0.071956
2039 |  | 84% | 135.9744 | 0.061677
2040 |  | 86.67% | 113.312 | 0.051397
2041 |  | 89.33% | 90.6496 | 0.041118
2042 |  | 92% | 67.9872 | 0.030838
2043 |  | 94.67% | 45.3248 | 0.020559
2044 |  | 97.33% | 22.6624 | 0.010279
2045 | 0 | 100% | 0 | 0
2046 |  | 100% | 0 | 0
2047 |  | 100% | 0 | 0
2048 |  | 100% | 0 | 0
2049 |  | 100% | 0 | 0
2050 |  | 100% | 0 | 0

## First Year Ramp Up
|  |  | Week 0 | Week 1 | Week 2 | Week 3 | Week 4 | Week 5 | Week 6 | Week 7 | Week 8 | Week 9 | Week 10
First year Ramp Up |  | Primary Sludge TS Mass (lb/day) | 29540 | 29540 | 29540 | 29540 | 29540 | 29540 | 29540 | 29540 | 29540 | 29540 | 29540
Max OLR Increase per Week | 10% | Primary Sludge TS (%) 1 | bar: Week 0 to Week 10
OLR at Total Feed | 0.11789 | Primary Sludge VS/TS (%) | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80%
Primary Sludge Biogas Potential (scf biogas/lb VS) | 9.3 | Primary Sludge VS Mass (lb/day) | 23632 | 23632 | 23632 | 23632 | 23632 | 23632 | 23632 | 23632 | 23632 | 23632 | 23632
WAS Biogas Potential (scf biogas/lb VS) | 4.7 | Primary Sludge Total Flow (gpd) | 118066 | 118066 | 118066 | 118066 | 118066 | 118066 | 118066 | 118066 | 118066 | 118066 | 118066
HSW Biogas Potential (scf biogas/lb VS) | 11.8 | WAS TS Mass (lb/day) | 13210 | 13210 | 13210 | 13210 | 13210 | 13210 | 13210 | 13210 | 13210 | 13210 | 13210
WAS TS (%) | bar: Week 0 to Week 10
|  | WAS VS/TS (%) | 83% | 83% | 83% | 83% | 83% | 83% | 83% | 83% | 83% | 83% | 83%
|  | WAS VS Mass (lb/day) | 10964 | 10964 | 10964 | 10964 | 10964 | 10964 | 10964 | 10964 | 10964 | 10964 | 10964
|  | WAS Total Flow (gpd) | 31679 | 31679 | 31679 | 31679 | 31679 | 31679 | 31679 | 31679 | 31679 | 31679 | 31679
|  | Plant Sludge TS Mass (lb/day) | 42750 | 42750 | 42750 | 42750 | 42750 | 42750 | 42750 | 42750 | 42750 | 42750 | 42750
|  | Plant Sludge TS (%) | 3.423% | 3.423% | 3.423% | 3.423% | 3.423% | 3.423% | 3.423% | 3.423% | 3.423% | 3.423% | 3.423%
|  | Plant Sludge VS/TS (%) | 80.93% | 80.93% | 80.93% | 80.93% | 80.93% | 80.93% | 80.93% | 80.93% | 80.93% | 80.93% | 80.93%
|  | Plant Sludge VS Mass (lb/day) | 34596 | 34596 | 34596 | 34596 | 34596 | 34596 | 34596 | 34596 | 34596 | 34596 | 34596
|  | Plant Sludge Total Flow (gpd) | 149745 | 149745 | 149745 | 149745 | 149745 | 149745 | 149745 | 149745 | 149745 | 149745 | 149745
Year Total HSW Feed (lb/yr) | 11512170.1779 | HSW TS Mass (lb/day) | 0 | 3980.4222 | 8360.2137 | 13175.7605 | 18473.0271 | 24299.9376 | 30706.3785 | 33600 | 33600 | 33600 | 33600
Daily Average HSW Feed (lb/d) | 31540.1923 | HSW TS (%) | 12% | 12% | 12% | 12% | 12% | 12% | 12% | 12% | 12% | 12% | 12%
Biogas From Primary Sludge (scfm) | 152.6233 | HSW VS/TS (%) | 87% | 87% | 87% | 87% | 87% | 87% | 87% | 87% | 87% | 87% | 87%
Biogas From WAS (scfm) | 35.7863 | HSW VS Mass (lb/day) | 0 | 3462.9673 | 7273.3859 | 11462.9117 | 16071.5336 | 21140.9457 | 26714.5493 | 29232 | 29232 | 29232 | 29232
Biogas From HSW (scfm) | 224.8553 | HSW VS Mass % of Total VS Fed | 0% | 9.099% | 17.37% | 24.89% | 31.72% | 37.93% | 43.57% | 45.8% | 45.8% | 45.8% | 45.8%
Total Biogas (scfm) | 413.2649 | HSW Total Flow (gpd) | 0 | 3977.2404 | 8353.5309 | 13165.2283 | 18458.2605 | 24280.5132 | 30681.833 | 33573.1415 | 33573.1415 | 33573.1415 | 33573.1415
|  | Total Digester TS Mass (lb/day) | 42750 | 46730.4222 | 51110.2137 | 55925.7605 | 61223.0271 | 67049.9376 | 73456.3785 | 76350 | 76350 | 76350 | 76350
|  | Total Digester TS (%) | 3.423% | 3.645% | 3.876% | 4.116% | 4.364% | 4.62% | 4.882% | 4.994% | 4.994% | 4.994% | 4.994%
|  | Total Digester VS/TS (%) | 80.93% | 81.44% | 81.92% | 82.36% | 82.76% | 83.13% | 83.47% | 83.6% | 83.6% | 83.6% | 83.6%
|  | Total Digester VS Mass (lb/day) | 34596 | 38058.9673 | 41869.3859 | 46058.9117 | 50667.5336 | 55736.9457 | 61310.5493 | 63828 | 63828 | 63828 | 63828
|  | Total Digester Total Flow (gpd) | 149745 | 153722.2404 | 158098.5309 | 162910.2283 | 168203.2605 | 174025.5132 | 180426.833 | 183318.1415 | 183318.1415 | 183318.1415 | 183318.1415
|  | Total Volume of Digestors in Service (ft3) | 541444 | 541444 | 541444 | 541444 | 541444 | 541444 | 541444 | 541444 | 541444 | 541444 | 541444
|  | OLR (lb VS/ft3 d) | 0.063896 | 0.070292 | 0.077329 | 0.085067 | 0.093579 | 0.10294 | 0.11324 | 0.11788 | 0.11788 | 0.11788 | 0.11788
|  | Max OLR increase for next week | 0.070285 | 0.077321 | 0.085062 | 0.093573 | 0.10294 | 0.11324 | 0.12456 | 0.12967 | 0.12967 | 0.12967 | 0.12967