## Emissions Summary
Total Emissions Reductions
Site | End-Use | Old System | Fuel Type | BAU Emissions 2025-2030 | BAU Emissions 2025-2050 | GHP Emissions 2025-2030 | GHP Emissions 2025-2050 | Difference in Emissions, 2025-2030 | Difference in Emisisons, 2025-2050
Union Station | Space Heating | 3 Gas Boilers | Gas | 1453.851 | 6212.1361 | 939.8904 | 1009.4383 | -513.9606 | -5202.6978
| Space Cooling | Chiller | Electric | 264.6503 | 522.6106 | 225.2239 | 415.7024 | -39.4264 | -106.9082
| ALL |  |  | 1718.5013 | 6734.7467 | 1165.1143 | 1425.1407 | -553.387 | -5309.606
Multifamily | Space Heating | Furnaces | Gas | 12727.0786 | 54381.3241 | 8574.3147 | 11141.2995 | -4152.7639 | -43240.0247
| Water Heating | Boilers | Gas | 3952.7787 | 16889.7628 | 2655.9674 | 3414.5979 | -1296.8113 | -13475.1649
| Space Cooling | Central Air | Electric | 2876.2406 | 5679.7742 | 2516.3066 | 4432.9886 | -359.934 | -1246.7856
| ALL |  |  | 19556.0979 | 76950.8611 | 13746.5888 | 18988.886 | -5809.5092 | -57961.9751
Total Emissions Reductions | Total (MT CO2e) | ALL |  | 21274.5992 | 83685.6078 | 14911.7031 | 20414.0267 | -6362.8962 | -63271.5811
| Difference (MT CO2e) |  |  |  |  | -6362.8962 | -63271.5811
| % Change |  |  |  |  | -29.91% | -75.61%
2025-2030 Emissions Graph | [7 empty] | 2025-2030 Emissions Graph
| Space Heating |  | Cooling |  | Water Heating |  |  |  | Space Heating | Cooling | Water Heating
| BAU | GHP | BAU | GHP | BAU | GHP |  | Union Station | -513.9606 | -39.4264 | 0
Union Station | 1453.851 | 939.8904 | 264.6503 | 225.2239 | 0 | 0 |  | Multifamily | -4152.7639 | -359.934 | -1296.8113
Multifamily | 12727.0786 | 8574.3147 | 2876.2406 | 2516.3066 | 3952.7787 | 2655.9674 |  | 2025-2050 Emissions Graph
2025-2050 Emissions Graph | [8 empty] | Space Heating | Cooling | Water Heating
| Space Heating |  | Cooling |  | Water Heating |  |  | Union Station | -5202.6978 | -1246.7856 | 0
| BAU | GHP | BAU | GHP | BAU | GHP |  | Multifamily | -43240.0247 | -1246.7856 | -13475.1649
Union Station | 6212.1361 | 1009.4383 | 522.6106 | 415.7024 | 0 | 0
Multifamily | 54381.3241 | 11141.2995 | 5679.7742 | 4432.9886 | 16889.7628 | 3414.5979

## Factor Sets
GRID EMISSIONS FACTORS
2022 Coefficient | 643 | lb/MWh |  |  | EGrid Subregion: NEWE Historical eGRID Data ¦ US EPA
2001 Coefficient | 930 | lb/MWh |  |  | Air Emissions (iso-ne.com)
2030 Coefficient (Goal: 45% below 2001 levels) | 511.5 | lb/MWh
Total 2040 CT Electrical Demand | 135 | TWh |  |  | Figure 12, p. 23 of https://portal.ct.gov/-/media/DEEP/energy/IRP/2020-IRP/Appendix-A1--Factor-Inputs-and-Assumptions.pdf | 2022 | 643.084
CT Fossil Fuel Output, 2040 | 19 | TWh | 14.07% |  | p. 18 of https://portal.ct.gov/-/media/DEEP/energy/IRP/2020-IRP/Appendix-A1--Factor-Inputs-and-Assumptions.pdf | 2030 | 511.5595
2040 Coefficient | 93 | lb/MWh |  |  | Since 14% of electrical demand will be met through fossil fuels in 2040, it is reasonable to assume that despite the 2040 Net Zero emissions goal, there will be a small amount of greenhouse gasses released from the grid. We assume 10% of 2001 levels. | 2040 | 93.0108
2050 Coefficient | 0 | lb/MWh |  |  | Assume net zero since CT has a zero emissions target for 2040, Massachusetts target is net zero 2050, Rhode Island renewable electricity 2033, and Maine 100% renewable energy 2050. | 2050 | 0
GAS EMISSIONS FACTORS
CO2 | 116.65 | lbs/MMBtu |  |  | https://www.eia.gov/environment/emissions/co2_vol_mass.php
Combustion
Heat Content | 0.001026 | mmBtu/scf |  |  | https://www.epa.gov/system/files/documents/2023-04/emission-factors_sept2021.pdf
CO2 Factor | 53.06 | kg/mmBtu | 0.05306 | MT/mmBtu
N2O Factor | 0.1 | g/mmBtu | 1e-07 | MT/mmBtu
CH4 factor | 1 | g/mmBtu | 1e-06 | MT/mmBtu
Transmission
Total NatGas Produced in US (tcf, 2021) | 34.53 | tcf |  |  | https://www.eia.gov/energyexplained/natural-gas/where-our-natural-gas-comes-from.php
Natural Gas weight/volume factor | 0.829 | kg/m^3 | 0.000829 | MT/m^3 | https://www.cbs.nl/en-gb/our-services/methods/definitions/weight-units-energy#:~:text=Calculating%20weight%20from%20cubic%20metres,gas%3A%20variable%20dependent%20on%20composition.
Total NatGas Produced in US (2021) | 0.81058 | trillion kg | 810.5789 | MMT
CH4 from Nat Gas, 2021 | 6478 | kt | 6.478 | MMT | https://www.epa.gov/system/files/documents/2023-04/US-GHG-Inventory-2023-Main-Text.pdf
% CH4 Fugitive Emissions | 0.7992%
N2O from Nat Gas, 2021 | 28.9 | MT | 2.89e-05 | MMT
% N2O Fugitive Emissions | 3.565e-06%
GLOBAL WARMING POTENTIALS | 100-Year Global Warming Potentials
CH4 | 28 |  |  |  | CPRG NOFO Appendix B
N2O | 265
MULTIFAMILY BUILDING SPECS
Units: | 1000
Square Footage | 1080000
Energystar Multifamily Site Energy Use Intensity | 59.6 | kBtu/sqft | 0.0596 | MMBtu/sqft | median Energy Star source energy use intensity for multifamily housing
Source-Site Adjustment for Natural Gas | 1.05 |  |  |  | Energy Star Source Energy Technical Reference
Source-Site Adjustment for Electricity | 2.8
Building Energy Use Intensity: Gas-Powered End-Uses | 0.06258 | MMBtu/sqft
Annual Projected Energy Use | 67586.4 | MMBtu | 19807.6138 | MWh
HOUSEHOLD ENERGY CONSUMPTION BY END-USE | trillion Btu | Share of Total |  |  | EIA: Table CE3.2 Annual household site end-use consumption in the Northeast—totals and averages, 2020
Total | 528 | 1
Space Heating | 293 | 55.49%
Water Heating | 91 | 17.23%
Air Conditioning | 19 | 3.598%
APPLIANCE EFFICIENCIES
Multifamily | Rating System | Assumed Rating | Conversion to COP/EER
Furnace | AFUE | 95 | 0.95 |  | https://www.energystar.gov/sites/default/files/asset/document/ENERGY%20STAR%20MFNC%20National%20Program%20Requirements%20Version%201.2.pdf
A/C | SEER | 14 | 4.102 |  | https://www.energystar.gov/sites/default/files/asset/document/ENERGY%20STAR%20MFNC%20National%20Program%20Requirements%20Version%201.2.pdf
Water Heater | UEF | 0.9 | 0.9 |  | https://www.energystar.gov/sites/default/files/asset/document/ENERGY%20STAR%20MFNC%20National%20Program%20Requirements%20Version%201.2.pdf
Union Station
Boilers | AFUE | 89.5333 | 0.89533 |  | See "Union Station Gas Consumption" tab.
Chiller | EER | 15.15 | 4.4402
GHP | COP | 6 | 6 | Conservative estimate based on: | Cost and Performance Analysis for Five Existing Geothermal Heat Pump-Based District Energy Systems in the United States (nrel.gov)

## Emissions Projection Factors
PRODUCTION EMISSIONS | [11 empty] | COMBUSTION EMISSIONS
Year | Annual Gas Production (tcf) | Annual Gas Production (MMT) | Gas Production Year:Year Slope | CH4 Emissions from Natural Gas Systems, WITHOUT LEAD RULE (kt) | CH4 Emissions from Natural Gas Systems, WITH LEAD RULE (MMT) | CH4 Emissions as % of Gas Production | N2O Emissions from Natural Gas Systems (MT) | N2O Emissions from Natural Gas Systems (MMT) | N2O Emissions as % of Gas Production | CO2 Emissions from Natural Gas Systems (MMT) | CO2 Emissions as % of Gas Production | Grid CO2 Emissions Intensity (lbs CO2/MWh) | Grid CO2 Emissions Intensity (lbs CO2/MMBtu) | Grid CO2 Emissions Intensity, Year:Year Slope | N2O Grid Emissions Intensity (lb/MWh) | CH4 Grid Emissions Intensity (lb/MWh) | Sources | [6 empty] | Year | CO2 | N2O | CH4
2001 | [11 empty] | 930 | 272.556 |  |  |  | Gas Production |  | https://www.eia.gov/energyexplained/natural-gas/where-our-natural-gas-comes-from.php |  |  |  |  | 2001 | 930
2017 | 27.306 | 640.9982 | - | 6652 | 6.652 | 1.038% | 26.4 | 2.64e-05 | 4.119e-06% | 31.9 | 4.977% |  |  |  | N/A | N/A | Gas Production Outlook 2023-2050 |  | https://www.eia.gov/outlooks/aeo/data/browser/#/?id=13-AEO2023&cases=ref2023&sourcekey=0 |  |  |  |  | 2022 | 643 | 0.01 | 0.074 | -16.4375
2018 | 30.774 | 722.4082 | 12.7% | 6939 | 6.939 | 0.9605% | 28 | 2.8e-05 | 3.876e-06% | 32.8 | 4.54% |  |  |  | 0.012 | 0.09 | CH4 Grid Emissions Intensity |  | https://www.epa.gov/climateleadership/ghg-emission-factors-hub |  |  |  |  | 2025 | 593.6875 | 0.0077845 | 0.061303 | 33879.625 | 593.6875 | 511.5
2019 | 33.899 | 795.7664 | 10.15% | 6914 | 6.914 | 0.8688% | 38.7 | 3.87e-05 | 4.863e-06% | 38.6 | 4.851% |  |  |  | N/A | N/A | N2O Grid Emissions Intensity |  | https://www.epa.gov/climateleadership/ghg-emission-factors-hub |  |  |  |  | 2030 | 511.5 | 0.0067068 | 0.052816
2020 | 33.811 | 793.7006 | -0.2596% | 6619 | 6.619 | 0.8339% | 32.7 | 3.27e-05 | 4.12e-06% | 36.5 | 4.599% |  |  |  | 0.011 | 0.082 | Table 3-2 Projected Annual Reductions of Methane, VOC, and HAP Emission Reductions under the Final NSPS OOOOb and EG OOOOc, 2024 2038 |  | https://www.epa.gov/system/files/documents/2023-12/eo12866_oil-and-gas-nsps-eg-climate-review-2060-av16-ria-20231130.pdf |  |  |  |  | 2040 | 93 | 0.0012194 | 0.009603
2021 | 34.529 | 810.5554 | 2.124% | 6478 | 6.478 | 0.7992% | 28.9 | 2.89e-05 | 3.565e-06% | 36.2 | 4.466% |  |  |  | 0.01 | 0.077 | [7 empty] | 2050 | 0 | 0 | 0
2022 | 36.353 | 853.3731 | 5.283% | 6820.2014 | 6.8202 | 0.7992% | 30.4266 | 3.0427e-05 | 3.565e-06% | 38.1123 | 4.466% | 643 | 188.4447 |  | 0.01 | 0.074 | Modeled on EIA Gas Production Forecast | [6 empty] | Contribution to Overall Emissions: BAU 2025-2050 | 7.365% | 0.02559% | 0.0195%
2023 | 36.4859 | 856.4918 | 0.3654% | 6845.1256 | 6.8451 | 0.7992% | 30.5378 | 3.0538e-05 | 3.565e-06% | 38.2516 | 4.466% | 626.5625 | 183.6273 | -2.556% | 0.009 | 0.072 | Modeled on State GHG Reduction Goals | [6 empty] | Contribution to Overall Emissions: GHP 2025-2050 | 96.43% | 0.192% | 3.378%
2024 | 35.567 | 834.9225 | -2.518% | 6672.7428 | 6.4459 | 0.772% | 29.7688 | 2.9769e-05 | 3.565e-06% | 37.2883 | 4.466% | 610.125 | 178.8099 | -2.623% | 0.008 | 0.063 | Modeled on Linear Regression
2025 | 35.7255 | 838.6423 | 0.4455% | 6702.4719 | 6.258 | 0.7462% | 29.9014 | 2.9901e-05 | 3.565e-06% | 37.4544 | 4.466% | 593.6875 | 173.9926 | -2.694% | 0.0077845 | 0.061303 | Value from EPA/EIA or Simple Unit Conversion
2026 | 36.1835 | 849.3934 | 1.282% | 6788.3954 | 6.1534 | 0.7244% | 30.2848 | 3.0285e-05 | 3.565e-06% | 37.9345 | 4.466% | 577.25 | 169.1752 | -2.769% | 0.0075689 | 0.059605 | Assumed 90% Reduction from 2001
2027 | 36.1362 | 848.2826 | -0.1308% | 6779.5181 | 5.9631 | 0.703% | 30.2451 | 3.0245e-05 | 3.565e-06% | 37.8849 | 4.466% | 560.8125 | 164.3579 | -2.848% | 0.0073534 | 0.057908 | Modeled on Federal Methane Rule Projections
2028 | 36.4378 | 855.3642 | 0.8348% | 6836.1145 | 2.3909 | 0.2795% | 30.4976 | 3.0498e-05 | 3.565e-06% | 38.2012 | 4.466% | 544.375 | 159.5405 | -2.931% | 0.0071379 | 0.056211
2029 | 36.6797 | 861.042 | 0.6638% | 6881.4915 | 2.4363 | 0.2829% | 30.7001 | 3.07e-05 | 3.565e-06% | 38.4548 | 4.466% | 527.9375 | 154.7232 | -3.02% | 0.0069224 | 0.054514 | GHG Reduction Goals
2030 | 37.0357 | 869.4001 | 0.9707% | 6948.2898 | 2.4124 | 0.2775% | 30.9981 | 3.0998e-05 | 3.565e-06% | 38.828 | 4.466% | 511.5 | 149.9058 | -3.114% | 0.0067068 | 0.052816 | Pollutant | Authority | Goal | Source
2031 | 37.4669 | 879.5214 | 1.164% | 7029.1799 | 2.4933 | 0.2835% | 31.359 | 3.1359e-05 | 3.565e-06% | 39.2801 | 4.466% | 469.65 | 137.6408 | -8.182% | 0.0061581 | 0.048495 | CO2 | State | 45% below 2001 levels by 2030, net zero by 2040 | https://portal.ct.gov/DEEP/Climate-Change/Connecticut-Legislation--Executive-Orders-on-Climate
2032 | 37.9731 | 891.4043 | 1.351% | 7124.1488 | 2.4975 | 0.2802% | 31.7826 | 3.1783e-05 | 3.565e-06% | 39.8108 | 4.466% | 427.8 | 125.3758 | -8.911% | 0.0056093 | 0.044174 | CH4 | Federal | 80% below what they would be otherwise | https://www.epa.gov/system/files/documents/2023-12/epas-final-rule-for-oil-and-gas-operations.-overview-fact-sheet.pdf
2033 | 38.551 | 904.9711 | 1.522% | 7232.5753 | 2.6059 | 0.288% | 32.2664 | 3.2266e-05 | 3.565e-06% | 40.4167 | 4.466% | 385.95 | 113.1108 | -9.783% | 0.0050606 | 0.039852 | N2O | ? | No goal set, assume same as CO2
2034 | 39.0459 | 916.5883 | 1.284% | 7325.4201 | 2.6988 | 0.2944% | 32.6806 | 3.2681e-05 | 3.565e-06% | 40.9355 | 4.466% | 344.1 | 100.8457 | -10.84% | 0.0045119 | 0.035531
2035 | 39.4974 | 927.1865 | 1.156% | 7410.1219 | 2.7835 | 0.3002% | 33.0584 | 3.3058e-05 | 3.565e-06% | 41.4088 | 4.466% | 302.25 | 88.5807 | -12.16% | 0.0039631 | 0.03121
2036 | 39.8574 | 935.6367 | 0.9114% | 7477.656 | 2.7603 | 0.295% | 33.3597 | 3.336e-05 | 3.565e-06% | 41.7862 | 4.466% | 260.4 | 76.3157 | -13.85% | 0.0034144 | 0.026888
2037 | 40.2193 | 944.1335 | 0.9081% | 7545.5629 | 2.8282 | 0.2996% | 33.6627 | 3.3663e-05 | 3.565e-06% | 42.1657 | 4.466% | 218.55 | 64.0507 | -16.07% | 0.0028656 | 0.022567
2038 | 40.491 | 950.5122 | 0.6756% | 7596.5421 | 2.8792 | 0.3029% | 33.8901 | 3.389e-05 | 3.565e-06% | 42.4506 | 4.466% | 176.7 | 51.7856 | -19.15% | 0.0023169 | 0.018246 | Linear Regression Model 2022-2030: |  |  | Linear Regression Model 2030-2040: |  | Linear Regression Model 2040-2050:
2039 | 40.7335 | 956.2029 | 0.5987% | 7642.0219 | 2.9247 | 0.3059% | 34.093 | 3.4093e-05 | 3.565e-06% | 42.7047 | 4.466% | 134.85 | 39.5206 | -23.68% | 0.0017682 | 0.013924 | Year | lbs CO2/MWh |  | Year | lbs CO2/MWh | Year | lbs CO2/MWh
2040 | 40.8709 | 959.429 | 0.3374% | 7667.805 | 2.9504 | 0.3075% | 34.208 | 3.4208e-05 | 3.565e-06% | 42.8488 | 4.466% | 93 | 27.2556 | -31.03% | 0.0012194 | 0.009603 | 2022 | 643 |  | 2030 | 511.5 | 2040 | 93
2041 | 40.9898 | 962.221 | 0.291% | 7690.119 | 2.9728 | 0.3089% | 34.3076 | 3.4308e-05 | 3.565e-06% | 42.9735 | 4.466% | 83.7 | 24.53 | -10% | 0.0010975 | 0.0086427 | 2030 | 511.5 |  | 2040 | 93 | 2050 | 0
2042 | 41.1649 | 966.3297 | 0.427% | 7722.9564 | 3.0056 | 0.311% | 34.4541 | 3.4454e-05 | 3.565e-06% | 43.157 | 4.466% | 74.4 | 21.8045 | -11.11% | 0.00097554 | 0.0076824 |  | CO2 2022-2030 |  |  | CO2 2022-2030 |  | CO2 2022-2030
2043 | 41.2772 | 968.9669 | 0.2729% | 7744.0324 | 3.0267 | 0.3124% | 34.5481 | 3.4548e-05 | 3.565e-06% | 43.2748 | 4.466% | 65.1 | 19.0789 | -12.5% | 0.0008536 | 0.0067221 | Slope | -16.4375 |  | Slope | -41.85 | Slope | -9.3
2044 | 41.3545 | 970.7814 | 0.1873% | 7758.5341 | 3.0412 | 0.3133% | 34.6128 | 3.4613e-05 | 3.565e-06% | 43.3558 | 4.466% | 55.8 | 16.3534 | -14.29% | 0.00073165 | 0.0057618 | Intercept | 33879.625 |  | Intercept | 85467 | Intercept | 19065
2045 | 41.5058 | 974.3328 | 0.3658% | 7786.9172 | 3.0696 | 0.315% | 34.7394 | 3.4739e-05 | 3.565e-06% | 43.5144 | 4.466% | 46.5 | 13.6278 | -16.67% | 0.00060971 | 0.0048015
2046 | 41.3406 | 970.4563 | -0.3979% | 7755.9363 | 3.0386 | 0.3131% | 34.6012 | 3.4601e-05 | 3.565e-06% | 43.3413 | 4.466% | 37.2 | 10.9022 | -20% | 0.00048777 | 0.0038412
2047 | 41.545 | 975.2532 | 0.4943% | 7794.2735 | 3.0769 | 0.3155% | 34.7722 | 3.4772e-05 | 3.565e-06% | 43.5555 | 4.466% | 27.9 | 8.1767 | -25% | 0.00036583 | 0.0028809
2048 | 41.6132 | 976.8555 | 0.1643% | 7807.0785 | 3.0897 | 0.3163% | 34.8294 | 3.4829e-05 | 3.565e-06% | 43.6271 | 4.466% | 18.6 | 5.4511 | -33.33% | 0.00024388 | 0.0019206
2049 | 41.693 | 978.7265 | 0.1915% | 7822.0318 | 3.1047 | 0.3172% | 34.8961 | 3.4896e-05 | 3.565e-06% | 43.7106 | 4.466% | 9.3 | 2.7256 | -50% | 0.00012194 | 0.0009603
2050 | 42.0654 | 987.469 | 0.8933% | 7891.9026 | 3.1745 | 0.3215% | 35.2078 | 3.5208e-05 | 3.565e-06% | 44.1011 | 4.466% | 0 | 0 | -100% | 0 | 0
Table 3-2 Projected Annual Reductions of Methane, VOC, and HAP Emission Reductions under the Final NSPS OOOOb and EG OOOOc, 2024 2038
Year | Methane [Reductions] (short tons) | VOC [Reductions] (short tons) | HAP [Reductions] (short tons) | Methane (metric tons CO2 Eq.) | [Methane Reductions (MMT)]
2017 | 0 | 0 | 0 | 0 | -
2018 | 0 | 0 | 0 | 0 | -
2019 | 0 | 0 | 0 | 0 | -
2020 | 0 | 0 | 0 | 0 | -
2021 | 0 | 0 | 0 | 0 | -
2024 | 250000 | 77000 | 2900 | 6400000 | 0.2268
2025 | 490000 | 150000 | 5600 | 12000000 | 0.44452
2026 | 700000 | 210000 | 8000 | 18000000 | 0.63503
2027 | 900000 | 270000 | 10000 | 23000000 | 0.81647
2028 | 4900000 | 1300000 | 48000 | 120000000 | 4.4452
2029 | 4900000 | 1300000 | 49000 | 130000000 | 4.4452
2030 | 5000000 | 1300000 | 49000 | 130000000 | 4.5359
2031 | 5000000 | 1300000 | 50000 | 130000000 | 4.5359
2032 | 5100000 | 1300000 | 50000 | 130000000 | 4.6266
2033 | 5100000 | 1400000 | 51000 | 130000000 | 4.6266
2034 | 5100000 | 1400000 | 51000 | 130000000 | 4.6266
2035 | 5100000 | 1400000 | 52000 | 130000000 | 4.6266
2036 | 5200000 | 1400000 | 53000 | 130000000 | 4.7174
2037 | 5200000 | 1400000 | 54000 | 130000000 | 4.7174
2038 | 5200000 | 1500000 | 55000 | 130000000 | 4.7174
2039 | 5200000 | 1500000 | 55000 | 130000000 | 4.7174 | ASSUME REDUCTIONS PLATEAU AT 2038
2040 | 5200000 | 1500000 | 55000 | 130000000 | 4.7174
2041 | 5200000 | 1500000 | 55000 | 130000000 | 4.7174
2042 | 5200000 | 1500000 | 55000 | 130000000 | 4.7174
2043 | 5200000 | 1500000 | 55000 | 130000000 | 4.7174
2044 | 5200000 | 1500000 | 55000 | 130000000 | 4.7174
2045 | 5200000 | 1500000 | 55000 | 130000000 | 4.7174
2046 | 5200000 | 1500000 | 55000 | 130000000 | 4.7174
2047 | 5200000 | 1500000 | 55000 | 130000000 | 4.7174
2048 | 5200000 | 1500000 | 55000 | 130000000 | 4.7174
2049 | 5200000 | 1500000 | 55000 | 130000000 | 4.7174
2050 | 5200000 | 1500000 | 55000 | 130000000 | 4.7174
Total 2024-2038 | 58000000 | 16000000 | 590000 | 1500000000 | 52.7437
Note: Values rounded to two significant figures. Totals may not appear to add correctly due to rounding.

## Multifamily
Total Annual Building Energy Consumption | End Use | BAU Fuel | Share of Total | Source-Site Adjustment | Annual Energy Consumption (MMBtu) | Annual Energy Consumption (cubic meter) | Annual Energy Consumption (MT) | BAU PY2028 Energy Consumption (June Start, MT) | 2028 CO2 Emissions Intensity | Unit | 2028 Combustion CO2 Emissions (MT) | BAU PY2028 Emissions (June Start) | Assumed BAU Efficiency | Amount of Energy Required for End Use (MMBtu) | Assumed GHP Efficiency | MWh Consumed by GHP to Reach Required Energy | 2028 CO2 Grid Emissions Intensity (lb/MWh) | 2028 Grid CO2 Emissions (MT) | GHP PY2028 Grid Emissions (June Start) | 2030 Grid CO2 Emissions (MT) | 2040 Grid CO2 Emissions (MT) | 2050 Grid CO2 Emissions (MT) | [10 empty] | Key:
64368 | Heating | Gas | 55.49% | 1.05 | 37505.3318 | 840429.1098 | 696.7157 | 348.3579 | 116.65 | lb/MMBtu | 1984.1256 | 992.0628 | 0.95 | 35630.0652 | 6 | 1740.3565 | 544.375 | 429.6628 | 214.8314 | 403.7153 | 73.4028 | 0 | [10 empty] | BAU Value
| Cooling | Electricity | 3.598% | 2.8 | 6485.5636 | 145330.176 | - | - | 544.375 | lb/MWh | 469.2563 | 234.6282 | 4.102 | 26603.782 | 6 | 1299.4662 | 544.375 | 320.8149 | 160.4075 | 301.4408 | 49.3267 | 0 | [10 empty] | GHP Begins in June 2028, value is 1/2 BAU, 1/2 GHP
| Water Heating | Gas | 17.23% | 1.05 | 11648.4136 | 261020.645 | 216.3861 | 108.1931 | 116.65 | lb/MMBtu | 616.2301 | 308.1151 | 0.9 | 10483.5723 | 6 | 512.0718 | 544.375 | 126.4214 | 63.2107 | 118.7867 | 17.2781 | 0 | [10 empty] | BAU
| CO2 (MT CO2e) | [7 empty] | N2O (MT CO2e) | [7 empty] | CH4 (MT CO2e) | [7 empty] | BAU Emissions (MT CO2e) |  |  | Project Emissions (MT CO2e)
| Heating |  |  | Cooling |  | Water Heating |  |  | Heating |  |  | Cooling |  | Water Heating |  |  | Heating |  |  | Cooling |  | Water Heating |  |  | Heating (BAU) | Cooling (BAU) | Water Heating (BAU) | Heating (GHP) | Cooling (GHP) | Water Heating (GHP) | Annual Change in Emissions (MT CO2e) | Annual Change in Emissions (%)
| BAU (Production) | BAU (Combustion) | GHP (Grid) | BAU (Grid) | GHP (Grid) | BAU (Production) | BAU (Combustion) | GHP (Grid) | BAU (Production) | BAU (Combustion) | GHP (Grid) | BAU (Grid) | GHP (Grid) | BAU (Production) | BAU (Combustion) | GHP (Grid) | BAU (Production) | BAU (Combustion) | GHP (Grid) | BAU (Grid) | GHP (Grid) | BAU (Production) | BAU (Combustion) | GHP (Grid)
2025 | 31.1158 | 1990.0329 | 2021.1487 | 511.7643 | 511.7643 | 9.664 | 618.0648 | 627.7288 | 0.0065829 | 0.99389 | 1.0005 | 1.7782 | 1.7782 | 0.0020445 | 0.30868 | 0.31073 | 145.5691 | 1.0501 | 146.6192 | 1.4796 | 1.4796 | 45.2109 | 0.32616 | 45.537 | 2168.7684 | 515.0221 | 673.5765 | 2168.7684 | 515.0221 | 673.5765 | 0 | -2.709e-14% | 2025
2026 | 31.1158 | 1990.0329 | 2021.1487 | 497.595 | 497.595 | 9.664 | 618.0648 | 627.7288 | 0.0065829 | 0.99389 | 1.0005 | 1.729 | 1.729 | 0.0020445 | 0.30868 | 0.31073 | 141.3245 | 1.0501 | 142.3747 | 1.4387 | 1.4387 | 43.8926 | 0.32616 | 44.2188 | 2164.5239 | 500.7627 | 672.2583 | 2164.5239 | 500.7627 | 672.2583 | 0 | 0% | 2026
2027 | 31.1158 | 1990.0329 | 2021.1487 | 483.4257 | 483.4257 | 9.664 | 618.0648 | 627.7288 | 0.0065829 | 0.99389 | 1.0005 | 1.6798 | 1.6798 | 0.0020445 | 0.30868 | 0.31073 | 137.1329 | 1.0501 | 138.183 | 1.3977 | 1.3977 | 42.5908 | 0.32616 | 42.9169 | 2160.3323 | 486.5032 | 670.9564 | 2160.3323 | 486.5032 | 670.9564 | 0 | 0% | 2027
2028 | 31.1158 | 1990.0329 | 1225.4058 | 469.2565 | 395.0357 | 9.664 | 618.0648 | 377.0751 | 0.0065829 | 0.99389 | 1.2467 | 1.6305 | 1.3726 | 0.0020445 | 0.30868 | 0.375 | 54.5288 | 1.0501 | 28.4106 | 1.3567 | 1.1421 | 16.9356 | 0.32616 | 17.7255 | 2077.7281 | 472.2437 | 645.3012 | 1255.0631 | 397.5504 | 395.1756 | -1147.484 | -35.91% | 2028
2029 | 31.1158 | 1990.0329 | 416.6891 | 455.0872 | 311.1279 | 9.664 | 618.0648 | 122.604 | 0.0065829 | 0.99389 | 1.4479 | 1.5813 | 1.0811 | 0.0020445 | 0.30868 | 0.42601 | 55.1973 | 1.0501 | 1.2047 | 1.3158 | 0.89954 | 17.1432 | 0.32616 | 0.89954 | 2078.3966 | 457.9842 | 645.5089 | 419.3417 | 313.1085 | 123.9296 | -2325.51 | -73.09% | 2029
2030 | 31.1158 | 1990.0329 | 403.7153 | 440.9179 | 301.4408 | 9.664 | 618.0648 | 118.7867 | 0.0065829 | 0.99389 | 1.4028 | 1.5321 | 1.0474 | 0.0020445 | 0.30868 | 0.41275 | 54.1299 | 1.0501 | 1.1672 | 1.2748 | 0.87153 | 16.8117 | 0.32616 | 0.87153 | 2077.3293 | 443.7247 | 645.1773 | 406.2854 | 303.3597 | 120.071 | -2336.5152 | -73.79% | 2030
2031 | 31.1158 | 1990.0329 | 370.6841 | 404.8428 | 276.7775 | 9.664 | 618.0648 | 109.0678 | 0.0065829 | 0.99389 | 1.288 | 1.4067 | 0.96172 | 0.0020445 | 0.30868 | 0.37898 | 55.3012 | 1.0501 | 1.0717 | 1.1705 | 0.80022 | 17.1754 | 0.32616 | 0.80022 | 2078.5005 | 407.42 | 645.5411 | 373.0438 | 278.5394 | 110.247 | -2369.6314 | -75.67% | 2031
2032 | 31.1158 | 1990.0329 | 337.6528 | 368.7677 | 252.1141 | 9.664 | 618.0648 | 99.3489 | 0.0065829 | 0.99389 | 1.1732 | 1.2814 | 0.87602 | 0.0020445 | 0.30868 | 0.34521 | 54.657 | 1.0501 | 0.97623 | 1.0662 | 0.72892 | 16.9754 | 0.32616 | 0.72892 | 2077.8563 | 371.1152 | 645.341 | 339.8023 | 253.7191 | 100.423 | -2400.3682 | -77.57% | 2032
2033 | 31.1158 | 1990.0329 | 304.6216 | 332.6926 | 227.4508 | 9.664 | 618.0648 | 89.63 | 0.0065829 | 0.99389 | 1.0585 | 1.156 | 0.79032 | 0.0020445 | 0.30868 | 0.31144 | 56.1749 | 1.0501 | 0.88073 | 0.96188 | 0.65761 | 17.4468 | 0.32616 | 0.65761 | 2079.3743 | 334.8105 | 645.8125 | 306.5608 | 228.8987 | 90.599 | -2433.9387 | -79.54% | 2033
2034 | 31.1158 | 1990.0329 | 271.5903 | 296.6175 | 202.7874 | 9.664 | 618.0648 | 79.9111 | 0.0065829 | 0.99389 | 0.94369 | 1.0307 | 0.70463 | 0.0020445 | 0.30868 | 0.27767 | 57.439 | 1.0501 | 0.78522 | 0.85758 | 0.5863 | 17.8394 | 0.32616 | 0.5863 | 2080.6383 | 298.5057 | 646.2051 | 273.3192 | 204.0784 | 80.775 | -2467.1765 | -81.55% | 2034
2035 | 31.1158 | 1990.0329 | 238.5591 | 260.5424 | 178.1241 | 9.664 | 618.0648 | 70.1922 | 0.0065829 | 0.99389 | 0.82892 | 0.90531 | 0.61893 | 0.0020445 | 0.30868 | 0.2439 | 58.5645 | 1.0501 | 0.68972 | 0.75328 | 0.51499 | 18.189 | 0.32616 | 0.51499 | 2081.7639 | 262.201 | 646.5547 | 240.0777 | 179.258 | 70.9511 | -2500.2327 | -83.61% | 2035
2036 | 31.1158 | 1990.0329 | 205.5278 | 224.4673 | 153.4608 | 9.664 | 618.0648 | 60.4732 | 0.0065829 | 0.99389 | 0.71415 | 0.77996 | 0.53323 | 0.0020445 | 0.30868 | 0.21013 | 57.5522 | 1.0501 | 0.59422 | 0.64898 | 0.44369 | 17.8746 | 0.32616 | 0.44369 | 2080.7516 | 225.8962 | 646.2403 | 206.8362 | 154.4377 | 61.1271 | -2530.4871 | -85.7% | 2036
2037 | 31.1158 | 1990.0329 | 172.4966 | 188.3922 | 128.7974 | 9.664 | 618.0648 | 50.7543 | 0.0065829 | 0.99389 | 0.59937 | 0.65461 | 0.44753 | 0.0020445 | 0.30868 | 0.17636 | 58.4374 | 1.0501 | 0.49872 | 0.54468 | 0.37238 | 18.1495 | 0.32616 | 0.37238 | 2081.6367 | 189.5915 | 646.5152 | 173.5947 | 129.6173 | 51.3031 | -2563.2283 | -87.85% | 2037
2038 | 31.1158 | 1990.0329 | 139.4653 | 152.3171 | 104.1341 | 9.664 | 618.0648 | 41.0354 | 0.0065829 | 0.99389 | 0.4846 | 0.52926 | 0.36183 | 0.0020445 | 0.30868 | 0.14259 | 59.0915 | 1.0501 | 0.40322 | 0.44038 | 0.30107 | 18.3526 | 0.32616 | 0.30107 | 2082.2909 | 153.2867 | 646.7183 | 140.3531 | 104.797 | 41.4791 | -2595.6667 | -90.06% | 2038
2039 | 31.1158 | 1990.0329 | 106.434 | 116.242 | 79.4708 | 9.664 | 618.0648 | 31.3165 | 0.0065829 | 0.99389 | 0.36983 | 0.40391 | 0.27614 | 0.0020445 | 0.30868 | 0.10882 | 59.6677 | 1.0501 | 0.30772 | 0.33608 | 0.22977 | 18.5316 | 0.32616 | 0.22977 | 2082.8671 | 116.982 | 646.8973 | 107.1116 | 79.9767 | 31.6551 | -2628.003 | -92.32% | 2039
2040 | 31.1158 | 1990.0329 | 73.4028 | 80.1669 | 54.8074 | 9.664 | 618.0648 | 21.5976 | 0.0065829 | 0.99389 | 0.25505 | 0.27856 | 0.19044 | 0.0020445 | 0.30868 | 0.075045 | 59.9913 | 1.0501 | 0.21222 | 0.23178 | 0.15846 | 18.6321 | 0.32616 | 0.15846 | 2083.1907 | 80.6772 | 646.9978 | 73.8701 | 55.1563 | 21.8311 | -2660.0082 | -94.63% | 2040
2041 | 31.1158 | 1990.0329 | 66.0625 | 72.1502 | 49.3267 | 9.664 | 618.0648 | 19.4378 | 0.0065829 | 0.99389 | 0.22955 | 0.2507 | 0.1714 | 0.0020445 | 0.30868 | 0.067541 | 60.2696 | 1.0501 | 0.191 | 0.2086 | 0.14261 | 18.7186 | 0.32616 | 0.14261 | 2083.469 | 72.6095 | 647.0842 | 66.4831 | 49.6407 | 19.648 | -2667.391 | -95.16% | 2041
2042 | 31.1158 | 1990.0329 | 58.7222 | 64.1335 | 43.8459 | 9.664 | 618.0648 | 17.2781 | 0.0065829 | 0.99389 | 0.20404 | 0.22284 | 0.15235 | 0.0020445 | 0.30868 | 0.060036 | 60.6763 | 1.0501 | 0.16978 | 0.18542 | 0.12677 | 18.8448 | 0.32616 | 0.12677 | 2083.8756 | 64.5418 | 647.2105 | 59.0961 | 44.1251 | 17.4649 | -2674.942 | -95.68% | 2042
2043 | 31.1158 | 1990.0329 | 51.382 | 56.1168 | 38.3652 | 9.664 | 618.0648 | 15.1183 | 0.0065829 | 0.99389 | 0.17854 | 0.19499 | 0.13331 | 0.0020445 | 0.30868 | 0.052532 | 60.9355 | 1.0501 | 0.14856 | 0.16225 | 0.11092 | 18.9253 | 0.32616 | 0.11092 | 2084.1348 | 56.4741 | 647.291 | 51.709 | 38.6094 | 15.2818 | -2682.2997 | -96.21% | 2043
2044 | 31.1158 | 1990.0329 | 44.0417 | 48.1001 | 32.8844 | 9.664 | 618.0648 | 12.9586 | 0.0065829 | 0.99389 | 0.15303 | 0.16713 | 0.11426 | 0.0020445 | 0.30868 | 0.045027 | 61.113 | 1.0501 | 0.12733 | 0.13907 | 0.095076 | 18.9805 | 0.32616 | 0.095076 | 2084.3123 | 48.4063 | 647.3462 | 44.322 | 33.0938 | 13.0987 | -2689.5503 | -96.74% | 2044
2045 | 31.1158 | 1990.0329 | 36.7014 | 40.0834 | 27.4037 | 9.664 | 618.0648 | 10.7988 | 0.0065829 | 0.99389 | 0.12753 | 0.13928 | 0.09522 | 0.0020445 | 0.30868 | 0.037523 | 61.4585 | 1.0501 | 0.10611 | 0.11589 | 0.07923 | 19.0878 | 0.32616 | 0.07923 | 2084.6579 | 40.3386 | 647.4535 | 36.935 | 27.5782 | 10.9155 | -2697.0212 | -97.28% | 2045
2046 | 31.1158 | 1990.0329 | 29.3611 | 32.0668 | 21.923 | 9.664 | 618.0648 | 8.639 | 0.0065829 | 0.99389 | 0.10202 | 0.11142 | 0.076176 | 0.0020445 | 0.30868 | 0.030018 | 61.0812 | 1.0501 | 0.084889 | 0.092712 | 0.063384 | 18.9706 | 0.32616 | 0.063384 | 2084.2806 | 32.2709 | 647.3363 | 29.548 | 22.0625 | 8.7324 | -2703.5448 | -97.82% | 2046
2047 | 31.1158 | 1990.0329 | 22.0208 | 24.0501 | 16.4422 | 9.664 | 618.0648 | 6.4793 | 0.0065829 | 0.99389 | 0.076516 | 0.083567 | 0.057132 | 0.0020445 | 0.30868 | 0.022514 | 61.5476 | 1.0501 | 0.063667 | 0.069534 | 0.047538 | 19.1155 | 0.32616 | 0.047538 | 2084.747 | 24.2032 | 647.4812 | 22.161 | 16.5469 | 6.5493 | -2711.1741 | -98.36% | 2047
2048 | 31.1158 | 1990.0329 | 14.6806 | 16.0334 | 10.9615 | 9.664 | 618.0648 | 4.3195 | 0.0065829 | 0.99389 | 0.051011 | 0.055711 | 0.038088 | 0.0020445 | 0.30868 | 0.015009 | 61.7024 | 1.0501 | 0.042445 | 0.046356 | 0.031692 | 19.1636 | 0.32616 | 0.031692 | 2084.9018 | 16.1354 | 647.5292 | 14.774 | 11.0313 | 4.3662 | -2718.395 | -98.9% | 2048
2049 | 31.1158 | 1990.0329 | 7.3403 | 8.0167 | 5.4807 | 9.664 | 618.0648 | 2.1598 | 0.0065829 | 0.99389 | 0.025505 | 0.027856 | 0.019044 | 0.0020445 | 0.30868 | 0.0075045 | 61.8825 | 1.0501 | 0.021222 | 0.023178 | 0.015846 | 19.2195 | 0.32616 | 0.015846 | 2085.0819 | 8.0677 | 647.5852 | 7.387 | 5.5156 | 2.1831 | -2725.649 | -99.45% | 2049
2050 | 31.1158 | 1990.0329 | 0 | 0 | 0 | 9.664 | 618.0648 | 0 | 0.0065829 | 0.99389 | 0 | 0 | 0 | 0.0020445 | 0.30868 | 0 | 62.715 | 1.0501 | 0 | 0 | 0 | 19.478 | 0.32616 | 0 | 2085.9143 | 0 | 647.8437 | 0 | 0 | 0 | -2733.758 | -100% | 2050
Cumulative 2025-2030 Emissions | 186.695 | 11940.1974 | 8109.2565 | 2858.0466 | 2500.3894 | 57.9838 | 3708.389 | 2501.6522 | 0.039497 | 5.9633 | 7.0988 | 9.9308 | 8.6881 | 0.012267 | 1.8521 | 2.1459 | 587.8824 | 6.3009 | 457.9595 | 8.2632 | 7.2292 | 182.5846 | 1.9569 | 152.1692 | 12727.0786 | 2876.2406 | 3952.7787 | 8574.3147 | 2516.3066 | 2655.9674 | -5809.5092 | -29.71% | Cumulative 2025-2030 Emissions
% Emissions Reduced (2025-2030) | -33.13% |  |  | -12.51% |  | -33.58% |  |  | 18.26% |  |  | -12.51% |  | 15.1% |  |  | -22.93% |  |  | -12.51% |  | -17.54% | [5 empty] | -32.63% | -12.51% | -32.81% |  |  | % Emissions Reduced (2025-2030)
Cumulative 2025-2050 Emissions | 809.0118 | 51740.8556 | 10660.0034 | 5643.846 | 4404.9471 | 251.263 | 16069.6855 | 3252.1684 | 0.17116 | 25.8412 | 15.9619 | 19.6107 | 15.3059 | 0.053157 | 8.0258 | 4.7538 | 1778.1406 | 27.3039 | 465.3342 | 16.3175 | 12.7356 | 552.2553 | 8.48 | 157.6757 | 54381.3241 | 5679.7742 | 16889.7628 | 11141.2995 | 4432.9886 | 3414.5979 | -57961.9751 | -75.32% | Cumulative 2025-2050 Emissions
% Emissions Reduced (2025-2050) | -79.71% |  |  | -21.95% |  | -80.07% |  |  | -38.64% |  |  | -21.95% |  | -41.16% |  |  | -74.23% |  |  | -21.95% |  | -71.88% | [5 empty] | -79.51% | -21.95% | -79.78% |  |  | % Emissions Reduced (2025-2050)
| BAU Emissions (MT CO2e) | [10 empty] | GHP Emissions (MT CO2e)
Total Cumulative Emissions 2025-2030 | 19556.0979 | [10 empty] | 13746.5888 | [20 empty] | Total Cumulative Emissions 2025-2030
Change in emissions 2025-2030 | [11 empty] | -29.71% | [20 empty] | Change in emissions 2025-2030
Total Cumulative Emisisons 2025-2050 | 76950.8611 | [10 empty] | 18988.886 | [20 empty] | Total Cumulative Emisisons 2025-2050
Change in emissions 2025-2050 | [11 empty] | -75.32% | [20 empty] | Change in emissions 2025-2050
2150.1807

## Union Station
End Use | Total Consumption (MMBtu & kWh) | Annual Energy Consumption (cubic meter) | Annual Energy Consumption (MT) | Units | 2025 CO2 Emissions Intensity | Unit | 2025 CO2 Emissions (MT) | PY2028 Emissions from BAU Equipment | Assumed BAU Efficiency | Amount of Energy Required for End Use (MMBtu) | Assumed GHP Efficiency | kWh Consumed by GHP to Reach Required Energy | kWh to MWh Conversion | 2028 CO2 Grid Emissions Intensity (lb/MWh) | 2028 Grid CO2 Emissions (MT) | PY2028 Grid Emissions from GHP | 2030 Grid CO2 Emissions (MT) | 2040 Grid CO2 Emissions (MT) | 2050 Grid CO2 Emissions (MT) |  |  | Key:
Boilers | 4284.3426 | 96004.6498 | 79.5879 | MMBtu | 116.65 | lb/MMBtu | 226.6524 | 113.3262 | 0.89533 | 3835.9148 | 6 | 187373.7179 | 187.3737 | 544.375 | 46.2592 | 23.1296 | 43.4656 | 7.9028 | 0 |  |  | BAU Value
Chiller | 174891.1474 | 3919005.7572 | -- | kWh | 593.6875 | lb/MWh | 47.0887 | 21.5887 | 4.4402 | 227.5188 | 6 | 129425.6 | 129.4256 | 544.375 | 31.9529 | 15.9764 | 30.0232 | 5.4588 | 0 |  |  | GHP Begins in June 2028, value is 1/2 BAU, 1/2 GHP
BAU
| CO2 (MT CO2e) |  |  |  |  | N2O (MT CO2e) |  |  |  |  | CH4 (MT CO2e) |  |  |  |  | BAU Emissions (MT CO2e) |  | Project Emissions (MT CO2e)
| Heating |  |  | Cooling |  | Heating |  |  | Cooling |  | Heating |  |  | Cooling |  | Heating (BAU) | Cooling (BAU) | Heating (GHP) | Cooling (GHP) | Annual Change in Emissions (MT CO2e) | Annual Change in Emissions (%)
| BAU (Production) | BAU (Combustion) | GHP (Grid) | BAU (Grid) | GHP (Grid) | BAU (Production) | BAU (Combustion) | GHP (Grid) | BAU (Grid) | GHP (Grid) | BAU (Production) | BAU (Combustion) | GHP (Grid) | BAU (Grid) | GHP (Grid)
2025 | 3.5545 | 227.3272 | 230.8817 | 47.0887 | 47.0887 | 0.00075198 | 0.11354 | 0.11429 | 0.16362 | 0.16362 | 16.6288 | 0.11996 | 16.7487 | 0.13614 | 0.13614 | 247.7447 | 47.3885 | 247.7447 | 47.3885 | 0 | 0% | 2025
2026 | 3.5545 | 227.3272 | 230.8817 | 45.785 | 45.785 | 0.00075198 | 0.11354 | 0.11429 | 0.15909 | 0.15909 | 16.1439 | 0.11996 | 16.2639 | 0.13237 | 0.13237 | 247.2598 | 46.0765 | 247.2598 | 46.0765 | 0 | 0% | 2026
2027 | 3.5545 | 227.3272 | 230.8817 | 44.4812 | 44.4812 | 0.00075198 | 0.11354 | 0.11429 | 0.15456 | 0.15456 | 15.6651 | 0.11996 | 15.785 | 0.1286 | 0.1286 | 246.781 | 44.7644 | 246.781 | 44.7644 | 0 | -1.95e-14% | 2027
2028 | 3.5545 | 227.3272 | 138.5704 | 43.1775 | 25.533 | 0.00075198 | 0.11354 | 0.13751 | 0.15003 | 0.08872 | 6.229 | 0.11996 | 3.2413 | 0.12484 | 0.10861 | 237.3449 | 43.4524 | 141.9493 | 25.7304 | -113.1176 | -40.28% | 2028
2029 | 3.5545 | 227.3272 | 44.8624 | 41.8737 | 30.988 | 0.00075198 | 0.11354 | 0.15588 | 0.1455 | 0.10767 | 6.3053 | 0.11996 | 0.12971 | 0.12107 | 0.020783 | 237.4213 | 42.1403 | 45.148 | 31.1165 | -203.2971 | -72.72% | 2029
2030 | 3.5545 | 227.3272 | 10.7309 | 40.57 | 30.0232 | 0.00075198 | 0.11354 | 0.15103 | 0.14097 | 0.10432 | 6.1834 | 0.11996 | 0.12567 | 0.1173 | 0.020136 | 237.2993 | 40.8283 | 11.0076 | 30.1477 | -236.9723 | -85.2% | 2030
2031 | 3.5545 | 227.3272 | 9.8529 | 37.2506 | 27.5668 | 0.00075198 | 0.11354 | 0.13867 | 0.12943 | 0.095786 | 6.3172 | 0.11996 | 0.11539 | 0.1077 | 0.018489 | 237.4331 | 37.4878 | 10.107 | 27.681 | -237.1329 | -86.25% | 2031
2032 | 3.5545 | 227.3272 | 8.9749 | 33.9313 | 25.1103 | 0.00075198 | 0.11354 | 0.12632 | 0.1179 | 0.087251 | 6.2436 | 0.11996 | 0.1051 | 0.098102 | 0.016841 | 237.3595 | 34.1473 | 9.2063 | 25.2144 | -237.0861 | -87.32% | 2032
2033 | 3.5545 | 227.3272 | 8.0969 | 30.6119 | 22.6539 | 0.00075198 | 0.11354 | 0.11396 | 0.10637 | 0.078715 | 6.417 | 0.11996 | 0.094822 | 0.088505 | 0.015194 | 237.5329 | 30.8068 | 8.3057 | 22.7478 | -237.2862 | -88.43% | 2033
2034 | 3.5545 | 227.3272 | 7.219 | 27.2925 | 20.1974 | 0.00075198 | 0.11354 | 0.1016 | 0.094833 | 0.07018 | 6.5614 | 0.11996 | 0.08454 | 0.078908 | 0.013546 | 237.6773 | 27.4663 | 7.4051 | 20.2812 | -237.4574 | -89.56% | 2034
2035 | 3.5545 | 227.3272 | 6.341 | 23.9732 | 17.741 | 0.00075198 | 0.11354 | 0.089245 | 0.0833 | 0.061645 | 6.69 | 0.11996 | 0.074258 | 0.069312 | 0.011899 | 237.8059 | 24.1258 | 6.5045 | 17.8145 | -237.6127 | -90.72% | 2035
2036 | 3.5545 | 227.3272 | 5.463 | 20.6538 | 15.2845 | 0.00075198 | 0.11354 | 0.076888 | 0.071766 | 0.053109 | 6.5744 | 0.11996 | 0.063977 | 0.059715 | 0.010251 | 237.6903 | 20.7853 | 5.6039 | 15.3479 | -237.5238 | -91.89% | 2036
2037 | 3.5545 | 227.3272 | 4.585 | 17.3344 | 12.8281 | 0.00075198 | 0.11354 | 0.064531 | 0.060232 | 0.044574 | 6.6755 | 0.11996 | 0.053695 | 0.050118 | 0.0086036 | 237.7914 | 17.4448 | 4.7032 | 12.8813 | -237.6517 | -93.11% | 2037
2038 | 3.5545 | 227.3272 | 3.707 | 14.0151 | 10.3717 | 0.00075198 | 0.11354 | 0.052174 | 0.048698 | 0.036038 | 6.7502 | 0.11996 | 0.043413 | 0.040521 | 0.0069561 | 237.8661 | 14.1043 | 3.8026 | 10.4147 | -237.7531 | -94.36% | 2038
2039 | 3.5545 | 227.3272 | 2.829 | 10.6957 | 7.9152 | 0.00075198 | 0.11354 | 0.039817 | 0.037164 | 0.027503 | 6.816 | 0.11996 | 0.033131 | 0.030924 | 0.0053086 | 237.9319 | 10.7638 | 2.902 | 7.948 | -237.8457 | -95.64% | 2039
2040 | 3.5545 | 227.3272 | 1.9511 | 7.3764 | 5.4588 | 0.00075198 | 0.11354 | 0.02746 | 0.025631 | 0.018968 | 6.853 | 0.11996 | 0.022849 | 0.021327 | 0.0036611 | 237.9689 | 7.4233 | 2.0014 | 5.4814 | -237.9094 | -96.95% | 2040
2041 | 3.5545 | 227.3272 | 1.756 | 6.6387 | 4.9129 | 0.00075198 | 0.11354 | 0.024714 | 0.023068 | 0.017071 | 6.8848 | 0.11996 | 0.020564 | 0.019194 | 0.003295 | 238.0007 | 6.681 | 1.8012 | 4.9333 | -237.9472 | -97.25% | 2041
2042 | 3.5545 | 227.3272 | 1.5609 | 5.9011 | 4.367 | 0.00075198 | 0.11354 | 0.021968 | 0.020505 | 0.015174 | 6.9312 | 0.11996 | 0.018279 | 0.017061 | 0.0029289 | 238.0471 | 5.9387 | 1.6011 | 4.3851 | -237.9996 | -97.55% | 2042
2043 | 3.5545 | 227.3272 | 1.3657 | 5.1635 | 3.8211 | 0.00075198 | 0.11354 | 0.019222 | 0.017941 | 0.013277 | 6.9608 | 0.11996 | 0.015994 | 0.014929 | 0.0025628 | 238.0768 | 5.1963 | 1.401 | 3.837 | -238.0351 | -97.85% | 2043
2044 | 3.5545 | 227.3272 | 1.1706 | 4.4258 | 3.2753 | 0.00075198 | 0.11354 | 0.016476 | 0.015378 | 0.011381 | 6.9811 | 0.11996 | 0.013709 | 0.012796 | 0.0021967 | 238.097 | 4.454 | 1.2008 | 3.2888 | -238.0614 | -98.15% | 2044
2045 | 3.5545 | 227.3272 | 0.97553 | 3.6882 | 2.7294 | 0.00075198 | 0.11354 | 0.01373 | 0.012815 | 0.0094838 | 7.0206 | 0.11996 | 0.011424 | 0.010663 | 0.0018305 | 238.1365 | 3.7117 | 1.0007 | 2.7407 | -238.1068 | -98.45% | 2045
2046 | 3.5545 | 227.3272 | 0.78043 | 2.9505 | 2.1835 | 0.00075198 | 0.11354 | 0.010984 | 0.010252 | 0.007587 | 6.9775 | 0.11996 | 0.0091395 | 0.0085306 | 0.0014644 | 238.0934 | 2.9693 | 0.80055 | 2.1926 | -238.0696 | -98.76% | 2046
2047 | 3.5545 | 227.3272 | 0.58532 | 2.2129 | 1.6376 | 0.00075198 | 0.11354 | 0.008238 | 0.0076892 | 0.0056903 | 7.0308 | 0.11996 | 0.0068546 | 0.006398 | 0.0010983 | 238.1467 | 2.227 | 0.60041 | 1.6444 | -238.1288 | -99.07% | 2047
2048 | 3.5545 | 227.3272 | 0.39021 | 1.4753 | 1.0918 | 0.00075198 | 0.11354 | 0.005492 | 0.0051261 | 0.0037935 | 7.0484 | 0.11996 | 0.0045698 | 0.0042653 | 0.00073222 | 238.1644 | 1.4847 | 0.40028 | 1.0963 | -238.1525 | -99.38% | 2048
2049 | 3.5545 | 227.3272 | 0.19511 | 0.73764 | 0.54588 | 0.00075198 | 0.11354 | 0.002746 | 0.0025631 | 0.0018968 | 7.069 | 0.11996 | 0.0022849 | 0.0021327 | 0.00036611 | 238.1849 | 0.74233 | 0.20014 | 0.54814 | -238.179 | -99.69% | 2049
2050 | 3.5545 | 227.3272 | 0 | 0 | 0 | 0.00075198 | 0.11354 | 0 | 0 | 0 | 7.1641 | 0.11996 | 0 | 0 | 0 | 238.28 | 0 | 0 | 0 | -238.28 | -100% | 2050
Cumulative 2025-2030 Emissions | 21.3267 | 1363.9633 | 886.8087 | 262.9762 | 223.8993 | 0.0045119 | 0.68121 | 0.78729 | 0.91376 | 0.77798 | 67.1555 | 0.71977 | 52.2944 | 0.76032 | 0.54665 | 1453.851 | 264.6503 | 939.8904 | 225.2239 | -553.387 | -32.2% | Cumulative 2025-2030 Emissions
% Emissions Reduced (2025-2030) | -35.98% |  |  | -14.86% |  | 14.81% |  |  | -14.86% |  | -22.96% |  |  | -28.1% |  |  |  | -35.35% | -14.9% |  |  | % Emissions Reduced (2025-2030)
Cumulative 2025-2050 Emissions | 92.4158 | 5910.5077 | 954.6084 | 519.3048 | 413.5914 | 0.019552 | 2.9519 | 1.7415 | 1.8044 | 1.4371 | 203.1221 | 3.119 | 53.0884 | 1.5014 | 0.67387 | 6212.1361 | 522.6106 | 1009.4383 | 415.7024 | -5309.606 | -78.84% | Cumulative 2025-2050 Emissions
% Emissions Reduced (2025-2050) | -84.1% |  |  | -20.36% |  | -41.39% |  |  | -20.36% |  | -74.26% |  |  | -55.12% |  |  |  | -83.75% | -20.46% |  |  | % Emissions Reduced (2025-2050)
| BAU Emissions (MT CO2e) | [10 empty] | GHP Emissions (MT CO2e)
Total Cumulative Emissions 2025-2030 | 1718.5013 | [10 empty] | 1165.1143 | [9 empty] | Total Cumulative Emissions 2025-2030
Change in emissions 2025-2030 | [11 empty] | -32.2% | [9 empty] | Change in emissions 2025-2030
Total Cumulative Emisisons 2025-2050 | 6734.7467 | [10 empty] | 1425.1407 | [9 empty] | Total Cumulative Emisisons 2025-2050
Change in emissions 2025-2050 | [11 empty] | -78.84% | [9 empty] | Change in emissions 2025-2050

## Union Electricity Consumption
Electricity Consumption | [5 empty] | Chiller Electricity Consumption
Start Date | End Date | Usage Total (kWh/MMBTU) |  |  |  | Chiller runs at full capacity for 6 months of the year, May through October
2024-01-05 | 2024-02-06 | 181692 | February |  |  | We assume chiller runs 12 hours per day.
2023-12-07 | 2024-01-04 | 163461 | January |  |  | Month | Days | Electricity Consumption (kWh)
2023-11-07 | 2023-12-06 | 170877 | December |  |  | May | 31 | 178292.9999
2023-10-09 | 2023-11-06 | 179529 | November |  |  | June | 30 | 183855
2023-09-08 | 2023-10-08 | 206721 | October |  |  | July | 31 | 226497
2023-08-08 | 2023-09-07 | 220935 | September |  |  | August | 31 | 222171
2023-07-10 | 2023-08-07 | 222171 | August |  |  | September | 30 | 220935
2023-06-08 | 2023-07-09 | 226497 | July | Total: | 2442644.9999 | October | 31 | 206721
2023-05-09 | 2023-06-07 | 183855 | June |  |  | Total | 184 | 1238471.9999
2023-04-10 | 2023-05-08 | 178292.9999 | May |  |  | On for | 2208 | hours in 2023
2023-03-09 | 2023-04-09 | 176439 | April |  |  | 460 Volt 60 Hz 3 Phase chiller
2023-03-09 | 2023-04-09 | 0 |  |  |  | Capacity | 100 tons | 351.7 | kW
2023-02-07 | 2023-03-08 | 159135 | March |  |  | Efficiencies range from 13.7-16.6 EER |  |  |  | https://www.trane.com/commercial/north-america/us/en/products-systems/chillers/air-cooled-chillers/cgam.html
2023-02-07 | 2023-03-08 | 0 |  |  |  | Avg EER: | 15.15
2023-01-06 | 2023-02-06 | 173040 | February |  |  | Converted to COP | 4.4402
2023-01-06 | 2023-02-06 | 0 |  |  |  | 174891.1474 | kWh (2023)
2022-12-07 | 2023-01-05 | 0
2022-11-07 | 2022-12-06 | 0
2022-10-07 | 2022-11-06 | 0
2022-09-08 | 2022-10-06 | 0
2022-08-08 | 2022-09-07 | 0
2022-07-08 | 2022-08-07 | 0
2022-06-08 | 2022-07-07 | 0
2022-05-09 | 2022-06-07 | 0
2022-04-08 | 2022-05-08 | 0

## Union Gas Consumption
Month | Gas Consumption (energy content) |  | 3 Boilers
January | 5709.599 | ccf |  | AFUE | Boiler Year
February | 6339.149 | ccf | Boiler 1 | 92.7 | 2019
March | 7813.135 | ccf | Boiler 2 | 92.7 | 2017
April | 6683.303 | ccf | Boiler 3 | 83.2 | 2010
May | 6424.768 | ccf | Average | 89.5333
June | 3656.426 | ccf
July | 787.357 | ccf
August | 0 | ccf
September | 1.679 | ccf
October | 3.358 | ccf
November | 787.357 | ccf
December | 3068.846 | ccf
TOTAL | 41274.977 | ccf
TOTAL | 4284.3426 | MMBtu
TOTAL | 120976.9576 | cubic meter
1 ccf = 103,800 Btu = 0.1038 MMBtu = 2.931 cubic meter |  |  | https://www.eia.gov/tools/faqs/faq.php?id=45&t=8

## CAPs & HAPs
Estimating Size Ratio of USATEN to Model "District Geothermal Pilot Installed in a Newly Constructed Neighborhood" |  |  |  | https://portal.ct.gov/-/media/deep/climatechange/cprg/ct_pcap.pdf
| Model from CTPCAP | USATEN | Unit
Boreholes |  | 285
Tons/Borehole |  | 5
Heating Capacity | 375 | 1425 | tons
Heating Capacity Ratio |  | 3.8
Modeling CAP Emissions Reductions
CAP | CT PCAP: 2030 Annual Emissions Reductions in Newly Constructed Neighborhood (lbs) | USATEN Annual Emissions Reductions (lbs) | USATEN Emissions Reductions, 2025-2050 (lbs)
CO | 194 | 737.2 | 15849.8
CH4 | 11 | 41.8 | 898.7
NOx | 457 | 1736.6 | 37336.9
PM (filterable) | 9 | 34.2 | 735.3
PM (primary) | 37 | 140.6 | 3022.9
Total Urban Toxics HAP | 12 | 45.6 | 980.4
SO2 | 3 | 11.4 | 245.1
Total | 723 | 2747.4 | 59069.1
USATEN Emissions Reductions by GHG
GHG | USATEN Annual Emissions Reductions, 2025-2030 (MT CO2e) | USATEN Annual Emissions Reductions, 2025-2050 (MT CO2e) | (lb)
CO2 | -6177.5719 | -61351.5713 | -135280214.7016
N2O | 0.10056 | -19.2777 | -42507.2848
CH4 | -185.4248 | -1900.7321 | -4191114.3407
Total | -6362.8962 | -63271.5811 | -139513836.3271