## Pump Station Energy Reductions
Palm Coast Pump Station Energy Reduction Calculations
Pump Station ID | Yearly Daily Average Energy Use, EY (kWh/day) | Yearly Daily Average Energy Use w/out Spike Events, EY-S (kWh/day) | Spike Event Daily Average Energy Use, ES (kWh/day) | Percent of Energy Increase during Spike Events from Yearly Daily Ave., SY = ES / EY | Percent of Energy Increase during Spike Events from Yearly Daily Ave. w/out Spike Events, SY-S = ES / EY-S | Comparison Pump % Difference from 39-1 (Yearly), DY = SY39-1 - SY22-2 | Comparison Pump % Difference from 39-1 (Yearly w/out Spike Events), DY-S = SY-S,39-1 - SY-S,22-2 | Percent Energy Usage Reduction Upper Range Target, PU = Average of DY & DY-S
22-2* | 34.14 | 31.39 | 51.89 | 152% | 165.3% | 21.19% | 30.04% | 24.59%
MPS-B* | 299.75 | 274.78 | 460.77 | 153.7% | 167.7% | 19.46% | 27.66%
39-1 | 122.42 | 108.53 | 212.01 | 173.2% | 195.3% | N/A
* Pumps used for comparison (pumps servicing drainage areas with new existing drainage systems where it is assumed to have little to no groundwater intrusion).
Dryer Months' Daily Average Energy Use, ED (kWh/day) | Wetter Months Daily Average Energy use w/Out Spike Events, EW-S (kWh/day) | Percent of Energy Increase during Wet Months w/Out Spike Events from Dry Months, SW = EW-S / ED | Comparison Pump % Difference from 39-1, DW = SW39-1 - SW | Percent Energy Usage Reduction Lower Range Target, PL = Average of DW
29.94 | 35.32 | 118% | 4.587% | 10.31%
270.04 | 287.67 | 106.5% | 16.03%
102.32 | 125.4 | 122.6% | N/A
Pump Station ID | Wet Months Average Energy Use, EW (kWh/day) | Percent Energy Usage Reduction Lower Range Target, PL | Percent Energy Usage Reduction Upper Range Target, PU | Energy Reduction (Lower Range), RLD (kWh/day) | Energy Reduction (Upper Range), RUD (kWh/day) | Energy Reduction (Lower Range), RLY (KWh/year) | Energy Reduction (Upper Range), RUY (kWh/year)
39-1 | 157.2105 | 10.31% | 24.59% | 16.2048 | 38.6559 | 1976.9873 | 4716.0241
CP-1** | 33.498 | 5.154% | 12.29% | 1.7264 | 4.1184 | 210.6258 | 502.4395
19-1** | 113.1244 | 5.154% | 12.29% | 5.8303 | 13.9079 | 711.2933 | 1696.7618
20-1** | 219.494 | 5.154% | 12.29% | 11.3124 | 26.9853 | 1380.1142 | 3292.2073
20-2** | 81.413 | 5.154% | 12.29% | 4.1959 | 10.0092 | 511.9008 | 1221.119
32-2** | 81.413 | 5.154% | 12.29% | 4.1959 | 10.0092 | 511.9008 | 1221.119
24-2** | 817.3766 | 5.154% | 12.29% | 42.1264 | 100.4909 | 5139.425 | 12259.8928
OKR Master** | 553.1026 | 5.154% | 12.29% | 28.5061 | 68.0002 | 3477.7474 | 8296.0275
57-4 | 342.9859 | 10.31% | 24.59% | 35.354 | 84.3356 | 4313.1903 | 10288.9429
57-1** | 11.3619 | 5.154% | 12.29% | 0.58558 | 1.3969 | 71.4402 | 170.4178
57-2** | 29.4108 | 5.154% | 12.29% | 1.5158 | 3.6159 | 184.9266 | 441.1351
57-3** | 41.9013 | 5.154% | 12.29% | 2.1595 | 5.1515 | 263.4632 | 628.4809
[5 empty] | Totals: | 18753.0152 | 44734.5678
[5 empty] | Cost Reductions: | 2507.3371 | 5981.1523
** Pump Stations impacted by flow reductions to Pump Stations 39-1 and 54-4.
NREL Projected CO2e Emissions Rates | Year | 2024 | 2026 | 2028 | 2030 | 2032 | 2034 | 2036
| MT CO2e / KWh | 0.00036792 | 0.00033509 | 0.00027803 | 0.00023902 | 0.00024177 | 0.00020165 | 0.00019661
| Year | 2038 | 2040 | 2042 | 2044 | 2046 | 2048 | 2050
| MT CO2e / KWh | 0.00018753 | 0.00019018 | 0.00017533 | 0.00017369 | 0.00016939 | 0.0001592 | 0.0001557
Average Yearly MT CO2e Reduction
2025 |  | 2038: 2026 - 2027; 2042: 2028 - 2029; 2046: 2030; 2050: Total by 2030
Lower | Upper | Lower | Upper | Lower | Upper | Lower | Upper | Lower | Upper
6.8997 | 16.4589 | 6.284 | 14.9903 | 5.214 | 12.4378 | 4.4824 | 10.6926 | 34.3781 | 98.4666
2031 |  | 2038: 2032 - 2033; 2042: 2034 - 2035; 2046: 2036 - 2037; 2050: 2038 - 2039
Lower | Upper | Lower | Upper | Lower | Upper | Lower | Upper | Lower | Upper
4.4824 | 10.6926 | 4.534 | 10.8156 | 3.7815 | 9.0206 | 3.6871 | 8.7954 | 3.5167 | 8.3889
2040 - 2041 |  | 2038: 2042 - 2043; 2042: 2044 - 2045; 2046: 2046 - 2047; 2050: 2048 - 2049
Lower | Upper | Lower | Upper | Lower | Upper | Lower | Upper | Lower | Upper
3.5664 | 8.5074 | 3.2879 | 7.8432 | 3.2573 | 7.7701 | 3.1766 | 7.5777 | 2.9854 | 7.1216
[6 empty] | 2050 |  | Total by 2050
|  | 2046: Lower; 2048: Upper; 2050: Lower | Upper
|  | 2046: 2.9198; 2048: 6.9651; 2050: 105.366 | 267.8052

## Tank Truck Reduction Calcs
Palm Coast Pump Truck Diesel Reduction Calculations
Additional Days Trucks Deployment (Dry Season)
Date | Company | # of Trucks | Time (City) | Time (Hr) | Total Hr/Day | Costs | Rainfall | Invoice/Order Number
2024-09-25 | All Daytona Septic Tank Service | 3 | 21 | 1.5 | 22.5 | 450 | .09" | 38814
2024-09-26 | All Daytona Septic Tank Service | 3 | 21 | 10.5 | 43.5 | 3150 | 1.94" | 38814
2024-09-26 | All Daytona Septic Tank Service | 3 |  | 12 |  | 3600 | 1.94" | 38815
2024-09-27 | All Daytona Septic Tank Service | 3 | 21 | 10.5 | 47.5 | 3150 | 0 | 38815
2024-09-27 | All Daytona Septic Tank Service | 4 |  | 16 |  | 4800 | 0 | 38834
2024-09-28 | All Daytona Septic Tank Service | 4 | 21 | 22 | 43 | 6600 | 1" | 38834
2024-09-29 | All Daytona Septic Tank Service | 2 | 21 | 26 | 47 | 7800 | .05" | 38851
2024-09-30 | All Daytona Septic Tank Service | 4 | 21 | 56 | 126 | 16800 | 0 | 38852
2024-09-30 | Brownies | 1 |  | 8 |  | 2800 | 0 | i119303
2024-09-30 | Brownies | 1 |  | 10 |  | 3500 | 0 | i119302
2024-09-30 | Brownies | 1 |  | 13 |  | 4550 | 0 | i119305
2024-09-30 | Environmental Control Systems Inc DBA | 1 |  | 18 |  | 4950 | 0 | 20200861
2024-10-01 | All Daytona Septic Tank Service | 4 | 21 | 31 | 121.5 | 9300 | 0 | 38853
2024-10-01 | Brownies | 1 |  | 10 |  | 3500 | 0 | 849017782
2024-10-01 | Brownies | 1 |  | 10.5 |  | 3675 | 0 | 8490177883
2024-10-01 | Brownies | 1 |  | 5 |  | 1750 | 0 | 8490177880
2024-10-01 | Brownies | 1 |  | 12 |  | 4200 | 0 | 8490177878
2024-10-01 | Brownies | 1 |  | 8 |  | 2800 | 0 | 8490177879
2024-10-01 | Brownies | 1 |  | 24 |  | 8400 | 0 | 8490177747
2024-10-02 | All Daytona Septic Tank Service | 4 | 21 | 57.5 | 197 | 17250 | 2.81" | 38862
2024-10-02 | Brownies | 1 |  | 24 |  | 8400 | 2.81" | 8490177751
2024-10-02 | Brownies | 1 |  | 11 |  | 3850 | 2.81" | 8490177750
2024-10-02 | Brownies | 1 |  | 24 |  | 8400 | 2.81" | 8490177748
2024-10-02 | Brownies | 1 |  | 11.5 |  | 4025 | 2.81" | 8490177749
2024-10-02 | Brownies | 1 |  | 24 |  | 8400 | 2.81" | 8490177764
2024-10-02 | Brownies | 1 |  | 24 |  | 8400 | 2.81" | 8490177752
2024-10-03 | All Daytona Septic Tank Service | 3 | 21 | 4.5 | 49.5 | 1350 | .04" | 38862
2024-10-03 | Brownies | 1 |  | 6 |  | 2100 | .04" | 8490177877
2024-10-03 | Brownies | 1 |  | 6 |  | 2100 | .04" | 8490177875
2024-10-03 | Brownies | 1 |  | 6 |  | 2100 | .04" | 8490177874
2024-10-03 | Brownies | 1 |  | 6 |  | 2100 | .04" | 8490177876
2024-10-10 | All Daytona Septic Tank Service | 2 | 21 | 13 | 34 | 3900 | .04" | 38917
2024-10-12 | Environmental Control Systems Inc DBA | 1 | 21 | 31 | 256.5 | 8525 | 2.39" | 20200861
2024-10-12 | All Daytona Septic Tank Service | 5 |  | 88 |  | 26400 | 2.39" | 38969
2024-10-12 | Brownies | 1 |  | 8 |  | 2000 | 2.39" | 8487010073
2024-10-12 | Brownies | 1 |  | 20.5 |  | 5125 | 2.39" | 8490178718
2024-10-12 | Brownies | 1 |  | 12.5 |  | 3125 | 2.39" | 8490178730
2024-10-12 | Brownies | 1 |  | 4.25 |  | 1062.5 | 2.39" | 8490178770
2024-10-12 | Brownies | 1 |  | 4 |  | 1000 | 2.39" | 8490178762
2024-10-12 | Brownies | 1 |  | 8.25 |  | 2062.5 | 2.39" | 8490178761
2024-10-12 | Brownies | 1 |  | 11.5 |  | 2875 | 2.39" | 8487010072
2024-10-12 | Brownies | 1 |  | 19 |  | 4750 | 2.39" | 8490178717
2024-10-12 | Brownies | 1 |  | 15 |  | 3750 | 2.39" | 8487010074
2024-10-12 | Brownies | 1 |  | 13.5 |  | 3375 | 2.39" | 8487010071
2024-10-13 | All Daytona Septic Tank Service | 5 | 21 | 99 | 237.5 | 29700 | 0 | 38969
2024-10-13 | Brownies | 1 |  | 16 |  | 4000 | 0 | 8487010182
2024-10-13 | Brownies | 1 |  | 16 |  | 4000 | 0 | 8487010184
2024-10-13 | Brownies | 1 |  | 16 |  | 4000 | 0 | 8487010183
2024-10-13 | Brownies | 1 |  | 16 |  | 4000 | 0 | 8487010181
2024-10-13 | Brownies | 1 |  | 9.5 |  | 2375 | 0 | 8490178772
2024-10-13 | Brownies | 1 |  | 11 |  | 2750 | 0 | 8490178829
2024-10-13 | Brownies | 1 |  | 18.5 |  | 4625 | 0 | 8490178771
2024-10-13 | Brownies | 1 |  | 7.25 |  | 1812.5 | 0 | 8490178810
2024-10-13 | Brownies | 1 |  | 7.25 |  | 1812.5 | 0 | 8490178831
2024-11-16 | All Daytona Septic Tank Service | 2 | 21 | 2 | 23 | 600 | 0.16" | 39296
2024-11-17 | All Daytona Septic Tank Service | 4 | 21 | 74 | 95 | 22200 | 2.10" | 39296
2024-11-18 | All Daytona Septic Tank Service | 4 | 21 | 4 | 25 | 1200 | .66" | 39296
2024-12-16 | All Daytona Septic Tank Service | 3 | 21 | 4.5 | 25.5 | 1350 | .11" | 39690
2024-12-17 | Brownies | 1 | 21 | 13.5 | 184 | 3375 | 4.04" | 6159323
2024-12-17 | Brownies | 1 |  | 8 |  | 2075 | 4.04" | 6159213
2024-12-17 | Brownies | 1 |  | 13.5 |  | 3450 | 4.04" | 6159216
2024-12-17 | Brownies | 1 |  | 13.5 |  | 3450 | 4.04" | 6159218
2024-12-17 | Brownies | 1 |  | 13.5 |  | 3450 | 4.04" | 6159219
2024-12-17 | Environmental Control Systems Inc DBA | 1 |  | 19 |  | 5225 | 4.04" | 28720
2024-12-17 | All Daytona Septic Tank Service | 4 |  | 82 |  | 24600 | 4.04" | 39690
2024-12-18 | All Daytona Septic Tank Service | 4 | 21 | 30 | 64.5 | 9000 | .05" | 39690
2024-12-18 | Brownies | 1 |  | 13.5 |  | 3450 | .05" | 6159939
Average Total Hours Per Day: |  |  |  |  | 91.25
Average Total Pumping Time for all Trucks per Day (Hours/Day) | [5 empty] | 91.25
Avereage Pump Truck Fuel Usage per Hour (Gallons/Hour/Truck) | [5 empty] | 4.25
Average Pump Truck Fuel Usage for all Trucks per day (GPD) | [5 empty] | 387.8125
Average Number of Days of Truck Deployment per Year (Days/Year) | [5 empty] | 127
Average Total Gallons of Diesel Fuel Used per Year by all Trucks (GPY) | [5 empty] | 49252.1875
Approx. Gallons of Fuel Saved by PS 39-1 Service Area Improvements per Year (10% of Total by Land Area) (GPY) | [5 empty] | 4925.2188
Approx. Cost Savings due to Fuel Saved by PS 39-1 Service Area Improvements per Year ($/Year) (Use $4.25/gallon) | [5 empty] | 20932.1797
Approx. Grams of CO2e Reduction per Year | [5 empty] | 501387268.75
Total MT CO2e Reduction per Year | [5 empty] | 501.3873
MT CO2e Reduction for 39-1 per Year (10% of Total by Land Area) | [5 empty] | 50.1387
Equation: |  |  |  |  | Palm Coast Pump Truck Diesel GHG Reduction
10,180 grams of CO2/gallon of diesel = 10.180 × 10-3 metric tons CO2/gallon of diesel |  |  |  |  | 2025 - 2030 MT CO2e Reduction |  |  | 300.8324
[5 empty] | 2025 - 2050 MT CO2e Reduction |  |  | 1303.6069
Additional Days Trucks Deployment (Dry Season)
03/13/2023 | 127.76 | 18.03 | 81 | 46 | 1.17
03/14/2023 | 122.77 | 17.34 | 70 | 43 | 0.6
04/09/2023 | 106.37 | 15.08 | 80 | 60 | 0.01
04/10/2023 | 105.56 | 14.97 | 79 | 58 | 0.68
04/11/2023 | 109.35 | 15.07 | 78 | 58 | 1.38
04/13/2023 | 138.83 | 19 | 87 | 61 | 0.07
04/14/2023 | 186.5 | 25.36 | 86 | 59 | 0.57
04/15/2023 | 158.74 | 21.66 | 87 | 60 | 0.02
04/16/2023 | 141.46 | 19.35 | 88 | 59 | 0
04/28/2023 | 197.24 | 26.79 | 87 | 62 | 1.62
04/29/2023 | 162.32 | 22.13 | 88 | 62 | 0
04/30/2023 | 162.69 | 22.18 | 85 | 57 | 0.52
05/18/2023 | 83.77 | 11.63 | 89 | 65 | 1.24
05/22/2023 | 103.91 | 14.31 | 88 | 67 | 0.65
05/23/2023 | 131.41 | 17.97 | 85 | 67 | 0.56
05/24/2023 | 131.06 | 17.93 | 83 | 66 | 0.12
06/07/2023 | 124.73 | 17.08 | 91 | 68 | 0
06/08/2023 | 96.99 | 13.39 | 92 | 68 | 1.64
06/09/2023 | 98.73 | 13.22 | 92 | 68 | 0
06/10/2023 | 100.35 | 13.43 | 88 | 67 | 0.54
06/11/2023 | 104.67 | 13.99 | 91 | 69 | 0.09
06/12/2023 | 102.99 | 13.77 | 94 | 69 | 0
06/16/2023 | 114.42 | 15.25 | 95 | 68 | 0.45
06/17/2023 | 131.94 | 17.51 | 93 | 68 | 0.91
06/18/2023 | 146.34 | 19.37 | 94 | 68 | 0.28
06/19/2023 | 161.42 | 21.32 | 93 | 70 | 0.63
06/20/2023 | 185.92 | 24.49 | 91 | 69 | 0.46
06/21/2023 | 146.5 | 19.39 | 91 | 71 | 0.24
06/22/2023 | 136.39 | 18.09 | 93 | 66 | 0.04
06/23/2023 | 145.21 | 19.23 | 91 | 69 | 0.35
06/24/2023 | 139.38 | 18.47 | 92 | 70 | 0.24
06/25/2023 | 131.47 | 17.45 | 91 | 70 | 0.15
06/29/2023 | 102.35 | 13.69 | 95 | 71 | 0.88
07/11/2023 | 93.67 | 12.59 | 94 | 73 | 0.78
07/15/2023 | 109.69 | 14.66 | 96 | 73 | 0.12
07/16/2023 | 113.57 | 15.16 | 96 | 74 | 0.15
07/17/2023 | 107.39 | 14.37 | 95 | 74 | 2.8
07/18/2023 | 104.17 | 13.95 | 95 | 72 | 0.22
07/19/2023 | 102.28 | 13.7 | 95 | 71 | 0.14
07/23/2023 | 135.17 | 17.95 | 94 | 71 | 0.7
07/24/2023 | 128.06 | 17.04 | 93 | 73 | 1.12
07/25/2023 | 122.92 | 16.37 | 93 | 73 | 0.3
07/28/2023 | 112.5 | 15.03 | 92 | 73 | 1
07/30/2023 | 123.68 | 16.47 | 95 | 74 | Trace Value
07/31/2023 | 146.23 | 19.38 | 95 | 71 | 0.74
08/01/2023 | 129.31 | 17.2 | 95 | 71 | 0.08
08/05/2023 | 147.44 | 19.54 | 94 | 73 | 0.17
08/06/2023 | 145.08 | 19.23 | 95 | 74 | 0.66
08/07/2023 | 143.6 | 19.04 | 97 | 75 | 0.03
08/08/2023 | 152.56 | 20.2 | 99 | 75 | 0
08/18/2023 | 134.32 | 17.82 | 93 | 73 | 1.09
08/19/2023 | 130.36 | 17.31 | 93 | 72 | 0.69
08/24/2023 | 97.02 | 13 | 93 | 74 | 0.99
08/30/2023 | 100.39 | 13.44 | 94 | 74 | 0.93
09/08/2023 | 163.24 | 21.56 | 95 | 69 | 0
09/13/2023 | 180.96 | 23.88 | 92 | 72 | 0.03
09/14/2023 | 185.97 | 24.53 | 91 | 71 | 0.29
09/12/2023 | 134.31 | 17.85 | 92 | 71 | Trace Value
09/13/2023 | 180.96 | 23.88 | 92 | 72 | 0.03
09/14/2023 | 185.97 | 24.53 | 91 | 71 | 0.29
Numbers of Days |  | = | 60

## Costs & Summary
Palm Coast Wastewater Efficiency Summary of CO2e Reduction Calculations
Average Yearly MT CO2e Reduction
Year: | 2025 |  | 2026 - 2027 |  | 2028 - 2029 |  | 2030 |  | Total by 2030
Range: | Lower | Upper | Lower | Upper | Lower | Upper | Lower | Upper | Lower | Upper
Pump Stations: | 6.8997 | 16.4589 | 6.284 | 14.9903 | 5.214 | 12.4378 | 4.4824 | 10.6926 | 34.3781 | 98.4666
Pump Trucks: | 50.1387 | 50.1387 | 50.1387 | 50.1387 | 50.1387 | 50.1387 | 50.1387 | 50.1387 | 300.8324 | 300.8324
Totals: | 57.0384 | 66.5976 | 56.4228 | 65.1291 | 55.3527 | 62.5765 | 54.6211 | 60.8313 | 335.2105 | 399.2989
Average Yearly MT CO2e Reduction
Year: | 2031 |  | 2032 - 2033 |  | 2034 - 2035 |  | 2036 - 2037 |  | 2038 - 2039
Range: | Lower | Upper | Lower | Upper | Lower | Upper | Lower | Upper | Lower | Upper
Pump Stations: | 4.4824 | 10.6926 | 4.534 | 10.8156 | 3.7815 | 9.0206 | 3.6871 | 8.7954 | 3.5167 | 8.3889
Pump Trucks: | 50.1387 | 50.1387 | 50.1387 | 50.1387 | 50.1387 | 50.1387 | 50.1387 | 50.1387 | 50.1387 | 50.1387
Totals: | 54.6211 | 60.8313 | 54.6727 | 60.9543 | 53.9202 | 59.1594 | 53.8258 | 58.9341 | 53.6554 | 58.5277
Year: | 2040 - 2041 |  | 2042 - 2043 |  | 2044 - 2045 |  | 2046 - 2047 |  | 2048 - 2049
Range: | Lower | Upper | Lower | Upper | Lower | Upper | Lower | Upper | Lower | Upper
Pump Stations: | 3.5664 | 8.5074 | 3.2879 | 7.8432 | 3.2573 | 7.7701 | 3.1766 | 7.5777 | 2.9854 | 7.1216
Pump Trucks: | 50.1387 | 50.1387 | 50.1387 | 50.1387 | 50.1387 | 50.1387 | 50.1387 | 50.1387 | 50.1387 | 50.1387
Totals: | 53.7051 | 58.6461 | 53.4266 | 57.9819 | 53.396 | 57.9088 | 53.3154 | 57.7164 | 53.1242 | 57.2603
[7 empty] | 2050 |  | Total by 2050
[7 empty] | Lower | Upper | Lower | Upper
[7 empty] | 2.9198 | 6.9651 | 105.366 | 267.8052
[7 empty] | 50.1387 | 50.1387 | 1303.6069 | 1303.6069
[7 empty] | 53.0586 | 57.1039 | 1408.9729 | 1571.4121
Improvement's Costs and Savings
Ave. Yearly Pump Station Energy Cost Reduction ($/year) |  | Ave. Pump Truck Diesel Cost Reduction ($/year) |  | Approx. Total Yearly Cost Reduction ($/year) |  | Approx. Total 2030 Cost Reduction ($) |  | Approx. Total Cost of Improvements |  | Difference ($)
Lower | Upper | Lower | Upper | Lower | Upper | Lower | Upper | Lower | Upper | Lower | Upper
2507.3371 | 5981.1523 | 20932.1797 | 20932.1797 | 23439.5167 | 26913.332 | 140637.1005 | 161479.9918 | 9947404 | 9947404 | 9806766.8995 | 9785924.0082
CO2e Reduction Summary Table
Total MT CO2e Reduction by 2030 |  | Total MT CO2e Reduction by 2050 |  | Cost per MT CO2e Removed by 2030
Lower | Upper | Lower | Upper | Lower | Upper
335.2105 | 399.2989 | 1408.9729 | 1571.4121 | 29255.548 | 24507.765
Note on I28: Amanda Polematidis: Total cost to be the award cost, not the construction costs. $9.9999M

## CO2e Emission Rates
Year | MT CO2e / MWh | MT CO2e / KWh
2024 | 0.36792 | 0.00036792
2026 | 0.33509 | 0.00033509
2028 | 0.27803 | 0.00027803
2030 | 0.23902 | 0.00023902
2032 | 0.24177 | 0.00024177
2034 | 0.20165 | 0.00020165
2036 | 0.19661 | 0.00019661
2038 | 0.18753 | 0.00018753
2040 | 0.19017 | 0.00019018
2042 | 0.17533 | 0.00017533
2044 | 0.17369 | 0.00017369
2046 | 0.16939 | 0.00016939
2048 | 0.1592 | 0.0001592
2050 | 0.1557 | 0.0001557
2030 Avg | 0.30502 | 0.00030502
2050 Avg | 0.21937 | 0.00021937

## 39-1
Daily Billed Information (PS 39-1: 2023 Reading Data)
Bill Account | Meter Number | Date | Consumption Recorded (kWh/day) | Estimated Cost ($/day) | Avg. High Temperature (°F) | Avg. Low Temperature (°F) | Rain Recorded by NOAA (inches)
3036943474 | KJ32732 | 01/01/2023 | 99.9 | 12.4 | 79 | 58 | 0.04 |  |  |  | 0.12412
3036943474 | KJ32732 | 01/02/2023 | 99.45 | 12.35 | 78 | 53 | 0 |  |  |  | 0.12418
3036943474 | KJ32732 | 01/03/2023 | 94.58 | 11.77 | 81 | 51 | 0 |  |  |  | 0.12444
3036943474 | KJ32732 | 01/04/2023 | 92.19 | 11.48 | 83 | 57 | 0 |  |  |  | 0.12453
3036943474 | KJ32732 | 01/05/2023 | 93.34 | 11.62 | 77 | 46 | 0.04 |  |  |  | 0.12449
3036943474 | KJ32732 | 01/06/2023 | 94.08 | 11.71 | 68 | 41 | 0 |  |  |  | 0.12447
3036943474 | KJ32732 | 01/07/2023 | 98.04 | 12.18 | 70 | 38 | 0 |  |  |  | 0.12424
3036943474 | KJ32732 | 01/08/2023 | 121.02 | 14.94 | 76 | 42 | 0 |  |  |  | 0.12345
3036943474 | KJ32732 | 01/09/2023 | 97.04 | 12.06 | 74 | 47 | 0 |  |  |  | 0.12428
3036943474 | KJ32732 | 01/10/2023 | 95.73 | 12.34 | 71 | 42 | 0 |  |  |  | 0.1289
3036943474 | KJ32732 | 01/11/2023 | 96.27 | 12.4 | 73 | 38 | 0 |  |  |  | 0.1288
3036943474 | KJ32732 | 01/12/2023 | 94.09 | 12.13 | 80 | 44 | 0 |  |  |  | 0.12892
3036943474 | KJ32732 | 01/13/2023 | 95.57 | 12.31 | 71 | 35 | 0.12 |  |  |  | 0.12881
3036943474 | KJ32732 | 01/14/2023 | 100.84 | 12.97 | 61 | 30 | 0 |  |  |  | 0.12862
3036943474 | KJ32732 | 01/15/2023 | 99.46 | 12.8 | 63 | 30 | 0 |  |  |  | 0.12869
3036943474 | KJ32732 | 01/16/2023 | 96.23 | 12.4 | 71 | 30 | 0 |  |  |  | 0.12886
3036943474 | KJ32732 | 01/17/2023 | 91.92 | 11.86 | 75 | 34 | 0 |  |  |  | 0.12903
3036943474 | KJ32732 | 01/18/2023 | 88.6 | 11.45 | 79 | 46 | N/A |  |  |  | 0.12923
3036943474 | KJ32732 | 01/19/2023 | 86.52 | 11.19 | 82 | 54 | 0 |  |  |  | 0.12933
3036943474 | KJ32732 | 01/20/2023 | 85.6 | 11.07 | 76 | 49 | 0 |  |  |  | 0.12932
3036943474 | KJ32732 | 01/21/2023 | 93.46 | 12.05 | 76 | 47 | T |  |  |  | 0.12893
3036943474 | KJ32732 | 01/22/2023 | 106.52 | 13.68 | 82 | 54 | 0.33 |  |  |  | 0.12843
3036943474 | KJ32732 | 01/23/2023 | 99.44 | 12.8 | 75 | 44 | 0.05 |  |  |  | 0.12872
3036943474 | KJ32732 | 01/24/2023 | 95.46 | 12.3 | 76 | 41 | 0 |  |  |  | 0.12885
3036943474 | KJ32732 | 01/25/2023 | 90.81 | 11.72 | 85 | 43 | 0 |  |  |  | 0.12906
3036943474 | KJ32732 | 01/26/2023 | 92.14 | 11.89 | 72 | 38 | 0.09 |  |  |  | 0.12904
3036943474 | KJ32732 | 01/27/2023 | 92.65 | 11.95 | 62 | 37 | 0 |  |  |  | 0.12898
3036943474 | KJ32732 | 01/28/2023 | 92.6 | 11.95 | 69 | 35 | 0 |  |  |  | 0.12905
3036943474 | KJ32732 | 01/29/2023 | 94.4 | 12.17 | 78 | 55 | 0 |  |  |  | 0.12892
3036943474 | KJ32732 | 01/30/2023 | 89.22 | 11.52 | 86 | 58 | 0 |  | kWh/day | $/day | 0.12912
3036943474 | KJ32732 | 01/31/2023 | 87.76 | 11.34 | 83 | 59 | 0 | Example Dry Month Daily Averages: | 95.3203 | 12.1548 | 0.12922
3036943474 | KJ32732 | 02/01/2023 | 87.26 | 11.28 | 82 | 58 | 0 |  |  |  | 0.12927
3036943474 | KJ32732 | 02/02/2023 | 85.48 | 11.06 | 82 | 57 | 0 |  |  |  | 0.12939
3036943474 | KJ32732 | 02/03/2023 | 94.76 | 12.21 | 78 | 50 | 0 |  |  |  | 0.12885
3036943474 | KJ32732 | 02/04/2023 | 96.34 | 12.41 | 70 | 47 | 0.17 |  |  |  | 0.12881
3036943474 | KJ32732 | 02/05/2023 | 96 | 12.37 | 73 | 48 | 0 |  |  |  | 0.12885
3036943474 | KJ32732 | 02/06/2023 | 95.39 | 12.29 | 71 | 46 | 0.01 |  |  |  | 0.12884
3036943474 | KJ32732 | 02/07/2023 | 108.02 | 13.86 | 76 | 44 |  |  |  |  | 0.12831
3036943474 | KJ32732 | 02/08/2023 | 86.95 | 11.24 | 79 | 49 | 0 |  |  |  | 0.12927
3036943474 | KJ32732 | 02/09/2023 | 84.62 | 10.97 | 83 | 58 | 0 |  |  |  | 0.12964
3036943474 | KJ32732 | 02/10/2023 | 83.99 | 10.89 | 85 | 46 | 0.16 |  |  |  | 0.12966
3036943474 | KJ32732 | 02/11/2023 | 87.25 | 11.29 | 79 | 40 | 0.57 |  |  |  | 0.1294
3036943474 | KJ32732 | 02/12/2023 | 96.69 | 12.47 | 71 | 40 | 0.12 |  |  |  | 0.12897
3036943474 | KJ32732 | 02/13/2023 | 87.66 | 11.35 | 71 | 40 | Trace Value |  |  |  | 0.12948
3036943474 | KJ32732 | 02/14/2023 | 86.77 | 11.23 | 75 | 39 | 0 |  |  |  | 0.12942
3036943474 | KJ32732 | 02/15/2023 | 84.14 | 10.91 | 82 | 50 | 0 |  |  |  | 0.12966
3036943474 | KJ32732 | 02/16/2023 | 84.16 | 10.91 | 85 | 57 | 0 |  |  |  | 0.12963
3036943474 | KJ32732 | 02/17/2023 | 84.3 | 10.93 | 89 | 45 |  |  |  |  | 0.12966
3036943474 | KJ32732 | 02/18/2023 | 79.82 | 10.37 | 67 | 46 | 0.04 |  |  |  | 0.12992
3036943474 | KJ32732 | 02/19/2023 | 80.91 | 10.51 | 80 | 48 | 0 |  |  |  | 0.1299
3036943474 | KJ32732 | 02/20/2023 | 80.44 | 10.45 | 82 | 53 | 0 |  |  |  | 0.12991
3036943474 | KJ32732 | 02/21/2023 | 84.61 | 10.97 | 85 | 57 | 0 |  |  |  | 0.12965
3036943474 | KJ32732 | 02/22/2023 | 84.64 | 10.97 | 87 | 58 | 0 |  |  |  | 0.12961
3036943474 | KJ32732 | 02/23/2023 | 87.14 | 11.28 | 89 | 60 | 0 |  |  |  | 0.12945
3036943474 | KJ32732 | 02/24/2023 | 86.86 | 11.25 | 87 | 58 | 0 |  |  |  | 0.12952
3036943474 | KJ32732 | 02/25/2023 | 88.51 | 11.45 | 87 | 58 |  |  |  |  | 0.12936
3036943474 | KJ32732 | 02/26/2023 | 92.52 | 11.95 | 87 | 56 | 0 |  |  |  | 0.12916
3036943474 | KJ32732 | 02/27/2023 | 84.23 | 10.92 | 87 | 57 | 0 |  | kWh/day | $/day | 0.12965
3036943474 | KJ32732 | 02/28/2023 | 87.47 | 11.32 | 87 | 57 | 0 | Month Daily Averages: | 88.1046 | 11.3968 | 0.12942
3036943474 | KJ32732 | 03/01/2023 | 86.37 | 11.18 | 86 | 58 | 0 |  |  |  | 0.12944
3036943474 | KJ32732 | 03/02/2023 | 85.34 | 11.06 | 87 | 56 | 0 |  |  |  | 0.1296
3036943474 | KJ32732 | 03/03/2023 | 83.52 | 10.83 | 90 | 55 | 0 |  |  |  | 0.12967
3036943474 | KJ32732 | 03/04/2023 | 90.2 | 11.66 | 88 | 52 | 0 |  |  |  | 0.12927
3036943474 | KJ32732 | 03/05/2023 | 95.65 | 12.34 | 81 | 54 | 0.05 |  |  |  | 0.12901
3036943474 | KJ32732 | 03/06/2023 | 87.32 | 11.3 | 84 | 56 | 0 |  |  |  | 0.12941
3036943474 | KJ32732 | 03/07/2023 | 90.02 | 11.64 | 87 | 56 |  |  |  |  | 0.1293
3036943474 | KJ32732 | 03/08/2023 | 107.94 | 13.87 | 85 | 58 | 0 |  |  |  | 0.1285
3036943474 | KJ32732 | 03/09/2023 | 89.38 | 11.56 | 80 | 51 | 0 |  |  |  | 0.12934
3036943474 | KJ32732 | 03/10/2023 | 92.2 | 13.13 | 85 | 54 |  |  |  |  | 0.14241
3036943474 | KJ32732 | 03/11/2023 | 94.85 | 13.5 | 81 | 51 | 1.3 |  |  |  | 0.14233
3036943474 | KJ32732 | 03/12/2023 | 89.43 | 12.75 | 86 | 48 | 0 |  |  |  | 0.14257
3036943474 | KJ32732 | 03/13/2023 | 127.76 | 18.03 | 81 | 46 | 1.17 |  |  |  | 0.14112
3036943474 | KJ32732 | 03/14/2023 | 122.77 | 17.34 | 70 | 43 | 0.6 |  |  |  | 0.14124
3036943474 | KJ32732 | 03/15/2023 | 113.73 | 16.1 | 68 | 43 | 0 |  |  |  | 0.14156
3036943474 | KJ32732 | 03/16/2023 | 120.41 | 17.01 | 77 | 37 | 0 |  |  |  | 0.14127
3036943474 | KJ32732 | 03/17/2023 | 113.94 | 16.12 | 84 | 48 |  |  |  |  | 0.14148
3036943474 | KJ32732 | 03/18/2023 | 109.34 | 15.49 | 80 | 45 | 0 |  |  |  | 0.14167
3036943474 | KJ32732 | 03/19/2023 | 109.22 | 15.47 | 68 | 43 | 0.02 |  |  |  | 0.14164
3036943474 | KJ32732 | 03/20/2023 | 96.66 | 13.75 | 69 | 42 | 0.02 |  |  |  | 0.14225
3036943474 | KJ32732 | 03/21/2023 | 92.49 | 13.17 | 77 | 42 | 0 |  |  |  | 0.14239
3036943474 | KJ32732 | 03/22/2023 | 90.43 | 12.89 | 80 | 53 | 0.08 |  |  |  | 0.14254
3036943474 | KJ32732 | 03/23/2023 | 87.98 | 12.55 | 83 | 53 |  |  |  |  | 0.14265
3036943474 | KJ32732 | 03/24/2023 | 87.67 | 12.51 | 86 | 53 | 0 |  |  |  | 0.14269
3036943474 | KJ32732 | 03/25/2023 | 88.17 | 12.58 | 91 | 60 | 0 |  |  |  | 0.14268
3036943474 | KJ32732 | 03/26/2023 | 93.25 | 13.28 | 91 | 63 | 0.68 |  |  |  | 0.14241
3036943474 | KJ32732 | 03/27/2023 | 84.7 | 12.1 | 92 | 62 | 0 |  |  |  | 0.14286
3036943474 | KJ32732 | 03/28/2023 | 88.8 | 12.67 | 88 | 55 | Trace Value |  |  |  | 0.14268
3036943474 | KJ32732 | 03/29/2023 | 90.03 | 12.83 | 75 | 55 | 0 |  |  |  | 0.14251
3036943474 | KJ32732 | 03/30/2023 | 87.43 | 12.48 | 79 | 51 | 0 |  | kWh/day | $/day | 0.14274
3036943474 | KJ32732 | 03/31/2023 | 83.84 | 11.98 | 85 | 55 | 0 | Month Daily Averages: | 96.1561 | 13.3281 | 0.14289
3036943474 | KJ32732 | 04/01/2023 | 83.26 | 11.9 | 90 | 60 | 0 |  |  |  | 0.14293
3036943474 | KJ32732 | 04/02/2023 | 88 | 12.56 | 85 | 60 |  |  |  |  | 0.14273
3036943474 | KJ32732 | 04/03/2023 | 81.2 | 11.62 | 86 | 61 | 0 |  |  |  | 0.1431
3036943474 | KJ32732 | 04/04/2023 | 81.77 | 11.7 | 88 | 60 | Trace Value |  |  |  | 0.14308
3036943474 | KJ32732 | 04/05/2023 | 80.2 | 11.48 | 87 | 63 | 0 |  |  |  | 0.14314
3036943474 | KJ32732 | 04/06/2023 | 78.48 | 11.25 | 87 | 64 | 0 |  |  |  | 0.14335
3036943474 | KJ32732 | 04/07/2023 | 81.7 | 11.69 | 85 | 64 |  |  |  |  | 0.14308
3036943474 | KJ32732 | 04/08/2023 | 82.72 | 11.83 | 86 | 62 |  |  |  |  | 0.14301
3036943474 | KJ32732 | 04/09/2023 | 106.37 | 15.08 | 80 | 60 | 0.01 |  |  |  | 0.14177
3036943474 | KJ32732 | 04/10/2023 | 105.56 | 14.97 | 79 | 58 | 0.68 |  |  |  | 0.14182
3036943474 | KJ32732 | 04/11/2023 | 109.35 | 15.07 | 78 | 58 | 1.38 |  |  |  | 0.13781
3036943474 | KJ32732 | 04/12/2023 | 100.79 | 13.93 | 79 | 59 | 0.03 |  |  |  | 0.13821
3036943474 | KJ32732 | 04/13/2023 | 138.83 | 19 | 87 | 61 | 0.07 |  |  |  | 0.13686
3036943474 | KJ32732 | 04/14/2023 | 186.5 | 25.36 | 86 | 59 | 0.57 |  |  |  | 0.13598
3036943474 | KJ32732 | 04/15/2023 | 158.74 | 21.66 | 87 | 60 | 0.02 |  |  |  | 0.13645
3036943474 | KJ32732 | 04/16/2023 | 141.46 | 19.35 | 88 | 59 | 0 |  |  |  | 0.13679
3036943474 | KJ32732 | 04/17/2023 | 127.33 | 17.47 | 81 | 50 | 0.04 |  |  |  | 0.1372
3036943474 | KJ32732 | 04/18/2023 | 123.12 | 16.91 | 81 | 46 | 0.02 |  |  |  | 0.13735
3036943474 | KJ32732 | 04/19/2023 | 119.44 | 16.42 | 82 | 50 | 0 |  |  |  | 0.13747
3036943474 | KJ32732 | 04/20/2023 | 112.56 | 15.5 | 84 | 55 | 0 |  |  |  | 0.1377
3036943474 | KJ32732 | 04/21/2023 | 110.85 | 15.27 | 87 | 59 |  |  |  |  | 0.13775
3036943474 | KJ32732 | 04/22/2023 | 108.97 | 15.02 | 89 | 57 | 0.3 |  |  |  | 0.13784
3036943474 | KJ32732 | 04/23/2023 | 116.02 | 15.96 | 84 | 53 | 0.42 |  |  |  | 0.13756
3036943474 | KJ32732 | 04/24/2023 | 120.33 | 16.53 | 80 | 55 | 0 |  |  |  | 0.13737
3036943474 | KJ32732 | 04/25/2023 | 124.91 | 17.14 | 82 | 61 | 0.25 |  |  |  | 0.13722
3036943474 | KJ32732 | 04/26/2023 | 125.56 | 17.23 | 84 | 62 | 0.07 |  |  |  | 0.13723
3036943474 | KJ32732 | 04/27/2023 | 141.63 | 19.37 | 86 | 63 | 0 |  |  |  | 0.13676
3036943474 | KJ32732 | 04/28/2023 | 197.24 | 26.79 | 87 | 62 | 1.62 |  |  |  | 0.13582
3036943474 | KJ32732 | 04/29/2023 | 162.32 | 22.13 | 88 | 62 | 0 |  | kWh/day | $/day | 0.13634
3036943474 | KJ32732 | 04/30/2023 | 162.69 | 22.18 | 85 | 57 | 0.52 | Month Daily Averages: | 118.5967 | 16.4123 | 0.13633
3036943474 | KJ32732 | 05/01/2023 | 144.02 | 19.69 | 85 | 56 | 0 |  |  |  | 0.13672
3036943474 | KJ32732 | 05/02/2023 | 132.84 | 18.2 | 87 | 56 | 0 |  |  |  | 0.13701
3036943474 | KJ32732 | 05/03/2023 | 125.82 | 17.27 | 86 | 53 | 0 |  |  |  | 0.13726
3036943474 | KJ32732 | 05/04/2023 | 124.92 | 17.15 | 84 | 53 | 0 |  |  |  | 0.13729
3036943474 | KJ32732 | 05/05/2023 | 122.66 | 16.84 | 87 | 57 | 0 |  |  |  | 0.13729
3036943474 | KJ32732 | 05/06/2023 | 115.95 | 15.95 | 86 | 65 | 0 |  |  |  | 0.13756
3036943474 | KJ32732 | 05/07/2023 | 114.55 | 15.76 | 88 | 61 | 0.02 |  |  |  | 0.13758
3036943474 | KJ32732 | 05/08/2023 | 129.02 | 17.69 | 87 | 55 | 0 |  |  |  | 0.13711
3036943474 | KJ32732 | 05/09/2023 | 104.89 | 14.48 | 91 | 63 | 0 |  |  |  | 0.13805
3036943474 | KJ32732 | 05/10/2023 | 101.38 | 13.97 | 92 | 66 | 0 |  |  |  | 0.1378
3036943474 | KJ32732 | 05/11/2023 | 97.84 | 13.5 | 88 | 67 | 0.04 |  |  |  | 0.13798
3036943474 | KJ32732 | 05/12/2023 | 100.94 | 13.92 | 86 | 66 | 0 |  |  |  | 0.1379
3036943474 | KJ32732 | 05/13/2023 | 103.45 | 14.25 | 85 | 64 | 0 |  |  |  | 0.13775
3036943474 | KJ32732 | 05/14/2023 | 96.88 | 13.38 | 86 | 63 | 0 |  |  |  | 0.13811
3036943474 | KJ32732 | 05/15/2023 | 94.33 | 13.04 | 89 | 62 | 0 |  |  |  | 0.13824
3036943474 | KJ32732 | 05/16/2023 | 88.21 | 12.22 | 88 | 64 | 0 |  |  |  | 0.13853
3036943474 | KJ32732 | 05/17/2023 | 84.67 | 11.75 | 92 | 67 | 0 |  |  |  | 0.13877
3036943474 | KJ32732 | 05/18/2023 | 83.77 | 11.63 | 89 | 65 | 1.24 |  |  |  | 0.13883
3036943474 | KJ32732 | 05/19/2023 | 81.54 | 11.33 | 88 | 66 | 0.02 |  |  |  | 0.13895
3036943474 | KJ32732 | 05/20/2023 | 82.21 | 11.42 | 88 | 66 | 0 |  |  |  | 0.13891
3036943474 | KJ32732 | 05/21/2023 | 83.21 | 11.56 | 88 | 67 |  |  |  |  | 0.13893
3036943474 | KJ32732 | 05/22/2023 | 103.91 | 14.31 | 88 | 67 | 0.65 |  |  |  | 0.13772
3036943474 | KJ32732 | 05/23/2023 | 131.41 | 17.97 | 85 | 67 | 0.56 |  |  |  | 0.13675
3036943474 | KJ32732 | 05/24/2023 | 131.06 | 17.93 | 83 | 66 | 0.12 |  |  |  | 0.13681
3036943474 | KJ32732 | 05/25/2023 | 115.24 | 15.82 | 83 | 66 | 0.16 |  |  |  | 0.13728
3036943474 | KJ32732 | 05/26/2023 | 111.34 | 15.3 | 82 | 62 | 0.05 |  |  |  | 0.13742
3036943474 | KJ32732 | 05/27/2023 | 109.89 | 15.11 | 81 | 56 | Trace Value |  |  |  | 0.1375
3036943474 | KJ32732 | 05/28/2023 | 109.61 | 15.07 | 85 | 55 | 0 |  |  |  | 0.13749
3036943474 | KJ32732 | 05/29/2023 | 103.43 | 14.25 | 87 | 60 | 0 |  |  |  | 0.13777
3036943474 | KJ32732 | 05/30/2023 | 100.74 | 13.89 | 88 | 62 | 0 |  | kWh/day | $/day | 0.13788
3036943474 | KJ32732 | 05/31/2023 | 97.65 | 13.48 | 87 | 68 | 0 | Month Daily Averages: | 107.3348 | 14.7784 | 0.13804
3036943474 | KJ32732 | 06/01/2023 | 94.63 | 13.08 | 85 | 68 | 0 |  |  |  | 0.13822
3036943474 | KJ32732 | 06/02/2023 | 92.78 | 12.83 | 85 | 67 | 0 |  |  |  | 0.13828
3036943474 | KJ32732 | 06/03/2023 | 95.72 | 13.22 | 84 | 67 | 0 |  |  |  | 0.13811
3036943474 | KJ32732 | 06/04/2023 | 98.58 | 13.6 | 84 | 66 | 0 |  |  |  | 0.13796
3036943474 | KJ32732 | 06/05/2023 | 86.76 | 12.03 | 84 | 64 | 0.3 |  |  |  | 0.13866
3036943474 | KJ32732 | 06/06/2023 | 87.94 | 12.19 | 88 | 62 |  |  |  |  | 0.13862
3036943474 | KJ32732 | 06/07/2023 | 124.73 | 17.08 | 91 | 68 | 0 |  |  |  | 0.13694
3036943474 | KJ32732 | 06/08/2023 | 96.99 | 13.39 | 92 | 68 | 1.64 |  |  |  | 0.13806
3036943474 | KJ32732 | 06/09/2023 | 98.73 | 13.22 | 92 | 68 | 0 |  |  |  | 0.1339
3036943474 | KJ32732 | 06/10/2023 | 100.35 | 13.43 | 88 | 67 | 0.54 |  |  |  | 0.13383
3036943474 | KJ32732 | 06/11/2023 | 104.67 | 13.99 | 91 | 69 | 0.09 |  |  |  | 0.13366
3036943474 | KJ32732 | 06/12/2023 | 102.99 | 13.77 | 94 | 69 | 0 |  |  |  | 0.1337
3036943474 | KJ32732 | 06/13/2023 | 97.41 | 13.05 | 95 | 71 |  |  |  |  | 0.13397
3036943474 | KJ32732 | 06/14/2023 | 92.8 | 12.45 | 95 | 71 | 0 |  |  |  | 0.13416
3036943474 | KJ32732 | 06/15/2023 | 99.19 | 13.28 | 95 | 66 | 0.44 |  |  |  | 0.13388
3036943474 | KJ32732 | 06/16/2023 | 114.42 | 15.25 | 95 | 68 | 0.45 |  |  |  | 0.13328
3036943474 | KJ32732 | 06/17/2023 | 131.94 | 17.51 | 93 | 68 | 0.91 |  |  |  | 0.13271
3036943474 | KJ32732 | 06/18/2023 | 146.34 | 19.37 | 94 | 68 | 0.28 |  |  |  | 0.13236
3036943474 | KJ32732 | 06/19/2023 | 161.42 | 21.32 | 93 | 70 | 0.63 |  |  |  | 0.13208
3036943474 | KJ32732 | 06/20/2023 | 185.92 | 24.49 | 91 | 69 | 0.46 |  |  |  | 0.13172
3036943474 | KJ32732 | 06/21/2023 | 146.5 | 19.39 | 91 | 71 | 0.24 |  |  |  | 0.13235
3036943474 | KJ32732 | 06/22/2023 | 136.39 | 18.09 | 93 | 66 | 0.04 |  |  |  | 0.13263
3036943474 | KJ32732 | 06/23/2023 | 145.21 | 19.23 | 91 | 69 | 0.35 |  |  |  | 0.13243
3036943474 | KJ32732 | 06/24/2023 | 139.38 | 18.47 | 92 | 70 | 0.24 |  |  |  | 0.13252
3036943474 | KJ32732 | 06/25/2023 | 131.47 | 17.45 | 91 | 70 | 0.15 |  |  |  | 0.13273
3036943474 | KJ32732 | 06/26/2023 | 114.76 | 15.29 | 94 | 70 | 0 |  |  |  | 0.13323
3036943474 | KJ32732 | 06/27/2023 | 110.88 | 14.79 | 97 | 71 | 0 |  |  |  | 0.13339
3036943474 | KJ32732 | 06/28/2023 | 106.54 | 14.23 | 95 | 72 | 0 |  |  |  | 0.13356
3036943474 | KJ32732 | 06/29/2023 | 102.35 | 13.69 | 95 | 71 | 0.88 |  | kWh/day | $/day | 0.13376
3036943474 | KJ32732 | 06/30/2023 | 99.32 | 13.3 | 94 | 71 | 0 | Month Daily Averages: | 114.9037 | 15.416 | 0.13391
3036943474 | KJ32732 | 07/01/2023 | 98.91 | 13.24 | 94 | 71 | 0 |  |  |  | 0.13386
3036943474 | KJ32732 | 07/02/2023 | 97.62 | 13.08 | 95 | 71 | 0 |  |  |  | 0.13399
3036943474 | KJ32732 | 07/03/2023 | 88.91 | 11.95 | 97 | 72 | 0 |  |  |  | 0.13441
3036943474 | KJ32732 | 07/04/2023 | 95.38 | 12.79 | 95 | 73 | 0 |  |  |  | 0.1341
3036943474 | KJ32732 | 07/05/2023 | 95.06 | 12.75 | 95 | 74 | 0 |  |  |  | 0.13413
3036943474 | KJ32732 | 07/06/2023 | 94.53 | 12.68 | 96 | 73 | 0.04 |  |  |  | 0.13414
3036943474 | KJ32732 | 07/07/2023 | 93.68 | 12.57 | 95 | 73 | 0.03 |  |  |  | 0.13418
3036943474 | KJ32732 | 07/08/2023 | 92.82 | 12.46 | 94 | 74 | 0.31 |  |  |  | 0.13424
3036943474 | KJ32732 | 07/09/2023 | 115.54 | 15.39 | 96 | 74 | 0.2 |  |  |  | 0.1332
3036943474 | KJ32732 | 07/10/2023 | 88.59 | 11.91 | 96 | 74 | 0 |  |  |  | 0.13444
3036943474 | KJ32732 | 07/11/2023 | 93.67 | 12.59 | 94 | 73 | 0.78 |  |  |  | 0.13441
3036943474 | KJ32732 | 07/12/2023 | 98.76 | 13.25 | 94 | 73 | 0.1 |  |  |  | 0.13416
3036943474 | KJ32732 | 07/13/2023 | 92.63 | 12.46 | 94 | 72 | Trace Value |  |  |  | 0.13451
3036943474 | KJ32732 | 07/14/2023 | 98.21 | 13.18 | 95 | 73 | 0.33 |  |  |  | 0.1342
3036943474 | KJ32732 | 07/15/2023 | 109.69 | 14.66 | 96 | 73 | 0.12 |  |  |  | 0.13365
3036943474 | KJ32732 | 07/16/2023 | 113.57 | 15.16 | 96 | 74 | 0.15 |  |  |  | 0.13349
3036943474 | KJ32732 | 07/17/2023 | 107.39 | 14.37 | 95 | 74 | 2.8 |  |  |  | 0.13381
3036943474 | KJ32732 | 07/18/2023 | 104.17 | 13.95 | 95 | 72 | 0.22 |  |  |  | 0.13392
3036943474 | KJ32732 | 07/19/2023 | 102.28 | 13.7 | 95 | 71 | 0.14 |  |  |  | 0.13395
3036943474 | KJ32732 | 07/20/2023 | 93.98 | 12.63 | 96 | 73 | 0 |  |  |  | 0.13439
3036943474 | KJ32732 | 07/21/2023 | 88.6 | 11.94 | 99 | 74 | 0 |  |  |  | 0.13476
3036943474 | KJ32732 | 07/22/2023 | 106.33 | 14.23 | 97 | 75 | 0 |  |  |  | 0.13383
3036943474 | KJ32732 | 07/23/2023 | 135.17 | 17.95 | 94 | 71 | 0.7 |  |  |  | 0.1328
3036943474 | KJ32732 | 07/24/2023 | 128.06 | 17.04 | 93 | 73 | 1.12 |  |  |  | 0.13306
3036943474 | KJ32732 | 07/25/2023 | 122.92 | 16.37 | 93 | 73 | 0.3 |  |  |  | 0.13318
3036943474 | KJ32732 | 07/26/2023 | 109.11 | 14.59 | 92 | 73 | 0 |  |  |  | 0.13372
3036943474 | KJ32732 | 07/27/2023 | 109.25 | 14.61 | 91 | 73 | 0 |  |  |  | 0.13373
3036943474 | KJ32732 | 07/28/2023 | 112.5 | 15.03 | 92 | 73 | 1 |  |  |  | 0.1336
3036943474 | KJ32732 | 07/29/2023 | 110.7 | 14.79 | 93 | 73 | 0.05 |  |  |  | 0.1336
3036943474 | KJ32732 | 07/30/2023 | 123.68 | 16.47 | 95 | 74 | Trace Value |  | kWh/day | $/day | 0.13317
3036943474 | KJ32732 | 07/31/2023 | 146.23 | 19.38 | 95 | 71 | 0.74 | Month Daily Averages: | 105.4174 | 14.1023 | 0.13253
3036943474 | KJ32732 | 08/01/2023 | 129.31 | 17.2 | 95 | 71 | 0.08 |  |  |  | 0.13301
3036943474 | KJ32732 | 08/02/2023 | 116.92 | 15.6 | 93 | 74 | 0 |  |  |  | 0.13342
3036943474 | KJ32732 | 08/03/2023 | 112.7 | 15.05 | 91 | 73 | 0 |  |  |  | 0.13354
3036943474 | KJ32732 | 08/04/2023 | 129.18 | 17.18 | 94 | 73 | 0 |  |  |  | 0.13299
3036943474 | KJ32732 | 08/05/2023 | 147.44 | 19.54 | 94 | 73 | 0.17 |  |  |  | 0.13253
3036943474 | KJ32732 | 08/06/2023 | 145.08 | 19.23 | 95 | 74 | 0.66 |  |  |  | 0.13255
3036943474 | KJ32732 | 08/07/2023 | 143.6 | 19.04 | 97 | 75 | 0.03 |  |  |  | 0.13259
3036943474 | KJ32732 | 08/08/2023 | 152.56 | 20.2 | 99 | 75 | 0 |  |  |  | 0.13241
3036943474 | KJ32732 | 08/09/2023 | 122.94 | 16.37 | 99 | 74 | 0 |  |  |  | 0.13315
3036943474 | KJ32732 | 08/10/2023 | 117.56 | 15.66 | 100 | 75 | 0.16 |  |  |  | 0.13321
3036943474 | KJ32732 | 08/11/2023 | 107.54 | 14.36 | 99 | 75 | 0 |  |  |  | 0.13353
3036943474 | KJ32732 | 08/12/2023 | 102.16 | 13.67 | 98 | 76 | 0.25 |  |  |  | 0.13381
3036943474 | KJ32732 | 08/13/2023 | 101.89 | 13.63 | 97 | 74 | 0 |  |  |  | 0.13377
3036943474 | KJ32732 | 08/14/2023 | 94.27 | 12.65 | 97 | 76 | 0 |  |  |  | 0.13419
3036943474 | KJ32732 | 08/15/2023 | 93.86 | 12.59 | 97 | 75 | 0 |  |  |  | 0.13414
3036943474 | KJ32732 | 08/16/2023 | 99.49 | 13.32 | 96 | 73 | 0.09 |  |  |  | 0.13388
3036943474 | KJ32732 | 08/17/2023 | 114.1 | 15.21 | 93 | 72 | 0.36 |  |  |  | 0.1333
3036943474 | KJ32732 | 08/18/2023 | 134.32 | 17.82 | 93 | 73 | 1.09 |  |  |  | 0.13267
3036943474 | KJ32732 | 08/19/2023 | 130.36 | 17.31 | 93 | 72 | 0.69 |  |  |  | 0.13279
3036943474 | KJ32732 | 08/20/2023 | 128.7 | 17.09 | 92 | 75 | 0 |  |  |  | 0.13279
3036943474 | KJ32732 | 08/21/2023 | 108.93 | 14.54 | 92 | 74 | 0 |  |  |  | 0.13348
3036943474 | KJ32732 | 08/22/2023 | 105.34 | 14.08 | 93 | 72 | 0 |  |  |  | 0.13366
3036943474 | KJ32732 | 08/23/2023 | 106.72 | 14.26 | 93 | 74 | 0 |  |  |  | 0.13362
3036943474 | KJ32732 | 08/24/2023 | 97.02 | 13 | 93 | 74 | 0.99 |  |  |  | 0.13399
3036943474 | KJ32732 | 08/25/2023 | 95.97 | 12.87 | 92 | 71 | 0 |  |  |  | 0.1341
3036943474 | KJ32732 | 08/26/2023 | 92.5 | 12.42 | 95 | 73 | 0 |  |  |  | 0.13427
3036943474 | KJ32732 | 08/27/2023 | 94.19 | 12.64 | 95 | 72 |  |  |  |  | 0.1342
3036943474 | KJ32732 | 08/28/2023 | 86.92 | 11.7 | 96 | 74 | Trace Value |  |  |  | 0.13461
3036943474 | KJ32732 | 08/29/2023 | 89.85 | 12.08 | 95 | 74 | 0 |  |  |  | 0.13445
3036943474 | KJ32732 | 08/30/2023 | 100.39 | 13.44 | 94 | 74 | 0.93 |  | kWh/day | $/day | 0.13388
3036943474 | KJ32732 | 08/31/2023 | 98.66 | 13.21 | 94 | 74 | 0.05 | Month Daily Averages: | 112.9184 | 15.0632 | 0.13389
3036943474 | KJ32732 | 09/01/2023 | 99.49 | 13.32 | 92 | 73 | 0 |  |  |  | 0.13388
3036943474 | KJ32732 | 09/02/2023 | 94.3 | 12.65 | 91 | 72 |  |  |  |  | 0.13415
3036943474 | KJ32732 | 09/03/2023 | 93.49 | 12.55 | 92 | 71 | 0.05 |  |  |  | 0.13424
3036943474 | KJ32732 | 09/04/2023 | 92.35 | 12.4 | 90 | 68 | 0 |  |  |  | 0.13427
3036943474 | KJ32732 | 09/05/2023 | 90.45 | 12.15 | 90 | 64 | 0 |  |  |  | 0.13433
3036943474 | KJ32732 | 09/06/2023 | 93.01 | 12.48 | 94 | 69 | 0 |  |  |  | 0.13418
3036943474 | KJ32732 | 09/07/2023 | 89.06 | 11.97 | 95 | 70 |  |  |  |  | 0.1344
3036943474 | KJ32732 | 09/08/2023 | 163.24 | 21.56 | 95 | 69 | 0 |  |  |  | 0.13208
3036943474 | KJ32732 | 09/09/2023 | 133.35 | 17.69 | 94 | 64 | 0.48 |  |  |  | 0.13266
3036943474 | KJ32732 | 09/10/2023 | 124.82 | 16.62 | 93 | 71 | Trace Value |  |  |  | 0.13315
3036943474 | KJ32732 | 09/11/2023 | 118.01 | 15.74 | 92 | 72 | 0 |  |  |  | 0.13338
3036943474 | KJ32732 | 09/12/2023 | 134.31 | 17.85 | 92 | 71 | Trace Value |  |  |  | 0.1329
3036943474 | KJ32732 | 09/13/2023 | 180.96 | 23.88 | 92 | 72 | 0.03 |  |  |  | 0.13196
3036943474 | KJ32732 | 09/14/2023 | 185.97 | 24.53 | 91 | 71 | 0.29 |  |  |  | 0.1319
3036943474 | KJ32732 | 09/15/2023 | 140.97 | 18.71 | 88 | 70 | 0 |  |  |  | 0.13272
3036943474 | KJ32732 | 09/16/2023 | 132.6 | 17.63 | 87 | 69 | 0.54 |  |  |  | 0.13296
3036943474 | KJ32732 | 09/17/2023 | 133.29 | 17.72 | 92 | 70 | 0 |  |  |  | 0.13294
3036943474 | KJ32732 | 09/18/2023 | 117.82 | 15.71 | 89 | 68 | 0.08 |  |  |  | 0.13334
3036943474 | KJ32732 | 09/19/2023 | 112.87 | 15.07 | 88 | 64 | 0 |  |  |  | 0.13352
3036943474 | KJ32732 | 09/20/2023 | 110.11 | 14.72 | 88 | 69 | 0 |  |  |  | 0.13368
3036943474 | KJ32732 | 09/21/2023 | 106.32 | 14.23 | 87 | 68 | 0.08 |  |  |  | 0.13384
3036943474 | KJ32732 | 09/22/2023 | 103.65 | 13.88 | 85 | 65 | 0.3 |  |  |  | 0.13391
3036943474 | KJ32732 | 09/23/2023 | 106.84 | 14.29 | 87 | 61 | 0 |  |  |  | 0.13375
3036943474 | KJ32732 | 09/24/2023 | 108.1 | 14.46 | 89 | 59 | 0 |  |  |  | 0.13377
3036943474 | KJ32732 | 09/25/2023 | 113.09 | 15.1 | 90 | 66 | 0 |  |  |  | 0.13352
3036943474 | KJ32732 | 09/26/2023 | 215.47 | 28.35 | 89 | 71 | 2.11 |  |  |  | 0.13157
3036943474 | KJ32732 | 09/27/2023 | 277.78 | 36.41 | 88 | 71 | 0.91 |  |  |  | 0.13107
3036943474 | KJ32732 | 09/28/2023 | 333.12 | 43.57 | 87 | 71 | 0.81 |  |  |  | 0.13079
3036943474 | KJ32732 | 09/29/2023 | 268.54 | 35.21 | 85 | 71 | 0.02 |  | kWh/day | $/day | 0.13112
3036943474 | KJ32732 | 09/30/2023 | 322.94 | 42.25 | 85 | 71 | 0.2 | Month Daily Averages: | 146.544 | 19.4233 | 0.13083
3036943474 | KJ32732 | 10/01/2023 | 371.66 | 48.56 | 85 | 70 | 2.53 | (Beginning of Wet Months) |  |  | 0.13066
3036943474 | KJ32732 | 10/02/2023 | 294.71 | 38.6 | 85 | 69 | 0.56 |  |  |  | 0.13098
3036943474 | KJ32732 | 10/03/2023 | 274.26 | 35.95 | 85 | 70 | 0 |  |  |  | 0.13108
3036943474 | KJ32732 | 10/04/2023 | 226.07 | 29.72 | 86 | 70 | 0.05 |  |  |  | 0.13146
3036943474 | KJ32732 | 10/05/2023 | 196.23 | 25.86 | 86 | 69 | 0 |  |  |  | 0.13178
3036943474 | KJ32732 | 10/06/2023 | 186.26 | 24.57 | 87 | 66 | 0 |  |  |  | 0.13191
3036943474 | KJ32732 | 10/07/2023 | 176.75 | 23.34 | 90 | 56 | 0 |  |  |  | 0.13205
3036943474 | KJ32732 | 10/08/2023 | 176.08 | 23.25 | 82 | 53 | 0 |  |  |  | 0.13204
3036943474 | KJ32732 | 10/09/2023 | 200.01 | 26.35 | 80 | 55 | 0 |  |  |  | 0.13174
3036943474 | KJ32732 | 10/10/2023 | 157.52 | 20.85 | 84 | 56 | 0 |  |  |  | 0.13236
3036943474 | KJ32732 | 10/11/2023 | 151.88 | 20.15 | 84 | 65 | 0 |  |  |  | 0.13267
3036943474 | KJ32732 | 10/12/2023 | 351.41 | 45.97 | 88 | 72 | 2.8 |  |  |  | 0.13082
3036943474 | KJ32732 | 10/13/2023 | 321.56 | 42.11 | 89 | 68 | 1.67 |  |  |  | 0.13096
3036943474 | KJ32732 | 10/14/2023 | 284.56 | 37.32 | 89 | 64 | 0 |  |  |  | 0.13115
3036943474 | KJ32732 | 10/15/2023 | 248.45 | 32.65 | 82 | 55 | 0 |  |  |  | 0.13141
3036943474 | KJ32732 | 10/16/2023 | 214 | 28.19 | 76 | 50 | 0 |  |  |  | 0.13173
3036943474 | KJ32732 | 10/17/2023 | 201.21 | 26.53 | 75 | 49 | 0 |  |  |  | 0.13185
3036943474 | KJ32732 | 10/18/2023 | 181.21 | 23.94 | 77 | 50 | 0 |  |  |  | 0.13211
3036943474 | KJ32732 | 10/19/2023 | 179.12 | 23.67 | 81 | 55 | 0 |  |  |  | 0.13215
3036943474 | KJ32732 | 10/20/2023 | 170.65 | 22.58 | 83 | 55 | 0 |  |  |  | 0.13232
3036943474 | KJ32732 | 10/21/2023 | 165.21 | 21.87 | 83 | 55 | 0 |  |  |  | 0.13238
3036943474 | KJ32732 | 10/22/2023 | 162.27 | 21.49 | 86 | 52 | 0 |  |  |  | 0.13243
3036943474 | KJ32732 | 10/23/2023 | 150.16 | 19.93 | 83 | 58 | 0 |  |  |  | 0.13273
3036943474 | KJ32732 | 10/24/2023 | 144.68 | 19.22 | 82 | 67 | 0 |  |  |  | 0.13284
3036943474 | KJ32732 | 10/25/2023 | 139.76 | 18.58 | 82 | 68 | 0 |  |  |  | 0.13294
3036943474 | KJ32732 | 10/26/2023 | 127.34 | 16.97 | 82 | 65 | 0 |  |  |  | 0.13327
3036943474 | KJ32732 | 10/27/2023 | 121.67 | 16.24 | 83 | 64 | 0 |  |  |  | 0.13348
3036943474 | KJ32732 | 10/28/2023 | 140.12 | 18.63 | 84 | 62 | 0 |  |  |  | 0.13296
3036943474 | KJ32732 | 10/29/2023 | 137.68 | 18.31 | 84 | 61 | 0 |  |  |  | 0.13299
3036943474 | KJ32732 | 10/30/2023 | 127.52 | 17 | 85 | 60 | 0 |  | kWh/day | $/day | 0.13331
3036943474 | KJ32732 | 10/31/2023 | 125.51 | 16.74 | 84 | 58 | 0 | Month Daily Averages: | 196.9523 | 25.9723 | 0.13338
3036943474 | KJ32732 | 11/01/2023 | 127.93 | 17.05 | 76 | 53 | 0 | (Wet Month) |  |  | 0.13328
3036943474 | KJ32732 | 11/02/2023 | 122.97 | 16.41 | 75 | 53 | 0 |  |  |  | 0.13345
3036943474 | KJ32732 | 11/03/2023 | 120.32 | 16.06 | 79 | 59 | 0 |  |  |  | 0.13348
3036943474 | KJ32732 | 11/04/2023 | 121.84 | 16.26 | 79 | 55 | 0 |  |  |  | 0.13345
3036943474 | KJ32732 | 11/05/2023 | 127.85 | 17.04 | 80 | 51 | 0 |  |  |  | 0.13328
3036943474 | KJ32732 | 11/06/2023 | 115.21 | 15.4 | 81 | 48 | 0 |  |  |  | 0.13367
3036943474 | KJ32732 | 11/07/2023 | 148.62 | 19.73 | 83 | 53 | 0 |  |  |  | 0.13275
3036943474 | KJ32732 | 11/08/2023 | 108.69 | 14.56 | 84 | 50 | 0 |  |  |  | 0.13396
3036943474 | KJ32732 | 11/09/2023 | 116.84 | 15.61 | 85 | 55 | 0 |  |  |  | 0.1336
3036943474 | KJ32732 | 11/10/2023 | 110.09 | 14.74 | 86 | 60 | 0 |  |  |  | 0.13389
3036943474 | KJ32732 | 11/11/2023 | 117.23 | 15.66 | 83 | 65 | 0.33 |  |  |  | 0.13358
3036943474 | KJ32732 | 11/12/2023 | 121.78 | 16.25 | 80 | 63 | 0 |  |  |  | 0.13344
3036943474 | KJ32732 | 11/13/2023 | 113.46 | 15.17 | 77 | 62 | 0 |  |  |  | 0.1337
3036943474 | KJ32732 | 11/14/2023 | 113.82 | 15.22 | 77 | 61 | 0.12 |  |  |  | 0.13372
3036943474 | KJ32732 | 11/15/2023 | 115.73 | 15.47 | 77 | 64 | 0.05 |  |  |  | 0.13367
3036943474 | KJ32732 | 11/16/2023 | 146.12 | 19.4 | 78 | 62 | 0.16 |  |  |  | 0.13277
3036943474 | KJ32732 | 11/17/2023 | 336.31 | 44.01 | 79 | 61 | 2.1 |  |  |  | 0.13086
3036943474 | KJ32732 | 11/18/2023 | 227.18 | 29.89 | 78 | 55 | 0.66 |  |  |  | 0.13157
3036943474 | KJ32732 | 11/19/2023 | 193.23 | 25.49 | 80 | 56 | 0 |  |  |  | 0.13192
3036943474 | KJ32732 | 11/20/2023 | 168.24 | 22.26 | 79 | 59 | 0.02 |  |  |  | 0.13231
3036943474 | KJ32732 | 11/21/2023 | 158.64 | 21.02 | 81 | 52 | 0.02 |  |  |  | 0.1325
3036943474 | KJ32732 | 11/22/2023 | 154.44 | 20.47 | 81 | 47 | 0 |  |  |  | 0.13254
3036943474 | KJ32732 | 11/23/2023 | 157.37 | 20.85 | 73 | 48 | 0.01 |  |  |  | 0.13249
3036943474 | KJ32732 | 11/24/2023 | 146.92 | 19.5 | 75 | 52 | 0.01 |  |  |  | 0.13273
3036943474 | KJ32732 | 11/25/2023 | 144.94 | 19.25 | 75 | 53 | 0.07 |  |  |  | 0.13281
3036943474 | KJ32732 | 11/26/2023 | 165.86 | 21.95 | 75 | 55 | 0.01 |  |  |  | 0.13234
3036943474 | KJ32732 | 11/27/2023 | 157.47 | 20.87 | 74 | 44 | 0.55 |  |  |  | 0.13253
3036943474 | KJ32732 | 11/28/2023 | 151.42 | 20.08 | 69 | 39 | 0 |  |  |  | 0.13261
3036943474 | KJ32732 | 11/29/2023 | 138.95 | 18.47 | 68 | 36 | 0 |  | kWh/day | $/day | 0.13293
3036943474 | KJ32732 | 11/30/2023 | 136.77 | 18.19 | 86 | 41 | 0 | Month Daily Averages: | 146.208 | 19.411 | 0.133
3036943474 | KJ32732 | 12/01/2023 | 126.28 | 16.83 | 82 | 55 | 0 | (Wet Month) |  |  | 0.13328
3036943474 | KJ32732 | 12/02/2023 | 129.58 | 17.26 | 83 | 64 | 0 |  |  |  | 0.1332
3036943474 | KJ32732 | 12/03/2023 | 142.53 | 18.93 | 82 | 62 | 0.02 |  |  |  | 0.13281
3036943474 | KJ32732 | 12/04/2023 | 124.51 | 16.6 | 79 | 51 | 0.23 |  |  |  | 0.13332
3036943474 | KJ32732 | 12/05/2023 | 114.31 | 15.28 | 72 | 47 | 0 |  |  |  | 0.13367
3036943474 | KJ32732 | 12/06/2023 | 134.85 | 17.94 | 69 | 41 | 0 |  |  |  | 0.13304
3036943474 | KJ32732 | 12/07/2023 | 108.35 | 14.51 | 67 | 41 | 0 |  |  |  | 0.13392
3036943474 | KJ32732 | 12/08/2023 | 102.27 | 13.56 | 74 | 47 | 0 |  |  |  | 0.13259
3036943474 | KJ32732 | 12/09/2023 | 99.95 | 13.26 | 82 | 56 | 0.04 |  |  |  | 0.13267
3036943474 | KJ32732 | 12/10/2023 | 103.89 | 13.77 | 83 | 44 | 0 |  |  |  | 0.13254
3036943474 | KJ32732 | 12/11/2023 | 101.32 | 13.44 | 67 | 43 | 0.25 |  |  |  | 0.13265
3036943474 | KJ32732 | 12/12/2023 | 103.4 | 13.7 | 71 | 43 | 0 |  |  |  | 0.1325
3036943474 | KJ32732 | 12/13/2023 | 94.93 | 12.62 | 73 | 58 | 0 |  |  |  | 0.13294
3036943474 | KJ32732 | 12/14/2023 | 111.67 | 14.76 | 72 | 59 | 0.66 |  |  |  | 0.13218
3036943474 | KJ32732 | 12/15/2023 | 104.28 | 13.82 | 72 | 60 | 0.07 |  |  |  | 0.13253
3036943474 | KJ32732 | 12/16/2023 | 116.62 | 15.4 | 73 | 58 | 0.11 |  |  |  | 0.13205
3036943474 | KJ32732 | 12/17/2023 | 275.16 | 35.75 | 74 | 48 | 4.04 |  |  |  | 0.12992
3036943474 | KJ32732 | 12/18/2023 | 234.16 | 30.49 | 68 | 40 | 0.05 |  |  |  | 0.13021
3036943474 | KJ32732 | 12/19/2023 | 180.03 | 23.54 | 65 | 41 | 0 |  |  |  | 0.13076
3036943474 | KJ32732 | 12/20/2023 | 163.65 | 21.44 | 66 | 44 | 0 |  |  |  | 0.13101
3036943474 | KJ32732 | 12/21/2023 | 152.85 | 20.05 | 68 | 46 | 0 |  |  |  | 0.13117
3036943474 | KJ32732 | 12/22/2023 | 147.04 | 19.3 | 70 | 49 | 0 |  |  |  | 0.13126
3036943474 | KJ32732 | 12/23/2023 | 197.58 | 25.79 | 73 | 53 | 0 |  |  |  | 0.13053
3036943474 | KJ32732 | 12/24/2023 | 210.93 | 27.51 | 73 | 53 | 0 |  |  |  | 0.13042
3036943474 | KJ32732 | 12/25/2023 | 142.12 | 18.67 | 73 | 60 | 0.09 |  |  |  | 0.13137
3036943474 | KJ32732 | 12/26/2023 | 140.97 | 18.52 | 74 | 54 | 0.1 |  |  |  | 0.13138
3036943474 | KJ32732 | 12/27/2023 | 130.34 | 17.16 | 71 | 49 | 0 |  |  |  | 0.13166
3036943474 | KJ32732 | 12/28/2023 | 127 | 16.73 | 66 | 44 | 0.04 |  |  |  | 0.13173
3036943474 | KJ32732 | 12/29/2023 | 126.79 | 16.7 | 55 | 46 | 0 |  |  |  | 0.13171
3036943474 | KJ32732 | 12/30/2023 | 121.98 | 16.09 | 59 | 37 | 0 |  | kWh/day | $/day | 0.13191
3036943474 | KJ32732 | 12/31/2023 | 122.26 | 16.12 | 63 | 36 | 0 | Month Daily Averages: | 138.4387 | 18.2432 | 0.13185
|  | Yearly Daily Average: | 122.4197 | 16.334 |  |  |  | (End of Wet Months) |  |  | 0.1337 | Average
|  | Yearly Daily Average (Less Spike Events): | 108.5277 | 14.5394
|  | Spike Event Daily Average: | 212.0086 | 27.9069 |  | Number of Spiked Days: | 49
|  | Dryer Months' Daily Average (Less Spikes): | 102.3178 | 14.0995
|  | Wetter Months' Daily Average (Less Spikes): | 125.404 | 20.7845
|  | Wetter Months' Daily Average: | 157.2105 | 20.7845 |  | Number of Spiked Days: | 122

## MPS-B Compare
Daily Billed Information [PS MPS-B - 21 Florida Park Dr (Comparison Pump): 2023 Reading Data]
Bill Account | Meter Number | Date | Consumption Recorded (kWh/day) | Estimated Cost ($/day) | Avg. High Temperature (°F) | Avg. Low Temperature (°F) | Rain Recorded by NOAA (inches)
0358748192 | KJJ0409 | 01/01/2023 | 251.51 | 25.69 | 79 | 58 | 0.04
0358748192 | KJJ0409 | 01/02/2023 | 258.46 | 26.37 | 78 | 53 | 0
0358748192 | KJJ0409 | 01/03/2023 | 246.5 | 25.19 | 81 | 51 | 0
0358748192 | KJJ0409 | 01/04/2023 | 243.05 | 24.85 | 83 | 57 | 0
0358748192 | KJJ0409 | 01/05/2023 | 239.78 | 24.53 | 77 | 46 | 0.04
0358748192 | KJJ0409 | 01/06/2023 | 241.45 | 24.7 | 68 | 41 | 0
0358748192 | KJJ0409 | 01/07/2023 | 237.17 | 24.27 | 70 | 38 | 0
0358748192 | KJJ0409 | 01/08/2023 | 245.25 | 25.07 | 76 | 42 | 0
0358748192 | KJJ0409 | 01/09/2023 | 233.12 | 23.88 | 74 | 47 | 0
0358748192 | KJJ0409 | 01/10/2023 | 233.93 | 23.95 | 71 | 42 | 0
0358748192 | KJJ0409 | 01/11/2023 | 234.59 | 24.02 | 73 | 38 | 0
0358748192 | KJJ0409 | 01/12/2023 | 233.41 | 23.9 | 80 | 44 | 0
0358748192 | KJJ0409 | 01/13/2023 | 234.71 | 24.03 | 71 | 35 | 0.12
0358748192 | KJJ0409 | 01/14/2023 | 243.71 | 24.92 | 61 | 30 | 0
0358748192 | KJJ0409 | 01/15/2023 | 241.87 | 24.74 | 63 | 30 | 0
0358748192 | KJJ0409 | 01/16/2023 | 243.06 | 24.85 | 71 | 30 | 0
0358748192 | KJJ0409 | 01/17/2023 | 227.99 | 23.37 | 75 | 34 | 0
0358748192 | KJJ0409 | 01/18/2023 | 271.94 | 27.7 | 79 | 46 | N/A
0358748192 | KJJ0409 | 01/19/2023 | 228.64 | 23.43 | 82 | 54 | 0
0358748192 | KJJ0409 | 01/20/2023 | 226.39 | 27.17 | 76 | 49 | 0
0358748192 | KJJ0409 | 01/21/2023 | 271.22 | 32.35 | 76 | 47 | T
0358748192 | KJJ0409 | 01/22/2023 | 331.9 | 39.36 | 82 | 54 | 0.33
0358748192 | KJJ0409 | 01/23/2023 | 282.91 | 33.7 | 75 | 44 | 0.05
0358748192 | KJJ0409 | 01/24/2023 | 269.83 | 32.19 | 76 | 41 | 0
0358748192 | KJJ0409 | 01/25/2023 | 261.12 | 31.19 | 85 | 43 | 0
0358748192 | KJJ0409 | 01/26/2023 | 256.33 | 30.63 | 72 | 38 | 0.09
0358748192 | KJJ0409 | 01/27/2023 | 256.31 | 30.63 | 62 | 37 | 0
0358748192 | KJJ0409 | 01/28/2023 | 252.69 | 30.21 | 69 | 35 | 0
0358748192 | KJJ0409 | 01/29/2023 | 267.58 | 31.93 | 78 | 55 | 0
0358748192 | KJJ0409 | 01/30/2023 | 253.01 | 30.25 | 86 | 58 | 0
0358748192 | KJJ0409 | 01/31/2023 | 247.05 | 29.56 | 83 | 59 | 0
0358748192 | KJJ0409 | 02/01/2023 | 244.78 | 29.3 | 82 | 58 | 0
0358748192 | KJJ0409 | 02/02/2023 | 240.75 | 28.83 | 82 | 57 | 0
0358748192 | KJJ0409 | 02/03/2023 | 251.56 | 30.08 | 78 | 50 | 0
0358748192 | KJJ0409 | 02/04/2023 | 262.47 | 31.34 | 70 | 47 | 0.17
0358748192 | KJJ0409 | 02/05/2023 | 268.41 | 32.03 | 73 | 48 | 0
0358748192 | KJJ0409 | 02/06/2023 | 253.6 | 30.32 | 71 | 46 | 0.01
0358748192 | KJJ0409 | 02/07/2023 | 244.31 | 29.24 | 76 | 44
0358748192 | KJJ0409 | 02/08/2023 | 238.37 | 28.56 | 79 | 49 | 0
0358748192 | KJJ0409 | 02/09/2023 | 238.4 | 28.56 | 83 | 58 | 0
0358748192 | KJJ0409 | 02/10/2023 | 243.99 | 29.21 | 85 | 46 | 0.16
0358748192 | KJJ0409 | 02/11/2023 | 268.32 | 32.02 | 79 | 40 | 0.57
0358748192 | KJJ0409 | 02/12/2023 | 286.49 | 34.12 | 71 | 40 | 0.12
0358748192 | KJJ0409 | 02/13/2023 | 263.8 | 31.5 | 71 | 40 | Trace Value
0358748192 | KJJ0409 | 02/14/2023 | 250.89 | 30 | 75 | 39 | 0
0358748192 | KJJ0409 | 02/15/2023 | 250.23 | 29.93 | 82 | 50 | 0
0358748192 | KJJ0409 | 02/16/2023 | 300.09 | 35.69 | 85 | 57 | 0
0358748192 | KJJ0409 | 02/17/2023 | 249.56 | 29.85 | 89 | 45
0358748192 | KJJ0409 | 02/18/2023 | 252.02 | 29.65 | 67 | 46 | 0.04
0358748192 | KJJ0409 | 02/19/2023 | 253.75 | 29.85 | 80 | 48 | 0
0358748192 | KJJ0409 | 02/20/2023 | 245.79 | 28.94 | 82 | 53 | 0
0358748192 | KJJ0409 | 02/21/2023 | 236.89 | 27.93 | 85 | 57 | 0
0358748192 | KJJ0409 | 02/22/2023 | 234.95 | 27.71 | 87 | 58 | 0
0358748192 | KJJ0409 | 02/23/2023 | 233.9 | 27.59 | 89 | 60 | 0
0358748192 | KJJ0409 | 02/24/2023 | 232.53 | 27.44 | 87 | 58 | 0
0358748192 | KJJ0409 | 02/25/2023 | 240.78 | 28.38 | 87 | 58
0358748192 | KJJ0409 | 02/26/2023 | 248.61 | 29.27 | 87 | 56 | 0
0358748192 | KJJ0409 | 02/27/2023 | 243.47 | 28.68 | 87 | 57 | 0
0358748192 | KJJ0409 | 02/28/2023 | 236.61 | 27.9 | 87 | 57 | 0
0358748192 | KJJ0409 | 03/01/2023 | 227.27 | 26.84 | 86 | 58 | 0
0358748192 | KJJ0409 | 03/02/2023 | 230.25 | 27.18 | 87 | 56 | 0
0358748192 | KJJ0409 | 03/03/2023 | 228.01 | 26.92 | 90 | 55 | 0
0358748192 | KJJ0409 | 03/04/2023 | 244.4 | 28.79 | 88 | 52 | 0
0358748192 | KJJ0409 | 03/05/2023 | 251.77 | 29.62 | 81 | 54 | 0.05
0358748192 | KJJ0409 | 03/06/2023 | 236.07 | 27.84 | 84 | 56 | 0
0358748192 | KJJ0409 | 03/07/2023 | 225.22 | 26.6 | 87 | 56
0358748192 | KJJ0409 | 03/08/2023 | 231.58 | 27.33 | 85 | 58 | 0
0358748192 | KJJ0409 | 03/09/2023 | 228.33 | 26.96 | 80 | 51 | 0
0358748192 | KJJ0409 | 03/10/2023 | 239.31 | 28.21 | 85 | 54
0358748192 | KJJ0409 | 03/11/2023 | 247.61 | 29.15 | 81 | 51 | 1.3
0358748192 | KJJ0409 | 03/12/2023 | 240.48 | 28.34 | 86 | 48 | 0
0358748192 | KJJ0409 | 03/13/2023 | 338.39 | 39.48 | 81 | 46 | 1.17
0358748192 | KJJ0409 | 03/14/2023 | 310.98 | 36.36 | 70 | 43 | 0.6
0358748192 | KJJ0409 | 03/15/2023 | 283.73 | 33.26 | 68 | 43 | 0
0358748192 | KJJ0409 | 03/16/2023 | 277.78 | 32.58 | 77 | 37 | 0
0358748192 | KJJ0409 | 03/17/2023 | 273.92 | 32.14 | 84 | 48
0358748192 | KJJ0409 | 03/18/2023 | 268.69 | 31.55 | 80 | 45 | 0
0358748192 | KJJ0409 | 03/19/2023 | 310.76 | 36.33 | 68 | 43 | 0.02
0358748192 | KJJ0409 | 03/20/2023 | 250.56 | 29.49 | 69 | 42 | 0.02
0358748192 | KJJ0409 | 03/21/2023 | 244.6 | 36.27 | 77 | 42 | 0
0358748192 | KJJ0409 | 03/22/2023 | 247.58 | 36.7 | 80 | 53 | 0.08
0358748192 | KJJ0409 | 03/23/2023 | 247.05 | 36.62 | 83 | 53
0358748192 | KJJ0409 | 03/24/2023 | 244.43 | 36.24 | 86 | 53 | 0
0358748192 | KJJ0409 | 03/25/2023 | 248.77 | 36.87 | 91 | 60 | 0
0358748192 | KJJ0409 | 03/26/2023 | 258.91 | 38.33 | 91 | 63 | 0.68
0358748192 | KJJ0409 | 03/27/2023 | 245.82 | 36.44 | 92 | 62 | 0
0358748192 | KJJ0409 | 03/28/2023 | 250.01 | 37.05 | 88 | 55 | Trace Value
0358748192 | KJJ0409 | 03/29/2023 | 244.39 | 36.24 | 75 | 55 | 0
0358748192 | KJJ0409 | 03/30/2023 | 244.25 | 36.22 | 79 | 51 | 0
0358748192 | KJJ0409 | 03/31/2023 | 244.18 | 36.21 | 85 | 55 | 0
0358748192 | KJJ0409 | 04/01/2023 | 244.13 | 36.2 | 90 | 60 | 0
0358748192 | KJJ0409 | 04/02/2023 | 253.36 | 37.53 | 85 | 60
0358748192 | KJJ0409 | 04/03/2023 | 233.05 | 34.61 | 86 | 61 | 0
0358748192 | KJJ0409 | 04/04/2023 | 228.32 | 33.93 | 88 | 60 | Trace Value
0358748192 | KJJ0409 | 04/05/2023 | 237.65 | 35.27 | 87 | 63 | 0
0358748192 | KJJ0409 | 04/06/2023 | 237.61 | 35.26 | 87 | 64 | 0
0358748192 | KJJ0409 | 04/07/2023 | 238.16 | 35.34 | 85 | 64
0358748192 | KJJ0409 | 04/08/2023 | 250.21 | 37.08 | 86 | 62
0358748192 | KJJ0409 | 04/09/2023 | 252.25 | 37.37 | 80 | 60 | 0.01
0358748192 | KJJ0409 | 04/10/2023 | 316.09 | 46.55 | 79 | 58 | 0.68
0358748192 | KJJ0409 | 04/11/2023 | 300.11 | 44.25 | 78 | 58 | 1.38
0358748192 | KJJ0409 | 04/12/2023 | 274.7 | 40.6 | 79 | 59 | 0.03
0358748192 | KJJ0409 | 04/13/2023 | 354.38 | 52.06 | 87 | 61 | 0.07
0358748192 | KJJ0409 | 04/14/2023 | 390.27 | 57.22 | 86 | 59 | 0.57
0358748192 | KJJ0409 | 04/15/2023 | 357.58 | 52.52 | 87 | 60 | 0.02
0358748192 | KJJ0409 | 04/16/2023 | 329.22 | 48.44 | 88 | 59 | 0
0358748192 | KJJ0409 | 04/17/2023 | 291.92 | 43.07 | 81 | 50 | 0.04
0358748192 | KJJ0409 | 04/18/2023 | 339.76 | 49.96 | 81 | 46 | 0.02
0358748192 | KJJ0409 | 04/19/2023 | 276.31 | 40.83 | 82 | 50 | 0
0358748192 | KJJ0409 | 04/20/2023 | 271.64 | 32.89 | 84 | 55 | 0
0358748192 | KJJ0409 | 04/21/2023 | 267.92 | 32.46 | 87 | 59
0358748192 | KJJ0409 | 04/22/2023 | 272.56 | 33 | 89 | 57 | 0.3
0358748192 | KJJ0409 | 04/23/2023 | 288.63 | 34.88 | 84 | 53 | 0.42
0358748192 | KJJ0409 | 04/24/2023 | 259.59 | 31.48 | 80 | 55 | 0
0358748192 | KJJ0409 | 04/25/2023 | 257.48 | 31.24 | 82 | 61 | 0.25
0358748192 | KJJ0409 | 04/26/2023 | 253.18 | 30.73 | 84 | 62 | 0.07
0358748192 | KJJ0409 | 04/27/2023 | 305.92 | 36.91 | 86 | 63 | 0
0358748192 | KJJ0409 | 04/28/2023 | 367.09 | 44.07 | 87 | 62 | 1.62
0358748192 | KJJ0409 | 04/29/2023 | 330.21 | 39.75 | 88 | 62 | 0
0358748192 | KJJ0409 | 04/30/2023 | 345.43 | 41.53 | 85 | 57 | 0.52
0358748192 | KJJ0409 | 05/01/2023 | 291.7 | 35.24 | 85 | 56 | 0
0358748192 | KJJ0409 | 05/02/2023 | 268.48 | 32.52 | 87 | 56 | 0
0358748192 | KJJ0409 | 05/03/2023 | 267.13 | 32.37 | 86 | 53 | 0
0358748192 | KJJ0409 | 05/04/2023 | 254.55 | 30.89 | 84 | 53 | 0
0358748192 | KJJ0409 | 05/05/2023 | 251.17 | 30.5 | 87 | 57 | 0
0358748192 | KJJ0409 | 05/06/2023 | 255.01 | 30.95 | 86 | 65 | 0
0358748192 | KJJ0409 | 05/07/2023 | 270 | 32.7 | 88 | 61 | 0.02
0358748192 | KJJ0409 | 05/08/2023 | 246.83 | 29.99 | 87 | 55 | 0
0358748192 | KJJ0409 | 05/09/2023 | 245.54 | 29.84 | 91 | 63 | 0
0358748192 | KJJ0409 | 05/10/2023 | 240.71 | 29.27 | 92 | 66 | 0
0358748192 | KJJ0409 | 05/11/2023 | 236.81 | 28.82 | 88 | 67 | 0.04
0358748192 | KJJ0409 | 05/12/2023 | 239.38 | 29.12 | 86 | 66 | 0
0358748192 | KJJ0409 | 05/13/2023 | 244.07 | 29.67 | 85 | 64 | 0
0358748192 | KJJ0409 | 05/14/2023 | 246.22 | 29.92 | 86 | 63 | 0
0358748192 | KJJ0409 | 05/15/2023 | 234.7 | 28.57 | 89 | 62 | 0
0358748192 | KJJ0409 | 05/16/2023 | 232.16 | 28.27 | 88 | 64 | 0
0358748192 | KJJ0409 | 05/17/2023 | 272.03 | 32.94 | 92 | 67 | 0
0358748192 | KJJ0409 | 05/18/2023 | 232.76 | 28.34 | 89 | 65 | 1.24
0358748192 | KJJ0409 | 05/19/2023 | 234.98 | 28.56 | 88 | 66 | 0.02
0358748192 | KJJ0409 | 05/20/2023 | 240.44 | 29.2 | 88 | 66 | 0
0358748192 | KJJ0409 | 05/21/2023 | 248.01 | 30.09 | 88 | 67
0358748192 | KJJ0409 | 05/22/2023 | 315.52 | 37.98 | 88 | 67 | 0.65
0358748192 | KJJ0409 | 05/23/2023 | 314.87 | 37.9 | 85 | 67 | 0.56
0358748192 | KJJ0409 | 05/24/2023 | 342.91 | 41.18 | 83 | 66 | 0.12
0358748192 | KJJ0409 | 05/25/2023 | 299.66 | 36.12 | 83 | 66 | 0.16
0358748192 | KJJ0409 | 05/26/2023 | 288.82 | 34.86 | 82 | 62 | 0.05
0358748192 | KJJ0409 | 05/27/2023 | 286.54 | 34.59 | 81 | 56 | Trace Value
0358748192 | KJJ0409 | 05/28/2023 | 279.84 | 33.81 | 85 | 55 | 0
0358748192 | KJJ0409 | 05/29/2023 | 270.72 | 32.74 | 87 | 60 | 0
0358748192 | KJJ0409 | 05/30/2023 | 256.63 | 31.09 | 88 | 62 | 0
0358748192 | KJJ0409 | 05/31/2023 | 252.36 | 30.6 | 87 | 68 | 0
0358748192 | KJJ0409 | 06/01/2023 | 244.48 | 29.67 | 85 | 68 | 0
0358748192 | KJJ0409 | 06/02/2023 | 241.43 | 29.32 | 85 | 67 | 0
0358748192 | KJJ0409 | 06/03/2023 | 249.19 | 30.22 | 84 | 67 | 0
0358748192 | KJJ0409 | 06/04/2023 | 254.56 | 30.85 | 84 | 66 | 0
0358748192 | KJJ0409 | 06/05/2023 | 238.87 | 29.02 | 84 | 64 | 0.3
0358748192 | KJJ0409 | 06/06/2023 | 241.17 | 29.29 | 88 | 62
0358748192 | KJJ0409 | 06/07/2023 | 293.89 | 35.45 | 91 | 68 | 0
0358748192 | KJJ0409 | 06/08/2023 | 286.48 | 34.58 | 92 | 68 | 1.64
0358748192 | KJJ0409 | 06/09/2023 | 296.63 | 35.77 | 92 | 68 | 0
0358748192 | KJJ0409 | 06/10/2023 | 306.91 | 36.97 | 88 | 67 | 0.54
0358748192 | KJJ0409 | 06/11/2023 | 317.64 | 38.23 | 91 | 69 | 0.09
0358748192 | KJJ0409 | 06/12/2023 | 309.13 | 37.23 | 94 | 69 | 0
0358748192 | KJJ0409 | 06/13/2023 | 294.4 | 35.51 | 95 | 71
0358748192 | KJJ0409 | 06/14/2023 | 269.91 | 32.65 | 95 | 71 | 0
0358748192 | KJJ0409 | 06/15/2023 | 278.36 | 33.64 | 95 | 66 | 0.44
0358748192 | KJJ0409 | 06/16/2023 | 376.05 | 45.06 | 95 | 68 | 0.45
0358748192 | KJJ0409 | 06/17/2023 | 310.84 | 37.43 | 93 | 68 | 0.91
0358748192 | KJJ0409 | 06/18/2023 | 316.27 | 35.34 | 94 | 68 | 0.28
0358748192 | KJJ0409 | 06/19/2023 | 307.26 | 34.36 | 93 | 70 | 0.63
0358748192 | KJJ0409 | 06/20/2023 | 345.99 | 38.56 | 91 | 69 | 0.46
0358748192 | KJJ0409 | 06/21/2023 | 328.41 | 36.66 | 91 | 71 | 0.24
0358748192 | KJJ0409 | 06/22/2023 | 303.55 | 33.96 | 93 | 66 | 0.04
0358748192 | KJJ0409 | 06/23/2023 | 340.09 | 37.92 | 91 | 69 | 0.35
0358748192 | KJJ0409 | 06/24/2023 | 325.18 | 36.31 | 92 | 70 | 0.24
0358748192 | KJJ0409 | 06/25/2023 | 312.7 | 34.95 | 91 | 70 | 0.15
0358748192 | KJJ0409 | 06/26/2023 | 279.89 | 31.39 | 94 | 70 | 0
0358748192 | KJJ0409 | 06/27/2023 | 273.17 | 30.66 | 97 | 71 | 0
0358748192 | KJJ0409 | 06/28/2023 | 265.76 | 29.86 | 95 | 72 | 0
0358748192 | KJJ0409 | 06/29/2023 | 260.4 | 29.28 | 95 | 71 | 0.88
0358748192 | KJJ0409 | 06/30/2023 | 261.18 | 29.36 | 94 | 71 | 0
0358748192 | KJJ0409 | 07/01/2023 | 263.5 | 29.61 | 94 | 71 | 0
0358748192 | KJJ0409 | 07/02/2023 | 261.43 | 29.39 | 95 | 71 | 0
0358748192 | KJJ0409 | 07/03/2023 | 250.5 | 28.2 | 97 | 72 | 0
0358748192 | KJJ0409 | 07/04/2023 | 256.99 | 28.91 | 95 | 73 | 0
0358748192 | KJJ0409 | 07/05/2023 | 254.35 | 28.62 | 95 | 74 | 0
0358748192 | KJJ0409 | 07/06/2023 | 247.17 | 27.84 | 96 | 73 | 0.04
0358748192 | KJJ0409 | 07/07/2023 | 250.72 | 28.22 | 95 | 73 | 0.03
0358748192 | KJJ0409 | 07/08/2023 | 261.23 | 29.37 | 94 | 74 | 0.31
0358748192 | KJJ0409 | 07/09/2023 | 263.52 | 29.61 | 96 | 74 | 0.2
0358748192 | KJJ0409 | 07/10/2023 | 261.51 | 29.4 | 96 | 74 | 0
0358748192 | KJJ0409 | 07/11/2023 | 260.77 | 29.32 | 94 | 73 | 0.78
0358748192 | KJJ0409 | 07/12/2023 | 256.78 | 28.88 | 94 | 73 | 0.1
0358748192 | KJJ0409 | 07/13/2023 | 249.09 | 28.05 | 94 | 72 | Trace Value
0358748192 | KJJ0409 | 07/14/2023 | 266.97 | 29.99 | 95 | 73 | 0.33
0358748192 | KJJ0409 | 07/15/2023 | 277.37 | 31.12 | 96 | 73 | 0.12
0358748192 | KJJ0409 | 07/16/2023 | 275.45 | 30.91 | 96 | 74 | 0.15
0358748192 | KJJ0409 | 07/17/2023 | 263.12 | 29.57 | 95 | 74 | 2.8
0358748192 | KJJ0409 | 07/18/2023 | 322.3 | 35.99 | 95 | 72 | 0.22
0358748192 | KJJ0409 | 07/19/2023 | 263.24 | 29.58 | 95 | 71 | 0.14
0358748192 | KJJ0409 | 07/20/2023 | 253.07 | 28.47 | 96 | 73 | 0
0358748192 | KJJ0409 | 07/21/2023 | 250 | 28.13 | 99 | 74 | 0
0358748192 | KJJ0409 | 07/22/2023 | 288.89 | 32.34 | 97 | 75 | 0
0358748192 | KJJ0409 | 07/23/2023 | 322.1 | 35.93 | 94 | 71 | 0.7
0358748192 | KJJ0409 | 07/24/2023 | 285.35 | 31.96 | 93 | 73 | 1.12
0358748192 | KJJ0409 | 07/25/2023 | 269.83 | 30.28 | 93 | 73 | 0.3
0358748192 | KJJ0409 | 07/26/2023 | 260.73 | 29.29 | 92 | 73 | 0
0358748192 | KJJ0409 | 07/27/2023 | 253.08 | 28.47 | 91 | 73 | 0
0358748192 | KJJ0409 | 07/28/2023 | 281.12 | 31.5 | 92 | 73 | 1
0358748192 | KJJ0409 | 07/29/2023 | 325.78 | 36.33 | 93 | 73 | 0.05
0358748192 | KJJ0409 | 07/30/2023 | 373.77 | 41.52 | 95 | 74 | Trace Value
0358748192 | KJJ0409 | 07/31/2023 | 429.04 | 47.5 | 95 | 71 | 0.74
0358748192 | KJJ0409 | 08/01/2023 | 366.82 | 40.77 | 95 | 71 | 0.08
0358748192 | KJJ0409 | 08/02/2023 | 334.41 | 37.26 | 93 | 74 | 0
0358748192 | KJJ0409 | 08/03/2023 | 353.65 | 39.34 | 91 | 73 | 0
0358748192 | KJJ0409 | 08/04/2023 | 428.99 | 47.49 | 94 | 73 | 0
0358748192 | KJJ0409 | 08/05/2023 | 488.98 | 53.98 | 94 | 73 | 0.17
0358748192 | KJJ0409 | 08/06/2023 | 465.55 | 51.45 | 95 | 74 | 0.66
0358748192 | KJJ0409 | 08/07/2023 | 459.7 | 50.82 | 97 | 75 | 0.03
0358748192 | KJJ0409 | 08/08/2023 | 391.28 | 43.42 | 99 | 75 | 0
0358748192 | KJJ0409 | 08/09/2023 | 360.16 | 40.05 | 99 | 74 | 0
0358748192 | KJJ0409 | 08/10/2023 | 332.38 | 37.04 | 100 | 75 | 0.16
0358748192 | KJJ0409 | 08/11/2023 | 316.1 | 35.28 | 99 | 75 | 0
0358748192 | KJJ0409 | 08/12/2023 | 309.93 | 34.62 | 98 | 76 | 0.25
0358748192 | KJJ0409 | 08/13/2023 | 311.34 | 34.77 | 97 | 74 | 0
0358748192 | KJJ0409 | 08/14/2023 | 275.09 | 30.85 | 97 | 76 | 0
0358748192 | KJJ0409 | 08/15/2023 | 268.06 | 30.09 | 97 | 75 | 0
0358748192 | KJJ0409 | 08/16/2023 | 279.59 | 31.33 | 96 | 73 | 0.09
0358748192 | KJJ0409 | 08/17/2023 | 407.79 | 45.2 | 93 | 72 | 0.36
0358748192 | KJJ0409 | 08/18/2023 | 344.93 | 38.4 | 93 | 73 | 1.09
0358748192 | KJJ0409 | 08/19/2023 | 333.38 | 38.97 | 93 | 72 | 0.69
0358748192 | KJJ0409 | 08/20/2023 | 319.2 | 37.36 | 92 | 75 | 0
0358748192 | KJJ0409 | 08/21/2023 | 282.34 | 33.16 | 92 | 74 | 0
0358748192 | KJJ0409 | 08/22/2023 | 278.59 | 32.73 | 93 | 72 | 0
0358748192 | KJJ0409 | 08/23/2023 | 267.65 | 31.49 | 93 | 74 | 0
0358748192 | KJJ0409 | 08/24/2023 | 258.28 | 30.42 | 93 | 74 | 0.99
0358748192 | KJJ0409 | 08/25/2023 | 258.98 | 30.5 | 92 | 71 | 0
0358748192 | KJJ0409 | 08/26/2023 | 262.3 | 30.88 | 95 | 73 | 0
0358748192 | KJJ0409 | 08/27/2023 | 266.7 | 31.38 | 95 | 72
0358748192 | KJJ0409 | 08/28/2023 | 247.71 | 29.22 | 96 | 74 | Trace Value
0358748192 | KJJ0409 | 08/29/2023 | 255.39 | 30.09 | 95 | 74 | 0
0358748192 | KJJ0409 | 08/30/2023 | 272.62 | 32.05 | 94 | 74 | 0.93
0358748192 | KJJ0409 | 08/31/2023 | 257.34 | 30.31 | 94 | 74 | 0.05
0358748192 | KJJ0409 | 09/01/2023 | 258.12 | 30.4 | 92 | 73 | 0
0358748192 | KJJ0409 | 09/02/2023 | 264.34 | 31.11 | 91 | 72
0358748192 | KJJ0409 | 09/03/2023 | 266.16 | 31.32 | 92 | 71 | 0.05
0358748192 | KJJ0409 | 09/04/2023 | 267.16 | 31.43 | 90 | 68 | 0
0358748192 | KJJ0409 | 09/05/2023 | 266.61 | 31.37 | 90 | 64 | 0
0358748192 | KJJ0409 | 09/06/2023 | 253.92 | 29.93 | 94 | 69 | 0
0358748192 | KJJ0409 | 09/07/2023 | 248.27 | 29.28 | 95 | 70
0358748192 | KJJ0409 | 09/08/2023 | 351.35 | 41.02 | 95 | 69 | 0
0358748192 | KJJ0409 | 09/09/2023 | 313.05 | 36.66 | 94 | 64 | 0.48
0358748192 | KJJ0409 | 09/10/2023 | 302.89 | 35.5 | 93 | 71 | Trace Value
0358748192 | KJJ0409 | 09/11/2023 | 269.5 | 31.7 | 92 | 72 | 0
0358748192 | KJJ0409 | 09/12/2023 | 271.5 | 31.93 | 92 | 71 | Trace Value
0358748192 | KJJ0409 | 09/13/2023 | 349.79 | 40.84 | 92 | 72 | 0.03
0358748192 | KJJ0409 | 09/14/2023 | 315.48 | 36.93 | 91 | 71 | 0.29
0358748192 | KJJ0409 | 09/15/2023 | 288.78 | 33.89 | 88 | 70 | 0
0358748192 | KJJ0409 | 09/16/2023 | 287.44 | 33.74 | 87 | 69 | 0.54
0358748192 | KJJ0409 | 09/17/2023 | 287.24 | 33.72 | 92 | 70 | 0
0358748192 | KJJ0409 | 09/18/2023 | 312.38 | 36.58 | 89 | 68 | 0.08
0358748192 | KJJ0409 | 09/19/2023 | 261.01 | 30.73 | 88 | 64 | 0
0358748192 | KJJ0409 | 09/20/2023 | 253.03 | 28.61 | 88 | 69 | 0
0358748192 | KJJ0409 | 09/21/2023 | 248.79 | 28.15 | 87 | 68 | 0.08
0358748192 | KJJ0409 | 09/22/2023 | 245.72 | 27.81 | 85 | 65 | 0.3
0358748192 | KJJ0409 | 09/23/2023 | 253.71 | 28.68 | 87 | 61 | 0
0358748192 | KJJ0409 | 09/24/2023 | 258.23 | 29.17 | 89 | 59 | 0
0358748192 | KJJ0409 | 09/25/2023 | 276.31 | 31.14 | 90 | 66 | 0
0358748192 | KJJ0409 | 09/26/2023 | 444.97 | 49.48 | 89 | 71 | 2.11
0358748192 | KJJ0409 | 09/27/2023 | 514.94 | 57.09 | 88 | 71 | 0.91
0358748192 | KJJ0409 | 09/28/2023 | 516.29 | 57.23 | 87 | 71 | 0.81
0358748192 | KJJ0409 | 09/29/2023 | 457.81 | 50.87 | 85 | 71 | 0.02
0358748192 | KJJ0409 | 09/30/2023 | 737.95 | 81.34 | 85 | 71 | 0.2
0358748192 | KJJ0409 | 10/01/2023 | 893.37 | 98.24 | 85 | 70 | 2.53
0358748192 | KJJ0409 | 10/02/2023 | 650.06 | 71.78 | 85 | 69 | 0.56
0358748192 | KJJ0409 | 10/03/2023 | 520.38 | 57.68 | 85 | 70 | 0
0358748192 | KJJ0409 | 10/04/2023 | 449.35 | 49.95 | 86 | 70 | 0.05
0358748192 | KJJ0409 | 10/05/2023 | 389.12 | 43.4 | 86 | 69 | 0
0358748192 | KJJ0409 | 10/06/2023 | 381.81 | 42.61 | 87 | 66 | 0
0358748192 | KJJ0409 | 10/07/2023 | 366.66 | 40.96 | 90 | 56 | 0
0358748192 | KJJ0409 | 10/08/2023 | 353.14 | 39.49 | 82 | 53 | 0
0358748192 | KJJ0409 | 10/09/2023 | 326.47 | 36.59 | 80 | 55 | 0
0358748192 | KJJ0409 | 10/10/2023 | 303.56 | 34.1 | 84 | 56 | 0
0358748192 | KJJ0409 | 10/11/2023 | 304.89 | 34.25 | 84 | 65 | 0
0358748192 | KJJ0409 | 10/12/2023 | 867.56 | 95.43 | 88 | 72 | 2.8
0358748192 | KJJ0409 | 10/13/2023 | 888.37 | 97.7 | 89 | 68 | 1.67
0358748192 | KJJ0409 | 10/14/2023 | 617.59 | 68.25 | 89 | 64 | 0
0358748192 | KJJ0409 | 10/15/2023 | 540.85 | 59.9 | 82 | 55 | 0
0358748192 | KJJ0409 | 10/16/2023 | 465.88 | 51.75 | 76 | 50 | 0
0358748192 | KJJ0409 | 10/17/2023 | 423.97 | 47.2 | 75 | 49 | 0
0358748192 | KJJ0409 | 10/18/2023 | 470.73 | 52.28 | 77 | 50 | 0
0358748192 | KJJ0409 | 10/19/2023 | 366.3 | 40.92 | 81 | 55 | 0
0358748192 | KJJ0409 | 10/20/2023 | 350.73 | 41.02 | 83 | 55 | 0
0358748192 | KJJ0409 | 10/21/2023 | 350.54 | 41 | 83 | 55 | 0
0358748192 | KJJ0409 | 10/22/2023 | 339.78 | 39.77 | 86 | 52 | 0
0358748192 | KJJ0409 | 10/23/2023 | 312.56 | 36.67 | 83 | 58 | 0
0358748192 | KJJ0409 | 10/24/2023 | 311.95 | 36.6 | 82 | 67 | 0
0358748192 | KJJ0409 | 10/25/2023 | 303.55 | 35.65 | 82 | 68 | 0
0358748192 | KJJ0409 | 10/26/2023 | 297.29 | 34.93 | 82 | 65 | 0
0358748192 | KJJ0409 | 10/27/2023 | 292.09 | 34.34 | 83 | 64 | 0
0358748192 | KJJ0409 | 10/28/2023 | 298.66 | 35.09 | 84 | 62 | 0
0358748192 | KJJ0409 | 10/29/2023 | 300.42 | 35.29 | 84 | 61 | 0
0358748192 | KJJ0409 | 10/30/2023 | 244.23 | 28.89 | 85 | 60 | 0
0358748192 | KJJ0409 | 10/31/2023 | 277.85 | 32.72 | 84 | 58 | 0
0358748192 | KJJ0409 | 11/01/2023 | 273.76 | 32.26 | 76 | 53 | 0
0358748192 | KJJ0409 | 11/02/2023 | 273.06 | 32.18 | 75 | 53 | 0
0358748192 | KJJ0409 | 11/03/2023 | 265.07 | 31.27 | 79 | 59 | 0
0358748192 | KJJ0409 | 11/04/2023 | 280.67 | 33.04 | 79 | 55 | 0
0358748192 | KJJ0409 | 11/05/2023 | 288.77 | 33.97 | 80 | 51 | 0
0358748192 | KJJ0409 | 11/06/2023 | 262.83 | 31.01 | 81 | 48 | 0
0358748192 | KJJ0409 | 11/07/2023 | 272.24 | 32.08 | 83 | 53 | 0
0358748192 | KJJ0409 | 11/08/2023 | 260.78 | 30.78 | 84 | 50 | 0
0358748192 | KJJ0409 | 11/09/2023 | 252.55 | 29.84 | 85 | 55 | 0
0358748192 | KJJ0409 | 11/10/2023 | 256.55 | 30.3 | 86 | 60 | 0
0358748192 | KJJ0409 | 11/11/2023 | 274.37 | 32.33 | 83 | 65 | 0.33
0358748192 | KJJ0409 | 11/12/2023 | 271.23 | 31.97 | 80 | 63 | 0
0358748192 | KJJ0409 | 11/13/2023 | 258.47 | 30.52 | 77 | 62 | 0
0358748192 | KJJ0409 | 11/14/2023 | 262.08 | 30.93 | 77 | 61 | 0.12
0358748192 | KJJ0409 | 11/15/2023 | 264.3 | 31.18 | 77 | 64 | 0.05
0358748192 | KJJ0409 | 11/16/2023 | 482.6 | 56.03 | 78 | 62 | 0.16
0358748192 | KJJ0409 | 11/17/2023 | 577.5 | 66.84 | 79 | 61 | 2.1
0358748192 | KJJ0409 | 11/18/2023 | 419.89 | 52.91 | 78 | 55 | 0.66
0358748192 | KJJ0409 | 11/19/2023 | 370.14 | 46.77 | 80 | 56 | 0
0358748192 | KJJ0409 | 11/20/2023 | 323.41 | 41 | 79 | 59 | 0.02
0358748192 | KJJ0409 | 11/21/2023 | 318.97 | 40.45 | 81 | 52 | 0.02
0358748192 | KJJ0409 | 11/22/2023 | 317.13 | 40.22 | 81 | 47 | 0
0358748192 | KJJ0409 | 11/23/2023 | 327.11 | 41.45 | 73 | 48 | 0.01
0358748192 | KJJ0409 | 11/24/2023 | 303.43 | 38.53 | 75 | 52 | 0.01
0358748192 | KJJ0409 | 11/25/2023 | 297.05 | 37.74 | 75 | 53 | 0.07
0358748192 | KJJ0409 | 11/26/2023 | 339.21 | 42.95 | 75 | 55 | 0.01
0358748192 | KJJ0409 | 11/27/2023 | 313.53 | 39.78 | 74 | 44 | 0.55
0358748192 | KJJ0409 | 11/28/2023 | 290.2 | 36.9 | 69 | 39 | 0
0358748192 | KJJ0409 | 11/29/2023 | 280.45 | 35.69 | 68 | 36 | 0
0358748192 | KJJ0409 | 11/30/2023 | 274.19 | 34.92 | 86 | 41 | 0
0358748192 | KJJ0409 | 12/01/2023 | 275.95 | 35.13 | 82 | 55 | 0
0358748192 | KJJ0409 | 12/02/2023 | 283.59 | 36.08 | 83 | 64 | 0
0358748192 | KJJ0409 | 12/03/2023 | 297.25 | 37.77 | 82 | 62 | 0.02
0358748192 | KJJ0409 | 12/04/2023 | 289.17 | 36.77 | 79 | 51 | 0.23
0358748192 | KJJ0409 | 12/05/2023 | 275.96 | 35.14 | 72 | 47 | 0
0358748192 | KJJ0409 | 12/06/2023 | 257.47 | 32.85 | 69 | 41 | 0
0358748192 | KJJ0409 | 12/07/2023 | 265.3 | 33.82 | 67 | 41 | 0
0358748192 | KJJ0409 | 12/08/2023 | 262 | 33.41 | 74 | 47 | 0
0358748192 | KJJ0409 | 12/09/2023 | 268.39 | 34.2 | 82 | 56 | 0.04
0358748192 | KJJ0409 | 12/10/2023 | 279.62 | 35.59 | 83 | 44 | 0
0358748192 | KJJ0409 | 12/11/2023 | 248.18 | 31.71 | 67 | 43 | 0.25
0358748192 | KJJ0409 | 12/12/2023 | 241.38 | 30.86 | 71 | 43 | 0
0358748192 | KJJ0409 | 12/13/2023 | 239.67 | 30.65 | 73 | 58 | 0
0358748192 | KJJ0409 | 12/14/2023 | 276.22 | 35.17 | 72 | 59 | 0.66
0358748192 | KJJ0409 | 12/15/2023 | 285.15 | 36.27 | 72 | 60 | 0.07
0358748192 | KJJ0409 | 12/16/2023 | 340.2 | 43.07 | 73 | 58 | 0.11
0358748192 | KJJ0409 | 12/17/2023 | 1027.51 | 127.97 | 74 | 48 | 4.04
0358748192 | KJJ0409 | 12/18/2023 | 507.2 | 63.7 | 68 | 40 | 0.05
358748192 | KJJ0409 | 2023-12-19 | 439.75 | 48.13 | 65 | 41 | 0
358748192 | KJJ0409 | 2023-12-20 | 312.53 | 34.5 | 66 | 44 | 0
358748192 | KJJ0409 | 2023-12-21 | 383.74 | 42.13 | 68 | 46 | 0
358748192 | KJJ0409 | 2023-12-22 | 360.54 | 39.65 | 70 | 49 | 0
358748192 | KJJ0409 | 2023-12-23 | 365.56 | 40.19 | 73 | 53 | 0
358748192 | KJJ0409 | 2023-12-24 | 366.17 | 40.25 | 73 | 53 | 0
358748192 | KJJ0409 | 2023-12-25 | 351.06 | 38.63 | 73 | 60 | 0.09
358748192 | KJJ0409 | 2023-12-26 | 344.88 | 37.97 | 74 | 54 | 0.1
358748192 | KJJ0409 | 2023-12-27 | 324.12 | 35.75 | 71 | 49 | 0
358748192 | KJJ0409 | 2023-12-28 | 320.11 | 35.32 | 66 | 44 | 0.04
358748192 | KJJ0409 | 2023-12-29 | 318.25 | 35.12 | 55 | 46 | 0
358748192 | KJJ0409 | 2023-12-30 | 316.05 | 34.88 | 59 | 37 | 0
358748192 | KJJ0409 | 2023-12-31 | 316.3 | 34.91 | 63 | 36 | 0
|  | Yearly Daily Average: | 299.7513 | 35.5245
|  | Yearly Daily Average (Less Spike Events): | 274.7837 | 32.9407
|  | Spike Event Daily Average: | 460.7669 | 52.1869
|  | Dryer Months' Daily Average (Less Spikes): | 270.0426 | 32.8844
|  | Wetter Months' Daily Average (Less Spikes): | 287.6684 | 40.783
|  | Wetter Months' Daily Average: | 349.1251 | 40.783

## 22-2 COMPARISON
Daily Billed Information [PS 22-2 - 212 Westhampton Drive (Comparison Pump): 2023 Reading Data]
Bill Account | Meter Number | Date | Consumption Recorded (kWh/day) | Estimated Cost ($/day) | Avg. High Temperature (°F) | Avg. Low Temperature (°F) | Rain Recorded by NOAA (inches)
6453411123 | KJ33453 | 01/01/2023 | 28.49 | 3.85 | 79 | 58 | 0.04
6453411123 | KJ33453 | 01/02/2023 | 28.92 | 3.9 | 78 | 53 | 0
6453411123 | KJ33453 | 01/03/2023 | 26.51 | 3.61 | 81 | 51 | 0
6453411123 | KJ33453 | 01/04/2023 | 26.08 | 3.56 | 83 | 57 | 0
6453411123 | KJ33453 | 01/05/2023 | 31.99 | 4.27 | 77 | 46 | 0.04
6453411123 | KJ33453 | 01/06/2023 | 30.08 | 4.04 | 68 | 41 | 0
6453411123 | KJ33453 | 01/07/2023 | 31.71 | 4.24 | 70 | 38 | 0
6453411123 | KJ33453 | 01/08/2023 | 30.1 | 4.04 | 76 | 42 | 0
6453411123 | KJ33453 | 01/09/2023 | 27.56 | 3.74 | 74 | 47 | 0
6453411123 | KJ33453 | 01/10/2023 | 28.73 | 3.88 | 71 | 42 | 0
6453411123 | KJ33453 | 01/11/2023 | 36.55 | 4.82 | 73 | 38 | 0
6453411123 | KJ33453 | 01/12/2023 | 28.27 | 3.82 | 80 | 44 | 0
6453411123 | KJ33453 | 01/13/2023 | 28.5 | 3.95 | 71 | 35 | 0.12
6453411123 | KJ33453 | 01/14/2023 | 32.66 | 4.47 | 61 | 30 | 0
6453411123 | KJ33453 | 01/15/2023 | 34.43 | 4.69 | 63 | 30 | 0
6453411123 | KJ33453 | 01/16/2023 | 28.4 | 3.94 | 71 | 30 | 0
6453411123 | KJ33453 | 01/17/2023 | 31.96 | 4.38 | 75 | 34 | 0
6453411123 | KJ33453 | 01/18/2023 | 25.73 | 3.61 | 79 | 46 | N/A
6453411123 | KJ33453 | 01/19/2023 | 28.77 | 3.99 | 82 | 54 | 0
6453411123 | KJ33453 | 01/20/2023 | 25.27 | 3.55 | 76 | 49 | 0
6453411123 | KJ33453 | 01/21/2023 | 32.3 | 4.43 | 76 | 47 | T
6453411123 | KJ33453 | 01/22/2023 | 31.69 | 4.35 | 82 | 54 | 0.33
6453411123 | KJ33453 | 01/23/2023 | 29.66 | 4.1 | 75 | 44 | 0.05
6453411123 | KJ33453 | 01/24/2023 | 30.1 | 4.15 | 76 | 41 | 0
6453411123 | KJ33453 | 01/25/2023 | 28.08 | 3.9 | 85 | 43 | 0
6453411123 | KJ33453 | 01/26/2023 | 29.79 | 4.11 | 72 | 38 | 0.09
6453411123 | KJ33453 | 01/27/2023 | 30.99 | 4.26 | 62 | 37 | 0
6453411123 | KJ33453 | 01/28/2023 | 30.03 | 4.14 | 69 | 35 | 0
6453411123 | KJ33453 | 01/29/2023 | 31.89 | 4.38 | 78 | 55 | 0
6453411123 | KJ33453 | 01/30/2023 | 26.12 | 3.66 | 86 | 58 | 0
6453411123 | KJ33453 | 01/31/2023 | 27.13 | 3.78 | 83 | 59 | 0
6453411123 | KJ33453 | 02/01/2023 | 25.42 | 3.57 | 82 | 58 | 0
6453411123 | KJ33453 | 02/02/2023 | 25.96 | 3.64 | 82 | 57 | 0
6453411123 | KJ33453 | 02/03/2023 | 29.54 | 4.08 | 78 | 50 | 0
6453411123 | KJ33453 | 02/04/2023 | 30.46 | 4.2 | 70 | 47 | 0.17
6453411123 | KJ33453 | 02/05/2023 | 32.31 | 4.43 | 73 | 48 | 0
6453411123 | KJ33453 | 02/06/2023 | 30.47 | 4.2 | 71 | 46 | 0.01
6453411123 | KJ33453 | 02/07/2023 | 30 | 4.14 | 76 | 44
6453411123 | KJ33453 | 02/08/2023 | 27.08 | 3.78 | 79 | 49 | 0
6453411123 | KJ33453 | 02/09/2023 | 24.09 | 3.41 | 83 | 58 | 0
6453411123 | KJ33453 | 02/10/2023 | 27.58 | 3.84 | 85 | 46 | 0.16
6453411123 | KJ33453 | 02/11/2023 | 30.63 | 4.22 | 79 | 40 | 0.57
6453411123 | KJ33453 | 02/12/2023 | 39.83 | 5.36 | 71 | 40 | 0.12
6453411123 | KJ33453 | 02/13/2023 | 28.11 | 3.91 | 71 | 40 | Trace Value
6453411123 | KJ33453 | 02/14/2023 | 28.47 | 3.99 | 75 | 39 | 0
6453411123 | KJ33453 | 02/15/2023 | 26.83 | 3.78 | 82 | 50 | 0
6453411123 | KJ33453 | 02/16/2023 | 26.51 | 3.74 | 85 | 57 | 0
6453411123 | KJ33453 | 02/17/2023 | 25.75 | 3.65 | 89 | 45
6453411123 | KJ33453 | 02/18/2023 | 28.98 | 4.05 | 67 | 46 | 0.04
6453411123 | KJ33453 | 02/19/2023 | 28.76 | 4.02 | 80 | 48 | 0
6453411123 | KJ33453 | 02/20/2023 | 27.32 | 3.84 | 82 | 53 | 0
6453411123 | KJ33453 | 02/21/2023 | 26.66 | 3.76 | 85 | 57 | 0
6453411123 | KJ33453 | 02/22/2023 | 25.63 | 3.63 | 87 | 58 | 0
6453411123 | KJ33453 | 02/23/2023 | 27.5 | 3.87 | 89 | 60 | 0
6453411123 | KJ33453 | 02/24/2023 | 24.85 | 3.53 | 87 | 58 | 0
6453411123 | KJ33453 | 02/25/2023 | 23.03 | 3.31 | 87 | 58
6453411123 | KJ33453 | 02/26/2023 | 29.72 | 4.14 | 87 | 56 | 0
6453411123 | KJ33453 | 02/27/2023 | 24.13 | 3.44 | 87 | 57 | 0
6453411123 | KJ33453 | 02/28/2023 | 24.49 | 3.49 | 87 | 57 | 0
6453411123 | KJ33453 | 03/01/2023 | 27.7 | 3.89 | 86 | 58 | 0
6453411123 | KJ33453 | 03/02/2023 | 24.46 | 3.49 | 87 | 56 | 0
6453411123 | KJ33453 | 03/03/2023 | 26.96 | 3.8 | 90 | 55 | 0
6453411123 | KJ33453 | 03/04/2023 | 24.07 | 3.44 | 88 | 52 | 0
6453411123 | KJ33453 | 03/05/2023 | 30.04 | 4.18 | 81 | 54 | 0.05
6453411123 | KJ33453 | 03/06/2023 | 22.73 | 3.27 | 84 | 56 | 0
6453411123 | KJ33453 | 03/07/2023 | 24.73 | 3.52 | 87 | 56
6453411123 | KJ33453 | 03/08/2023 | 26.83 | 3.78 | 85 | 58 | 0
6453411123 | KJ33453 | 03/09/2023 | 25.13 | 3.57 | 80 | 51 | 0
6453411123 | KJ33453 | 03/10/2023 | 31.5 | 4.37 | 85 | 54
6453411123 | KJ33453 | 03/11/2023 | 31.43 | 4.36 | 81 | 51 | 1.3
6453411123 | KJ33453 | 03/12/2023 | 29.58 | 4.13 | 86 | 48 | 0
6453411123 | KJ33453 | 03/13/2023 | 43.48 | 5.86 | 81 | 46 | 1.17
6453411123 | KJ33453 | 03/14/2023 | 34.3 | 4.71 | 70 | 43 | 0.6
6453411123 | KJ33453 | 03/15/2023 | 31.94 | 4.84 | 68 | 43 | 0
6453411123 | KJ33453 | 03/16/2023 | 29 | 4.44 | 77 | 37 | 0
6453411123 | KJ33453 | 03/17/2023 | 28.77 | 4.41 | 84 | 48
6453411123 | KJ33453 | 03/18/2023 | 29.9 | 4.56 | 80 | 45 | 0
6453411123 | KJ33453 | 03/19/2023 | 32.39 | 4.9 | 68 | 43 | 0.02
6453411123 | KJ33453 | 03/20/2023 | 32.74 | 4.95 | 69 | 42 | 0.02
6453411123 | KJ33453 | 03/21/2023 | 29.12 | 4.45 | 77 | 42 | 0
6453411123 | KJ33453 | 03/22/2023 | 26.89 | 4.15 | 80 | 53 | 0.08
6453411123 | KJ33453 | 03/23/2023 | 25.99 | 4.03 | 83 | 53
6453411123 | KJ33453 | 03/24/2023 | 25.38 | 3.94 | 86 | 53 | 0
6453411123 | KJ33453 | 03/25/2023 | 25.82 | 4 | 91 | 60 | 0
6453411123 | KJ33453 | 03/26/2023 | 32.22 | 4.88 | 91 | 63 | 0.68
6453411123 | KJ33453 | 03/27/2023 | 25.6 | 3.97 | 92 | 62 | 0
6453411123 | KJ33453 | 03/28/2023 | 27.43 | 4.22 | 88 | 55 | Trace Value
6453411123 | KJ33453 | 03/29/2023 | 28.35 | 4.35 | 75 | 55 | 0
6453411123 | KJ33453 | 03/30/2023 | 27.84 | 4.28 | 79 | 51 | 0
6453411123 | KJ33453 | 03/31/2023 | 27.32 | 4.21 | 85 | 55 | 0
6453411123 | KJ33453 | 04/01/2023 | 27.82 | 4.28 | 90 | 60 | 0
6453411123 | KJ33453 | 04/02/2023 | 27.46 | 4.23 | 85 | 60
6453411123 | KJ33453 | 04/03/2023 | 25.31 | 3.93 | 86 | 61 | 0
6453411123 | KJ33453 | 04/04/2023 | 26.92 | 4.15 | 88 | 60 | Trace Value
6453411123 | KJ33453 | 04/05/2023 | 26.35 | 4.08 | 87 | 63 | 0
6453411123 | KJ33453 | 04/06/2023 | 23.64 | 3.71 | 87 | 64 | 0
6453411123 | KJ33453 | 04/07/2023 | 25.12 | 3.91 | 85 | 64
6453411123 | KJ33453 | 04/08/2023 | 25.97 | 4.02 | 86 | 62
6453411123 | KJ33453 | 04/09/2023 | 29.07 | 4.45 | 80 | 60 | 0.01
6453411123 | KJ33453 | 04/10/2023 | 31.74 | 4.81 | 79 | 58 | 0.68
6453411123 | KJ33453 | 04/11/2023 | 32.78 | 4.95 | 78 | 58 | 1.38
6453411123 | KJ33453 | 04/12/2023 | 36.38 | 5.44 | 79 | 59 | 0.03
6453411123 | KJ33453 | 04/13/2023 | 37.4 | 5.58 | 87 | 61 | 0.07
6453411123 | KJ33453 | 04/14/2023 | 45.79 | 6.55 | 86 | 59 | 0.57
6453411123 | KJ33453 | 04/15/2023 | 40.44 | 5.84 | 87 | 60 | 0.02
6453411123 | KJ33453 | 04/16/2023 | 37.03 | 5.39 | 88 | 59 | 0
6453411123 | KJ33453 | 04/17/2023 | 33.92 | 4.98 | 81 | 50 | 0.04
6453411123 | KJ33453 | 04/18/2023 | 34.83 | 5.1 | 81 | 46 | 0.02
6453411123 | KJ33453 | 04/19/2023 | 33.49 | 4.92 | 82 | 50 | 0
6453411123 | KJ33453 | 04/20/2023 | 31.83 | 4.7 | 84 | 55 | 0
6453411123 | KJ33453 | 04/21/2023 | 31.07 | 4.6 | 87 | 59
6453411123 | KJ33453 | 04/22/2023 | 30.83 | 4.57 | 89 | 57 | 0.3
6453411123 | KJ33453 | 04/23/2023 | 32.51 | 4.79 | 84 | 53 | 0.42
6453411123 | KJ33453 | 04/24/2023 | 29.34 | 4.37 | 80 | 55 | 0
6453411123 | KJ33453 | 04/25/2023 | 31.03 | 4.6 | 82 | 61 | 0.25
6453411123 | KJ33453 | 04/26/2023 | 28.99 | 4.33 | 84 | 62 | 0.07
6453411123 | KJ33453 | 04/27/2023 | 35.39 | 5.17 | 86 | 63 | 0
6453411123 | KJ33453 | 04/28/2023 | 41.82 | 6.03 | 87 | 62 | 1.62
6453411123 | KJ33453 | 04/29/2023 | 36.77 | 5.36 | 88 | 62 | 0
6453411123 | KJ33453 | 04/30/2023 | 38.05 | 5.53 | 85 | 57 | 0.52
6453411123 | KJ33453 | 05/01/2023 | 33.36 | 4.91 | 85 | 56 | 0
6453411123 | KJ33453 | 05/02/2023 | 32.5 | 4.79 | 87 | 56 | 0
6453411123 | KJ33453 | 05/03/2023 | 30.46 | 4.52 | 86 | 53 | 0
6453411123 | KJ33453 | 05/04/2023 | 28.42 | 4.25 | 84 | 53 | 0
6453411123 | KJ33453 | 05/05/2023 | 30.6 | 4.54 | 87 | 57 | 0
6453411123 | KJ33453 | 05/06/2023 | 30.44 | 4.52 | 86 | 65 | 0
6453411123 | KJ33453 | 05/07/2023 | 31.16 | 4.61 | 88 | 61 | 0.02
6453411123 | KJ33453 | 05/08/2023 | 29.02 | 4.33 | 87 | 55 | 0
6453411123 | KJ33453 | 05/09/2023 | 29.65 | 4.41 | 91 | 63 | 0
6453411123 | KJ33453 | 05/10/2023 | 29.71 | 4.42 | 92 | 66 | 0
6453411123 | KJ33453 | 05/11/2023 | 34.88 | 5.11 | 88 | 67 | 0.04
6453411123 | KJ33453 | 05/12/2023 | 26.9 | 4.05 | 86 | 66 | 0
6453411123 | KJ33453 | 05/13/2023 | 28.78 | 4.25 | 85 | 64 | 0
6453411123 | KJ33453 | 05/14/2023 | 29.04 | 4.29 | 86 | 63 | 0
6453411123 | KJ33453 | 05/15/2023 | 28.02 | 4.15 | 89 | 62 | 0
6453411123 | KJ33453 | 05/16/2023 | 26.79 | 3.99 | 88 | 64 | 0
6453411123 | KJ33453 | 05/17/2023 | 27.39 | 4.07 | 92 | 67 | 0
6453411123 | KJ33453 | 05/18/2023 | 27.68 | 4.11 | 89 | 65 | 1.24
6453411123 | KJ33453 | 05/19/2023 | 26.98 | 4.01 | 88 | 66 | 0.02
6453411123 | KJ33453 | 05/20/2023 | 27.2 | 4.04 | 88 | 66 | 0
6453411123 | KJ33453 | 05/21/2023 | 26.93 | 4.01 | 88 | 67
6453411123 | KJ33453 | 05/22/2023 | 28.68 | 4.24 | 88 | 67 | 0.65
6453411123 | KJ33453 | 05/23/2023 | 30.79 | 4.52 | 85 | 67 | 0.56
6453411123 | KJ33453 | 05/24/2023 | 33.87 | 4.92 | 83 | 66 | 0.12
6453411123 | KJ33453 | 05/25/2023 | 31.91 | 4.66 | 83 | 66 | 0.16
6453411123 | KJ33453 | 05/26/2023 | 30.52 | 4.48 | 82 | 62 | 0.05
6453411123 | KJ33453 | 05/27/2023 | 31.34 | 4.59 | 81 | 56 | Trace Value
6453411123 | KJ33453 | 05/28/2023 | 30.35 | 4.46 | 85 | 55 | 0
6453411123 | KJ33453 | 05/29/2023 | 29.14 | 4.3 | 87 | 60 | 0
6453411123 | KJ33453 | 05/30/2023 | 28.12 | 4.16 | 88 | 62 | 0
6453411123 | KJ33453 | 05/31/2023 | 27.3 | 4.06 | 87 | 68 | 0
6453411123 | KJ33453 | 06/01/2023 | 27.33 | 4.06 | 85 | 68 | 0
6453411123 | KJ33453 | 06/02/2023 | 27.05 | 4.02 | 85 | 67 | 0
6453411123 | KJ33453 | 06/03/2023 | 27.34 | 4.06 | 84 | 67 | 0
6453411123 | KJ33453 | 06/04/2023 | 27.12 | 4.03 | 84 | 66 | 0
6453411123 | KJ33453 | 06/05/2023 | 25.62 | 3.83 | 84 | 64 | 0.3
6453411123 | KJ33453 | 06/06/2023 | 24.8 | 3.73 | 88 | 62
6453411123 | KJ33453 | 06/07/2023 | 29.07 | 4.29 | 91 | 68 | 0
6453411123 | KJ33453 | 06/08/2023 | 29.14 | 4.3 | 92 | 68 | 1.64
6453411123 | KJ33453 | 06/09/2023 | 29.25 | 4.31 | 92 | 68 | 0
6453411123 | KJ33453 | 06/10/2023 | 30.46 | 4.47 | 88 | 67 | 0.54
6453411123 | KJ33453 | 06/11/2023 | 29.21 | 4.31 | 91 | 69 | 0.09
6453411123 | KJ33453 | 06/12/2023 | 35.54 | 5.14 | 94 | 69 | 0
6453411123 | KJ33453 | 06/13/2023 | 29.3 | 4.32 | 95 | 71
6453411123 | KJ33453 | 06/14/2023 | 28.33 | 4.11 | 95 | 71 | 0
6453411123 | KJ33453 | 06/15/2023 | 29.69 | 4.29 | 95 | 66 | 0.44
6453411123 | KJ33453 | 06/16/2023 | 31.48 | 4.51 | 95 | 68 | 0.45
6453411123 | KJ33453 | 06/17/2023 | 32.91 | 4.7 | 93 | 68 | 0.91
6453411123 | KJ33453 | 06/18/2023 | 33.95 | 4.83 | 94 | 68 | 0.28
6453411123 | KJ33453 | 06/19/2023 | 36.22 | 5.12 | 93 | 70 | 0.63
6453411123 | KJ33453 | 06/20/2023 | 45.17 | 6.27 | 91 | 69 | 0.46
6453411123 | KJ33453 | 06/21/2023 | 39.39 | 5.53 | 91 | 71 | 0.24
6453411123 | KJ33453 | 06/22/2023 | 37.97 | 5.35 | 93 | 66 | 0.04
6453411123 | KJ33453 | 06/23/2023 | 42.42 | 5.92 | 91 | 69 | 0.35
6453411123 | KJ33453 | 06/24/2023 | 39.73 | 5.57 | 92 | 70 | 0.24
6453411123 | KJ33453 | 06/25/2023 | 37.43 | 5.28 | 91 | 70 | 0.15
6453411123 | KJ33453 | 06/26/2023 | 32.76 | 4.68 | 94 | 70 | 0
6453411123 | KJ33453 | 06/27/2023 | 31.91 | 4.57 | 97 | 71 | 0
6453411123 | KJ33453 | 06/28/2023 | 31.46 | 4.51 | 95 | 72 | 0
6453411123 | KJ33453 | 06/29/2023 | 30.69 | 4.41 | 95 | 71 | 0.88
6453411123 | KJ33453 | 06/30/2023 | 29.67 | 4.28 | 94 | 71 | 0
6453411123 | KJ33453 | 07/01/2023 | 29.74 | 4.29 | 94 | 71 | 0
6453411123 | KJ33453 | 07/02/2023 | 28.9 | 4.18 | 95 | 71 | 0
6453411123 | KJ33453 | 07/03/2023 | 27.12 | 3.96 | 97 | 72 | 0
6453411123 | KJ33453 | 07/04/2023 | 28.37 | 4.12 | 95 | 73 | 0
6453411123 | KJ33453 | 07/05/2023 | 27.99 | 4.07 | 95 | 74 | 0
6453411123 | KJ33453 | 07/06/2023 | 28.48 | 4.13 | 96 | 73 | 0.04
6453411123 | KJ33453 | 07/07/2023 | 28.59 | 4.14 | 95 | 73 | 0.03
6453411123 | KJ33453 | 07/08/2023 | 28.94 | 4.19 | 94 | 74 | 0.31
6453411123 | KJ33453 | 07/09/2023 | 28.27 | 4.1 | 96 | 74 | 0.2
6453411123 | KJ33453 | 07/10/2023 | 27.45 | 4 | 96 | 74 | 0
6453411123 | KJ33453 | 07/11/2023 | 28.41 | 4.12 | 94 | 73 | 0.78
6453411123 | KJ33453 | 07/12/2023 | 36.76 | 5.19 | 94 | 73 | 0.1
6453411123 | KJ33453 | 07/13/2023 | 27.47 | 4 | 94 | 72 | Trace Value
6453411123 | KJ33453 | 07/14/2023 | 29.25 | 4.2 | 95 | 73 | 0.33
6453411123 | KJ33453 | 07/15/2023 | 32.7 | 4.64 | 96 | 73 | 0.12
6453411123 | KJ33453 | 07/16/2023 | 33.91 | 4.8 | 96 | 74 | 0.15
6453411123 | KJ33453 | 07/17/2023 | 30.87 | 4.41 | 95 | 74 | 2.8
6453411123 | KJ33453 | 07/18/2023 | 32.66 | 4.64 | 95 | 72 | 0.22
6453411123 | KJ33453 | 07/19/2023 | 33.1 | 4.7 | 95 | 71 | 0.14
6453411123 | KJ33453 | 07/20/2023 | 31.97 | 4.55 | 96 | 73 | 0
6453411123 | KJ33453 | 07/21/2023 | 28.56 | 4.11 | 99 | 74 | 0
6453411123 | KJ33453 | 07/22/2023 | 32.04 | 4.56 | 97 | 75 | 0
6453411123 | KJ33453 | 07/23/2023 | 37.27 | 5.23 | 94 | 71 | 0.7
6453411123 | KJ33453 | 07/24/2023 | 33.65 | 4.77 | 93 | 73 | 1.12
6453411123 | KJ33453 | 07/25/2023 | 32.99 | 4.68 | 93 | 73 | 0.3
6453411123 | KJ33453 | 07/26/2023 | 32.19 | 4.58 | 92 | 73 | 0
6453411123 | KJ33453 | 07/27/2023 | 30.87 | 4.41 | 91 | 73 | 0
6453411123 | KJ33453 | 07/28/2023 | 32.3 | 4.59 | 92 | 73 | 1
6453411123 | KJ33453 | 07/29/2023 | 33.18 | 4.71 | 93 | 73 | 0.05
6453411123 | KJ33453 | 07/30/2023 | 35.85 | 5.05 | 95 | 74 | Trace Value
6453411123 | KJ33453 | 07/31/2023 | 41.75 | 5.81 | 95 | 71 | 0.74
6453411123 | KJ33453 | 08/01/2023 | 38.29 | 5.36 | 95 | 71 | 0.08
6453411123 | KJ33453 | 08/02/2023 | 35.52 | 5.01 | 93 | 74 | 0
6453411123 | KJ33453 | 08/03/2023 | 34.01 | 4.81 | 91 | 73 | 0
6453411123 | KJ33453 | 08/04/2023 | 32.22 | 4.58 | 94 | 73 | 0
6453411123 | KJ33453 | 08/05/2023 | 34.03 | 4.82 | 94 | 73 | 0.17
6453411123 | KJ33453 | 08/06/2023 | 36.21 | 5.1 | 95 | 74 | 0.66
6453411123 | KJ33453 | 08/07/2023 | 34.07 | 4.82 | 97 | 75 | 0.03
6453411123 | KJ33453 | 08/08/2023 | 33.6 | 4.76 | 99 | 75 | 0
6453411123 | KJ33453 | 08/09/2023 | 32.78 | 4.66 | 99 | 74 | 0
6453411123 | KJ33453 | 08/10/2023 | 31.6 | 4.5 | 100 | 75 | 0.16
6453411123 | KJ33453 | 08/11/2023 | 29.34 | 4.21 | 99 | 75 | 0
6453411123 | KJ33453 | 08/12/2023 | 29.31 | 4.21 | 98 | 76 | 0.25
6453411123 | KJ33453 | 08/13/2023 | 36.16 | 5.09 | 97 | 74 | 0
6453411123 | KJ33453 | 08/14/2023 | 27.25 | 3.95 | 97 | 76 | 0
6453411123 | KJ33453 | 08/15/2023 | 27.58 | 4.01 | 97 | 75 | 0
6453411123 | KJ33453 | 08/16/2023 | 28.47 | 4.12 | 96 | 73 | 0.09
6453411123 | KJ33453 | 08/17/2023 | 29.38 | 4.24 | 93 | 72 | 0.36
6453411123 | KJ33453 | 08/18/2023 | 31.17 | 4.47 | 93 | 73 | 1.09
6453411123 | KJ33453 | 08/19/2023 | 31.23 | 4.48 | 93 | 72 | 0.69
6453411123 | KJ33453 | 08/20/2023 | 31.28 | 4.48 | 92 | 75 | 0
6453411123 | KJ33453 | 08/21/2023 | 29.11 | 4.21 | 92 | 74 | 0
6453411123 | KJ33453 | 08/22/2023 | 29.41 | 4.24 | 93 | 72 | 0
6453411123 | KJ33453 | 08/23/2023 | 26.7 | 3.9 | 93 | 74 | 0
6453411123 | KJ33453 | 08/24/2023 | 26.87 | 3.92 | 93 | 74 | 0.99
6453411123 | KJ33453 | 08/25/2023 | 25.91 | 3.8 | 92 | 71 | 0
6453411123 | KJ33453 | 08/26/2023 | 26.92 | 3.93 | 95 | 73 | 0
6453411123 | KJ33453 | 08/27/2023 | 27.05 | 3.94 | 95 | 72
6453411123 | KJ33453 | 08/28/2023 | 24.97 | 3.68 | 96 | 74 | Trace Value
6453411123 | KJ33453 | 08/29/2023 | 26.64 | 3.89 | 95 | 74 | 0
6453411123 | KJ33453 | 08/30/2023 | 30.53 | 4.39 | 94 | 74 | 0.93
6453411123 | KJ33453 | 08/31/2023 | 28.8 | 4.17 | 94 | 74 | 0.05
6453411123 | KJ33453 | 09/01/2023 | 28.77 | 4.16 | 92 | 73 | 0
6453411123 | KJ33453 | 09/02/2023 | 28.27 | 4.1 | 91 | 72
6453411123 | KJ33453 | 09/03/2023 | 27.4 | 3.99 | 92 | 71 | 0.05
6453411123 | KJ33453 | 09/04/2023 | 27.08 | 3.95 | 90 | 68 | 0
6453411123 | KJ33453 | 09/05/2023 | 26.88 | 3.92 | 90 | 64 | 0
6453411123 | KJ33453 | 09/06/2023 | 25.68 | 3.77 | 94 | 69 | 0
6453411123 | KJ33453 | 09/07/2023 | 25.24 | 3.71 | 95 | 70
6453411123 | KJ33453 | 09/08/2023 | 35.85 | 5.07 | 95 | 69 | 0
6453411123 | KJ33453 | 09/09/2023 | 36.21 | 5.12 | 94 | 64 | 0.48
6453411123 | KJ33453 | 09/10/2023 | 35.16 | 4.98 | 93 | 71 | Trace Value
6453411123 | KJ33453 | 09/11/2023 | 33.06 | 4.71 | 92 | 72 | 0
6453411123 | KJ33453 | 09/12/2023 | 45.54 | 6.31 | 92 | 71 | Trace Value
6453411123 | KJ33453 | 09/13/2023 | 48.73 | 6.72 | 92 | 72 | 0.03
6453411123 | KJ33453 | 09/14/2023 | 41.72 | 5.85 | 91 | 71 | 0.29
6453411123 | KJ33453 | 09/15/2023 | 36.92 | 5.23 | 88 | 70 | 0
6453411123 | KJ33453 | 09/16/2023 | 36.57 | 5.19 | 87 | 69 | 0.54
6453411123 | KJ33453 | 09/17/2023 | 35.54 | 5.05 | 92 | 70 | 0
6453411123 | KJ33453 | 09/18/2023 | 31.78 | 4.57 | 89 | 68 | 0.08
6453411123 | KJ33453 | 09/19/2023 | 32.37 | 4.64 | 88 | 64 | 0
6453411123 | KJ33453 | 09/20/2023 | 31.24 | 4.5 | 88 | 69 | 0
6453411123 | KJ33453 | 09/21/2023 | 30.32 | 4.38 | 87 | 68 | 0.08
6453411123 | KJ33453 | 09/22/2023 | 30.38 | 4.39 | 85 | 65 | 0.3
6453411123 | KJ33453 | 09/23/2023 | 30.68 | 4.43 | 87 | 61 | 0
6453411123 | KJ33453 | 09/24/2023 | 31.56 | 4.54 | 89 | 59 | 0
6453411123 | KJ33453 | 09/25/2023 | 35.16 | 5 | 90 | 66 | 0
6453411123 | KJ33453 | 09/26/2023 | 59.44 | 8.13 | 89 | 71 | 2.11
6453411123 | KJ33453 | 09/27/2023 | 67.03 | 9.1 | 88 | 71 | 0.91
6453411123 | KJ33453 | 09/28/2023 | 65.8 | 8.95 | 87 | 71 | 0.81
6453411123 | KJ33453 | 09/29/2023 | 64.22 | 8.74 | 85 | 71 | 0.02
6453411123 | KJ33453 | 09/30/2023 | 78.28 | 10.55 | 85 | 71 | 0.2
6453411123 | KJ33453 | 10/01/2023 | 99.31 | 13.26 | 85 | 70 | 2.53
6453411123 | KJ33453 | 10/02/2023 | 69.87 | 9.47 | 85 | 69 | 0.56
6453411123 | KJ33453 | 10/03/2023 | 56.4 | 7.74 | 85 | 70 | 0
6453411123 | KJ33453 | 10/04/2023 | 48.27 | 6.69 | 86 | 70 | 0.05
6453411123 | KJ33453 | 10/05/2023 | 46.66 | 6.48 | 86 | 69 | 0
6453411123 | KJ33453 | 10/06/2023 | 45.15 | 6.29 | 87 | 66 | 0
6453411123 | KJ33453 | 10/07/2023 | 42.81 | 5.99 | 90 | 56 | 0
6453411123 | KJ33453 | 10/08/2023 | 42.65 | 5.97 | 82 | 53 | 0
6453411123 | KJ33453 | 10/09/2023 | 38.26 | 5.4 | 80 | 55 | 0
6453411123 | KJ33453 | 10/10/2023 | 39.67 | 5.58 | 84 | 56 | 0
6453411123 | KJ33453 | 10/11/2023 | 38.99 | 5.5 | 84 | 65 | 0
6453411123 | KJ33453 | 10/12/2023 | 138.19 | 18.26 | 88 | 72 | 2.8
6453411123 | KJ33453 | 10/13/2023 | 78.81 | 10.62 | 89 | 68 | 1.67
6453411123 | KJ33453 | 10/14/2023 | 58.54 | 7.99 | 89 | 64 | 0
6453411123 | KJ33453 | 10/15/2023 | 53.28 | 7.31 | 82 | 55 | 0
6453411123 | KJ33453 | 10/16/2023 | 49.27 | 6.8 | 76 | 50 | 0
6453411123 | KJ33453 | 10/17/2023 | 44.96 | 6.24 | 75 | 49 | 0
6453411123 | KJ33453 | 10/18/2023 | 47.28 | 6.54 | 77 | 50 | 0
6453411123 | KJ33453 | 10/19/2023 | 43.46 | 6.05 | 81 | 55 | 0
6453411123 | KJ33453 | 10/20/2023 | 38.22 | 5.38 | 83 | 55 | 0
6453411123 | KJ33453 | 10/21/2023 | 42.06 | 5.87 | 83 | 55 | 0
6453411123 | KJ33453 | 10/22/2023 | 39.93 | 5.6 | 86 | 52 | 0
6453411123 | KJ33453 | 10/23/2023 | 37 | 5.22 | 83 | 58 | 0
6453411123 | KJ33453 | 10/24/2023 | 36.79 | 5.19 | 82 | 67 | 0
6453411123 | KJ33453 | 10/25/2023 | 34.85 | 4.94 | 82 | 68 | 0
6453411123 | KJ33453 | 10/26/2023 | 34.13 | 4.85 | 82 | 65 | 0
6453411123 | KJ33453 | 10/27/2023 | 34.24 | 4.87 | 83 | 64 | 0
6453411123 | KJ33453 | 10/28/2023 | 34.22 | 4.86 | 84 | 62 | 0
6453411123 | KJ33453 | 10/29/2023 | 34.62 | 4.92 | 84 | 61 | 0
6453411123 | KJ33453 | 10/30/2023 | 32.5 | 4.64 | 85 | 60 | 0
6453411123 | KJ33453 | 10/31/2023 | 33.04 | 4.71 | 84 | 58 | 0
6453411123 | KJ33453 | 11/01/2023 | 33.19 | 4.73 | 76 | 53 | 0
6453411123 | KJ33453 | 11/02/2023 | 32.6 | 4.66 | 75 | 53 | 0
6453411123 | KJ33453 | 11/03/2023 | 32.11 | 4.59 | 79 | 59 | 0
6453411123 | KJ33453 | 11/04/2023 | 33.17 | 4.73 | 79 | 55 | 0
6453411123 | KJ33453 | 11/05/2023 | 35.08 | 4.97 | 80 | 51 | 0
6453411123 | KJ33453 | 11/06/2023 | 30.52 | 4.39 | 81 | 48 | 0
6453411123 | KJ33453 | 11/07/2023 | 30.72 | 4.41 | 83 | 53 | 0
6453411123 | KJ33453 | 11/08/2023 | 31.42 | 4.5 | 84 | 50 | 0
6453411123 | KJ33453 | 11/09/2023 | 30.2 | 4.35 | 85 | 55 | 0
6453411123 | KJ33453 | 11/10/2023 | 29.65 | 4.28 | 86 | 60 | 0
6453411123 | KJ33453 | 11/11/2023 | 31.32 | 4.49 | 83 | 65 | 0.33
6453411123 | KJ33453 | 11/12/2023 | 41.02 | 5.74 | 80 | 63 | 0
6453411123 | KJ33453 | 11/13/2023 | 30.29 | 4.36 | 77 | 62 | 0
6453411123 | KJ33453 | 11/14/2023 | 31.06 | 4.48 | 77 | 61 | 0.12
6453411123 | KJ33453 | 11/15/2023 | 31.41 | 4.52 | 77 | 64 | 0.05
6453411123 | KJ33453 | 11/16/2023 | 37.02 | 5.25 | 78 | 62 | 0.16
6453411123 | KJ33453 | 11/17/2023 | 68.62 | 9.32 | 79 | 61 | 2.1
6453411123 | KJ33453 | 11/18/2023 | 51.3 | 7.09 | 78 | 55 | 0.66
6453411123 | KJ33453 | 11/19/2023 | 45.03 | 6.28 | 80 | 56 | 0
6453411123 | KJ33453 | 11/20/2023 | 40.05 | 5.64 | 79 | 59 | 0.02
6453411123 | KJ33453 | 11/21/2023 | 38.64 | 5.46 | 81 | 52 | 0.02
6453411123 | KJ33453 | 11/22/2023 | 39.84 | 5.61 | 81 | 47 | 0
6453411123 | KJ33453 | 11/23/2023 | 41.78 | 5.86 | 73 | 48 | 0.01
6453411123 | KJ33453 | 11/24/2023 | 39.28 | 5.54 | 75 | 52 | 0.01
6453411123 | KJ33453 | 11/25/2023 | 38.4 | 5.42 | 75 | 53 | 0.07
6453411123 | KJ33453 | 11/26/2023 | 41.48 | 5.82 | 75 | 55 | 0.01
6453411123 | KJ33453 | 11/27/2023 | 40.32 | 5.67 | 74 | 44 | 0.55
6453411123 | KJ33453 | 11/28/2023 | 40.39 | 5.68 | 69 | 39 | 0
6453411123 | KJ33453 | 11/29/2023 | 38.22 | 5.4 | 68 | 36 | 0
6453411123 | KJ33453 | 11/30/2023 | 36.69 | 5.2 | 86 | 41 | 0
6453411123 | KJ33453 | 12/01/2023 | 35.03 | 4.99 | 82 | 55 | 0
6453411123 | KJ33453 | 12/02/2023 | 34.67 | 4.95 | 83 | 64 | 0
6453411123 | KJ33453 | 12/03/2023 | 37.95 | 5.37 | 82 | 62 | 0.02
6453411123 | KJ33453 | 12/04/2023 | 36.85 | 5.23 | 79 | 51 | 0.23
6453411123 | KJ33453 | 12/05/2023 | 36.78 | 5.22 | 72 | 47 | 0
6453411123 | KJ33453 | 12/06/2023 | 36.55 | 5.19 | 69 | 41 | 0
6453411123 | KJ33453 | 12/07/2023 | 35.82 | 5.09 | 67 | 41 | 0
6453411123 | KJ33453 | 12/08/2023 | 34.74 | 4.95 | 74 | 47 | 0
6453411123 | KJ33453 | 12/09/2023 | 33.78 | 4.83 | 82 | 56 | 0.04
6453411123 | KJ33453 | 12/10/2023 | 34.65 | 4.94 | 83 | 44 | 0
6453411123 | KJ33453 | 12/11/2023 | 44.14 | 6.16 | 67 | 43 | 0.25
6453411123 | KJ33453 | 12/12/2023 | 33.4 | 4.78 | 71 | 43 | 0
6453411123 | KJ33453 | 12/13/2023 | 34.16 | 4.82 | 73 | 58 | 0
6453411123 | KJ33453 | 12/14/2023 | 37.84 | 5.3 | 72 | 59 | 0.66
6453411123 | KJ33453 | 12/15/2023 | 36.73 | 5.15 | 72 | 60 | 0.07
6453411123 | KJ33453 | 12/16/2023 | 43.54 | 6.03 | 73 | 58 | 0.11
6453411123 | KJ33453 | 12/17/2023 | 103.1 | 13.65 | 74 | 48 | 4.04
6453411123 | KJ33453 | 12/18/2023 | 56.17 | 7.64 | 68 | 40 | 0.05
6453411123 | KJ33453 | 12/19/2023 | 52.98 | 7.23 | 65 | 41 | 0
6453411123 | KJ33453 | 12/20/2023 | 48.71 | 6.69 | 66 | 44 | 0
6453411123 | KJ33453 | 12/21/2023 | 46.35 | 6.38 | 68 | 46 | 0
6453411123 | KJ33453 | 12/22/2023 | 43.48 | 6.02 | 70 | 49 | 0
6453411123 | KJ33453 | 12/23/2023 | 42.64 | 5.91 | 73 | 53 | 0
6453411123 | KJ33453 | 12/24/2023 | 41.77 | 5.8 | 73 | 53 | 0
6453411123 | KJ33453 | 12/25/2023 | 40.47 | 5.63 | 73 | 60 | 0.09
6453411123 | KJ33453 | 12/26/2023 | 40.24 | 5.6 | 74 | 54 | 0.1
6453411123 | KJ33453 | 12/27/2023 | 39.81 | 5.55 | 71 | 49 | 0
6453411123 | KJ33453 | 12/28/2023 | 40.86 | 5.68 | 66 | 44 | 0.04
6453411123 | KJ33453 | 12/29/2023 | 41.34 | 5.74 | 55 | 46 | 0
6453411123 | KJ33453 | 12/30/2023 | 41.16 | 5.72 | 59 | 37 | 0
6453411123 | KJ33453 | 12/31/2023 | 42.11 | 5.84 | 63 | 36 | 0
|  | Yearly Daily Average: | 34.1387 | 4.8567
|  | Yearly Daily Average (Less Spike Events): | 31.3861 | 4.5016
|  | Spike Event Daily Average: | 51.8902 | 7.1465
|  | Dryer Months' Daily Average (Less Spikes): | 29.938 | 4.3588
|  | Wetter Months' Daily Average (Less Spikes): | 35.3216 | 5.8484
|  | Wetter Months' Daily Average: | 41.8439 | 5.8484

## 57-4
Daily Billed Information (PS 57-4 - 122 Universal Trail: 2023 Reading Data)
Bill Account | Meter Number | Date | Consumption Recorded (kWh/day) | Estimated Cost ($/day) | Avg. High Temperature (°F) | Avg. Low Temperature (°F) | Rain Recorded by NOAA (inches)
6028032529 | KNJ7680 | 01/01/2023 | 277.94 | 31.27 | 79 | 58 | 0.04
6028032529 | KNJ7680 | 01/02/2023 | 285.25 | 32.07 | 78 | 53 | 0
6028032529 | KNJ7680 | 01/03/2023 | 268.41 | 30.23 | 81 | 51 | 0
6028032529 | KNJ7680 | 01/04/2023 | 322.73 | 36.15 | 83 | 57 | 0
6028032529 | KNJ7680 | 01/05/2023 | 270.97 | 30.51 | 77 | 46 | 0.04
6028032529 | KNJ7680 | 01/06/2023 | 261.38 | 32 | 68 | 41 | 0
6028032529 | KNJ7680 | 01/07/2023 | 271.97 | 33.25 | 70 | 38 | 0
6028032529 | KNJ7680 | 01/08/2023 | 294.51 | 35.92 | 76 | 42 | 0
6028032529 | KNJ7680 | 01/09/2023 | 270.39 | 33.07 | 74 | 47 | 0
6028032529 | KNJ7680 | 01/10/2023 | 265.95 | 32.54 | 71 | 42 | 0
6028032529 | KNJ7680 | 01/11/2023 | 267.95 | 32.78 | 73 | 38 | 0
6028032529 | KNJ7680 | 01/12/2023 | 268.48 | 32.84 | 80 | 44 | 0
6028032529 | KNJ7680 | 01/13/2023 | 266.14 | 32.56 | 71 | 35 | 0.12
6028032529 | KNJ7680 | 01/14/2023 | 277.32 | 33.89 | 61 | 30 | 0
6028032529 | KNJ7680 | 01/15/2023 | 277.37 | 33.89 | 63 | 30 | 0
6028032529 | KNJ7680 | 01/16/2023 | 280.09 | 34.22 | 71 | 30 | 0
6028032529 | KNJ7680 | 01/17/2023 | 261.14 | 31.97 | 75 | 34 | 0
6028032529 | KNJ7680 | 01/18/2023 | 256.75 | 31.45 | 79 | 46 | N/A
6028032529 | KNJ7680 | 01/19/2023 | 258.76 | 31.69 | 82 | 54 | 0
6028032529 | KNJ7680 | 01/20/2023 | 254.09 | 31.13 | 76 | 49 | 0
6028032529 | KNJ7680 | 01/21/2023 | 266.01 | 32.55 | 76 | 47 | T
6028032529 | KNJ7680 | 01/22/2023 | 313.15 | 38.13 | 82 | 54 | 0.33
6028032529 | KNJ7680 | 01/23/2023 | 271.99 | 33.26 | 75 | 44 | 0.05
6028032529 | KNJ7680 | 01/24/2023 | 266.82 | 32.64 | 76 | 41 | 0
6028032529 | KNJ7680 | 01/25/2023 | 264.02 | 32.31 | 85 | 43 | 0
6028032529 | KNJ7680 | 01/26/2023 | 265.59 | 32.5 | 72 | 38 | 0.09
6028032529 | KNJ7680 | 01/27/2023 | 258.06 | 31.6 | 62 | 37 | 0
6028032529 | KNJ7680 | 01/28/2023 | 266.31 | 32.58 | 69 | 35 | 0
6028032529 | KNJ7680 | 01/29/2023 | 284.33 | 34.72 | 78 | 55 | 0
6028032529 | KNJ7680 | 01/30/2023 | 269.5 | 32.96 | 86 | 58 | 0
6028032529 | KNJ7680 | 01/31/2023 | 265.64 | 32.5 | 83 | 59 | 0
6028032529 | KNJ7680 | 02/01/2023 | 269.66 | 32.98 | 82 | 58 | 0
6028032529 | KNJ7680 | 02/02/2023 | 304.52 | 37.11 | 82 | 57 | 0
6028032529 | KNJ7680 | 02/03/2023 | 270.98 | 33.14 | 78 | 50 | 0
6028032529 | KNJ7680 | 02/04/2023 | 279.47 | 32.61 | 70 | 47 | 0.17
6028032529 | KNJ7680 | 02/05/2023 | 305.8 | 35.59 | 73 | 48 | 0
6028032529 | KNJ7680 | 02/06/2023 | 275.04 | 32.11 | 71 | 46 | 0.01
6028032529 | KNJ7680 | 02/07/2023 | 268.27 | 31.35 | 76 | 44
6028032529 | KNJ7680 | 02/08/2023 | 272.55 | 31.83 | 79 | 49 | 0
6028032529 | KNJ7680 | 02/09/2023 | 269.81 | 31.52 | 83 | 58 | 0
6028032529 | KNJ7680 | 02/10/2023 | 276.32 | 32.26 | 85 | 46 | 0.16
6028032529 | KNJ7680 | 02/11/2023 | 292.24 | 34.06 | 79 | 40 | 0.57
6028032529 | KNJ7680 | 02/12/2023 | 313.7 | 36.49 | 71 | 40 | 0.12
6028032529 | KNJ7680 | 02/13/2023 | 278.13 | 32.46 | 71 | 40 | Trace Value
6028032529 | KNJ7680 | 02/14/2023 | 272.44 | 31.82 | 75 | 39 | 0
6028032529 | KNJ7680 | 02/15/2023 | 258.35 | 30.22 | 82 | 50 | 0
6028032529 | KNJ7680 | 02/16/2023 | 273.1 | 31.89 | 85 | 57 | 0
6028032529 | KNJ7680 | 02/17/2023 | 263.33 | 30.79 | 89 | 45
6028032529 | KNJ7680 | 02/18/2023 | 276.73 | 32.3 | 67 | 46 | 0.04
6028032529 | KNJ7680 | 02/19/2023 | 283.84 | 33.11 | 80 | 48 | 0
6028032529 | KNJ7680 | 02/20/2023 | 272.33 | 31.81 | 82 | 53 | 0
6028032529 | KNJ7680 | 02/21/2023 | 262.23 | 30.66 | 85 | 57 | 0
6028032529 | KNJ7680 | 02/22/2023 | 267.21 | 31.23 | 87 | 58 | 0
6028032529 | KNJ7680 | 02/23/2023 | 265.62 | 31.05 | 89 | 60 | 0
6028032529 | KNJ7680 | 02/24/2023 | 257.11 | 30.08 | 87 | 58 | 0
6028032529 | KNJ7680 | 02/25/2023 | 269.85 | 31.53 | 87 | 58
6028032529 | KNJ7680 | 02/26/2023 | 290.41 | 33.85 | 87 | 56 | 0
6028032529 | KNJ7680 | 02/27/2023 | 265.61 | 31.05 | 87 | 57 | 0
6028032529 | KNJ7680 | 02/28/2023 | 250.96 | 29.39 | 87 | 57 | 0
6028032529 | KNJ7680 | 03/01/2023 | 258.08 | 30.19 | 86 | 58 | 0
6028032529 | KNJ7680 | 03/02/2023 | 260.44 | 30.46 | 87 | 56 | 0
6028032529 | KNJ7680 | 03/03/2023 | 255.52 | 29.9 | 90 | 55 | 0
6028032529 | KNJ7680 | 03/04/2023 | 274.51 | 32.05 | 88 | 52 | 0
6028032529 | KNJ7680 | 03/05/2023 | 330.22 | 38.36 | 81 | 54 | 0.05
6028032529 | KNJ7680 | 03/06/2023 | 262.85 | 30.73 | 84 | 56 | 0
6028032529 | KNJ7680 | 03/07/2023 | 257.77 | 29.68 | 87 | 56
6028032529 | KNJ7680 | 03/08/2023 | 257.72 | 29.67 | 85 | 58 | 0
6028032529 | KNJ7680 | 03/09/2023 | 250.67 | 28.89 | 80 | 51 | 0
6028032529 | KNJ7680 | 03/10/2023 | 260.47 | 29.98 | 85 | 54
6028032529 | KNJ7680 | 03/11/2023 | 271.22 | 31.17 | 81 | 51 | 1.3
6028032529 | KNJ7680 | 03/12/2023 | 272.16 | 31.27 | 86 | 48 | 0
6028032529 | KNJ7680 | 03/13/2023 | 287.7 | 33 | 81 | 46 | 1.17
6028032529 | KNJ7680 | 03/14/2023 | 278.75 | 32 | 70 | 43 | 0.6
6028032529 | KNJ7680 | 03/15/2023 | 272.96 | 31.36 | 68 | 43 | 0
6028032529 | KNJ7680 | 03/16/2023 | 268.23 | 30.84 | 77 | 37 | 0
6028032529 | KNJ7680 | 03/17/2023 | 261.98 | 30.14 | 84 | 48
6028032529 | KNJ7680 | 03/18/2023 | 266.17 | 30.61 | 80 | 45 | 0
6028032529 | KNJ7680 | 03/19/2023 | 267.51 | 30.76 | 68 | 43 | 0.02
6028032529 | KNJ7680 | 03/20/2023 | 254.24 | 29.29 | 69 | 42 | 0.02
6028032529 | KNJ7680 | 03/21/2023 | 252.54 | 29.1 | 77 | 42 | 0
6028032529 | KNJ7680 | 03/22/2023 | 257.97 | 29.7 | 80 | 53 | 0.08
6028032529 | KNJ7680 | 03/23/2023 | 255.3 | 29.4 | 83 | 53
6028032529 | KNJ7680 | 03/24/2023 | 255.01 | 29.37 | 86 | 53 | 0
6028032529 | KNJ7680 | 03/25/2023 | 260.46 | 29.98 | 91 | 60 | 0
6028032529 | KNJ7680 | 03/26/2023 | 279.96 | 32.14 | 91 | 63 | 0.68
6028032529 | KNJ7680 | 03/27/2023 | 255.67 | 29.44 | 92 | 62 | 0
6028032529 | KNJ7680 | 03/28/2023 | 251.54 | 28.99 | 88 | 55 | Trace Value
6028032529 | KNJ7680 | 03/29/2023 | 247.77 | 28.57 | 75 | 55 | 0
6028032529 | KNJ7680 | 03/30/2023 | 248.28 | 28.62 | 79 | 51 | 0
6028032529 | KNJ7680 | 03/31/2023 | 244.46 | 28.2 | 85 | 55 | 0
6028032529 | KNJ7680 | 04/01/2023 | 255.06 | 29.38 | 90 | 60 | 0
6028032529 | KNJ7680 | 04/02/2023 | 273.48 | 31.42 | 85 | 60
6028032529 | KNJ7680 | 04/03/2023 | 253.16 | 29.17 | 86 | 61 | 0
6028032529 | KNJ7680 | 04/04/2023 | 288.81 | 33.12 | 88 | 60 | Trace Value
6028032529 | KNJ7680 | 04/05/2023 | 242.09 | 27.94 | 87 | 63 | 0
6028032529 | KNJ7680 | 04/06/2023 | 245.09 | 27.71 | 87 | 64 | 0
6028032529 | KNJ7680 | 04/07/2023 | 245.43 | 27.75 | 85 | 64
6028032529 | KNJ7680 | 04/08/2023 | 259.05 | 29.23 | 86 | 62
6028032529 | KNJ7680 | 04/09/2023 | 271.82 | 30.62 | 80 | 60 | 0.01
6028032529 | KNJ7680 | 04/10/2023 | 298.74 | 33.54 | 79 | 58 | 0.68
6028032529 | KNJ7680 | 04/11/2023 | 294.81 | 33.11 | 78 | 58 | 1.38
6028032529 | KNJ7680 | 04/12/2023 | 279.2 | 31.42 | 79 | 59 | 0.03
6028032529 | KNJ7680 | 04/13/2023 | 280.52 | 31.56 | 87 | 61 | 0.07
6028032529 | KNJ7680 | 04/14/2023 | 290.68 | 32.67 | 86 | 59 | 0.57
6028032529 | KNJ7680 | 04/15/2023 | 295.32 | 33.17 | 87 | 60 | 0.02
6028032529 | KNJ7680 | 04/16/2023 | 300.01 | 33.68 | 88 | 59 | 0
6028032529 | KNJ7680 | 04/17/2023 | 267.82 | 30.18 | 81 | 50 | 0.04
6028032529 | KNJ7680 | 04/18/2023 | 270.35 | 30.46 | 81 | 46 | 0.02
6028032529 | KNJ7680 | 04/19/2023 | 266.19 | 30.01 | 82 | 50 | 0
6028032529 | KNJ7680 | 04/20/2023 | 261.6 | 29.51 | 84 | 55 | 0
6028032529 | KNJ7680 | 04/21/2023 | 259.69 | 29.3 | 87 | 59
6028032529 | KNJ7680 | 04/22/2023 | 267.35 | 30.13 | 89 | 57 | 0.3
6028032529 | KNJ7680 | 04/23/2023 | 288.74 | 32.45 | 84 | 53 | 0.42
6028032529 | KNJ7680 | 04/24/2023 | 267.86 | 30.19 | 80 | 55 | 0
6028032529 | KNJ7680 | 04/25/2023 | 272.2 | 30.66 | 82 | 61 | 0.25
6028032529 | KNJ7680 | 04/26/2023 | 263.18 | 29.68 | 84 | 62 | 0.07
6028032529 | KNJ7680 | 04/27/2023 | 283.8 | 31.92 | 86 | 63 | 0
6028032529 | KNJ7680 | 04/28/2023 | 319.49 | 35.79 | 87 | 62 | 1.62
6028032529 | KNJ7680 | 04/29/2023 | 308.53 | 34.6 | 88 | 62 | 0
6028032529 | KNJ7680 | 04/30/2023 | 334.8 | 37.46 | 85 | 57 | 0.52
6028032529 | KNJ7680 | 05/01/2023 | 293.45 | 32.97 | 85 | 56 | 0
6028032529 | KNJ7680 | 05/02/2023 | 288.9 | 32.47 | 87 | 56 | 0
6028032529 | KNJ7680 | 05/03/2023 | 326.57 | 36.56 | 86 | 53 | 0
6028032529 | KNJ7680 | 05/04/2023 | 270.93 | 30.52 | 84 | 53 | 0
6028032529 | KNJ7680 | 05/05/2023 | 264.22 | 30.74 | 87 | 57 | 0
6028032529 | KNJ7680 | 05/06/2023 | 274.65 | 31.91 | 86 | 65 | 0
6028032529 | KNJ7680 | 05/07/2023 | 295.12 | 34.21 | 88 | 61 | 0.02
6028032529 | KNJ7680 | 05/08/2023 | 278.36 | 32.33 | 87 | 55 | 0
6028032529 | KNJ7680 | 05/09/2023 | 270.05 | 31.39 | 91 | 63 | 0
6028032529 | KNJ7680 | 05/10/2023 | 267.59 | 31.12 | 92 | 66 | 0
6028032529 | KNJ7680 | 05/11/2023 | 260.38 | 30.31 | 88 | 67 | 0.04
6028032529 | KNJ7680 | 05/12/2023 | 259.49 | 30.21 | 86 | 66 | 0
6028032529 | KNJ7680 | 05/13/2023 | 273.66 | 31.8 | 85 | 64 | 0
6028032529 | KNJ7680 | 05/14/2023 | 280.85 | 32.61 | 86 | 63 | 0
6028032529 | KNJ7680 | 05/15/2023 | 264.37 | 30.76 | 89 | 62 | 0
6028032529 | KNJ7680 | 05/16/2023 | 261.21 | 30.4 | 88 | 64 | 0
6028032529 | KNJ7680 | 05/17/2023 | 262.71 | 30.57 | 92 | 67 | 0
6028032529 | KNJ7680 | 05/18/2023 | 260.55 | 30.33 | 89 | 65 | 1.24
6028032529 | KNJ7680 | 05/19/2023 | 255.65 | 29.77 | 88 | 66 | 0.02
6028032529 | KNJ7680 | 05/20/2023 | 264.18 | 30.73 | 88 | 66 | 0
6028032529 | KNJ7680 | 05/21/2023 | 286.62 | 33.26 | 88 | 67
6028032529 | KNJ7680 | 05/22/2023 | 314.61 | 36.41 | 88 | 67 | 0.65
6028032529 | KNJ7680 | 05/23/2023 | 299.16 | 34.67 | 85 | 67 | 0.56
6028032529 | KNJ7680 | 05/24/2023 | 286.63 | 33.26 | 83 | 66 | 0.12
6028032529 | KNJ7680 | 05/25/2023 | 283.87 | 32.95 | 83 | 66 | 0.16
6028032529 | KNJ7680 | 05/26/2023 | 295.43 | 34.25 | 82 | 62 | 0.05
6028032529 | KNJ7680 | 05/27/2023 | 300.55 | 34.82 | 81 | 56 | Trace Value
6028032529 | KNJ7680 | 05/28/2023 | 288.89 | 33.51 | 85 | 55 | 0
6028032529 | KNJ7680 | 05/29/2023 | 305.59 | 35.39 | 87 | 60 | 0
6028032529 | KNJ7680 | 05/30/2023 | 283.38 | 32.89 | 88 | 62 | 0
6028032529 | KNJ7680 | 05/31/2023 | 275.86 | 32.05 | 87 | 68 | 0
6028032529 | KNJ7680 | 06/01/2023 | 274.97 | 31.95 | 85 | 68 | 0
6028032529 | KNJ7680 | 06/02/2023 | 268.26 | 31.19 | 85 | 67 | 0
6028032529 | KNJ7680 | 06/03/2023 | 275.74 | 32.03 | 84 | 67 | 0
6028032529 | KNJ7680 | 06/04/2023 | 352.38 | 40.65 | 84 | 66 | 0
6028032529 | KNJ7680 | 06/05/2023 | 271.23 | 31.53 | 84 | 64 | 0.3
6028032529 | KNJ7680 | 06/06/2023 | 261.27 | 26.59 | 88 | 62
6028032529 | KNJ7680 | 06/07/2023 | 289.08 | 29.31 | 91 | 68 | 0
6028032529 | KNJ7680 | 06/08/2023 | 299.46 | 30.33 | 92 | 68 | 1.64
6028032529 | KNJ7680 | 06/09/2023 | 296.07 | 29.99 | 92 | 68 | 0
6028032529 | KNJ7680 | 06/10/2023 | 310.71 | 31.42 | 88 | 67 | 0.54
6028032529 | KNJ7680 | 06/11/2023 | 305.62 | 30.93 | 91 | 69 | 0.09
6028032529 | KNJ7680 | 06/12/2023 | 290.46 | 29.45 | 94 | 69 | 0
6028032529 | KNJ7680 | 06/13/2023 | 275.49 | 27.98 | 95 | 71
6028032529 | KNJ7680 | 06/14/2023 | 283.16 | 28.73 | 95 | 71 | 0
6028032529 | KNJ7680 | 06/15/2023 | 280.6 | 28.48 | 95 | 66 | 0.44
6028032529 | KNJ7680 | 06/16/2023 | 294.69 | 29.86 | 95 | 68 | 0.45
6028032529 | KNJ7680 | 06/17/2023 | 300.05 | 30.38 | 93 | 68 | 0.91
6028032529 | KNJ7680 | 06/18/2023 | 309.38 | 31.29 | 94 | 68 | 0.28
6028032529 | KNJ7680 | 06/19/2023 | 300.32 | 30.41 | 93 | 70 | 0.63
6028032529 | KNJ7680 | 06/20/2023 | 296.86 | 30.07 | 91 | 69 | 0.46
6028032529 | KNJ7680 | 06/21/2023 | 295.16 | 29.91 | 91 | 71 | 0.24
6028032529 | KNJ7680 | 06/22/2023 | 291.48 | 29.55 | 93 | 66 | 0.04
6028032529 | KNJ7680 | 06/23/2023 | 320.43 | 32.37 | 91 | 69 | 0.35
6028032529 | KNJ7680 | 06/24/2023 | 325.81 | 32.9 | 92 | 70 | 0.24
6028032529 | KNJ7680 | 06/25/2023 | 317.6 | 32.1 | 91 | 70 | 0.15
6028032529 | KNJ7680 | 06/26/2023 | 285.92 | 29 | 94 | 70 | 0
6028032529 | KNJ7680 | 06/27/2023 | 281.45 | 28.57 | 97 | 71 | 0
6028032529 | KNJ7680 | 06/28/2023 | 290.36 | 29.44 | 95 | 72 | 0
6028032529 | KNJ7680 | 06/29/2023 | 295.35 | 29.92 | 95 | 71 | 0.88
6028032529 | KNJ7680 | 06/30/2023 | 285.62 | 28.97 | 94 | 71 | 0
6028032529 | KNJ7680 | 07/01/2023 | 284.46 | 28.86 | 94 | 71 | 0
6028032529 | KNJ7680 | 07/02/2023 | 288.32 | 29.24 | 95 | 71 | 0
6028032529 | KNJ7680 | 07/03/2023 | 281.56 | 28.58 | 97 | 72 | 0
6028032529 | KNJ7680 | 07/04/2023 | 289.7 | 29.37 | 95 | 73 | 0
6028032529 | KNJ7680 | 07/05/2023 | 347.67 | 35.04 | 95 | 74 | 0
6028032529 | KNJ7680 | 07/06/2023 | 281.52 | 28.57 | 96 | 73 | 0.04
6028032529 | KNJ7680 | 07/07/2023 | 279.47 | 32.07 | 95 | 73 | 0.03
6028032529 | KNJ7680 | 07/08/2023 | 288.84 | 33.11 | 94 | 74 | 0.31
6028032529 | KNJ7680 | 07/09/2023 | 293.61 | 33.63 | 96 | 74 | 0.2
6028032529 | KNJ7680 | 07/10/2023 | 276.78 | 31.77 | 96 | 74 | 0
6028032529 | KNJ7680 | 07/11/2023 | 285.16 | 32.7 | 94 | 73 | 0.78
6028032529 | KNJ7680 | 07/12/2023 | 292.26 | 33.48 | 94 | 73 | 0.1
6028032529 | KNJ7680 | 07/13/2023 | 292.98 | 33.56 | 94 | 72 | Trace Value
6028032529 | KNJ7680 | 07/14/2023 | 298.53 | 34.18 | 95 | 73 | 0.33
6028032529 | KNJ7680 | 07/15/2023 | 318.33 | 36.37 | 96 | 73 | 0.12
6028032529 | KNJ7680 | 07/16/2023 | 346.96 | 39.55 | 96 | 74 | 0.15
6028032529 | KNJ7680 | 07/17/2023 | 327.18 | 37.36 | 95 | 74 | 2.8
6028032529 | KNJ7680 | 07/18/2023 | 328.72 | 37.53 | 95 | 72 | 0.22
6028032529 | KNJ7680 | 07/19/2023 | 315.64 | 36.08 | 95 | 71 | 0.14
6028032529 | KNJ7680 | 07/20/2023 | 309.17 | 35.36 | 96 | 73 | 0
6028032529 | KNJ7680 | 07/21/2023 | 292.39 | 33.5 | 99 | 74 | 0
6028032529 | KNJ7680 | 07/22/2023 | 308.39 | 35.27 | 97 | 75 | 0
6028032529 | KNJ7680 | 07/23/2023 | 364.73 | 41.52 | 94 | 71 | 0.7
6028032529 | KNJ7680 | 07/24/2023 | 333.78 | 38.09 | 93 | 73 | 1.12
6028032529 | KNJ7680 | 07/25/2023 | 320.65 | 36.63 | 93 | 73 | 0.3
6028032529 | KNJ7680 | 07/26/2023 | 312.9 | 35.77 | 92 | 73 | 0
6028032529 | KNJ7680 | 07/27/2023 | 307.85 | 35.21 | 91 | 73 | 0
6028032529 | KNJ7680 | 07/28/2023 | 320.13 | 36.57 | 92 | 73 | 1
6028032529 | KNJ7680 | 07/29/2023 | 331.32 | 37.81 | 93 | 73 | 0.05
6028032529 | KNJ7680 | 07/30/2023 | 353.56 | 40.28 | 95 | 74 | Trace Value
6028032529 | KNJ7680 | 07/31/2023 | 334.97 | 38.22 | 95 | 71 | 0.74
6028032529 | KNJ7680 | 08/01/2023 | 329.18 | 37.58 | 95 | 71 | 0.08
6028032529 | KNJ7680 | 08/02/2023 | 322.23 | 36.81 | 93 | 74 | 0
6028032529 | KNJ7680 | 08/03/2023 | 345.65 | 39.4 | 91 | 73 | 0
6028032529 | KNJ7680 | 08/04/2023 | 306.96 | 35.11 | 94 | 73 | 0
6028032529 | KNJ7680 | 08/05/2023 | 376.43 | 44.17 | 94 | 73 | 0.17
6028032529 | KNJ7680 | 08/06/2023 | 371.23 | 43.57 | 95 | 74 | 0.66
6028032529 | KNJ7680 | 08/07/2023 | 343.09 | 40.35 | 97 | 75 | 0.03
6028032529 | KNJ7680 | 08/08/2023 | 321.93 | 37.92 | 99 | 75 | 0
6028032529 | KNJ7680 | 08/09/2023 | 329.74 | 38.81 | 99 | 74 | 0
6028032529 | KNJ7680 | 08/10/2023 | 328.46 | 38.67 | 100 | 75 | 0.16
6028032529 | KNJ7680 | 08/11/2023 | 318.06 | 37.48 | 99 | 75 | 0
6028032529 | KNJ7680 | 08/12/2023 | 353.46 | 41.54 | 98 | 76 | 0.25
6028032529 | KNJ7680 | 08/13/2023 | 346.52 | 40.74 | 97 | 74 | 0
6028032529 | KNJ7680 | 08/14/2023 | 335.94 | 39.53 | 97 | 76 | 0
6028032529 | KNJ7680 | 08/15/2023 | 295.29 | 34.86 | 97 | 75 | 0
6028032529 | KNJ7680 | 08/16/2023 | 370.21 | 43.46 | 96 | 73 | 0.09
6028032529 | KNJ7680 | 08/17/2023 | 378.16 | 44.37 | 93 | 72 | 0.36
6028032529 | KNJ7680 | 08/18/2023 | 380.79 | 44.67 | 93 | 73 | 1.09
6028032529 | KNJ7680 | 08/19/2023 | 374.83 | 43.99 | 93 | 72 | 0.69
6028032529 | KNJ7680 | 08/20/2023 | 370 | 43.43 | 92 | 75 | 0
6028032529 | KNJ7680 | 08/21/2023 | 337.13 | 39.66 | 92 | 74 | 0
6028032529 | KNJ7680 | 08/22/2023 | 325.41 | 38.32 | 93 | 72 | 0
6028032529 | KNJ7680 | 08/23/2023 | 308.48 | 36.38 | 93 | 74 | 0
6028032529 | KNJ7680 | 08/24/2023 | 303.34 | 35.79 | 93 | 74 | 0.99
6028032529 | KNJ7680 | 08/25/2023 | 289.22 | 34.17 | 92 | 71 | 0
6028032529 | KNJ7680 | 08/26/2023 | 300.2 | 35.43 | 95 | 73 | 0
6028032529 | KNJ7680 | 08/27/2023 | 324.07 | 38.16 | 95 | 72
6028032529 | KNJ7680 | 08/28/2023 | 294.92 | 34.82 | 96 | 74 | Trace Value
6028032529 | KNJ7680 | 08/29/2023 | 295.64 | 34.9 | 95 | 74 | 0
6028032529 | KNJ7680 | 08/30/2023 | 321.34 | 37.85 | 94 | 74 | 0.93
6028032529 | KNJ7680 | 08/31/2023 | 297.74 | 35.14 | 94 | 74 | 0.05
6028032529 | KNJ7680 | 09/01/2023 | 297.17 | 35.08 | 92 | 73 | 0
6028032529 | KNJ7680 | 09/02/2023 | 299.86 | 35.39 | 91 | 72
6028032529 | KNJ7680 | 09/03/2023 | 291.41 | 34.42 | 92 | 71 | 0.05
6028032529 | KNJ7680 | 09/04/2023 | 306.75 | 36.18 | 90 | 68 | 0
6028032529 | KNJ7680 | 09/05/2023 | 341.11 | 40.12 | 90 | 64 | 0
6028032529 | KNJ7680 | 09/06/2023 | 273.81 | 32.4 | 94 | 69 | 0
6028032529 | KNJ7680 | 09/07/2023 | 276.55 | 35.25 | 95 | 70
6028032529 | KNJ7680 | 09/08/2023 | 279.44 | 35.61 | 95 | 69 | 0
6028032529 | KNJ7680 | 09/09/2023 | 291.67 | 37.12 | 94 | 64 | 0.48
6028032529 | KNJ7680 | 09/10/2023 | 301.15 | 38.29 | 93 | 71 | Trace Value
6028032529 | KNJ7680 | 09/11/2023 | 280.33 | 35.72 | 92 | 72 | 0
6028032529 | KNJ7680 | 09/12/2023 | 282.97 | 36.05 | 92 | 71 | Trace Value
6028032529 | KNJ7680 | 09/13/2023 | 305.17 | 38.79 | 92 | 72 | 0.03
6028032529 | KNJ7680 | 09/14/2023 | 303.55 | 38.59 | 91 | 71 | 0.29
6028032529 | KNJ7680 | 09/15/2023 | 279.35 | 35.6 | 88 | 70 | 0
6028032529 | KNJ7680 | 09/16/2023 | 298.54 | 37.97 | 87 | 69 | 0.54
6028032529 | KNJ7680 | 09/17/2023 | 313.09 | 39.77 | 92 | 70 | 0
6028032529 | KNJ7680 | 09/18/2023 | 276.37 | 35.23 | 89 | 68 | 0.08
6028032529 | KNJ7680 | 09/19/2023 | 272.69 | 34.78 | 88 | 64 | 0
6028032529 | KNJ7680 | 09/20/2023 | 275.79 | 35.16 | 88 | 69 | 0
6028032529 | KNJ7680 | 09/21/2023 | 273.58 | 34.89 | 87 | 68 | 0.08
6028032529 | KNJ7680 | 09/22/2023 | 263.82 | 33.68 | 85 | 65 | 0.3
6028032529 | KNJ7680 | 09/23/2023 | 279.68 | 35.64 | 87 | 61 | 0
6028032529 | KNJ7680 | 09/24/2023 | 295.2 | 37.56 | 89 | 59 | 0
6028032529 | KNJ7680 | 09/25/2023 | 309.52 | 39.33 | 90 | 66 | 0
6028032529 | KNJ7680 | 09/26/2023 | 345.38 | 43.76 | 89 | 71 | 2.11
6028032529 | KNJ7680 | 09/27/2023 | 512.77 | 64.44 | 88 | 71 | 0.91
6028032529 | KNJ7680 | 09/28/2023 | 457.95 | 57.66 | 87 | 71 | 0.81
6028032529 | KNJ7680 | 09/29/2023 | 389.5 | 49.21 | 85 | 71 | 0.02
6028032529 | KNJ7680 | 09/30/2023 | 612.06 | 76.7 | 85 | 71 | 0.2
6028032529 | KNJ7680 | 10/01/2023 | 477.62 | 60.09 | 85 | 70 | 2.53
6028032529 | KNJ7680 | 10/02/2023 | 423.03 | 53.35 | 85 | 69 | 0.56
6028032529 | KNJ7680 | 10/03/2023 | 453.84 | 57.16 | 85 | 70 | 0
6028032529 | KNJ7680 | 10/04/2023 | 356.01 | 45.07 | 86 | 70 | 0.05
6028032529 | KNJ7680 | 10/05/2023 | 346.88 | 42.21 | 86 | 69 | 0
6028032529 | KNJ7680 | 10/06/2023 | 340.32 | 41.43 | 87 | 66 | 0
6028032529 | KNJ7680 | 10/07/2023 | 345 | 41.98 | 90 | 56 | 0
6028032529 | KNJ7680 | 10/08/2023 | 353.12 | 42.94 | 82 | 53 | 0
6028032529 | KNJ7680 | 10/09/2023 | 328.35 | 40.01 | 80 | 55 | 0
6028032529 | KNJ7680 | 10/10/2023 | 323 | 39.37 | 84 | 56 | 0
6028032529 | KNJ7680 | 10/11/2023 | 322.01 | 39.26 | 84 | 65 | 0
6028032529 | KNJ7680 | 10/12/2023 | 556.07 | 67 | 88 | 72 | 2.8
6028032529 | KNJ7680 | 10/13/2023 | 534.72 | 64.47 | 89 | 68 | 1.67
6028032529 | KNJ7680 | 10/14/2023 | 397.91 | 48.25 | 89 | 64 | 0
6028032529 | KNJ7680 | 10/15/2023 | 393.39 | 47.72 | 82 | 55 | 0
6028032529 | KNJ7680 | 10/16/2023 | 368.51 | 44.77 | 76 | 50 | 0
6028032529 | KNJ7680 | 10/17/2023 | 342.89 | 41.73 | 75 | 49 | 0
6028032529 | KNJ7680 | 10/18/2023 | 334.6 | 40.75 | 77 | 50 | 0
6028032529 | KNJ7680 | 10/19/2023 | 328.73 | 40.05 | 81 | 55 | 0
6028032529 | KNJ7680 | 10/20/2023 | 310.11 | 37.85 | 83 | 55 | 0
6028032529 | KNJ7680 | 10/21/2023 | 329.02 | 40.09 | 83 | 55 | 0
6028032529 | KNJ7680 | 10/22/2023 | 341.03 | 41.51 | 86 | 52 | 0
6028032529 | KNJ7680 | 10/23/2023 | 315.38 | 38.47 | 83 | 58 | 0
6028032529 | KNJ7680 | 10/24/2023 | 302.4 | 36.93 | 82 | 67 | 0
6028032529 | KNJ7680 | 10/25/2023 | 299.59 | 36.6 | 82 | 68 | 0
6028032529 | KNJ7680 | 10/26/2023 | 295.87 | 36.16 | 82 | 65 | 0
6028032529 | KNJ7680 | 10/27/2023 | 288.47 | 35.28 | 83 | 64 | 0
6028032529 | KNJ7680 | 10/28/2023 | 306.2 | 37.38 | 84 | 62 | 0
6028032529 | KNJ7680 | 10/29/2023 | 326.54 | 39.79 | 84 | 61 | 0
6028032529 | KNJ7680 | 10/30/2023 | 297.1 | 36.3 | 85 | 60 | 0
6028032529 | KNJ7680 | 10/31/2023 | 291.02 | 35.58 | 84 | 58 | 0
6028032529 | KNJ7680 | 11/01/2023 | 295.88 | 36.16 | 76 | 53 | 0
6028032529 | KNJ7680 | 11/02/2023 | 331.23 | 40.35 | 75 | 53 | 0
6028032529 | KNJ7680 | 11/03/2023 | 281.54 | 34.46 | 79 | 59 | 0
6028032529 | KNJ7680 | 11/04/2023 | 288.75 | 34.56 | 79 | 55 | 0
6028032529 | KNJ7680 | 11/05/2023 | 323.9 | 38.64 | 80 | 51 | 0
6028032529 | KNJ7680 | 11/06/2023 | 286.51 | 34.3 | 81 | 48 | 0
6028032529 | KNJ7680 | 11/07/2023 | 277.96 | 33.31 | 83 | 53 | 0
6028032529 | KNJ7680 | 11/08/2023 | 279.29 | 33.46 | 84 | 50 | 0
6028032529 | KNJ7680 | 11/09/2023 | 272.3 | 32.65 | 85 | 55 | 0
6028032529 | KNJ7680 | 11/10/2023 | 279.33 | 33.46 | 86 | 60 | 0
6028032529 | KNJ7680 | 11/11/2023 | 295.01 | 35.28 | 83 | 65 | 0.33
6028032529 | KNJ7680 | 11/12/2023 | 309.75 | 37 | 80 | 63 | 0
6028032529 | KNJ7680 | 11/13/2023 | 289.29 | 34.62 | 77 | 62 | 0
6028032529 | KNJ7680 | 11/14/2023 | 310.1 | 37.04 | 77 | 61 | 0.12
6028032529 | KNJ7680 | 11/15/2023 | 328.4 | 39.16 | 77 | 64 | 0.05
6028032529 | KNJ7680 | 11/16/2023 | 458.38 | 54.24 | 78 | 62 | 0.16
6028032529 | KNJ7680 | 11/17/2023 | 703.75 | 82.72 | 79 | 61 | 2.1
6028032529 | KNJ7680 | 11/18/2023 | 430.43 | 51 | 78 | 55 | 0.66
6028032529 | KNJ7680 | 11/19/2023 | 394.37 | 46.82 | 80 | 56 | 0
6028032529 | KNJ7680 | 11/20/2023 | 368.45 | 43.81 | 79 | 59 | 0.02
6028032529 | KNJ7680 | 11/21/2023 | 364.87 | 43.39 | 81 | 52 | 0.02
6028032529 | KNJ7680 | 11/22/2023 | 366.6 | 43.59 | 81 | 47 | 0
6028032529 | KNJ7680 | 11/23/2023 | 367.26 | 43.67 | 73 | 48 | 0.01
6028032529 | KNJ7680 | 11/24/2023 | 349.5 | 41.61 | 75 | 52 | 0.01
6028032529 | KNJ7680 | 11/25/2023 | 347.21 | 41.34 | 75 | 53 | 0.07
6028032529 | KNJ7680 | 11/26/2023 | 390.18 | 46.33 | 75 | 55 | 0.01
6028032529 | KNJ7680 | 11/27/2023 | 365.02 | 43.41 | 74 | 44 | 0.55
6028032529 | KNJ7680 | 11/28/2023 | 338.05 | 40.28 | 69 | 39 | 0
6028032529 | KNJ7680 | 11/29/2023 | 346.12 | 41.22 | 68 | 36 | 0
6028032529 | KNJ7680 | 11/30/2023 | 319.75 | 38.16 | 86 | 41 | 0
6028032529 | KNJ7680 | 12/01/2023 | 309.15 | 36.93 | 82 | 55 | 0
6028032529 | KNJ7680 | 12/02/2023 | 324.93 | 38.76 | 83 | 64 | 0
6028032529 | KNJ7680 | 12/03/2023 | 433.86 | 51.4 | 82 | 62 | 0.02
6028032529 | KNJ7680 | 12/04/2023 | 344.76 | 41.06 | 79 | 51 | 0.23
6028032529 | KNJ7680 | 12/05/2023 | 319.94 | 39.22 | 72 | 47 | 0
6028032529 | KNJ7680 | 12/06/2023 | 306.56 | 37.62 | 69 | 41 | 0
6028032529 | KNJ7680 | 12/07/2023 | 302.9 | 37.19 | 67 | 41 | 0
6028032529 | KNJ7680 | 12/08/2023 | 301.5 | 37.02 | 74 | 47 | 0
6028032529 | KNJ7680 | 12/09/2023 | 317.16 | 38.89 | 82 | 56 | 0.04
6028032529 | KNJ7680 | 12/10/2023 | 336.86 | 41.24 | 83 | 44 | 0
6028032529 | KNJ7680 | 12/11/2023 | 317.2 | 38.89 | 67 | 43 | 0.25
6028032529 | KNJ7680 | 12/12/2023 | 299.91 | 36.83 | 71 | 43 | 0
6028032529 | KNJ7680 | 12/13/2023 | 297.86 | 36.59 | 73 | 58 | 0
6028032529 | KNJ7680 | 12/14/2023 | 308.24 | 37.83 | 72 | 59 | 0.66
6028032529 | KNJ7680 | 12/15/2023 | 301.22 | 36.99 | 72 | 60 | 0.07
6028032529 | KNJ7680 | 12/16/2023 | 364.29 | 44.52 | 73 | 58 | 0.11
6028032529 | KNJ7680 | 12/17/2023 | 742.47 | 89.67 | 74 | 48 | 4.04
6028032529 | KNJ7680 | 12/18/2023 | 392.74 | 47.91 | 68 | 40 | 0.05
6028032529 | KNJ7680 | 12/19/2023 | 374.99 | 45.8 | 65 | 41 | 0
6028032529 | KNJ7680 | 12/20/2023 | 360.84 | 44.11 | 66 | 44 | 0
6028032529 | KNJ7680 | 12/21/2023 | 355.68 | 43.49 | 68 | 46 | 0
6028032529 | KNJ7680 | 12/22/2023 | 344.62 | 42.17 | 70 | 49 | 0
6028032529 | KNJ7680 | 12/23/2023 | 359.71 | 43.97 | 73 | 53 | 0
6028032529 | KNJ7680 | 12/24/2023 | 356.66 | 43.61 | 73 | 53 | 0
6028032529 | KNJ7680 | 12/25/2023 | 356.3 | 43.56 | 73 | 60 | 0.09
6028032529 | KNJ7680 | 12/26/2023 | 352.67 | 43.13 | 74 | 54 | 0.1
6028032529 | KNJ7680 | 12/27/2023 | 341.4 | 41.78 | 71 | 49 | 0
6028032529 | KNJ7680 | 12/28/2023 | 344.58 | 42.16 | 66 | 44 | 0.04
6028032529 | KNJ7680 | 12/29/2023 | 333.91 | 40.89 | 55 | 46 | 0
6028032529 | KNJ7680 | 12/30/2023 | 330.1 | 40.44 | 59 | 37 | 0
6028032529 | KNJ7680 | 12/31/2023 | 337.13 | 41.28 | 63 | 36 | 0
|  | Yearly Daily Average: | 306.585 | 35.9422
|  | Wetter Months' Daily Average: | 342.9859 | 41.8929

## 57-1
Daily Billed Information (PS 57-1 - 48 Utica Path: 2023 Reading Data)
Bill Account | Meter Number | Date | Consumption Recorded (kWh/day) | Estimated Cost ($/day) | Avg. High Temperature (°F) | Avg. Low Temperature (°F) | Rain Recorded by NOAA (inches)
7094733081 | AC06609 | 01/01/2023 | 8.33 | 1.42 | 79 | 58 | 0.04
7094733081 | AC06609 | 01/02/2023 | 8.6 | 1.45 | 78 | 53 | 0
7094733081 | AC06609 | 01/03/2023 | 8 | 1.38 | 81 | 51 | 0
7094733081 | AC06609 | 01/04/2023 | 7.08 | 1.27 | 83 | 57 | 0
7094733081 | AC06609 | 01/05/2023 | 7.22 | 1.29 | 77 | 46 | 0.04
7094733081 | AC06609 | 01/06/2023 | 6.79 | 1.29 | 68 | 41 | 0
7094733081 | AC06609 | 01/07/2023 | 6.76 | 1.28 | 70 | 38 | 0
7094733081 | AC06609 | 01/08/2023 | 6.35 | 1.23 | 76 | 42 | 0
7094733081 | AC06609 | 01/09/2023 | 6.81 | 1.29 | 74 | 47 | 0
7094733081 | AC06609 | 01/10/2023 | 9.18 | 1.59 | 71 | 42 | 0
7094733081 | AC06609 | 01/11/2023 | 9.4 | 1.62 | 73 | 38 | 0
7094733081 | AC06609 | 01/12/2023 | 9.39 | 1.61 | 80 | 44 | 0
7094733081 | AC06609 | 01/13/2023 | 8.9 | 1.55 | 71 | 35 | 0.12
7094733081 | AC06609 | 01/14/2023 | 8.74 | 1.53 | 61 | 30 | 0
7094733081 | AC06609 | 01/15/2023 | 8.75 | 1.53 | 63 | 30 | 0
7094733081 | AC06609 | 01/16/2023 | 8.48 | 1.5 | 71 | 30 | 0
7094733081 | AC06609 | 01/17/2023 | 6.66 | 1.27 | 75 | 34 | 0
7094733081 | AC06609 | 01/18/2023 | 6.9 | 1.3 | 79 | 46 | N/A
7094733081 | AC06609 | 01/19/2023 | 8.02 | 1.44 | 82 | 54 | 0
7094733081 | AC06609 | 01/20/2023 | 7.2 | 1.34 | 76 | 49 | 0
7094733081 | AC06609 | 01/21/2023 | 8.14 | 1.46 | 76 | 47 | T
7094733081 | AC06609 | 01/22/2023 | 9.51 | 1.63 | 82 | 54 | 0.33
7094733081 | AC06609 | 01/23/2023 | 9.45 | 1.62 | 75 | 44 | 0.05
7094733081 | AC06609 | 01/24/2023 | 9.07 | 1.57 | 76 | 41 | 0
7094733081 | AC06609 | 01/25/2023 | 8.54 | 1.51 | 85 | 43 | 0
7094733081 | AC06609 | 01/26/2023 | 8.74 | 1.53 | 72 | 38 | 0.09
7094733081 | AC06609 | 01/27/2023 | 8.78 | 1.54 | 62 | 37 | 0
7094733081 | AC06609 | 01/28/2023 | 8.88 | 1.55 | 69 | 35 | 0
7094733081 | AC06609 | 01/29/2023 | 9.78 | 1.66 | 78 | 55 | 0
7094733081 | AC06609 | 01/30/2023 | 8.26 | 1.47 | 86 | 58 | 0
7094733081 | AC06609 | 01/31/2023 | 8.12 | 1.46 | 83 | 59 | 0
7094733081 | AC06609 | 02/01/2023 | 8.06 | 1.45 | 82 | 58 | 0
7094733081 | AC06609 | 02/02/2023 | 7.58 | 1.39 | 82 | 57 | 0
7094733081 | AC06609 | 02/03/2023 | 8.47 | 1.5 | 78 | 50 | 0
7094733081 | AC06609 | 02/04/2023 | 9.15 | 1.56 | 70 | 47 | 0.17
7094733081 | AC06609 | 02/05/2023 | 9.73 | 1.63 | 73 | 48 | 0
7094733081 | AC06609 | 02/06/2023 | 8.88 | 1.52 | 71 | 46 | 0.01
7094733081 | AC06609 | 02/07/2023 | 8.6 | 1.49 | 76 | 44
7094733081 | AC06609 | 02/08/2023 | 8.46 | 1.47 | 79 | 49 | 0
7094733081 | AC06609 | 02/09/2023 | 8.14 | 1.43 | 83 | 58 | 0
7094733081 | AC06609 | 02/10/2023 | 8.38 | 1.46 | 85 | 46 | 0.16
7094733081 | AC06609 | 02/11/2023 | 8.82 | 1.52 | 79 | 40 | 0.57
7094733081 | AC06609 | 02/12/2023 | 10.05 | 1.67 | 71 | 40 | 0.12
7094733081 | AC06609 | 02/13/2023 | 9.5 | 1.6 | 71 | 40 | Trace Value
7094733081 | AC06609 | 02/14/2023 | 9.81 | 1.64 | 75 | 39 | 0
7094733081 | AC06609 | 02/15/2023 | 9.8 | 1.64 | 82 | 50 | 0
7094733081 | AC06609 | 02/16/2023 | 9.44 | 1.59 | 85 | 57 | 0
7094733081 | AC06609 | 02/17/2023 | 9.92 | 1.65 | 89 | 45
7094733081 | AC06609 | 02/18/2023 | 9.57 | 1.61 | 67 | 46 | 0.04
7094733081 | AC06609 | 02/19/2023 | 9.01 | 1.54 | 80 | 48 | 0
7094733081 | AC06609 | 02/20/2023 | 9.31 | 1.58 | 82 | 53 | 0
7094733081 | AC06609 | 02/21/2023 | 8.79 | 1.51 | 85 | 57 | 0
7094733081 | AC06609 | 02/22/2023 | 7.1 | 1.3 | 87 | 58 | 0
7094733081 | AC06609 | 02/23/2023 | 8.11 | 1.43 | 89 | 60 | 0
7094733081 | AC06609 | 02/24/2023 | 7.54 | 1.36 | 87 | 58 | 0
7094733081 | AC06609 | 02/25/2023 | 6.87 | 1.27 | 87 | 58
7094733081 | AC06609 | 02/26/2023 | 6.53 | 1.23 | 87 | 56 | 0
7094733081 | AC06609 | 02/27/2023 | 5.79 | 1.14 | 87 | 57 | 0
7094733081 | AC06609 | 02/28/2023 | 6.22 | 1.19 | 87 | 57 | 0
7094733081 | AC06609 | 03/01/2023 | 7.71 | 1.38 | 86 | 58 | 0
7094733081 | AC06609 | 03/02/2023 | 8.53 | 1.48 | 87 | 56 | 0
7094733081 | AC06609 | 03/03/2023 | 8.13 | 1.43 | 90 | 55 | 0
7094733081 | AC06609 | 03/04/2023 | 8.73 | 1.51 | 88 | 52 | 0
7094733081 | AC06609 | 03/05/2023 | 8.57 | 1.49 | 81 | 54 | 0.05
7094733081 | AC06609 | 03/06/2023 | 8.82 | 1.52 | 84 | 56 | 0
7094733081 | AC06609 | 03/07/2023 | 7.61 | 1.49 | 87 | 56
7094733081 | AC06609 | 03/08/2023 | 7.35 | 1.45 | 85 | 58 | 0
7094733081 | AC06609 | 03/09/2023 | 6.72 | 1.37 | 80 | 51 | 0
7094733081 | AC06609 | 03/10/2023 | 7.18 | 1.43 | 85 | 54
7094733081 | AC06609 | 03/11/2023 | 8.77 | 1.64 | 81 | 51 | 1.3
7094733081 | AC06609 | 03/12/2023 | 7.85 | 1.52 | 86 | 48 | 0
7094733081 | AC06609 | 03/13/2023 | 11.03 | 1.94 | 81 | 46 | 1.17
7094733081 | AC06609 | 03/14/2023 | 10.71 | 1.9 | 70 | 43 | 0.6
7094733081 | AC06609 | 03/15/2023 | 9.82 | 1.78 | 68 | 43 | 0
7094733081 | AC06609 | 03/16/2023 | 9 | 1.67 | 77 | 37 | 0
7094733081 | AC06609 | 03/17/2023 | 8.63 | 1.62 | 84 | 48
7094733081 | AC06609 | 03/18/2023 | 8.83 | 1.65 | 80 | 45 | 0
7094733081 | AC06609 | 03/19/2023 | 8.77 | 1.64 | 68 | 43 | 0.02
7094733081 | AC06609 | 03/20/2023 | 7.68 | 1.5 | 69 | 42 | 0.02
7094733081 | AC06609 | 03/21/2023 | 7.82 | 1.52 | 77 | 42 | 0
7094733081 | AC06609 | 03/22/2023 | 8.52 | 1.61 | 80 | 53 | 0.08
7094733081 | AC06609 | 03/23/2023 | 8.32 | 1.58 | 83 | 53
7094733081 | AC06609 | 03/24/2023 | 8.16 | 1.56 | 86 | 53 | 0
7094733081 | AC06609 | 03/25/2023 | 9.13 | 1.69 | 91 | 60 | 0
7094733081 | AC06609 | 03/26/2023 | 9.37 | 1.72 | 91 | 63 | 0.68
7094733081 | AC06609 | 03/27/2023 | 7.47 | 1.47 | 92 | 62 | 0
7094733081 | AC06609 | 03/28/2023 | 7.39 | 1.46 | 88 | 55 | Trace Value
7094733081 | AC06609 | 03/29/2023 | 7.85 | 1.52 | 75 | 55 | 0
7094733081 | AC06609 | 03/30/2023 | 7.05 | 1.41 | 79 | 51 | 0
7094733081 | AC06609 | 03/31/2023 | 8.07 | 1.55 | 85 | 55 | 0
7094733081 | AC06609 | 04/01/2023 | 8.66 | 1.63 | 90 | 60 | 0
7094733081 | AC06609 | 04/02/2023 | 8.28 | 1.58 | 85 | 60
7094733081 | AC06609 | 04/03/2023 | 7.54 | 1.48 | 86 | 61 | 0
7094733081 | AC06609 | 04/04/2023 | 7.37 | 1.46 | 88 | 60 | Trace Value
7094733081 | AC06609 | 04/05/2023 | 7.63 | 1.49 | 87 | 63 | 0
7094733081 | AC06609 | 04/06/2023 | 7.99 | 1.52 | 87 | 64 | 0
7094733081 | AC06609 | 04/07/2023 | 8.74 | 1.61 | 85 | 64
7094733081 | AC06609 | 04/08/2023 | 8.47 | 1.58 | 86 | 62
7094733081 | AC06609 | 04/09/2023 | 8.23 | 1.55 | 80 | 60 | 0.01
7094733081 | AC06609 | 04/10/2023 | 9.74 | 1.75 | 79 | 58 | 0.68
7094733081 | AC06609 | 04/11/2023 | 9.47 | 1.71 | 78 | 58 | 1.38
7094733081 | AC06609 | 04/12/2023 | 9.23 | 1.68 | 79 | 59 | 0.03
7094733081 | AC06609 | 04/13/2023 | 8.61 | 1.6 | 87 | 61 | 0.07
7094733081 | AC06609 | 04/14/2023 | 9.08 | 1.66 | 86 | 59 | 0.57
7094733081 | AC06609 | 04/15/2023 | 8.91 | 1.64 | 87 | 60 | 0.02
7094733081 | AC06609 | 04/16/2023 | 8.44 | 1.58 | 88 | 59 | 0
7094733081 | AC06609 | 04/17/2023 | 7.16 | 1.41 | 81 | 50 | 0.04
7094733081 | AC06609 | 04/18/2023 | 7 | 1.39 | 81 | 46 | 0.02
7094733081 | AC06609 | 04/19/2023 | 7.47 | 1.45 | 82 | 50 | 0
7094733081 | AC06609 | 04/20/2023 | 8.56 | 1.59 | 84 | 55 | 0
7094733081 | AC06609 | 04/21/2023 | 7.6 | 1.47 | 87 | 59
7094733081 | AC06609 | 04/22/2023 | 7.89 | 1.5 | 89 | 57 | 0.3
7094733081 | AC06609 | 04/23/2023 | 7.94 | 1.51 | 84 | 53 | 0.42
7094733081 | AC06609 | 04/24/2023 | 6.68 | 1.34 | 80 | 55 | 0
7094733081 | AC06609 | 04/25/2023 | 6.25 | 1.29 | 82 | 61 | 0.25
7094733081 | AC06609 | 04/26/2023 | 7.04 | 1.39 | 84 | 62 | 0.07
7094733081 | AC06609 | 04/27/2023 | 6.9 | 1.37 | 86 | 63 | 0
7094733081 | AC06609 | 04/28/2023 | 9.66 | 1.74 | 87 | 62 | 1.62
7094733081 | AC06609 | 04/29/2023 | 9.18 | 1.67 | 88 | 62 | 0
7094733081 | AC06609 | 04/30/2023 | 9.52 | 1.72 | 85 | 57 | 0.52
7094733081 | AC06609 | 05/01/2023 | 8.95 | 1.64 | 85 | 56 | 0
7094733081 | AC06609 | 05/02/2023 | 8.19 | 1.54 | 87 | 56 | 0
7094733081 | AC06609 | 05/03/2023 | 7.55 | 1.46 | 86 | 53 | 0
7094733081 | AC06609 | 05/04/2023 | 7.73 | 1.48 | 84 | 53 | 0
7094733081 | AC06609 | 05/05/2023 | 8.92 | 1.59 | 87 | 57 | 0
7094733081 | AC06609 | 05/06/2023 | 8.62 | 1.55 | 86 | 65 | 0
7094733081 | AC06609 | 05/07/2023 | 7.36 | 1.39 | 88 | 61 | 0.02
7094733081 | AC06609 | 05/08/2023 | 6.69 | 1.3 | 87 | 55 | 0
7094733081 | AC06609 | 05/09/2023 | 6.69 | 1.3 | 91 | 63 | 0
7094733081 | AC06609 | 05/10/2023 | 6.62 | 1.29 | 92 | 66 | 0
7094733081 | AC06609 | 05/11/2023 | 6.74 | 1.31 | 88 | 67 | 0.04
7094733081 | AC06609 | 05/12/2023 | 6.61 | 1.29 | 86 | 66 | 0
7094733081 | AC06609 | 05/13/2023 | 6.35 | 1.26 | 85 | 64 | 0
7094733081 | AC06609 | 05/14/2023 | 7.22 | 1.37 | 86 | 63 | 0
7094733081 | AC06609 | 05/15/2023 | 6.29 | 1.25 | 89 | 62 | 0
7094733081 | AC06609 | 05/16/2023 | 7.14 | 1.36 | 88 | 64 | 0
7094733081 | AC06609 | 05/17/2023 | 6.53 | 1.28 | 92 | 67 | 0
7094733081 | AC06609 | 05/18/2023 | 6.86 | 1.33 | 89 | 65 | 1.24
7094733081 | AC06609 | 05/19/2023 | 7.2 | 1.37 | 88 | 66 | 0.02
7094733081 | AC06609 | 05/20/2023 | 7.88 | 1.46 | 88 | 66 | 0
7094733081 | AC06609 | 05/21/2023 | 7.42 | 1.4 | 88 | 67
7094733081 | AC06609 | 05/22/2023 | 9.2 | 1.63 | 88 | 67 | 0.65
7094733081 | AC06609 | 05/23/2023 | 8.88 | 1.59 | 85 | 67 | 0.56
7094733081 | AC06609 | 05/24/2023 | 9.51 | 1.67 | 83 | 66 | 0.12
7094733081 | AC06609 | 05/25/2023 | 9.18 | 1.63 | 83 | 66 | 0.16
7094733081 | AC06609 | 05/26/2023 | 8.48 | 1.54 | 82 | 62 | 0.05
7094733081 | AC06609 | 05/27/2023 | 9.37 | 1.65 | 81 | 56 | Trace Value
7094733081 | AC06609 | 05/28/2023 | 8.86 | 1.58 | 85 | 55 | 0
7094733081 | AC06609 | 05/29/2023 | 8.77 | 1.57 | 87 | 60 | 0
7094733081 | AC06609 | 05/30/2023 | 7.68 | 1.43 | 88 | 62 | 0
7094733081 | AC06609 | 05/31/2023 | 7.69 | 1.43 | 87 | 68 | 0
7094733081 | AC06609 | 06/01/2023 | 8.09 | 1.49 | 85 | 68 | 0
7094733081 | AC06609 | 06/02/2023 | 8.71 | 1.57 | 85 | 67 | 0
7094733081 | AC06609 | 06/03/2023 | 7.03 | 1.35 | 84 | 67 | 0
7094733081 | AC06609 | 06/04/2023 | 8.58 | 1.55 | 84 | 66 | 0
7094733081 | AC06609 | 06/05/2023 | 7.67 | 1.43 | 84 | 64 | 0.3
7094733081 | AC06609 | 06/06/2023 | 7.44 | 1.4 | 88 | 62
7094733081 | AC06609 | 06/07/2023 | 9.35 | 1.64 | 91 | 68 | 0
7094733081 | AC06609 | 06/08/2023 | 12.72 | 2.06 | 92 | 68 | 1.64
7094733081 | AC06609 | 06/09/2023 | 14.66 | 2.31 | 92 | 68 | 0
7094733081 | AC06609 | 06/10/2023 | 14.91 | 2.34 | 88 | 67 | 0.54
7094733081 | AC06609 | 06/11/2023 | 14.78 | 2.32 | 91 | 69 | 0.09
7094733081 | AC06609 | 06/12/2023 | 11.23 | 1.88 | 94 | 69 | 0
7094733081 | AC06609 | 06/13/2023 | 9.69 | 1.68 | 95 | 71
7094733081 | AC06609 | 06/14/2023 | 7.47 | 1.4 | 95 | 71 | 0
7094733081 | AC06609 | 06/15/2023 | 7.96 | 1.46 | 95 | 66 | 0.44
7094733081 | AC06609 | 06/16/2023 | 10.27 | 1.76 | 95 | 68 | 0.45
7094733081 | AC06609 | 06/17/2023 | 11.13 | 1.86 | 93 | 68 | 0.91
7094733081 | AC06609 | 06/18/2023 | 11.92 | 1.96 | 94 | 68 | 0.28
7094733081 | AC06609 | 06/19/2023 | 12.6 | 2.05 | 93 | 70 | 0.63
7094733081 | AC06609 | 06/20/2023 | 14.43 | 2.28 | 91 | 69 | 0.46
7094733081 | AC06609 | 06/21/2023 | 13.96 | 2.22 | 91 | 71 | 0.24
7094733081 | AC06609 | 06/22/2023 | 12.71 | 2.06 | 93 | 66 | 0.04
7094733081 | AC06609 | 06/23/2023 | 10.92 | 1.84 | 91 | 69 | 0.35
7094733081 | AC06609 | 06/24/2023 | 12.22 | 2 | 92 | 70 | 0.24
7094733081 | AC06609 | 06/25/2023 | 12.07 | 1.98 | 91 | 70 | 0.15
7094733081 | AC06609 | 06/26/2023 | 12.59 | 2.05 | 94 | 70 | 0
7094733081 | AC06609 | 06/27/2023 | 11.75 | 1.94 | 97 | 71 | 0
7094733081 | AC06609 | 06/28/2023 | 12.29 | 2.01 | 95 | 72 | 0
7094733081 | AC06609 | 06/29/2023 | 11.13 | 1.86 | 95 | 71 | 0.88
7094733081 | AC06609 | 06/30/2023 | 9.63 | 1.68 | 94 | 71 | 0
7094733081 | AC06609 | 07/01/2023 | 8.9 | 1.58 | 94 | 71 | 0
7094733081 | AC06609 | 07/02/2023 | 9.35 | 1.64 | 95 | 71 | 0
7094733081 | AC06609 | 07/03/2023 | 9.26 | 1.63 | 97 | 72 | 0
7094733081 | AC06609 | 07/04/2023 | 11.57 | 1.92 | 95 | 73 | 0
7094733081 | AC06609 | 07/05/2023 | 10.82 | 1.82 | 95 | 74 | 0
7094733081 | AC06609 | 07/06/2023 | 9.53 | 1.66 | 96 | 73 | 0.04
7094733081 | AC06609 | 07/07/2023 | 9.71 | 1.71 | 95 | 73 | 0.03
7094733081 | AC06609 | 07/08/2023 | 9.33 | 1.66 | 94 | 74 | 0.31
7094733081 | AC06609 | 07/09/2023 | 11.1 | 1.88 | 96 | 74 | 0.2
7094733081 | AC06609 | 07/10/2023 | 10.53 | 1.81 | 96 | 74 | 0
7094733081 | AC06609 | 07/11/2023 | 11.03 | 1.87 | 94 | 73 | 0.78
7094733081 | AC06609 | 07/12/2023 | 11.62 | 1.95 | 94 | 73 | 0.1
7094733081 | AC06609 | 07/13/2023 | 11.04 | 1.87 | 94 | 72 | Trace Value
7094733081 | AC06609 | 07/14/2023 | 11.21 | 1.9 | 95 | 73 | 0.33
7094733081 | AC06609 | 07/15/2023 | 11.35 | 1.91 | 96 | 73 | 0.12
7094733081 | AC06609 | 07/16/2023 | 12.86 | 2.11 | 96 | 74 | 0.15
7094733081 | AC06609 | 07/17/2023 | 10.3 | 1.78 | 95 | 74 | 2.8
7094733081 | AC06609 | 07/18/2023 | 10.4 | 1.79 | 95 | 72 | 0.22
7094733081 | AC06609 | 07/19/2023 | 11.67 | 1.95 | 95 | 71 | 0.14
7094733081 | AC06609 | 07/20/2023 | 11.93 | 1.99 | 96 | 73 | 0
7094733081 | AC06609 | 07/21/2023 | 11.45 | 1.93 | 99 | 74 | 0
7094733081 | AC06609 | 07/22/2023 | 9.78 | 1.72 | 97 | 75 | 0
7094733081 | AC06609 | 07/23/2023 | 8.72 | 1.58 | 94 | 71 | 0.7
7094733081 | AC06609 | 07/24/2023 | 9.74 | 1.71 | 93 | 73 | 1.12
7094733081 | AC06609 | 07/25/2023 | 8.79 | 1.59 | 93 | 73 | 0.3
7094733081 | AC06609 | 07/26/2023 | 8.82 | 1.59 | 92 | 73 | 0
7094733081 | AC06609 | 07/27/2023 | 8.48 | 1.55 | 91 | 73 | 0
7094733081 | AC06609 | 07/28/2023 | 9.3 | 1.65 | 92 | 73 | 1
7094733081 | AC06609 | 07/29/2023 | 11.84 | 1.98 | 93 | 73 | 0.05
7094733081 | AC06609 | 07/30/2023 | 13.32 | 2.17 | 95 | 74 | Trace Value
7094733081 | AC06609 | 07/31/2023 | 11.29 | 1.91 | 95 | 71 | 0.74
7094733081 | AC06609 | 08/01/2023 | 10.02 | 1.74 | 95 | 71 | 0.08
7094733081 | AC06609 | 08/02/2023 | 11.71 | 1.96 | 93 | 74 | 0
7094733081 | AC06609 | 08/03/2023 | 10.18 | 1.77 | 91 | 73 | 0
7094733081 | AC06609 | 08/04/2023 | 11 | 1.87 | 94 | 73 | 0
7094733081 | AC06609 | 08/05/2023 | 13.36 | 2.12 | 94 | 73 | 0.17
7094733081 | AC06609 | 08/06/2023 | 13.63 | 2.15 | 95 | 74 | 0.66
7094733081 | AC06609 | 08/07/2023 | 12.81 | 2.05 | 97 | 75 | 0.03
7094733081 | AC06609 | 08/08/2023 | 12.81 | 2.05 | 99 | 75 | 0
7094733081 | AC06609 | 08/09/2023 | 15.83 | 2.43 | 99 | 74 | 0
7094733081 | AC06609 | 08/10/2023 | 11.06 | 1.83 | 100 | 75 | 0.16
7094733081 | AC06609 | 08/11/2023 | 9.62 | 1.64 | 99 | 75 | 0
7094733081 | AC06609 | 08/12/2023 | 11.17 | 1.84 | 98 | 76 | 0.25
7094733081 | AC06609 | 08/13/2023 | 11.07 | 1.83 | 97 | 74 | 0
7094733081 | AC06609 | 08/14/2023 | 9.28 | 1.6 | 97 | 76 | 0
7094733081 | AC06609 | 08/15/2023 | 10.3 | 1.73 | 97 | 75 | 0
7094733081 | AC06609 | 08/16/2023 | 12.82 | 2.05 | 96 | 73 | 0.09
7094733081 | AC06609 | 08/17/2023 | 13.41 | 2.12 | 93 | 72 | 0.36
7094733081 | AC06609 | 08/18/2023 | 12.02 | 1.95 | 93 | 73 | 1.09
7094733081 | AC06609 | 08/19/2023 | 11.52 | 1.88 | 93 | 72 | 0.69
7094733081 | AC06609 | 08/20/2023 | 10.93 | 1.81 | 92 | 75 | 0
7094733081 | AC06609 | 08/21/2023 | 12.03 | 1.95 | 92 | 74 | 0
7094733081 | AC06609 | 08/22/2023 | 7.63 | 1.39 | 93 | 72 | 0
7094733081 | AC06609 | 08/23/2023 | 8.02 | 1.44 | 93 | 74 | 0
7094733081 | AC06609 | 08/24/2023 | 8.7 | 1.53 | 93 | 74 | 0.99
7094733081 | AC06609 | 08/25/2023 | 8.13 | 1.46 | 92 | 71 | 0
7094733081 | AC06609 | 08/26/2023 | 9.41 | 1.62 | 95 | 73 | 0
7094733081 | AC06609 | 08/27/2023 | 8.18 | 1.46 | 95 | 72
7094733081 | AC06609 | 08/28/2023 | 8.03 | 1.44 | 96 | 74 | Trace Value
7094733081 | AC06609 | 08/29/2023 | 9.34 | 1.61 | 95 | 74 | 0
7094733081 | AC06609 | 08/30/2023 | 12.78 | 2.04 | 94 | 74 | 0.93
7094733081 | AC06609 | 08/31/2023 | 12.4 | 2 | 94 | 74 | 0.05
7094733081 | AC06609 | 09/01/2023 | 11.45 | 1.88 | 92 | 73 | 0
7094733081 | AC06609 | 09/02/2023 | 12.66 | 2.03 | 91 | 72
7094733081 | AC06609 | 09/03/2023 | 12.13 | 1.96 | 92 | 71 | 0.05
7094733081 | AC06609 | 09/04/2023 | 12.28 | 1.98 | 90 | 68 | 0
7094733081 | AC06609 | 09/05/2023 | 9 | 1.57 | 90 | 64 | 0
7094733081 | AC06609 | 09/06/2023 | 7.54 | 1.38 | 94 | 69 | 0
7094733081 | AC06609 | 09/07/2023 | 7.47 | 1.43 | 95 | 70
7094733081 | AC06609 | 09/08/2023 | 9.76 | 1.73 | 95 | 69 | 0
7094733081 | AC06609 | 09/09/2023 | 9.84 | 1.74 | 94 | 64 | 0.48
7094733081 | AC06609 | 09/10/2023 | 10.76 | 1.86 | 93 | 71 | Trace Value
7094733081 | AC06609 | 09/11/2023 | 8.61 | 1.58 | 92 | 72 | 0
7094733081 | AC06609 | 09/12/2023 | 8.92 | 1.62 | 92 | 71 | Trace Value
7094733081 | AC06609 | 09/13/2023 | 10.22 | 1.79 | 92 | 72 | 0.03
7094733081 | AC06609 | 09/14/2023 | 10.03 | 1.76 | 91 | 71 | 0.29
7094733081 | AC06609 | 09/15/2023 | 9.59 | 1.71 | 88 | 70 | 0
7094733081 | AC06609 | 09/16/2023 | 11.36 | 1.93 | 87 | 69 | 0.54
7094733081 | AC06609 | 09/17/2023 | 13.16 | 2.17 | 92 | 70 | 0
7094733081 | AC06609 | 09/18/2023 | 11.26 | 1.92 | 89 | 68 | 0.08
7094733081 | AC06609 | 09/19/2023 | 11.51 | 1.95 | 88 | 64 | 0
7094733081 | AC06609 | 09/20/2023 | 10.84 | 1.87 | 88 | 69 | 0
7094733081 | AC06609 | 09/21/2023 | 7.3 | 1.41 | 87 | 68 | 0.08
7094733081 | AC06609 | 09/22/2023 | 8.03 | 1.5 | 85 | 65 | 0.3
7094733081 | AC06609 | 09/23/2023 | 7.98 | 1.5 | 87 | 61 | 0
7094733081 | AC06609 | 09/24/2023 | 8.54 | 1.57 | 89 | 59 | 0
7094733081 | AC06609 | 09/25/2023 | 10 | 1.76 | 90 | 66 | 0
7094733081 | AC06609 | 09/26/2023 | 9.05 | 1.64 | 89 | 71 | 2.11
7094733081 | AC06609 | 09/27/2023 | 10.18 | 1.78 | 88 | 71 | 0.91
7094733081 | AC06609 | 09/28/2023 | 10.12 | 1.77 | 87 | 71 | 0.81
7094733081 | AC06609 | 09/29/2023 | 10.43 | 1.81 | 85 | 71 | 0.02
7094733081 | AC06609 | 09/30/2023 | 11.68 | 1.98 | 85 | 71 | 0.2
7094733081 | AC06609 | 10/01/2023 | 13.57 | 2.22 | 85 | 70 | 2.53
7094733081 | AC06609 | 10/02/2023 | 12.85 | 2.13 | 85 | 69 | 0.56
7094733081 | AC06609 | 10/03/2023 | 10.31 | 1.8 | 85 | 70 | 0
7094733081 | AC06609 | 10/04/2023 | 10.19 | 1.78 | 86 | 70 | 0.05
7094733081 | AC06609 | 10/05/2023 | 11 | 1.87 | 86 | 69 | 0
7094733081 | AC06609 | 10/06/2023 | 10.18 | 1.77 | 87 | 66 | 0
7094733081 | AC06609 | 10/07/2023 | 10.33 | 1.78 | 90 | 56 | 0
7094733081 | AC06609 | 10/08/2023 | 10.2 | 1.77 | 82 | 53 | 0
7094733081 | AC06609 | 10/09/2023 | 10.37 | 1.79 | 80 | 55 | 0
7094733081 | AC06609 | 10/10/2023 | 11.82 | 1.97 | 84 | 56 | 0
7094733081 | AC06609 | 10/11/2023 | 12.4 | 2.05 | 84 | 65 | 0
7094733081 | AC06609 | 10/12/2023 | 18.71 | 2.84 | 88 | 72 | 2.8
7094733081 | AC06609 | 10/13/2023 | 18.26 | 2.79 | 89 | 68 | 1.67
7094733081 | AC06609 | 10/14/2023 | 17.29 | 2.66 | 89 | 64 | 0
7094733081 | AC06609 | 10/15/2023 | 16.11 | 2.51 | 82 | 55 | 0
7094733081 | AC06609 | 10/16/2023 | 15.22 | 2.4 | 76 | 50 | 0
7094733081 | AC06609 | 10/17/2023 | 13.92 | 2.24 | 75 | 49 | 0
7094733081 | AC06609 | 10/18/2023 | 13.81 | 2.22 | 77 | 50 | 0
7094733081 | AC06609 | 10/19/2023 | 14.65 | 2.33 | 81 | 55 | 0
7094733081 | AC06609 | 10/20/2023 | 14.15 | 2.27 | 83 | 55 | 0
7094733081 | AC06609 | 10/21/2023 | 15.17 | 2.4 | 83 | 55 | 0
7094733081 | AC06609 | 10/22/2023 | 14.27 | 2.28 | 86 | 52 | 0
7094733081 | AC06609 | 10/23/2023 | 8.5 | 1.55 | 83 | 58 | 0
7094733081 | AC06609 | 10/24/2023 | 9.6 | 1.69 | 82 | 67 | 0
7094733081 | AC06609 | 10/25/2023 | 10.15 | 1.76 | 82 | 68 | 0
7094733081 | AC06609 | 10/26/2023 | 8.88 | 1.6 | 82 | 65 | 0
7094733081 | AC06609 | 10/27/2023 | 9.71 | 1.71 | 83 | 64 | 0
7094733081 | AC06609 | 10/28/2023 | 12.93 | 2.11 | 84 | 62 | 0
7094733081 | AC06609 | 10/29/2023 | 13.35 | 2.17 | 84 | 61 | 0
7094733081 | AC06609 | 10/30/2023 | 14.19 | 2.27 | 85 | 60 | 0
7094733081 | AC06609 | 10/31/2023 | 10.22 | 1.77 | 84 | 58 | 0
7094733081 | AC06609 | 11/01/2023 | 8.46 | 1.55 | 76 | 53 | 0
7094733081 | AC06609 | 11/02/2023 | 8.01 | 1.49 | 75 | 53 | 0
7094733081 | AC06609 | 11/03/2023 | 9.02 | 1.62 | 79 | 59 | 0
7094733081 | AC06609 | 11/04/2023 | 9.05 | 1.6 | 79 | 55 | 0
7094733081 | AC06609 | 11/05/2023 | 9.39 | 1.65 | 80 | 51 | 0
7094733081 | AC06609 | 11/06/2023 | 7.93 | 1.46 | 81 | 48 | 0
7094733081 | AC06609 | 11/07/2023 | 8.3 | 1.51 | 83 | 53 | 0
7094733081 | AC06609 | 11/08/2023 | 8.59 | 1.54 | 84 | 50 | 0
7094733081 | AC06609 | 11/09/2023 | 7.97 | 1.47 | 85 | 55 | 0
7094733081 | AC06609 | 11/10/2023 | 9.08 | 1.61 | 86 | 60 | 0
7094733081 | AC06609 | 11/11/2023 | 11.88 | 1.96 | 83 | 65 | 0.33
7094733081 | AC06609 | 11/12/2023 | 11.72 | 1.94 | 80 | 63 | 0
7094733081 | AC06609 | 11/13/2023 | 10.83 | 1.83 | 77 | 62 | 0
7094733081 | AC06609 | 11/14/2023 | 12.08 | 1.98 | 77 | 61 | 0.12
7094733081 | AC06609 | 11/15/2023 | 10.39 | 1.77 | 77 | 64 | 0.05
7094733081 | AC06609 | 11/16/2023 | 12.87 | 2.08 | 78 | 62 | 0.16
7094733081 | AC06609 | 11/17/2023 | 16.39 | 2.53 | 79 | 61 | 2.1
7094733081 | AC06609 | 11/18/2023 | 16.39 | 2.53 | 78 | 55 | 0.66
7094733081 | AC06609 | 11/19/2023 | 17.23 | 2.64 | 80 | 56 | 0
7094733081 | AC06609 | 11/20/2023 | 11.81 | 1.95 | 79 | 59 | 0.02
7094733081 | AC06609 | 11/21/2023 | 11.45 | 1.9 | 81 | 52 | 0.02
7094733081 | AC06609 | 11/22/2023 | 11.36 | 1.89 | 81 | 47 | 0
7094733081 | AC06609 | 11/23/2023 | 14.3 | 2.27 | 73 | 48 | 0.01
7094733081 | AC06609 | 11/24/2023 | 13.73 | 2.19 | 75 | 52 | 0.01
7094733081 | AC06609 | 11/25/2023 | 11 | 1.85 | 75 | 53 | 0.07
7094733081 | AC06609 | 11/26/2023 | 16.34 | 2.52 | 75 | 55 | 0.01
7094733081 | AC06609 | 11/27/2023 | 15.88 | 2.46 | 74 | 44 | 0.55
7094733081 | AC06609 | 11/28/2023 | 11.93 | 1.97 | 69 | 39 | 0
7094733081 | AC06609 | 11/29/2023 | 8.96 | 1.59 | 68 | 36 | 0
7094733081 | AC06609 | 11/30/2023 | 9.39 | 1.64 | 86 | 41 | 0
7094733081 | AC06609 | 12/01/2023 | 9.47 | 1.66 | 82 | 55 | 0
7094733081 | AC06609 | 12/02/2023 | 11.42 | 1.9 | 83 | 64 | 0
7094733081 | AC06609 | 12/03/2023 | 15.13 | 2.37 | 82 | 62 | 0.02
7094733081 | AC06609 | 12/04/2023 | 16.08 | 2.49 | 79 | 51 | 0.23
7094733081 | AC06609 | 12/05/2023 | 15.6 | 2.42 | 72 | 47 | 0
7094733081 | AC06609 | 12/06/2023 | 11.63 | 1.92 | 69 | 41 | 0
7094733081 | AC06609 | 12/07/2023 | 11.04 | 1.84 | 67 | 41 | 0
7094733081 | AC06609 | 12/08/2023 | 11.18 | 1.86 | 74 | 47 | 0
7094733081 | AC06609 | 12/09/2023 | 9.47 | 1.64 | 82 | 56 | 0.04
7094733081 | AC06609 | 12/10/2023 | 8.78 | 1.56 | 83 | 44 | 0
7094733081 | AC06609 | 12/11/2023 | 8.18 | 1.48 | 67 | 43 | 0.25
7094733081 | AC06609 | 12/12/2023 | 8.46 | 1.51 | 71 | 43 | 0
7094733081 | AC06609 | 12/13/2023 | 11.13 | 1.85 | 73 | 58 | 0
7094733081 | AC06609 | 12/14/2023 | 10.65 | 1.79 | 72 | 59 | 0.66
7094733081 | AC06609 | 12/15/2023 | 10.1 | 1.72 | 72 | 60 | 0.07
7094733081 | AC06609 | 12/16/2023 | 9.1 | 1.6 | 73 | 58 | 0.11
7094733081 | AC06609 | 12/17/2023 | 16.09 | 2.48 | 74 | 48 | 4.04
7094733081 | AC06609 | 12/18/2023 | 9.89 | 1.7 | 68 | 40 | 0.05
7094733081 | AC06609 | 12/19/2023 | 9.55 | 1.65 | 65 | 41 | 0
7094733081 | AC06609 | 12/20/2023 | 8.75 | 1.55 | 66 | 44 | 0
7094733081 | AC06609 | 12/21/2023 | 8.96 | 1.58 | 68 | 46 | 0
7094733081 | AC06609 | 12/22/2023 | 9.31 | 1.62 | 70 | 49 | 0
7094733081 | AC06609 | 12/23/2023 | 9.66 | 1.67 | 73 | 53 | 0
7094733081 | AC06609 | 12/24/2023 | 8.55 | 1.53 | 73 | 53 | 0
7094733081 | AC06609 | 12/25/2023 | 10.54 | 1.78 | 73 | 60 | 0.09
7094733081 | AC06609 | 12/26/2023 | 11.04 | 1.84 | 74 | 54 | 0.1
7094733081 | AC06609 | 12/27/2023 | 26.36 | 3.79 | 71 | 49 | 0
7094733081 | AC06609 | 12/28/2023 | 19.49 | 2.92 | 66 | 44 | 0.04
7094733081 | AC06609 | 12/29/2023 | 7.93 | 1.45 | 55 | 46 | 0
7094733081 | AC06609 | 12/30/2023 | 7.96 | 1.45 | 59 | 37 | 0
7094733081 | AC06609 | 12/31/2023 | 8.91 | 1.57 | 63 | 36 | 0
|  | Yearly Daily Average: | 9.9144 | 1.7156
|  | Wetter Months' Daily Average: | 11.3619 | 1.9038

## 57-2
Daily Billed Information (PS 57-2 - 6 Ullian Trail: 2023 Reading Data)
Bill Account | Meter Number | Date | Consumption Recorded (kWh/day) | Estimated Cost ($/day) | Avg. High Temperature (°F) | Avg. Low Temperature (°F) | Rain Recorded by NOAA (inches)
2125633178 | AC06628 | 01/01/2023 | 23.71 | 3.27 | 79 | 58 | 0.04
2125633178 | AC06628 | 01/02/2023 | 24.04 | 3.31 | 78 | 53 | 0
2125633178 | AC06628 | 01/03/2023 | 24.62 | 3.38 | 81 | 51 | 0
2125633178 | AC06628 | 01/04/2023 | 23.45 | 3.24 | 83 | 57 | 0
2125633178 | AC06628 | 01/05/2023 | 24.44 | 3.35 | 77 | 46 | 0.04
2125633178 | AC06628 | 01/06/2023 | 26.72 | 3.77 | 68 | 41 | 0
2125633178 | AC06628 | 01/07/2023 | 26.56 | 3.75 | 70 | 38 | 0
2125633178 | AC06628 | 01/08/2023 | 26.16 | 3.7 | 76 | 42 | 0
2125633178 | AC06628 | 01/09/2023 | 23.92 | 3.42 | 74 | 47 | 0
2125633178 | AC06628 | 01/10/2023 | 26.25 | 3.71 | 71 | 42 | 0
2125633178 | AC06628 | 01/11/2023 | 26.7 | 3.77 | 73 | 38 | 0
2125633178 | AC06628 | 01/12/2023 | 24.4 | 3.48 | 80 | 44 | 0
2125633178 | AC06628 | 01/13/2023 | 26.16 | 3.7 | 71 | 35 | 0.12
2125633178 | AC06628 | 01/14/2023 | 29.35 | 4.1 | 61 | 30 | 0
2125633178 | AC06628 | 01/15/2023 | 29.5 | 4.12 | 63 | 30 | 0
2125633178 | AC06628 | 01/16/2023 | 27 | 3.8 | 71 | 30 | 0
2125633178 | AC06628 | 01/17/2023 | 25.14 | 3.57 | 75 | 34 | 0
2125633178 | AC06628 | 01/18/2023 | 24.39 | 3.48 | 79 | 46 | N/A
2125633178 | AC06628 | 01/19/2023 | 21.97 | 3.17 | 82 | 54 | 0
2125633178 | AC06628 | 01/20/2023 | 22.82 | 3.28 | 76 | 49 | 0
2125633178 | AC06628 | 01/21/2023 | 26.17 | 3.7 | 76 | 47 | T
2125633178 | AC06628 | 01/22/2023 | 25.67 | 3.64 | 82 | 54 | 0.33
2125633178 | AC06628 | 01/23/2023 | 24.35 | 3.47 | 75 | 44 | 0.05
2125633178 | AC06628 | 01/24/2023 | 25.72 | 3.64 | 76 | 41 | 0
2125633178 | AC06628 | 01/25/2023 | 22.41 | 3.23 | 85 | 43 | 0
2125633178 | AC06628 | 01/26/2023 | 24.42 | 3.48 | 72 | 38 | 0.09
2125633178 | AC06628 | 01/27/2023 | 27.52 | 3.87 | 62 | 37 | 0
2125633178 | AC06628 | 01/28/2023 | 26.1 | 3.69 | 69 | 35 | 0
2125633178 | AC06628 | 01/29/2023 | 24.32 | 3.47 | 78 | 55 | 0
2125633178 | AC06628 | 01/30/2023 | 21.92 | 3.17 | 86 | 58 | 0
2125633178 | AC06628 | 01/31/2023 | 23.63 | 3.38 | 83 | 59 | 0
2125633178 | AC06628 | 02/01/2023 | 23.6 | 3.38 | 82 | 58 | 0
2125633178 | AC06628 | 02/02/2023 | 23.33 | 3.34 | 82 | 57 | 0
2125633178 | AC06628 | 02/03/2023 | 26.17 | 3.7 | 78 | 50 | 0
2125633178 | AC06628 | 02/04/2023 | 27.23 | 3.81 | 70 | 47 | 0.17
2125633178 | AC06628 | 02/05/2023 | 27.55 | 3.85 | 73 | 48 | 0
2125633178 | AC06628 | 02/06/2023 | 26.37 | 3.7 | 71 | 46 | 0.01
2125633178 | AC06628 | 02/07/2023 | 26.27 | 3.69 | 76 | 44
2125633178 | AC06628 | 02/08/2023 | 24.51 | 3.47 | 79 | 49 | 0
2125633178 | AC06628 | 02/09/2023 | 23.43 | 3.33 | 83 | 58 | 0
2125633178 | AC06628 | 02/10/2023 | 24.56 | 3.47 | 85 | 46 | 0.16
2125633178 | AC06628 | 02/11/2023 | 25.32 | 3.57 | 79 | 40 | 0.57
2125633178 | AC06628 | 02/12/2023 | 27.25 | 3.81 | 71 | 40 | 0.12
2125633178 | AC06628 | 02/13/2023 | 26.17 | 3.67 | 71 | 40 | Trace Value
2125633178 | AC06628 | 02/14/2023 | 27.19 | 3.8 | 75 | 39 | 0
2125633178 | AC06628 | 02/15/2023 | 24.3 | 3.44 | 82 | 50 | 0
2125633178 | AC06628 | 02/16/2023 | 23.07 | 3.29 | 85 | 57 | 0
2125633178 | AC06628 | 02/17/2023 | 22.39 | 3.2 | 89 | 45
2125633178 | AC06628 | 02/18/2023 | 24.81 | 3.51 | 67 | 46 | 0.04
2125633178 | AC06628 | 02/19/2023 | 25.44 | 3.58 | 80 | 48 | 0
2125633178 | AC06628 | 02/20/2023 | 23.63 | 3.36 | 82 | 53 | 0
2125633178 | AC06628 | 02/21/2023 | 22.94 | 3.27 | 85 | 57 | 0
2125633178 | AC06628 | 02/22/2023 | 22.92 | 3.27 | 87 | 58 | 0
2125633178 | AC06628 | 02/23/2023 | 22.08 | 3.17 | 89 | 60 | 0
2125633178 | AC06628 | 02/24/2023 | 21.48 | 3.09 | 87 | 58 | 0
2125633178 | AC06628 | 02/25/2023 | 23.04 | 3.29 | 87 | 58
2125633178 | AC06628 | 02/26/2023 | 24.41 | 3.46 | 87 | 56 | 0
2125633178 | AC06628 | 02/27/2023 | 22.49 | 3.22 | 87 | 57 | 0
2125633178 | AC06628 | 02/28/2023 | 21.44 | 3.09 | 87 | 57 | 0
2125633178 | AC06628 | 03/01/2023 | 22.91 | 3.27 | 86 | 58 | 0
2125633178 | AC06628 | 03/02/2023 | 22.15 | 3.17 | 87 | 56 | 0
2125633178 | AC06628 | 03/03/2023 | 20.39 | 2.96 | 90 | 55 | 0
2125633178 | AC06628 | 03/04/2023 | 20.93 | 3.02 | 88 | 52 | 0
2125633178 | AC06628 | 03/05/2023 | 21.77 | 3.13 | 81 | 54 | 0.05
2125633178 | AC06628 | 03/06/2023 | 20.82 | 3.01 | 84 | 56 | 0
2125633178 | AC06628 | 03/07/2023 | 20.63 | 3.29 | 87 | 56
2125633178 | AC06628 | 03/08/2023 | 20.89 | 3.32 | 85 | 58 | 0
2125633178 | AC06628 | 03/09/2023 | 21.78 | 3.45 | 80 | 51 | 0
2125633178 | AC06628 | 03/10/2023 | 21.9 | 3.46 | 85 | 54
2125633178 | AC06628 | 03/11/2023 | 25.06 | 3.89 | 81 | 51 | 1.3
2125633178 | AC06628 | 03/12/2023 | 23.27 | 3.65 | 86 | 48 | 0
2125633178 | AC06628 | 03/13/2023 | 26.29 | 4.06 | 81 | 46 | 1.17
2125633178 | AC06628 | 03/14/2023 | 28.85 | 4.41 | 70 | 43 | 0.6
2125633178 | AC06628 | 03/15/2023 | 28.63 | 4.38 | 68 | 43 | 0
2125633178 | AC06628 | 03/16/2023 | 27.36 | 4.2 | 77 | 37 | 0
2125633178 | AC06628 | 03/17/2023 | 24.31 | 3.79 | 84 | 48
2125633178 | AC06628 | 03/18/2023 | 25.01 | 3.89 | 80 | 45 | 0
2125633178 | AC06628 | 03/19/2023 | 27.83 | 4.27 | 68 | 43 | 0.02
2125633178 | AC06628 | 03/20/2023 | 26.7 | 4.12 | 69 | 42 | 0.02
2125633178 | AC06628 | 03/21/2023 | 24.84 | 3.86 | 77 | 42 | 0
2125633178 | AC06628 | 03/22/2023 | 23.92 | 3.74 | 80 | 53 | 0.08
2125633178 | AC06628 | 03/23/2023 | 23.18 | 3.64 | 83 | 53
2125633178 | AC06628 | 03/24/2023 | 21.65 | 3.43 | 86 | 53 | 0
2125633178 | AC06628 | 03/25/2023 | 21.3 | 3.38 | 91 | 60 | 0
2125633178 | AC06628 | 03/26/2023 | 21.54 | 3.41 | 91 | 63 | 0.68
2125633178 | AC06628 | 03/27/2023 | 20.75 | 3.31 | 92 | 62 | 0
2125633178 | AC06628 | 03/28/2023 | 21.48 | 3.4 | 88 | 55 | Trace Value
2125633178 | AC06628 | 03/29/2023 | 20.72 | 3.3 | 75 | 55 | 0
2125633178 | AC06628 | 03/30/2023 | 21.52 | 3.41 | 79 | 51 | 0
2125633178 | AC06628 | 03/31/2023 | 21.45 | 3.4 | 85 | 55 | 0
2125633178 | AC06628 | 04/01/2023 | 20.86 | 3.32 | 90 | 60 | 0
2125633178 | AC06628 | 04/02/2023 | 21.47 | 3.4 | 85 | 60
2125633178 | AC06628 | 04/03/2023 | 19.53 | 3.14 | 86 | 61 | 0
2125633178 | AC06628 | 04/04/2023 | 19.94 | 3.2 | 88 | 60 | Trace Value
2125633178 | AC06628 | 04/05/2023 | 19.93 | 3.19 | 87 | 63 | 0
2125633178 | AC06628 | 04/06/2023 | 20.59 | 3.21 | 87 | 64 | 0
2125633178 | AC06628 | 04/07/2023 | 19.81 | 3.1 | 85 | 64
2125633178 | AC06628 | 04/08/2023 | 20.18 | 3.15 | 86 | 62
2125633178 | AC06628 | 04/09/2023 | 22.47 | 3.45 | 80 | 60 | 0.01
2125633178 | AC06628 | 04/10/2023 | 27.29 | 4.09 | 79 | 58 | 0.68
2125633178 | AC06628 | 04/11/2023 | 28.68 | 4.28 | 78 | 58 | 1.38
2125633178 | AC06628 | 04/12/2023 | 25.89 | 3.91 | 79 | 59 | 0.03
2125633178 | AC06628 | 04/13/2023 | 25.74 | 3.89 | 87 | 61 | 0.07
2125633178 | AC06628 | 04/14/2023 | 27.55 | 4.13 | 86 | 59 | 0.57
2125633178 | AC06628 | 04/15/2023 | 25.92 | 3.91 | 87 | 60 | 0.02
2125633178 | AC06628 | 04/16/2023 | 26.33 | 3.97 | 88 | 59 | 0
2125633178 | AC06628 | 04/17/2023 | 24.33 | 3.7 | 81 | 50 | 0.04
2125633178 | AC06628 | 04/18/2023 | 26.51 | 3.99 | 81 | 46 | 0.02
2125633178 | AC06628 | 04/19/2023 | 24.63 | 3.74 | 82 | 50 | 0
2125633178 | AC06628 | 04/20/2023 | 23.62 | 3.61 | 84 | 55 | 0
2125633178 | AC06628 | 04/21/2023 | 22.55 | 3.46 | 87 | 59
2125633178 | AC06628 | 04/22/2023 | 22.54 | 3.46 | 89 | 57 | 0.3
2125633178 | AC06628 | 04/23/2023 | 22.7 | 3.48 | 84 | 53 | 0.42
2125633178 | AC06628 | 04/24/2023 | 21.47 | 3.32 | 80 | 55 | 0
2125633178 | AC06628 | 04/25/2023 | 21.95 | 3.39 | 82 | 61 | 0.25
2125633178 | AC06628 | 04/26/2023 | 22.07 | 3.4 | 84 | 62 | 0.07
2125633178 | AC06628 | 04/27/2023 | 25.46 | 3.85 | 86 | 63 | 0
2125633178 | AC06628 | 04/28/2023 | 31.22 | 4.61 | 87 | 62 | 1.62
2125633178 | AC06628 | 04/29/2023 | 28.3 | 4.23 | 88 | 62 | 0
2125633178 | AC06628 | 04/30/2023 | 31.08 | 4.59 | 85 | 57 | 0.52
2125633178 | AC06628 | 05/01/2023 | 27.47 | 4.12 | 85 | 56 | 0
2125633178 | AC06628 | 05/02/2023 | 26.36 | 3.97 | 87 | 56 | 0
2125633178 | AC06628 | 05/03/2023 | 26.54 | 3.99 | 86 | 53 | 0
2125633178 | AC06628 | 05/04/2023 | 24.72 | 3.75 | 84 | 53 | 0
2125633178 | AC06628 | 05/05/2023 | 25.25 | 3.78 | 87 | 57 | 0
2125633178 | AC06628 | 05/06/2023 | 25.76 | 3.84 | 86 | 65 | 0
2125633178 | AC06628 | 05/07/2023 | 25.1 | 3.76 | 88 | 61 | 0.02
2125633178 | AC06628 | 05/08/2023 | 22.98 | 3.48 | 87 | 55 | 0
2125633178 | AC06628 | 05/09/2023 | 22.92 | 3.47 | 91 | 63 | 0
2125633178 | AC06628 | 05/10/2023 | 22.15 | 3.37 | 92 | 66 | 0
2125633178 | AC06628 | 05/11/2023 | 20.8 | 3.19 | 88 | 67 | 0.04
2125633178 | AC06628 | 05/12/2023 | 21.55 | 3.29 | 86 | 66 | 0
2125633178 | AC06628 | 05/13/2023 | 22.03 | 3.35 | 85 | 64 | 0
2125633178 | AC06628 | 05/14/2023 | 21.46 | 3.28 | 86 | 63 | 0
2125633178 | AC06628 | 05/15/2023 | 20.85 | 3.2 | 89 | 62 | 0
2125633178 | AC06628 | 05/16/2023 | 20.14 | 3.1 | 88 | 64 | 0
2125633178 | AC06628 | 05/17/2023 | 20.19 | 3.11 | 92 | 67 | 0
2125633178 | AC06628 | 05/18/2023 | 20.55 | 3.16 | 89 | 65 | 1.24
2125633178 | AC06628 | 05/19/2023 | 21.42 | 3.27 | 88 | 66 | 0.02
2125633178 | AC06628 | 05/20/2023 | 20.39 | 3.14 | 88 | 66 | 0
2125633178 | AC06628 | 05/21/2023 | 21.13 | 3.23 | 88 | 67
2125633178 | AC06628 | 05/22/2023 | 24.8 | 3.72 | 88 | 67 | 0.65
2125633178 | AC06628 | 05/23/2023 | 25.62 | 3.83 | 85 | 67 | 0.56
2125633178 | AC06628 | 05/24/2023 | 25.38 | 3.79 | 83 | 66 | 0.12
2125633178 | AC06628 | 05/25/2023 | 24.89 | 3.73 | 83 | 66 | 0.16
2125633178 | AC06628 | 05/26/2023 | 27.21 | 4.04 | 82 | 62 | 0.05
2125633178 | AC06628 | 05/27/2023 | 27.06 | 4.02 | 81 | 56 | Trace Value
2125633178 | AC06628 | 05/28/2023 | 25.65 | 3.83 | 85 | 55 | 0
2125633178 | AC06628 | 05/29/2023 | 25.56 | 3.82 | 87 | 60 | 0
2125633178 | AC06628 | 05/30/2023 | 24.22 | 3.64 | 88 | 62 | 0
2125633178 | AC06628 | 05/31/2023 | 22.32 | 3.39 | 87 | 68 | 0
2125633178 | AC06628 | 06/01/2023 | 22.69 | 3.44 | 85 | 68 | 0
2125633178 | AC06628 | 06/02/2023 | 21.94 | 3.34 | 85 | 67 | 0
2125633178 | AC06628 | 06/03/2023 | 21.89 | 3.33 | 84 | 67 | 0
2125633178 | AC06628 | 06/04/2023 | 22.59 | 3.43 | 84 | 66 | 0
2125633178 | AC06628 | 06/05/2023 | 20.76 | 3.19 | 84 | 64 | 0.3
2125633178 | AC06628 | 06/06/2023 | 21.02 | 3.16 | 88 | 62
2125633178 | AC06628 | 06/07/2023 | 24.71 | 3.63 | 91 | 68 | 0
2125633178 | AC06628 | 06/08/2023 | 26.26 | 3.83 | 92 | 68 | 1.64
2125633178 | AC06628 | 06/09/2023 | 28.67 | 4.14 | 92 | 68 | 0
2125633178 | AC06628 | 06/10/2023 | 27.57 | 3.99 | 88 | 67 | 0.54
2125633178 | AC06628 | 06/11/2023 | 27.37 | 3.97 | 91 | 69 | 0.09
2125633178 | AC06628 | 06/12/2023 | 25.18 | 3.69 | 94 | 69 | 0
2125633178 | AC06628 | 06/13/2023 | 24.52 | 3.6 | 95 | 71
2125633178 | AC06628 | 06/14/2023 | 24.53 | 3.61 | 95 | 71 | 0
2125633178 | AC06628 | 06/15/2023 | 25.22 | 3.69 | 95 | 66 | 0.44
2125633178 | AC06628 | 06/16/2023 | 26.02 | 3.8 | 95 | 68 | 0.45
2125633178 | AC06628 | 06/17/2023 | 25.91 | 3.78 | 93 | 68 | 0.91
2125633178 | AC06628 | 06/18/2023 | 26.09 | 3.8 | 94 | 68 | 0.28
2125633178 | AC06628 | 06/19/2023 | 24.26 | 3.57 | 93 | 70 | 0.63
2125633178 | AC06628 | 06/20/2023 | 29.12 | 4.19 | 91 | 69 | 0.46
2125633178 | AC06628 | 06/21/2023 | 26.72 | 3.89 | 91 | 71 | 0.24
2125633178 | AC06628 | 06/22/2023 | 26.38 | 3.84 | 93 | 66 | 0.04
2125633178 | AC06628 | 06/23/2023 | 28.08 | 4.06 | 91 | 69 | 0.35
2125633178 | AC06628 | 06/24/2023 | 28.46 | 4.11 | 92 | 70 | 0.24
2125633178 | AC06628 | 06/25/2023 | 26.21 | 3.82 | 91 | 70 | 0.15
2125633178 | AC06628 | 06/26/2023 | 23.87 | 3.52 | 94 | 70 | 0
2125633178 | AC06628 | 06/27/2023 | 22.64 | 3.36 | 97 | 71 | 0
2125633178 | AC06628 | 06/28/2023 | 24.21 | 3.56 | 95 | 72 | 0
2125633178 | AC06628 | 06/29/2023 | 24.94 | 3.66 | 95 | 71 | 0.88
2125633178 | AC06628 | 06/30/2023 | 23.88 | 3.52 | 94 | 71 | 0
2125633178 | AC06628 | 07/01/2023 | 22.81 | 3.39 | 94 | 71 | 0
2125633178 | AC06628 | 07/02/2023 | 22.47 | 3.34 | 95 | 71 | 0
2125633178 | AC06628 | 07/03/2023 | 20.88 | 3.14 | 97 | 72 | 0
2125633178 | AC06628 | 07/04/2023 | 22.31 | 3.32 | 95 | 73 | 0
2125633178 | AC06628 | 07/05/2023 | 21.32 | 3.2 | 95 | 74 | 0
2125633178 | AC06628 | 07/06/2023 | 20.4 | 3.08 | 96 | 73 | 0.04
2125633178 | AC06628 | 07/07/2023 | 21.21 | 3.2 | 95 | 73 | 0.03
2125633178 | AC06628 | 07/08/2023 | 21.62 | 3.25 | 94 | 74 | 0.31
2125633178 | AC06628 | 07/09/2023 | 21.29 | 3.21 | 96 | 74 | 0.2
2125633178 | AC06628 | 07/10/2023 | 21.37 | 3.22 | 96 | 74 | 0
2125633178 | AC06628 | 07/11/2023 | 21.61 | 3.25 | 94 | 73 | 0.78
2125633178 | AC06628 | 07/12/2023 | 22.12 | 3.32 | 94 | 73 | 0.1
2125633178 | AC06628 | 07/13/2023 | 21.44 | 3.23 | 94 | 72 | Trace Value
2125633178 | AC06628 | 07/14/2023 | 23.7 | 3.52 | 95 | 73 | 0.33
2125633178 | AC06628 | 07/15/2023 | 23.43 | 3.49 | 96 | 73 | 0.12
2125633178 | AC06628 | 07/16/2023 | 25.58 | 3.76 | 96 | 74 | 0.15
2125633178 | AC06628 | 07/17/2023 | 24.4 | 3.61 | 95 | 74 | 2.8
2125633178 | AC06628 | 07/18/2023 | 24.68 | 3.65 | 95 | 72 | 0.22
2125633178 | AC06628 | 07/19/2023 | 25.51 | 3.75 | 95 | 71 | 0.14
2125633178 | AC06628 | 07/20/2023 | 24.79 | 3.66 | 96 | 73 | 0
2125633178 | AC06628 | 07/21/2023 | 23.04 | 3.44 | 99 | 74 | 0
2125633178 | AC06628 | 07/22/2023 | 23.9 | 3.55 | 97 | 75 | 0
2125633178 | AC06628 | 07/23/2023 | 26.89 | 3.93 | 94 | 71 | 0.7
2125633178 | AC06628 | 07/24/2023 | 25.05 | 3.69 | 93 | 73 | 1.12
2125633178 | AC06628 | 07/25/2023 | 24.04 | 3.57 | 93 | 73 | 0.3
2125633178 | AC06628 | 07/26/2023 | 23.76 | 3.53 | 92 | 73 | 0
2125633178 | AC06628 | 07/27/2023 | 23.81 | 3.54 | 91 | 73 | 0
2125633178 | AC06628 | 07/28/2023 | 24.86 | 3.67 | 92 | 73 | 1
2125633178 | AC06628 | 07/29/2023 | 25.71 | 3.78 | 93 | 73 | 0.05
2125633178 | AC06628 | 07/30/2023 | 27.75 | 4.04 | 95 | 74 | Trace Value
2125633178 | AC06628 | 07/31/2023 | 26.94 | 3.94 | 95 | 71 | 0.74
2125633178 | AC06628 | 08/01/2023 | 26.81 | 3.92 | 95 | 71 | 0.08
2125633178 | AC06628 | 08/02/2023 | 25.39 | 3.74 | 93 | 74 | 0
2125633178 | AC06628 | 08/03/2023 | 23.74 | 3.53 | 91 | 73 | 0
2125633178 | AC06628 | 08/04/2023 | 25.52 | 3.75 | 94 | 73 | 0
2125633178 | AC06628 | 08/05/2023 | 27.46 | 3.95 | 94 | 73 | 0.17
2125633178 | AC06628 | 08/06/2023 | 26.55 | 3.84 | 95 | 74 | 0.66
2125633178 | AC06628 | 08/07/2023 | 25.35 | 3.68 | 97 | 75 | 0.03
2125633178 | AC06628 | 08/08/2023 | 24.59 | 3.59 | 99 | 75 | 0
2125633178 | AC06628 | 08/09/2023 | 26.3 | 3.81 | 99 | 74 | 0
2125633178 | AC06628 | 08/10/2023 | 26.53 | 3.84 | 100 | 75 | 0.16
2125633178 | AC06628 | 08/11/2023 | 27.58 | 3.97 | 99 | 75 | 0
2125633178 | AC06628 | 08/12/2023 | 31.66 | 4.49 | 98 | 76 | 0.25
2125633178 | AC06628 | 08/13/2023 | 29.1 | 4.16 | 97 | 74 | 0
2125633178 | AC06628 | 08/14/2023 | 25.71 | 3.73 | 97 | 76 | 0
2125633178 | AC06628 | 08/15/2023 | 24.95 | 3.63 | 97 | 75 | 0
2125633178 | AC06628 | 08/16/2023 | 30.84 | 4.39 | 96 | 73 | 0.09
2125633178 | AC06628 | 08/17/2023 | 31.71 | 4.5 | 93 | 72 | 0.36
2125633178 | AC06628 | 08/18/2023 | 29.85 | 4.26 | 93 | 73 | 1.09
2125633178 | AC06628 | 08/19/2023 | 30.56 | 4.35 | 93 | 72 | 0.69
2125633178 | AC06628 | 08/20/2023 | 27.95 | 4.02 | 92 | 75 | 0
2125633178 | AC06628 | 08/21/2023 | 25.09 | 3.65 | 92 | 74 | 0
2125633178 | AC06628 | 08/22/2023 | 24.87 | 3.62 | 93 | 72 | 0
2125633178 | AC06628 | 08/23/2023 | 23.85 | 3.49 | 93 | 74 | 0
2125633178 | AC06628 | 08/24/2023 | 22.72 | 3.35 | 93 | 74 | 0.99
2125633178 | AC06628 | 08/25/2023 | 21.93 | 3.25 | 92 | 71 | 0
2125633178 | AC06628 | 08/26/2023 | 22.43 | 3.31 | 95 | 73 | 0
2125633178 | AC06628 | 08/27/2023 | 22.98 | 3.38 | 95 | 72
2125633178 | AC06628 | 08/28/2023 | 21.07 | 3.14 | 96 | 74 | Trace Value
2125633178 | AC06628 | 08/29/2023 | 20.62 | 3.08 | 95 | 74 | 0
2125633178 | AC06628 | 08/30/2023 | 24.91 | 3.63 | 94 | 74 | 0.93
2125633178 | AC06628 | 08/31/2023 | 22.58 | 3.33 | 94 | 74 | 0.05
2125633178 | AC06628 | 09/01/2023 | 23.11 | 3.4 | 92 | 73 | 0
2125633178 | AC06628 | 09/02/2023 | 22.53 | 3.32 | 91 | 72
2125633178 | AC06628 | 09/03/2023 | 22.15 | 3.27 | 92 | 71 | 0.05
2125633178 | AC06628 | 09/04/2023 | 21.74 | 3.22 | 90 | 68 | 0
2125633178 | AC06628 | 09/05/2023 | 22.4 | 3.31 | 90 | 64 | 0
2125633178 | AC06628 | 09/06/2023 | 20.87 | 3.11 | 94 | 69 | 0
2125633178 | AC06628 | 09/07/2023 | 21.2 | 3.22 | 95 | 70
2125633178 | AC06628 | 09/08/2023 | 23.72 | 3.54 | 95 | 69 | 0
2125633178 | AC06628 | 09/09/2023 | 24.16 | 3.6 | 94 | 64 | 0.48
2125633178 | AC06628 | 09/10/2023 | 23.73 | 3.54 | 93 | 71 | Trace Value
2125633178 | AC06628 | 09/11/2023 | 21.24 | 3.22 | 92 | 72 | 0
2125633178 | AC06628 | 09/12/2023 | 22.06 | 3.33 | 92 | 71 | Trace Value
2125633178 | AC06628 | 09/13/2023 | 26.07 | 3.84 | 92 | 72 | 0.03
2125633178 | AC06628 | 09/14/2023 | 25.72 | 3.8 | 91 | 71 | 0.29
2125633178 | AC06628 | 09/15/2023 | 23.98 | 3.57 | 88 | 70 | 0
2125633178 | AC06628 | 09/16/2023 | 24.02 | 3.58 | 87 | 69 | 0.54
2125633178 | AC06628 | 09/17/2023 | 24.17 | 3.6 | 92 | 70 | 0
2125633178 | AC06628 | 09/18/2023 | 22.89 | 3.43 | 89 | 68 | 0.08
2125633178 | AC06628 | 09/19/2023 | 22.58 | 3.39 | 88 | 64 | 0
2125633178 | AC06628 | 09/20/2023 | 21.3 | 3.23 | 88 | 69 | 0
2125633178 | AC06628 | 09/21/2023 | 22.27 | 3.35 | 87 | 68 | 0.08
2125633178 | AC06628 | 09/22/2023 | 21.08 | 3.2 | 85 | 65 | 0.3
2125633178 | AC06628 | 09/23/2023 | 22.38 | 3.37 | 87 | 61 | 0
2125633178 | AC06628 | 09/24/2023 | 22.71 | 3.41 | 89 | 59 | 0
2125633178 | AC06628 | 09/25/2023 | 21.54 | 3.26 | 90 | 66 | 0
2125633178 | AC06628 | 09/26/2023 | 25 | 3.71 | 89 | 71 | 2.11
2125633178 | AC06628 | 09/27/2023 | 30.58 | 4.43 | 88 | 71 | 0.91
2125633178 | AC06628 | 09/28/2023 | 34.45 | 4.93 | 87 | 71 | 0.81
2125633178 | AC06628 | 09/29/2023 | 32.48 | 4.67 | 85 | 71 | 0.02
2125633178 | AC06628 | 09/30/2023 | 41.09 | 5.78 | 85 | 71 | 0.2
2125633178 | AC06628 | 10/01/2023 | 40.2 | 5.67 | 85 | 70 | 2.53
2125633178 | AC06628 | 10/02/2023 | 35.68 | 5.09 | 85 | 69 | 0.56
2125633178 | AC06628 | 10/03/2023 | 33.44 | 4.8 | 85 | 70 | 0
2125633178 | AC06628 | 10/04/2023 | 31.71 | 4.57 | 86 | 70 | 0.05
2125633178 | AC06628 | 10/05/2023 | 29.11 | 4.21 | 86 | 69 | 0
2125633178 | AC06628 | 10/06/2023 | 28.54 | 4.13 | 87 | 66 | 0
2125633178 | AC06628 | 10/07/2023 | 28.13 | 4.08 | 90 | 56 | 0
2125633178 | AC06628 | 10/08/2023 | 28.91 | 4.18 | 82 | 53 | 0
2125633178 | AC06628 | 10/09/2023 | 26.55 | 3.88 | 80 | 55 | 0
2125633178 | AC06628 | 10/10/2023 | 26.49 | 3.87 | 84 | 56 | 0
2125633178 | AC06628 | 10/11/2023 | 26.91 | 3.93 | 84 | 65 | 0
2125633178 | AC06628 | 10/12/2023 | 47.66 | 6.58 | 88 | 72 | 2.8
2125633178 | AC06628 | 10/13/2023 | 36.96 | 5.21 | 89 | 68 | 1.67
2125633178 | AC06628 | 10/14/2023 | 35.94 | 5.08 | 89 | 64 | 0
2125633178 | AC06628 | 10/15/2023 | 35.53 | 5.03 | 82 | 55 | 0
2125633178 | AC06628 | 10/16/2023 | 33.3 | 4.74 | 76 | 50 | 0
2125633178 | AC06628 | 10/17/2023 | 33.32 | 4.75 | 75 | 49 | 0
2125633178 | AC06628 | 10/18/2023 | 32.11 | 4.59 | 77 | 50 | 0
2125633178 | AC06628 | 10/19/2023 | 29.42 | 4.25 | 81 | 55 | 0
2125633178 | AC06628 | 10/20/2023 | 30.13 | 4.34 | 83 | 55 | 0
2125633178 | AC06628 | 10/21/2023 | 28.93 | 4.18 | 83 | 55 | 0
2125633178 | AC06628 | 10/22/2023 | 30.36 | 4.37 | 86 | 52 | 0
2125633178 | AC06628 | 10/23/2023 | 26.82 | 3.91 | 83 | 58 | 0
2125633178 | AC06628 | 10/24/2023 | 27.4 | 3.99 | 82 | 67 | 0
2125633178 | AC06628 | 10/25/2023 | 26.5 | 3.87 | 82 | 68 | 0
2125633178 | AC06628 | 10/26/2023 | 26.69 | 3.9 | 82 | 65 | 0
2125633178 | AC06628 | 10/27/2023 | 25.95 | 3.8 | 83 | 64 | 0
2125633178 | AC06628 | 10/28/2023 | 26.48 | 3.87 | 84 | 62 | 0
2125633178 | AC06628 | 10/29/2023 | 27.08 | 3.95 | 84 | 61 | 0
2125633178 | AC06628 | 10/30/2023 | 25.43 | 3.74 | 85 | 60 | 0
2125633178 | AC06628 | 10/31/2023 | 25.65 | 3.76 | 84 | 58 | 0
2125633178 | AC06628 | 11/01/2023 | 25.86 | 3.79 | 76 | 53 | 0
2125633178 | AC06628 | 11/02/2023 | 25.63 | 3.76 | 75 | 53 | 0
2125633178 | AC06628 | 11/03/2023 | 25.21 | 3.71 | 79 | 59 | 0
2125633178 | AC06628 | 11/04/2023 | 26.5 | 3.87 | 79 | 55 | 0
2125633178 | AC06628 | 11/05/2023 | 29.94 | 4.31 | 80 | 51 | 0
2125633178 | AC06628 | 11/06/2023 | 26.29 | 3.84 | 81 | 48 | 0
2125633178 | AC06628 | 11/07/2023 | 25.43 | 3.73 | 83 | 53 | 0
2125633178 | AC06628 | 11/08/2023 | 25.63 | 3.75 | 84 | 50 | 0
2125633178 | AC06628 | 11/09/2023 | 25.02 | 3.68 | 85 | 55 | 0
2125633178 | AC06628 | 11/10/2023 | 24.31 | 3.58 | 86 | 60 | 0
2125633178 | AC06628 | 11/11/2023 | 25.58 | 3.75 | 83 | 65 | 0.33
2125633178 | AC06628 | 11/12/2023 | 27.91 | 4.05 | 80 | 63 | 0
2125633178 | AC06628 | 11/13/2023 | 24.3 | 3.58 | 77 | 62 | 0
2125633178 | AC06628 | 11/14/2023 | 28.36 | 4.1 | 77 | 61 | 0.12
2125633178 | AC06628 | 11/15/2023 | 28.31 | 4.1 | 77 | 64 | 0.05
2125633178 | AC06628 | 11/16/2023 | 33.69 | 4.79 | 78 | 62 | 0.16
2125633178 | AC06628 | 11/17/2023 | 43.14 | 6 | 79 | 61 | 2.1
2125633178 | AC06628 | 11/18/2023 | 37.15 | 5.23 | 78 | 55 | 0.66
2125633178 | AC06628 | 11/19/2023 | 35.1 | 4.97 | 80 | 56 | 0
2125633178 | AC06628 | 11/20/2023 | 30.93 | 4.43 | 79 | 59 | 0.02
2125633178 | AC06628 | 11/21/2023 | 31.09 | 4.45 | 81 | 52 | 0.02
2125633178 | AC06628 | 11/22/2023 | 31.59 | 4.52 | 81 | 47 | 0
2125633178 | AC06628 | 11/23/2023 | 33.8 | 4.8 | 73 | 48 | 0.01
2125633178 | AC06628 | 11/24/2023 | 32.6 | 4.65 | 75 | 52 | 0.01
2125633178 | AC06628 | 11/25/2023 | 30.85 | 4.42 | 75 | 53 | 0.07
2125633178 | AC06628 | 11/26/2023 | 33.48 | 4.76 | 75 | 55 | 0.01
2125633178 | AC06628 | 11/27/2023 | 33.02 | 4.7 | 74 | 44 | 0.55
2125633178 | AC06628 | 11/28/2023 | 34.21 | 4.85 | 69 | 39 | 0
2125633178 | AC06628 | 11/29/2023 | 33.11 | 4.71 | 68 | 36 | 0
2125633178 | AC06628 | 11/30/2023 | 32.32 | 4.61 | 86 | 41 | 0
2125633178 | AC06628 | 12/01/2023 | 29.79 | 4.29 | 82 | 55 | 0
2125633178 | AC06628 | 12/02/2023 | 29.19 | 4.21 | 83 | 64 | 0
2125633178 | AC06628 | 12/03/2023 | 31.56 | 4.51 | 82 | 62 | 0.02
2125633178 | AC06628 | 12/04/2023 | 32.92 | 4.69 | 79 | 51 | 0.23
2125633178 | AC06628 | 12/05/2023 | 32.59 | 4.61 | 72 | 47 | 0
2125633178 | AC06628 | 12/06/2023 | 32.98 | 4.66 | 69 | 41 | 0
2125633178 | AC06628 | 12/07/2023 | 32.7 | 4.62 | 67 | 41 | 0
2125633178 | AC06628 | 12/08/2023 | 30.85 | 4.39 | 74 | 47 | 0
2125633178 | AC06628 | 12/09/2023 | 29.78 | 4.25 | 82 | 56 | 0.04
2125633178 | AC06628 | 12/10/2023 | 30.19 | 4.3 | 83 | 44 | 0
2125633178 | AC06628 | 12/11/2023 | 30.89 | 4.39 | 67 | 43 | 0.25
2125633178 | AC06628 | 12/12/2023 | 30.19 | 4.3 | 71 | 43 | 0
2125633178 | AC06628 | 12/13/2023 | 28.93 | 4.14 | 73 | 58 | 0
2125633178 | AC06628 | 12/14/2023 | 29.66 | 4.23 | 72 | 59 | 0.66
2125633178 | AC06628 | 12/15/2023 | 29.34 | 4.19 | 72 | 60 | 0.07
2125633178 | AC06628 | 12/16/2023 | 33.31 | 4.7 | 73 | 58 | 0.11
2125633178 | AC06628 | 12/17/2023 | 45.15 | 6.22 | 74 | 48 | 4.04
2125633178 | AC06628 | 12/18/2023 | 33.61 | 4.74 | 68 | 40 | 0.05
2125633178 | AC06628 | 12/19/2023 | 37.7 | 5.26 | 65 | 41 | 0
2125633178 | AC06628 | 12/20/2023 | 35.41 | 4.97 | 66 | 44 | 0
2125633178 | AC06628 | 12/21/2023 | 34.51 | 4.85 | 68 | 46 | 0
2125633178 | AC06628 | 12/22/2023 | 33.08 | 4.67 | 70 | 49 | 0
2125633178 | AC06628 | 12/23/2023 | 33.17 | 4.68 | 73 | 53 | 0
2125633178 | AC06628 | 12/24/2023 | 32.69 | 4.62 | 73 | 53 | 0
2125633178 | AC06628 | 12/25/2023 | 30.98 | 4.4 | 73 | 60 | 0.09
2125633178 | AC06628 | 12/26/2023 | 30.8 | 4.38 | 74 | 54 | 0.1
2125633178 | AC06628 | 12/27/2023 | 31.33 | 4.45 | 71 | 49 | 0
2125633178 | AC06628 | 12/28/2023 | 32.12 | 4.55 | 66 | 44 | 0.04
2125633178 | AC06628 | 12/29/2023 | 33.3 | 4.7 | 55 | 46 | 0
2125633178 | AC06628 | 12/30/2023 | 34.22 | 4.82 | 59 | 37 | 0
2125633178 | AC06628 | 12/31/2023 | 34.27 | 4.82 | 63 | 36 | 0
|  | Yearly Daily Average: | 26.0426 | 3.811
|  | Wetter Months' Daily Average: | 29.4108 | 4.2381

## 57-3
Daily Billed Information (PS 57-3 - 371 Underwood Trail: 2023 Reading Data)
Bill Account | Meter Number | Date | Consumption Recorded (kWh/day) | Estimated Cost ($/day) | Avg. High Temperature (°F) | Avg. Low Temperature (°F) | Rain Recorded by NOAA (inches)
1938397534 | AC85272 | 01/01/2023 | 34.75 | 4.59 | 79 | 58 | 0.04
1938397534 | AC85272 | 01/02/2023 | 34.89 | 4.61 | 78 | 53 | 0
1938397534 | AC85272 | 01/03/2023 | 34.85 | 4.61 | 81 | 51 | 0
1938397534 | AC85272 | 01/04/2023 | 33.2 | 4.41 | 83 | 57 | 0
1938397534 | AC85272 | 01/05/2023 | 34.72 | 4.59 | 77 | 46 | 0.04
1938397534 | AC85272 | 01/06/2023 | 36.36 | 4.97 | 68 | 41 | 0
1938397534 | AC85272 | 01/07/2023 | 36.97 | 5.04 | 70 | 38 | 0
1938397534 | AC85272 | 01/08/2023 | 36.82 | 5.02 | 76 | 42 | 0
1938397534 | AC85272 | 01/09/2023 | 33.57 | 4.62 | 74 | 47 | 0
1938397534 | AC85272 | 01/10/2023 | 36.27 | 4.96 | 71 | 42 | 0
1938397534 | AC85272 | 01/11/2023 | 35.24 | 4.83 | 73 | 38 | 0
1938397534 | AC85272 | 01/12/2023 | 35.06 | 4.8 | 80 | 44 | 0
1938397534 | AC85272 | 01/13/2023 | 36.69 | 5.01 | 71 | 35 | 0.12
1938397534 | AC85272 | 01/14/2023 | 39.83 | 5.4 | 61 | 30 | 0
1938397534 | AC85272 | 01/15/2023 | 39.11 | 5.31 | 63 | 30 | 0
1938397534 | AC85272 | 01/16/2023 | 36.49 | 4.98 | 71 | 30 | 0
1938397534 | AC85272 | 01/17/2023 | 34.38 | 4.72 | 75 | 34 | 0
1938397534 | AC85272 | 01/18/2023 | 34.14 | 4.69 | 79 | 46 | N/A
1938397534 | AC85272 | 01/19/2023 | 31.36 | 4.34 | 82 | 54 | 0
1938397534 | AC85272 | 01/20/2023 | 32 | 4.42 | 76 | 49 | 0
1938397534 | AC85272 | 01/21/2023 | 35.57 | 4.87 | 76 | 47 | T
1938397534 | AC85272 | 01/22/2023 | 36.73 | 5.01 | 82 | 54 | 0.33
1938397534 | AC85272 | 01/23/2023 | 36.92 | 5.04 | 75 | 44 | 0.05
1938397534 | AC85272 | 01/24/2023 | 36.59 | 5 | 76 | 41 | 0
1938397534 | AC85272 | 01/25/2023 | 32.73 | 4.51 | 85 | 43 | 0
1938397534 | AC85272 | 01/26/2023 | 35.84 | 4.9 | 72 | 38 | 0.09
1938397534 | AC85272 | 01/27/2023 | 37.79 | 5.14 | 62 | 37 | 0
1938397534 | AC85272 | 01/28/2023 | 37.72 | 5.14 | 69 | 35 | 0
1938397534 | AC85272 | 01/29/2023 | 35.21 | 4.82 | 78 | 55 | 0
1938397534 | AC85272 | 01/30/2023 | 31.84 | 4.4 | 86 | 58 | 0
1938397534 | AC85272 | 01/31/2023 | 33.94 | 4.66 | 83 | 59 | 0
1938397534 | AC85272 | 02/01/2023 | 34.92 | 4.79 | 82 | 58 | 0
1938397534 | AC85272 | 02/02/2023 | 33.68 | 4.63 | 82 | 57 | 0
1938397534 | AC85272 | 02/03/2023 | 37.62 | 5.12 | 78 | 50 | 0
1938397534 | AC85272 | 02/04/2023 | 38.79 | 5.24 | 70 | 47 | 0.17
1938397534 | AC85272 | 02/05/2023 | 39.38 | 5.32 | 73 | 48 | 0
1938397534 | AC85272 | 02/06/2023 | 36.08 | 4.91 | 71 | 46 | 0.01
1938397534 | AC85272 | 02/07/2023 | 36.17 | 4.92 | 76 | 44
1938397534 | AC85272 | 02/08/2023 | 34.47 | 4.71 | 79 | 49 | 0
1938397534 | AC85272 | 02/09/2023 | 34.16 | 4.67 | 83 | 58 | 0
1938397534 | AC85272 | 02/10/2023 | 36.77 | 4.99 | 85 | 46 | 0.16
1938397534 | AC85272 | 02/11/2023 | 38.05 | 5.15 | 79 | 40 | 0.57
1938397534 | AC85272 | 02/12/2023 | 40.88 | 5.5 | 71 | 40 | 0.12
1938397534 | AC85272 | 02/13/2023 | 37.27 | 5.05 | 71 | 40 | Trace Value
1938397534 | AC85272 | 02/14/2023 | 36.92 | 5.01 | 75 | 39 | 0
1938397534 | AC85272 | 02/15/2023 | 35.03 | 4.78 | 82 | 50 | 0
1938397534 | AC85272 | 02/16/2023 | 33.13 | 4.54 | 85 | 57 | 0
1938397534 | AC85272 | 02/17/2023 | 31.91 | 4.39 | 89 | 45
1938397534 | AC85272 | 02/18/2023 | 36.95 | 5.01 | 67 | 46 | 0.04
1938397534 | AC85272 | 02/19/2023 | 35.84 | 4.88 | 80 | 48 | 0
1938397534 | AC85272 | 02/20/2023 | 32.9 | 4.51 | 82 | 53 | 0
1938397534 | AC85272 | 02/21/2023 | 32.58 | 4.47 | 85 | 57 | 0
1938397534 | AC85272 | 02/22/2023 | 32.44 | 4.45 | 87 | 58 | 0
1938397534 | AC85272 | 02/23/2023 | 31.71 | 4.36 | 89 | 60 | 0
1938397534 | AC85272 | 02/24/2023 | 32.14 | 4.42 | 87 | 58 | 0
1938397534 | AC85272 | 02/25/2023 | 32.59 | 4.47 | 87 | 58
1938397534 | AC85272 | 02/26/2023 | 34.38 | 4.7 | 87 | 56 | 0
1938397534 | AC85272 | 02/27/2023 | 32.08 | 4.41 | 87 | 57 | 0
1938397534 | AC85272 | 02/28/2023 | 29.9 | 4.14 | 87 | 57 | 0
1938397534 | AC85272 | 03/01/2023 | 32.31 | 4.44 | 86 | 58 | 0
1938397534 | AC85272 | 03/02/2023 | 32.19 | 4.42 | 87 | 56 | 0
1938397534 | AC85272 | 03/03/2023 | 29.54 | 4.09 | 90 | 55 | 0
1938397534 | AC85272 | 03/04/2023 | 29.6 | 4.1 | 88 | 52 | 0
1938397534 | AC85272 | 03/05/2023 | 31.28 | 4.31 | 81 | 54 | 0.05
1938397534 | AC85272 | 03/06/2023 | 28.91 | 4.01 | 84 | 56 | 0
1938397534 | AC85272 | 03/07/2023 | 29.32 | 4.49 | 87 | 56
1938397534 | AC85272 | 03/08/2023 | 31.7 | 4.81 | 85 | 58 | 0
1938397534 | AC85272 | 03/09/2023 | 31.27 | 4.75 | 80 | 51 | 0
1938397534 | AC85272 | 03/10/2023 | 30.92 | 4.71 | 85 | 54
1938397534 | AC85272 | 03/11/2023 | 34.79 | 5.23 | 81 | 51 | 1.3
1938397534 | AC85272 | 03/12/2023 | 32.59 | 4.93 | 86 | 48 | 0
1938397534 | AC85272 | 03/13/2023 | 37.95 | 5.67 | 81 | 46 | 1.17
1938397534 | AC85272 | 03/14/2023 | 40.82 | 6.06 | 70 | 43 | 0.6
1938397534 | AC85272 | 03/15/2023 | 40.66 | 6.04 | 68 | 43 | 0
1938397534 | AC85272 | 03/16/2023 | 37.92 | 5.66 | 77 | 37 | 0
1938397534 | AC85272 | 03/17/2023 | 33.84 | 5.11 | 84 | 48
1938397534 | AC85272 | 03/18/2023 | 36.12 | 5.42 | 80 | 45 | 0
1938397534 | AC85272 | 03/19/2023 | 42.77 | 6.33 | 68 | 43 | 0.02
1938397534 | AC85272 | 03/20/2023 | 37.29 | 5.58 | 69 | 42 | 0.02
1938397534 | AC85272 | 03/21/2023 | 35.68 | 5.36 | 77 | 42 | 0
1938397534 | AC85272 | 03/22/2023 | 35 | 5.26 | 80 | 53 | 0.08
1938397534 | AC85272 | 03/23/2023 | 33.58 | 5.07 | 83 | 53
1938397534 | AC85272 | 03/24/2023 | 34.46 | 5.19 | 86 | 53 | 0
1938397534 | AC85272 | 03/25/2023 | 31.47 | 4.78 | 91 | 60 | 0
1938397534 | AC85272 | 03/26/2023 | 32.09 | 4.87 | 91 | 63 | 0.68
1938397534 | AC85272 | 03/27/2023 | 30.65 | 4.67 | 92 | 62 | 0
1938397534 | AC85272 | 03/28/2023 | 30.4 | 4.64 | 88 | 55 | Trace Value
1938397534 | AC85272 | 03/29/2023 | 32.72 | 4.95 | 75 | 55 | 0
1938397534 | AC85272 | 03/30/2023 | 31.44 | 4.78 | 79 | 51 | 0
1938397534 | AC85272 | 03/31/2023 | 30.99 | 4.72 | 85 | 55 | 0
1938397534 | AC85272 | 04/01/2023 | 30 | 4.58 | 90 | 60 | 0
1938397534 | AC85272 | 04/02/2023 | 31.48 | 4.78 | 85 | 60
1938397534 | AC85272 | 04/03/2023 | 29.51 | 4.51 | 86 | 61 | 0
1938397534 | AC85272 | 04/04/2023 | 29.31 | 4.49 | 88 | 60 | Trace Value
1938397534 | AC85272 | 04/05/2023 | 28.17 | 4.33 | 87 | 63 | 0
1938397534 | AC85272 | 04/06/2023 | 28.82 | 4.31 | 87 | 64 | 0
1938397534 | AC85272 | 04/07/2023 | 29.38 | 4.38 | 85 | 64
1938397534 | AC85272 | 04/08/2023 | 29.52 | 4.4 | 86 | 62
1938397534 | AC85272 | 04/09/2023 | 34.92 | 5.11 | 80 | 60 | 0.01
1938397534 | AC85272 | 04/10/2023 | 40.39 | 5.84 | 79 | 58 | 0.68
1938397534 | AC85272 | 04/11/2023 | 42.72 | 6.15 | 78 | 58 | 1.38
1938397534 | AC85272 | 04/12/2023 | 39.85 | 5.77 | 79 | 59 | 0.03
1938397534 | AC85272 | 04/13/2023 | 38.69 | 5.61 | 87 | 61 | 0.07
1938397534 | AC85272 | 04/14/2023 | 40.96 | 5.92 | 86 | 59 | 0.57
1938397534 | AC85272 | 04/15/2023 | 38.64 | 5.61 | 87 | 60 | 0.02
1938397534 | AC85272 | 04/16/2023 | 46.17 | 6.61 | 88 | 59 | 0
1938397534 | AC85272 | 04/17/2023 | 38.75 | 5.62 | 81 | 50 | 0.04
1938397534 | AC85272 | 04/18/2023 | 40.09 | 5.8 | 81 | 46 | 0.02
1938397534 | AC85272 | 04/19/2023 | 35.22 | 5.15 | 82 | 50 | 0
1938397534 | AC85272 | 04/20/2023 | 33.63 | 4.94 | 84 | 55 | 0
1938397534 | AC85272 | 04/21/2023 | 33.37 | 4.91 | 87 | 59
1938397534 | AC85272 | 04/22/2023 | 33 | 4.86 | 89 | 57 | 0.3
1938397534 | AC85272 | 04/23/2023 | 35.15 | 5.14 | 84 | 53 | 0.42
1938397534 | AC85272 | 04/24/2023 | 31.79 | 4.7 | 80 | 55 | 0
1938397534 | AC85272 | 04/25/2023 | 32.72 | 4.82 | 82 | 61 | 0.25
1938397534 | AC85272 | 04/26/2023 | 32.68 | 4.82 | 84 | 62 | 0.07
1938397534 | AC85272 | 04/27/2023 | 37.49 | 5.46 | 86 | 63 | 0
1938397534 | AC85272 | 04/28/2023 | 48.59 | 6.93 | 87 | 62 | 1.62
1938397534 | AC85272 | 04/29/2023 | 44.5 | 6.39 | 88 | 62 | 0
1938397534 | AC85272 | 04/30/2023 | 47.12 | 6.73 | 85 | 57 | 0.52
1938397534 | AC85272 | 05/01/2023 | 41.31 | 5.96 | 85 | 56 | 0
1938397534 | AC85272 | 05/02/2023 | 39.67 | 5.74 | 87 | 56 | 0
1938397534 | AC85272 | 05/03/2023 | 39 | 5.66 | 86 | 53 | 0
1938397534 | AC85272 | 05/04/2023 | 37.19 | 5.42 | 84 | 53 | 0
1938397534 | AC85272 | 05/05/2023 | 38.53 | 5.55 | 87 | 57 | 0
1938397534 | AC85272 | 05/06/2023 | 37.79 | 5.45 | 86 | 65 | 0
1938397534 | AC85272 | 05/07/2023 | 37.07 | 5.36 | 88 | 61 | 0.02
1938397534 | AC85272 | 05/08/2023 | 34.43 | 5.01 | 87 | 55 | 0
1938397534 | AC85272 | 05/09/2023 | 34.35 | 5 | 91 | 63 | 0
1938397534 | AC85272 | 05/10/2023 | 33.06 | 4.82 | 92 | 66 | 0
1938397534 | AC85272 | 05/11/2023 | 32.3 | 4.72 | 88 | 67 | 0.04
1938397534 | AC85272 | 05/12/2023 | 31.5 | 4.62 | 86 | 66 | 0
1938397534 | AC85272 | 05/13/2023 | 32.59 | 4.76 | 85 | 64 | 0
1938397534 | AC85272 | 05/14/2023 | 33.52 | 4.89 | 86 | 63 | 0
1938397534 | AC85272 | 05/15/2023 | 31.21 | 4.58 | 89 | 62 | 0
1938397534 | AC85272 | 05/16/2023 | 30.85 | 4.53 | 88 | 64 | 0
1938397534 | AC85272 | 05/17/2023 | 30.55 | 4.49 | 92 | 67 | 0
1938397534 | AC85272 | 05/18/2023 | 30.35 | 4.47 | 89 | 65 | 1.24
1938397534 | AC85272 | 05/19/2023 | 31.57 | 4.63 | 88 | 66 | 0.02
1938397534 | AC85272 | 05/20/2023 | 30.52 | 4.49 | 88 | 66 | 0
1938397534 | AC85272 | 05/21/2023 | 31.87 | 4.67 | 88 | 67
1938397534 | AC85272 | 05/22/2023 | 37.7 | 5.44 | 88 | 67 | 0.65
1938397534 | AC85272 | 05/23/2023 | 40.86 | 5.86 | 85 | 67 | 0.56
1938397534 | AC85272 | 05/24/2023 | 39.21 | 5.64 | 83 | 66 | 0.12
1938397534 | AC85272 | 05/25/2023 | 38.46 | 5.54 | 83 | 66 | 0.16
1938397534 | AC85272 | 05/26/2023 | 41.66 | 5.96 | 82 | 62 | 0.05
1938397534 | AC85272 | 05/27/2023 | 41.14 | 5.89 | 81 | 56 | Trace Value
1938397534 | AC85272 | 05/28/2023 | 39.3 | 5.65 | 85 | 55 | 0
1938397534 | AC85272 | 05/29/2023 | 38.87 | 5.59 | 87 | 60 | 0
1938397534 | AC85272 | 05/30/2023 | 34.99 | 5.08 | 88 | 62 | 0
1938397534 | AC85272 | 05/31/2023 | 32.37 | 4.73 | 87 | 68 | 0
1938397534 | AC85272 | 06/01/2023 | 32.92 | 4.81 | 85 | 68 | 0
1938397534 | AC85272 | 06/02/2023 | 33.53 | 4.89 | 85 | 67 | 0
1938397534 | AC85272 | 06/03/2023 | 33.11 | 4.83 | 84 | 67 | 0
1938397534 | AC85272 | 06/04/2023 | 33.93 | 4.94 | 84 | 66 | 0
1938397534 | AC85272 | 06/05/2023 | 31.82 | 4.66 | 84 | 64 | 0.3
1938397534 | AC85272 | 06/06/2023 | 32.01 | 4.58 | 88 | 62
1938397534 | AC85272 | 06/07/2023 | 36.6 | 5.17 | 91 | 68 | 0
1938397534 | AC85272 | 06/08/2023 | 41.57 | 5.81 | 92 | 68 | 1.64
1938397534 | AC85272 | 06/09/2023 | 42.08 | 5.87 | 92 | 68 | 0
1938397534 | AC85272 | 06/10/2023 | 40.69 | 5.69 | 88 | 67 | 0.54
1938397534 | AC85272 | 06/11/2023 | 38.8 | 5.45 | 91 | 69 | 0.09
1938397534 | AC85272 | 06/12/2023 | 37.4 | 5.27 | 94 | 69 | 0
1938397534 | AC85272 | 06/13/2023 | 34.56 | 4.91 | 95 | 71
1938397534 | AC85272 | 06/14/2023 | 34.91 | 4.95 | 95 | 71 | 0
1938397534 | AC85272 | 06/15/2023 | 36.65 | 5.18 | 95 | 66 | 0.44
1938397534 | AC85272 | 06/16/2023 | 37.37 | 5.27 | 95 | 68 | 0.45
1938397534 | AC85272 | 06/17/2023 | 37.67 | 5.3 | 93 | 68 | 0.91
1938397534 | AC85272 | 06/18/2023 | 38.86 | 5.46 | 94 | 68 | 0.28
1938397534 | AC85272 | 06/19/2023 | 36.01 | 5.09 | 93 | 70 | 0.63
1938397534 | AC85272 | 06/20/2023 | 41.48 | 5.79 | 91 | 69 | 0.46
1938397534 | AC85272 | 06/21/2023 | 39.73 | 5.57 | 91 | 71 | 0.24
1938397534 | AC85272 | 06/22/2023 | 38.46 | 5.41 | 93 | 66 | 0.04
1938397534 | AC85272 | 06/23/2023 | 40.48 | 5.67 | 91 | 69 | 0.35
1938397534 | AC85272 | 06/24/2023 | 41.57 | 5.81 | 92 | 70 | 0.24
1938397534 | AC85272 | 06/25/2023 | 39.34 | 5.52 | 91 | 70 | 0.15
1938397534 | AC85272 | 06/26/2023 | 37.42 | 5.27 | 94 | 70 | 0
1938397534 | AC85272 | 06/27/2023 | 33.99 | 4.83 | 97 | 71 | 0
1938397534 | AC85272 | 06/28/2023 | 35.47 | 5.02 | 95 | 72 | 0
1938397534 | AC85272 | 06/29/2023 | 37.81 | 5.32 | 95 | 71 | 0.88
1938397534 | AC85272 | 06/30/2023 | 34.85 | 4.94 | 94 | 71 | 0
1938397534 | AC85272 | 07/01/2023 | 34.16 | 4.86 | 94 | 71 | 0
1938397534 | AC85272 | 07/02/2023 | 34.09 | 4.85 | 95 | 71 | 0
1938397534 | AC85272 | 07/03/2023 | 32.28 | 4.61 | 97 | 72 | 0
1938397534 | AC85272 | 07/04/2023 | 32.63 | 4.66 | 95 | 73 | 0
1938397534 | AC85272 | 07/05/2023 | 32.17 | 4.6 | 95 | 74 | 0
1938397534 | AC85272 | 07/06/2023 | 30.96 | 4.44 | 96 | 73 | 0.04
1938397534 | AC85272 | 07/07/2023 | 32.36 | 4.65 | 95 | 73 | 0.03
1938397534 | AC85272 | 07/08/2023 | 33.6 | 4.81 | 94 | 74 | 0.31
1938397534 | AC85272 | 07/09/2023 | 32.18 | 4.62 | 96 | 74 | 0.2
1938397534 | AC85272 | 07/10/2023 | 32.01 | 4.6 | 96 | 74 | 0
1938397534 | AC85272 | 07/11/2023 | 33.38 | 4.78 | 94 | 73 | 0.78
1938397534 | AC85272 | 07/12/2023 | 33.45 | 4.79 | 94 | 73 | 0.1
1938397534 | AC85272 | 07/13/2023 | 34.05 | 4.86 | 94 | 72 | Trace Value
1938397534 | AC85272 | 07/14/2023 | 36.22 | 5.14 | 95 | 73 | 0.33
1938397534 | AC85272 | 07/15/2023 | 38.03 | 5.38 | 96 | 73 | 0.12
1938397534 | AC85272 | 07/16/2023 | 39.72 | 5.59 | 96 | 74 | 0.15
1938397534 | AC85272 | 07/17/2023 | 38.9 | 5.49 | 95 | 74 | 2.8
1938397534 | AC85272 | 07/18/2023 | 40.59 | 5.7 | 95 | 72 | 0.22
1938397534 | AC85272 | 07/19/2023 | 38.98 | 5.5 | 95 | 71 | 0.14
1938397534 | AC85272 | 07/20/2023 | 38.18 | 5.4 | 96 | 73 | 0
1938397534 | AC85272 | 07/21/2023 | 35.44 | 5.04 | 99 | 74 | 0
1938397534 | AC85272 | 07/22/2023 | 36.19 | 5.14 | 97 | 75 | 0
1938397534 | AC85272 | 07/23/2023 | 42.23 | 5.92 | 94 | 71 | 0.7
1938397534 | AC85272 | 07/24/2023 | 39.4 | 5.55 | 93 | 73 | 1.12
1938397534 | AC85272 | 07/25/2023 | 37.57 | 5.32 | 93 | 73 | 0.3
1938397534 | AC85272 | 07/26/2023 | 35.28 | 5.02 | 92 | 73 | 0
1938397534 | AC85272 | 07/27/2023 | 35.8 | 5.09 | 91 | 73 | 0
1938397534 | AC85272 | 07/28/2023 | 37.94 | 5.36 | 92 | 73 | 1
1938397534 | AC85272 | 07/29/2023 | 38.18 | 5.4 | 93 | 73 | 0.05
1938397534 | AC85272 | 07/30/2023 | 43.41 | 6.07 | 95 | 74 | Trace Value
1938397534 | AC85272 | 07/31/2023 | 41.92 | 5.88 | 95 | 71 | 0.74
1938397534 | AC85272 | 08/01/2023 | 42.22 | 5.91 | 95 | 71 | 0.08
1938397534 | AC85272 | 08/02/2023 | 38.48 | 5.43 | 93 | 74 | 0
1938397534 | AC85272 | 08/03/2023 | 36.3 | 5.15 | 91 | 73 | 0
1938397534 | AC85272 | 08/04/2023 | 38.44 | 5.43 | 94 | 73 | 0
1938397534 | AC85272 | 08/05/2023 | 43 | 5.96 | 94 | 73 | 0.17
1938397534 | AC85272 | 08/06/2023 | 41.39 | 5.76 | 95 | 74 | 0.66
1938397534 | AC85272 | 08/07/2023 | 39.59 | 5.53 | 97 | 75 | 0.03
1938397534 | AC85272 | 08/08/2023 | 37.95 | 5.32 | 99 | 75 | 0
1938397534 | AC85272 | 08/09/2023 | 39.96 | 5.57 | 99 | 74 | 0
1938397534 | AC85272 | 08/10/2023 | 41.68 | 5.8 | 100 | 75 | 0.16
1938397534 | AC85272 | 08/11/2023 | 41.79 | 5.81 | 99 | 75 | 0
1938397534 | AC85272 | 08/12/2023 | 48.48 | 6.67 | 98 | 76 | 0.25
1938397534 | AC85272 | 08/13/2023 | 44.39 | 6.14 | 97 | 74 | 0
1938397534 | AC85272 | 08/14/2023 | 41.51 | 5.77 | 97 | 76 | 0
1938397534 | AC85272 | 08/15/2023 | 38.75 | 5.42 | 97 | 75 | 0
1938397534 | AC85272 | 08/16/2023 | 46.44 | 6.41 | 96 | 73 | 0.09
1938397534 | AC85272 | 08/17/2023 | 49.24 | 6.77 | 93 | 72 | 0.36
1938397534 | AC85272 | 08/18/2023 | 45.27 | 6.26 | 93 | 73 | 1.09
1938397534 | AC85272 | 08/19/2023 | 44.4 | 6.14 | 93 | 72 | 0.69
1938397534 | AC85272 | 08/20/2023 | 40.94 | 5.7 | 92 | 75 | 0
1938397534 | AC85272 | 08/21/2023 | 36.18 | 5.09 | 92 | 74 | 0
1938397534 | AC85272 | 08/22/2023 | 36.73 | 5.16 | 93 | 72 | 0
1938397534 | AC85272 | 08/23/2023 | 35.71 | 5.03 | 93 | 74 | 0
1938397534 | AC85272 | 08/24/2023 | 33.4 | 4.73 | 93 | 74 | 0.99
1938397534 | AC85272 | 08/25/2023 | 33 | 4.68 | 92 | 71 | 0
1938397534 | AC85272 | 08/26/2023 | 32.89 | 4.67 | 95 | 73 | 0
1938397534 | AC85272 | 08/27/2023 | 33.74 | 4.77 | 95 | 72
1938397534 | AC85272 | 08/28/2023 | 30.37 | 4.34 | 96 | 74 | Trace Value
1938397534 | AC85272 | 08/29/2023 | 31.13 | 4.44 | 95 | 74 | 0
1938397534 | AC85272 | 08/30/2023 | 36.69 | 5.15 | 94 | 74 | 0.93
1938397534 | AC85272 | 08/31/2023 | 32.89 | 4.67 | 94 | 74 | 0.05
1938397534 | AC85272 | 09/01/2023 | 32.99 | 4.68 | 92 | 73 | 0
1938397534 | AC85272 | 09/02/2023 | 32.38 | 4.6 | 91 | 72
1938397534 | AC85272 | 09/03/2023 | 31.68 | 4.51 | 92 | 71 | 0.05
1938397534 | AC85272 | 09/04/2023 | 32.47 | 4.61 | 90 | 68 | 0
1938397534 | AC85272 | 09/05/2023 | 31.57 | 4.5 | 90 | 64 | 0
1938397534 | AC85272 | 09/06/2023 | 30.32 | 4.34 | 94 | 69 | 0
1938397534 | AC85272 | 09/07/2023 | 30.26 | 4.39 | 95 | 70
1938397534 | AC85272 | 09/08/2023 | 33.83 | 4.85 | 95 | 69 | 0
1938397534 | AC85272 | 09/09/2023 | 34.11 | 4.89 | 94 | 64 | 0.48
1938397534 | AC85272 | 09/10/2023 | 32.9 | 4.73 | 93 | 71 | Trace Value
1938397534 | AC85272 | 09/11/2023 | 29.84 | 4.34 | 92 | 72 | 0
1938397534 | AC85272 | 09/12/2023 | 30.05 | 4.36 | 92 | 71 | Trace Value
1938397534 | AC85272 | 09/13/2023 | 36.46 | 5.19 | 92 | 72 | 0.03
1938397534 | AC85272 | 09/14/2023 | 36.38 | 5.18 | 91 | 71 | 0.29
1938397534 | AC85272 | 09/15/2023 | 33.56 | 4.82 | 88 | 70 | 0
1938397534 | AC85272 | 09/16/2023 | 32.63 | 4.69 | 87 | 69 | 0.54
1938397534 | AC85272 | 09/17/2023 | 34.15 | 4.89 | 92 | 70 | 0
1938397534 | AC85272 | 09/18/2023 | 30.95 | 4.48 | 89 | 68 | 0.08
1938397534 | AC85272 | 09/19/2023 | 31.02 | 4.49 | 88 | 64 | 0
1938397534 | AC85272 | 09/20/2023 | 30.29 | 4.39 | 88 | 69 | 0
1938397534 | AC85272 | 09/21/2023 | 30.58 | 4.43 | 87 | 68 | 0.08
1938397534 | AC85272 | 09/22/2023 | 30.38 | 4.4 | 85 | 65 | 0.3
1938397534 | AC85272 | 09/23/2023 | 31.79 | 4.59 | 87 | 61 | 0
1938397534 | AC85272 | 09/24/2023 | 32.25 | 4.65 | 89 | 59 | 0
1938397534 | AC85272 | 09/25/2023 | 31.67 | 4.57 | 90 | 66 | 0
1938397534 | AC85272 | 09/26/2023 | 35.79 | 5.1 | 89 | 71 | 2.11
1938397534 | AC85272 | 09/27/2023 | 45.88 | 6.41 | 88 | 71 | 0.91
1938397534 | AC85272 | 09/28/2023 | 54.12 | 7.47 | 87 | 71 | 0.81
1938397534 | AC85272 | 09/29/2023 | 50.05 | 6.95 | 85 | 71 | 0.02
1938397534 | AC85272 | 09/30/2023 | 59.13 | 8.12 | 85 | 71 | 0.2
1938397534 | AC85272 | 10/01/2023 | 56.27 | 7.75 | 85 | 70 | 2.53
1938397534 | AC85272 | 10/02/2023 | 49.2 | 6.84 | 85 | 69 | 0.56
1938397534 | AC85272 | 10/03/2023 | 46.7 | 6.51 | 85 | 70 | 0
1938397534 | AC85272 | 10/04/2023 | 43.91 | 6.15 | 86 | 70 | 0.05
1938397534 | AC85272 | 10/05/2023 | 41.91 | 5.87 | 86 | 69 | 0
1938397534 | AC85272 | 10/06/2023 | 40.37 | 5.67 | 87 | 66 | 0
1938397534 | AC85272 | 10/07/2023 | 40.01 | 5.62 | 90 | 56 | 0
1938397534 | AC85272 | 10/08/2023 | 42.03 | 5.88 | 82 | 53 | 0
1938397534 | AC85272 | 10/09/2023 | 38.76 | 5.46 | 80 | 55 | 0
1938397534 | AC85272 | 10/10/2023 | 38.86 | 5.47 | 84 | 56 | 0
1938397534 | AC85272 | 10/11/2023 | 39.23 | 5.52 | 84 | 65 | 0
1938397534 | AC85272 | 10/12/2023 | 70.8 | 9.58 | 88 | 72 | 2.8
1938397534 | AC85272 | 10/13/2023 | 55.86 | 7.66 | 89 | 68 | 1.67
1938397534 | AC85272 | 10/14/2023 | 51.8 | 7.14 | 89 | 64 | 0
1938397534 | AC85272 | 10/15/2023 | 50.47 | 6.97 | 82 | 55 | 0
1938397534 | AC85272 | 10/16/2023 | 48.18 | 6.67 | 76 | 50 | 0
1938397534 | AC85272 | 10/17/2023 | 46.99 | 6.52 | 75 | 49 | 0
1938397534 | AC85272 | 10/18/2023 | 45.39 | 6.31 | 77 | 50 | 0
1938397534 | AC85272 | 10/19/2023 | 43.18 | 6.03 | 81 | 55 | 0
1938397534 | AC85272 | 10/20/2023 | 39.85 | 5.6 | 83 | 55 | 0
1938397534 | AC85272 | 10/21/2023 | 41.12 | 5.76 | 83 | 55 | 0
1938397534 | AC85272 | 10/22/2023 | 42.12 | 5.89 | 86 | 52 | 0
1938397534 | AC85272 | 10/23/2023 | 37.45 | 5.29 | 83 | 58 | 0
1938397534 | AC85272 | 10/24/2023 | 38.16 | 5.38 | 82 | 67 | 0
1938397534 | AC85272 | 10/25/2023 | 36.63 | 5.19 | 82 | 68 | 0
1938397534 | AC85272 | 10/26/2023 | 36.33 | 5.15 | 82 | 65 | 0
1938397534 | AC85272 | 10/27/2023 | 35.44 | 5.03 | 83 | 64 | 0
1938397534 | AC85272 | 10/28/2023 | 36.64 | 5.19 | 84 | 62 | 0
1938397534 | AC85272 | 10/29/2023 | 37.41 | 5.29 | 84 | 61 | 0
1938397534 | AC85272 | 10/30/2023 | 35.38 | 5.03 | 85 | 60 | 0
1938397534 | AC85272 | 10/31/2023 | 34.59 | 4.92 | 84 | 58 | 0
1938397534 | AC85272 | 11/01/2023 | 38.31 | 5.4 | 76 | 53 | 0
1938397534 | AC85272 | 11/02/2023 | 35.56 | 5.05 | 75 | 53 | 0
1938397534 | AC85272 | 11/03/2023 | 34.55 | 4.92 | 79 | 59 | 0
1938397534 | AC85272 | 11/04/2023 | 36.24 | 5.13 | 79 | 55 | 0
1938397534 | AC85272 | 11/05/2023 | 39.37 | 5.53 | 80 | 51 | 0
1938397534 | AC85272 | 11/06/2023 | 34.68 | 4.93 | 81 | 48 | 0
1938397534 | AC85272 | 11/07/2023 | 34.07 | 4.85 | 83 | 53 | 0
1938397534 | AC85272 | 11/08/2023 | 34.95 | 4.96 | 84 | 50 | 0
1938397534 | AC85272 | 11/09/2023 | 33.02 | 4.71 | 85 | 55 | 0
1938397534 | AC85272 | 11/10/2023 | 32.82 | 4.69 | 86 | 60 | 0
1938397534 | AC85272 | 11/11/2023 | 34.14 | 4.86 | 83 | 65 | 0.33
1938397534 | AC85272 | 11/12/2023 | 37.83 | 5.33 | 80 | 63 | 0
1938397534 | AC85272 | 11/13/2023 | 33.84 | 4.82 | 77 | 62 | 0
1938397534 | AC85272 | 11/14/2023 | 38.88 | 5.47 | 77 | 61 | 0.12
1938397534 | AC85272 | 11/15/2023 | 38.76 | 5.45 | 77 | 64 | 0.05
1938397534 | AC85272 | 11/16/2023 | 43.73 | 6.09 | 78 | 62 | 0.16
1938397534 | AC85272 | 11/17/2023 | 57.99 | 7.92 | 79 | 61 | 2.1
1938397534 | AC85272 | 11/18/2023 | 56.39 | 7.72 | 78 | 55 | 0.66
1938397534 | AC85272 | 11/19/2023 | 52.05 | 7.16 | 80 | 56 | 0
1938397534 | AC85272 | 11/20/2023 | 46.27 | 6.42 | 79 | 59 | 0.02
1938397534 | AC85272 | 11/21/2023 | 45.23 | 6.28 | 81 | 52 | 0.02
1938397534 | AC85272 | 11/22/2023 | 45.71 | 6.34 | 81 | 47 | 0
1938397534 | AC85272 | 11/23/2023 | 47.23 | 6.54 | 73 | 48 | 0.01
1938397534 | AC85272 | 11/24/2023 | 45.73 | 6.35 | 75 | 52 | 0.01
1938397534 | AC85272 | 11/25/2023 | 43.6 | 6.07 | 75 | 53 | 0.07
1938397534 | AC85272 | 11/26/2023 | 47.05 | 6.52 | 75 | 55 | 0.01
1938397534 | AC85272 | 11/27/2023 | 45.28 | 6.29 | 74 | 44 | 0.55
1938397534 | AC85272 | 11/28/2023 | 46.32 | 6.42 | 69 | 39 | 0
1938397534 | AC85272 | 11/29/2023 | 45.81 | 6.36 | 68 | 36 | 0
1938397534 | AC85272 | 11/30/2023 | 43.67 | 6.08 | 86 | 41 | 0
1938397534 | AC85272 | 12/01/2023 | 40.58 | 5.68 | 82 | 55 | 0
1938397534 | AC85272 | 12/02/2023 | 40.55 | 5.68 | 83 | 64 | 0
1938397534 | AC85272 | 12/03/2023 | 44.86 | 6.23 | 82 | 62 | 0.02
1938397534 | AC85272 | 12/04/2023 | 47.8 | 6.61 | 79 | 51 | 0.23
1938397534 | AC85272 | 12/05/2023 | 46.44 | 6.39 | 72 | 47 | 0
1938397534 | AC85272 | 12/06/2023 | 46.53 | 6.4 | 69 | 41 | 0
1938397534 | AC85272 | 12/07/2023 | 45.07 | 6.21 | 67 | 41 | 0
1938397534 | AC85272 | 12/08/2023 | 43.45 | 6.01 | 74 | 47 | 0
1938397534 | AC85272 | 12/09/2023 | 43.31 | 5.99 | 82 | 56 | 0.04
1938397534 | AC85272 | 12/10/2023 | 43.56 | 6.02 | 83 | 44 | 0
1938397534 | AC85272 | 12/11/2023 | 45.01 | 6.21 | 67 | 43 | 0.25
1938397534 | AC85272 | 12/12/2023 | 44.52 | 6.14 | 71 | 43 | 0
1938397534 | AC85272 | 12/13/2023 | 43.52 | 6.02 | 73 | 58 | 0
1938397534 | AC85272 | 12/14/2023 | 44.28 | 6.11 | 72 | 59 | 0.66
1938397534 | AC85272 | 12/15/2023 | 42.93 | 5.94 | 72 | 60 | 0.07
1938397534 | AC85272 | 12/16/2023 | 45.92 | 6.32 | 73 | 58 | 0.11
1938397534 | AC85272 | 12/17/2023 | 72.91 | 9.78 | 74 | 48 | 4.04
1938397534 | AC85272 | 12/18/2023 | 53.95 | 7.35 | 68 | 40 | 0.05
1938397534 | AC85272 | 12/19/2023 | 54.91 | 7.47 | 65 | 41 | 0
1938397534 | AC85272 | 12/20/2023 | 53.11 | 7.24 | 66 | 44 | 0
1938397534 | AC85272 | 12/21/2023 | 51.17 | 7 | 68 | 46 | 0
1938397534 | AC85272 | 12/22/2023 | 49.34 | 6.76 | 70 | 49 | 0
1938397534 | AC85272 | 12/23/2023 | 49.02 | 6.72 | 73 | 53 | 0
1938397534 | AC85272 | 12/24/2023 | 48.37 | 6.64 | 73 | 53 | 0
1938397534 | AC85272 | 12/25/2023 | 45.96 | 6.33 | 73 | 60 | 0.09
1938397534 | AC85272 | 12/26/2023 | 46.22 | 6.36 | 74 | 54 | 0.1
1938397534 | AC85272 | 12/27/2023 | 45.7 | 6.29 | 71 | 49 | 0
1938397534 | AC85272 | 12/28/2023 | 47.86 | 6.57 | 66 | 44 | 0.04
1938397534 | AC85272 | 12/29/2023 | 49.48 | 6.78 | 55 | 46 | 0
1938397534 | AC85272 | 12/30/2023 | 48.82 | 6.7 | 59 | 37 | 0
1938397534 | AC85272 | 12/31/2023 | 47.21 | 6.49 | 63 | 36 | 0
|  | Yearly Daily Average: | 37.9735 | 5.36
|  | Wetter Months' Daily Average: | 41.9013 | 5.853

## CP-1
Daily Billed Information (PS CP-1: 2023 Reading Data)
Bill Account | Meter Number | Date | Consumption Recorded (kWh/day) | Estimated Cost ($/day) | Avg. High Temperature (°F) | Avg. Low Temperature (°F) | Rain Recorded by NOAA (inches)
5360466410 | KJ38887 | 01/01/2023 | 15.63 | 2.29 | 79 | 58 | 0.04
5360466410 | KJ38887 | 01/02/2023 | 24.87 | 3.4 | 78 | 53 | 0
5360466410 | KJ38887 | 01/03/2023 | 22.75 | 3.14 | 81 | 51 | 0
5360466410 | KJ38887 | 01/04/2023 | 21.82 | 3.03 | 83 | 57 | 0
5360466410 | KJ38887 | 01/05/2023 | 22.87 | 3.16 | 77 | 46 | 0.04
5360466410 | KJ38887 | 01/06/2023 | 24.9 | 3.4 | 68 | 41 | 0
5360466410 | KJ38887 | 01/07/2023 | 23.63 | 3.25 | 70 | 38 | 0
5360466410 | KJ38887 | 01/08/2023 | 22.09 | 3.06 | 76 | 42 | 0
5360466410 | KJ38887 | 01/09/2023 | 21.51 | 2.99 | 74 | 47 | 0
5360466410 | KJ38887 | 01/10/2023 | 20.8 | 3.02 | 71 | 42 | 0
5360466410 | KJ38887 | 01/11/2023 | 22.87 | 3.27 | 73 | 38 | 0
5360466410 | KJ38887 | 01/12/2023 | 23.55 | 3.36 | 80 | 44 | 0
5360466410 | KJ38887 | 01/13/2023 | 23.39 | 3.34 | 71 | 35 | 0.12
5360466410 | KJ38887 | 01/14/2023 | 22.67 | 3.25 | 61 | 30 | 0
5360466410 | KJ38887 | 01/15/2023 | 21.87 | 3.15 | 63 | 30 | 0
5360466410 | KJ38887 | 01/16/2023 | 22.91 | 3.28 | 71 | 30 | 0
5360466410 | KJ38887 | 01/17/2023 | 20.14 | 2.93 | 75 | 34 | 0
5360466410 | KJ38887 | 01/18/2023 | 18.53 | 2.73 | 79 | 46 | N/A
5360466410 | KJ38887 | 01/19/2023 | 20.85 | 3.02 | 82 | 54 | 0
5360466410 | KJ38887 | 01/20/2023 | 23.57 | 3.36 | 76 | 49 | 0
5360466410 | KJ38887 | 01/21/2023 | 21.71 | 3.13 | 76 | 47 | T
5360466410 | KJ38887 | 01/22/2023 | 20.45 | 2.97 | 82 | 54 | 0.33
5360466410 | KJ38887 | 01/23/2023 | 20.71 | 3.01 | 75 | 44 | 0.05
5360466410 | KJ38887 | 01/24/2023 | 24.09 | 3.43 | 76 | 41 | 0
5360466410 | KJ38887 | 01/25/2023 | 25.83 | 3.64 | 85 | 43 | 0
5360466410 | KJ38887 | 01/26/2023 | 25.45 | 3.59 | 72 | 38 | 0.09
5360466410 | KJ38887 | 01/27/2023 | 25.63 | 3.62 | 62 | 37 | 0
5360466410 | KJ38887 | 01/28/2023 | 26.17 | 3.69 | 69 | 35 | 0
5360466410 | KJ38887 | 01/29/2023 | 23.08 | 3.3 | 78 | 55 | 0
5360466410 | KJ38887 | 01/30/2023 | 24.37 | 3.46 | 86 | 58 | 0
5360466410 | KJ38887 | 01/31/2023 | 23.52 | 3.36 | 83 | 59 | 0
5360466410 | KJ38887 | 02/01/2023 | 23.65 | 3.37 | 82 | 58 | 0
5360466410 | KJ38887 | 02/02/2023 | 24.02 | 3.42 | 82 | 57 | 0
5360466410 | KJ38887 | 02/03/2023 | 20.95 | 3.04 | 78 | 50 | 0
5360466410 | KJ38887 | 02/04/2023 | 25.31 | 3.58 | 70 | 47 | 0.17
5360466410 | KJ38887 | 02/05/2023 | 21.09 | 3.05 | 73 | 48 | 0
5360466410 | KJ38887 | 02/06/2023 | 26.52 | 3.73 | 71 | 46 | 0.01
5360466410 | KJ38887 | 02/07/2023 | 29.23 | 4.07 | 76 | 44
5360466410 | KJ38887 | 02/08/2023 | 25.39 | 3.59 | 79 | 49 | 0
5360466410 | KJ38887 | 02/09/2023 | 24.75 | 3.52 | 83 | 58 | 0
5360466410 | KJ38887 | 02/10/2023 | 28.18 | 3.95 | 85 | 46 | 0.16
5360466410 | KJ38887 | 02/11/2023 | 27.55 | 3.87 | 79 | 40 | 0.57
5360466410 | KJ38887 | 02/12/2023 | 24.22 | 3.46 | 71 | 40 | 0.12
5360466410 | KJ38887 | 02/13/2023 | 23.55 | 3.37 | 71 | 40 | Trace Value
5360466410 | KJ38887 | 02/14/2023 | 24.21 | 3.46 | 75 | 39 | 0
5360466410 | KJ38887 | 02/15/2023 | 23.79 | 3.4 | 82 | 50 | 0
5360466410 | KJ38887 | 02/16/2023 | 24.26 | 3.46 | 85 | 57 | 0
5360466410 | KJ38887 | 02/17/2023 | 25.82 | 3.66 | 89 | 45
5360466410 | KJ38887 | 02/18/2023 | 26.26 | 3.71 | 67 | 46 | 0.04
5360466410 | KJ38887 | 02/19/2023 | 23.14 | 3.32 | 80 | 48 | 0
5360466410 | KJ38887 | 02/20/2023 | 23.34 | 3.35 | 82 | 53 | 0
5360466410 | KJ38887 | 02/21/2023 | 24.14 | 3.45 | 85 | 57 | 0
5360466410 | KJ38887 | 02/22/2023 | 23.6 | 3.38 | 87 | 58 | 0
5360466410 | KJ38887 | 02/23/2023 | 24.48 | 3.49 | 89 | 60 | 0
5360466410 | KJ38887 | 02/24/2023 | 24.64 | 3.51 | 87 | 58 | 0
5360466410 | KJ38887 | 02/25/2023 | 25.76 | 3.65 | 87 | 58
5360466410 | KJ38887 | 02/26/2023 | 20.13 | 2.95 | 87 | 56 | 0
5360466410 | KJ38887 | 02/27/2023 | 24.34 | 3.47 | 87 | 57 | 0
5360466410 | KJ38887 | 02/28/2023 | 22.5 | 3.24 | 87 | 57 | 0
5360466410 | KJ38887 | 03/01/2023 | 21.48 | 3.11 | 86 | 58 | 0
5360466410 | KJ38887 | 03/02/2023 | 20.84 | 3.03 | 87 | 56 | 0
5360466410 | KJ38887 | 03/03/2023 | 25.12 | 3.57 | 90 | 55 | 0
5360466410 | KJ38887 | 03/04/2023 | 25.05 | 3.56 | 88 | 52 | 0
5360466410 | KJ38887 | 03/05/2023 | 23.49 | 3.36 | 81 | 54 | 0.05
5360466410 | KJ38887 | 03/06/2023 | 24.92 | 3.54 | 84 | 56 | 0
5360466410 | KJ38887 | 03/07/2023 | 23.48 | 3.36 | 87 | 56
5360466410 | KJ38887 | 03/08/2023 | 26.97 | 3.8 | 85 | 58 | 0
5360466410 | KJ38887 | 03/09/2023 | 25.2 | 3.58 | 80 | 51 | 0
5360466410 | KJ38887 | 03/10/2023 | 28.6 | 4.35 | 85 | 54
5360466410 | KJ38887 | 03/11/2023 | 27.31 | 4.17 | 81 | 51 | 1.3
5360466410 | KJ38887 | 03/12/2023 | 22.84 | 3.56 | 86 | 48 | 0
5360466410 | KJ38887 | 03/13/2023 | 23.02 | 3.59 | 81 | 46 | 1.17
5360466410 | KJ38887 | 03/14/2023 | 24.41 | 3.78 | 70 | 43 | 0.6
5360466410 | KJ38887 | 03/15/2023 | 24.64 | 3.81 | 68 | 43 | 0
5360466410 | KJ38887 | 03/16/2023 | 25.65 | 3.95 | 77 | 37 | 0
5360466410 | KJ38887 | 03/17/2023 | 24.39 | 3.78 | 84 | 48
5360466410 | KJ38887 | 03/18/2023 | 23.3 | 3.63 | 80 | 45 | 0
5360466410 | KJ38887 | 03/19/2023 | 23.29 | 3.63 | 68 | 43 | 0.02
5360466410 | KJ38887 | 03/20/2023 | 24.29 | 3.76 | 69 | 42 | 0.02
5360466410 | KJ38887 | 03/21/2023 | 22.46 | 3.51 | 77 | 42 | 0
5360466410 | KJ38887 | 03/22/2023 | 23.11 | 3.6 | 80 | 53 | 0.08
5360466410 | KJ38887 | 03/23/2023 | 24.34 | 3.77 | 83 | 53
5360466410 | KJ38887 | 03/24/2023 | 24.05 | 3.73 | 86 | 53 | 0
5360466410 | KJ38887 | 03/25/2023 | 25.66 | 3.95 | 91 | 60 | 0
5360466410 | KJ38887 | 03/26/2023 | 23.79 | 3.69 | 91 | 63 | 0.68
5360466410 | KJ38887 | 03/27/2023 | 21.88 | 3.43 | 92 | 62 | 0
5360466410 | KJ38887 | 03/28/2023 | 25.64 | 3.95 | 88 | 55 | Trace Value
5360466410 | KJ38887 | 03/29/2023 | 24.03 | 3.73 | 75 | 55 | 0
5360466410 | KJ38887 | 03/30/2023 | 26.47 | 4.06 | 79 | 51 | 0
5360466410 | KJ38887 | 03/31/2023 | 27.9 | 4.26 | 85 | 55 | 0
5360466410 | KJ38887 | 04/01/2023 | 29.53 | 4.48 | 90 | 60 | 0
5360466410 | KJ38887 | 04/02/2023 | 25.42 | 3.92 | 85 | 60
5360466410 | KJ38887 | 04/03/2023 | 25.96 | 3.99 | 86 | 61 | 0
5360466410 | KJ38887 | 04/04/2023 | 27.83 | 4.25 | 88 | 60 | Trace Value
5360466410 | KJ38887 | 04/05/2023 | 27.2 | 4.16 | 87 | 63 | 0
5360466410 | KJ38887 | 04/06/2023 | 27.04 | 4.14 | 87 | 64 | 0
5360466410 | KJ38887 | 04/07/2023 | 29.11 | 4.42 | 85 | 64
5360466410 | KJ38887 | 04/08/2023 | 26.8 | 4.1 | 86 | 62
5360466410 | KJ38887 | 04/09/2023 | 21.9 | 3.44 | 80 | 60 | 0.01
5360466410 | KJ38887 | 04/10/2023 | 23.12 | 3.6 | 79 | 58 | 0.68
5360466410 | KJ38887 | 04/11/2023 | 24.65 | 3.74 | 78 | 58 | 1.38
5360466410 | KJ38887 | 04/12/2023 | 22.01 | 3.39 | 79 | 59 | 0.03
5360466410 | KJ38887 | 04/13/2023 | 25 | 3.79 | 87 | 61 | 0.07
5360466410 | KJ38887 | 04/14/2023 | 27.91 | 4.18 | 86 | 59 | 0.57
5360466410 | KJ38887 | 04/15/2023 | 26.64 | 4.01 | 87 | 60 | 0.02
5360466410 | KJ38887 | 04/16/2023 | 24.1 | 3.67 | 88 | 59 | 0
5360466410 | KJ38887 | 04/17/2023 | 23.14 | 3.54 | 81 | 50 | 0.04
5360466410 | KJ38887 | 04/18/2023 | 24.82 | 3.77 | 81 | 46 | 0.02
5360466410 | KJ38887 | 04/19/2023 | 24.58 | 3.73 | 82 | 50 | 0
5360466410 | KJ38887 | 04/20/2023 | 24.04 | 3.66 | 84 | 55 | 0
5360466410 | KJ38887 | 04/21/2023 | 27.71 | 4.15 | 87 | 59
5360466410 | KJ38887 | 04/22/2023 | 25.01 | 3.79 | 89 | 57 | 0.3
5360466410 | KJ38887 | 04/23/2023 | 21.71 | 3.35 | 84 | 53 | 0.42
5360466410 | KJ38887 | 04/24/2023 | 23.23 | 3.56 | 80 | 55 | 0
5360466410 | KJ38887 | 04/25/2023 | 25.01 | 3.79 | 82 | 61 | 0.25
5360466410 | KJ38887 | 04/26/2023 | 26.28 | 3.96 | 84 | 62 | 0.07
5360466410 | KJ38887 | 04/27/2023 | 26.49 | 3.99 | 86 | 63 | 0
5360466410 | KJ38887 | 04/28/2023 | 25.2 | 3.82 | 87 | 62 | 1.62
5360466410 | KJ38887 | 04/29/2023 | 26.46 | 3.98 | 88 | 62 | 0
5360466410 | KJ38887 | 04/30/2023 | 24.49 | 3.72 | 85 | 57 | 0.52
5360466410 | KJ38887 | 05/01/2023 | 26.42 | 3.98 | 85 | 56 | 0
5360466410 | KJ38887 | 05/02/2023 | 26.53 | 3.99 | 87 | 56 | 0
5360466410 | KJ38887 | 05/03/2023 | 26.97 | 4.05 | 86 | 53 | 0
5360466410 | KJ38887 | 05/04/2023 | 26.48 | 3.99 | 84 | 53 | 0
5360466410 | KJ38887 | 05/05/2023 | 26.67 | 4.01 | 87 | 57 | 0
5360466410 | KJ38887 | 05/06/2023 | 25.14 | 3.81 | 86 | 65 | 0
5360466410 | KJ38887 | 05/07/2023 | 24.81 | 3.76 | 88 | 61 | 0.02
5360466410 | KJ38887 | 05/08/2023 | 31.88 | 4.7 | 87 | 55 | 0
5360466410 | KJ38887 | 05/09/2023 | 27.99 | 4.19 | 91 | 63 | 0
5360466410 | KJ38887 | 05/10/2023 | 26.75 | 4.01 | 92 | 66 | 0
5360466410 | KJ38887 | 05/11/2023 | 27.47 | 4.1 | 88 | 67 | 0.04
5360466410 | KJ38887 | 05/12/2023 | 29.13 | 4.32 | 86 | 66 | 0
5360466410 | KJ38887 | 05/13/2023 | 28.54 | 4.24 | 85 | 64 | 0
5360466410 | KJ38887 | 05/14/2023 | 25.34 | 3.82 | 86 | 63 | 0
5360466410 | KJ38887 | 05/15/2023 | 26.81 | 4.01 | 89 | 62 | 0
5360466410 | KJ38887 | 05/16/2023 | 26.38 | 3.96 | 88 | 64 | 0
5360466410 | KJ38887 | 05/17/2023 | 25.29 | 3.81 | 92 | 67 | 0
5360466410 | KJ38887 | 05/18/2023 | 26.06 | 3.91 | 89 | 65 | 1.24
5360466410 | KJ38887 | 05/19/2023 | 27.94 | 4.16 | 88 | 66 | 0.02
5360466410 | KJ38887 | 05/20/2023 | 27.34 | 4.08 | 88 | 66 | 0
5360466410 | KJ38887 | 05/21/2023 | 24.4 | 3.7 | 88 | 67
5360466410 | KJ38887 | 05/22/2023 | 25.58 | 3.85 | 88 | 67 | 0.65
5360466410 | KJ38887 | 05/23/2023 | 25.92 | 3.9 | 85 | 67 | 0.56
5360466410 | KJ38887 | 05/24/2023 | 25.88 | 3.89 | 83 | 66 | 0.12
5360466410 | KJ38887 | 05/25/2023 | 27.59 | 4.12 | 83 | 66 | 0.16
5360466410 | KJ38887 | 05/26/2023 | 27.1 | 4.05 | 82 | 62 | 0.05
5360466410 | KJ38887 | 05/27/2023 | 28.97 | 4.3 | 81 | 56 | Trace Value
5360466410 | KJ38887 | 05/28/2023 | 25.43 | 3.83 | 85 | 55 | 0
5360466410 | KJ38887 | 05/29/2023 | 24.9 | 3.76 | 87 | 60 | 0
5360466410 | KJ38887 | 05/30/2023 | 26.19 | 3.93 | 88 | 62 | 0
5360466410 | KJ38887 | 05/31/2023 | 23.7 | 3.6 | 87 | 68 | 0
5360466410 | KJ38887 | 06/01/2023 | 25.01 | 3.78 | 85 | 68 | 0
5360466410 | KJ38887 | 06/02/2023 | 25.05 | 3.78 | 85 | 67 | 0
5360466410 | KJ38887 | 06/03/2023 | 25.08 | 3.79 | 84 | 67 | 0
5360466410 | KJ38887 | 06/04/2023 | 22.69 | 3.47 | 84 | 66 | 0
5360466410 | KJ38887 | 06/05/2023 | 23.67 | 3.6 | 84 | 64 | 0.3
5360466410 | KJ38887 | 06/06/2023 | 23.69 | 3.6 | 88 | 62
5360466410 | KJ38887 | 06/07/2023 | 25.38 | 3.83 | 91 | 68 | 0
5360466410 | KJ38887 | 06/08/2023 | 23.03 | 3.52 | 92 | 68 | 1.64
5360466410 | KJ38887 | 06/09/2023 | 50.78 | 6.97 | 92 | 68 | 0
5360466410 | KJ38887 | 06/10/2023 | 95.78 | 12.75 | 88 | 67 | 0.54
5360466410 | KJ38887 | 06/11/2023 | 95.56 | 12.73 | 91 | 69 | 0.09
5360466410 | KJ38887 | 06/12/2023 | 96.22 | 12.81 | 94 | 69 | 0
5360466410 | KJ38887 | 06/13/2023 | 98.61 | 13.12 | 95 | 71
5360466410 | KJ38887 | 06/14/2023 | 98.06 | 13.05 | 95 | 71 | 0
5360466410 | KJ38887 | 06/15/2023 | 98.38 | 13.09 | 95 | 66 | 0.44
5360466410 | KJ38887 | 06/16/2023 | 70.36 | 9.49 | 95 | 68 | 0.45
5360466410 | KJ38887 | 06/17/2023 | 24.64 | 3.62 | 93 | 68 | 0.91
5360466410 | KJ38887 | 06/18/2023 | 23.09 | 3.42 | 94 | 68 | 0.28
5360466410 | KJ38887 | 06/19/2023 | 26.59 | 3.87 | 93 | 70 | 0.63
5360466410 | KJ38887 | 06/20/2023 | 21.18 | 3.17 | 91 | 69 | 0.46
5360466410 | KJ38887 | 06/21/2023 | 22.56 | 3.35 | 91 | 71 | 0.24
5360466410 | KJ38887 | 06/22/2023 | 21.88 | 3.26 | 93 | 66 | 0.04
5360466410 | KJ38887 | 06/23/2023 | 24.43 | 3.59 | 91 | 69 | 0.35
5360466410 | KJ38887 | 06/24/2023 | 24.23 | 3.56 | 92 | 70 | 0.24
5360466410 | KJ38887 | 06/25/2023 | 21.7 | 3.24 | 91 | 70 | 0.15
5360466410 | KJ38887 | 06/26/2023 | 23.57 | 3.48 | 94 | 70 | 0
5360466410 | KJ38887 | 06/27/2023 | 22.81 | 3.38 | 97 | 71 | 0
5360466410 | KJ38887 | 06/28/2023 | 22.77 | 3.38 | 95 | 72 | 0
5360466410 | KJ38887 | 06/29/2023 | 23.42 | 3.46 | 95 | 71 | 0.88
5360466410 | KJ38887 | 06/30/2023 | 24.02 | 3.54 | 94 | 71 | 0
5360466410 | KJ38887 | 07/01/2023 | 23.67 | 3.49 | 94 | 71 | 0
5360466410 | KJ38887 | 07/02/2023 | 22 | 3.28 | 95 | 71 | 0
5360466410 | KJ38887 | 07/03/2023 | 23.43 | 3.46 | 97 | 72 | 0
5360466410 | KJ38887 | 07/04/2023 | 17.75 | 2.73 | 95 | 73 | 0
5360466410 | KJ38887 | 07/05/2023 | 21.54 | 3.22 | 95 | 74 | 0
5360466410 | KJ38887 | 07/06/2023 | 21.45 | 3.21 | 96 | 73 | 0.04
5360466410 | KJ38887 | 07/07/2023 | 22.91 | 3.39 | 95 | 73 | 0.03
5360466410 | KJ38887 | 07/08/2023 | 20.45 | 3.08 | 94 | 74 | 0.31
5360466410 | KJ38887 | 07/09/2023 | 21.89 | 3.26 | 96 | 74 | 0.2
5360466410 | KJ38887 | 07/10/2023 | 20.6 | 3.1 | 96 | 74 | 0
5360466410 | KJ38887 | 07/11/2023 | 25.09 | 3.68 | 94 | 73 | 0.78
5360466410 | KJ38887 | 07/12/2023 | 23.05 | 3.42 | 94 | 73 | 0.1
5360466410 | KJ38887 | 07/13/2023 | 22.06 | 3.3 | 94 | 72 | Trace Value
5360466410 | KJ38887 | 07/14/2023 | 24.37 | 3.59 | 95 | 73 | 0.33
5360466410 | KJ38887 | 07/15/2023 | 22.78 | 3.39 | 96 | 73 | 0.12
5360466410 | KJ38887 | 07/16/2023 | 21.61 | 3.24 | 96 | 74 | 0.15
5360466410 | KJ38887 | 07/17/2023 | 23.14 | 3.43 | 95 | 74 | 2.8
5360466410 | KJ38887 | 07/18/2023 | 22.88 | 3.4 | 95 | 72 | 0.22
5360466410 | KJ38887 | 07/19/2023 | 23.38 | 3.46 | 95 | 71 | 0.14
5360466410 | KJ38887 | 07/20/2023 | 23 | 3.42 | 96 | 73 | 0
5360466410 | KJ38887 | 07/21/2023 | 23.22 | 3.44 | 99 | 74 | 0
5360466410 | KJ38887 | 07/22/2023 | 24.44 | 3.6 | 97 | 75 | 0
5360466410 | KJ38887 | 07/23/2023 | 20.86 | 3.14 | 94 | 71 | 0.7
5360466410 | KJ38887 | 07/24/2023 | 21.05 | 3.17 | 93 | 73 | 1.12
5360466410 | KJ38887 | 07/25/2023 | 22.57 | 3.36 | 93 | 73 | 0.3
5360466410 | KJ38887 | 07/26/2023 | 21.5 | 3.22 | 92 | 73 | 0
5360466410 | KJ38887 | 07/27/2023 | 20.71 | 3.12 | 91 | 73 | 0
5360466410 | KJ38887 | 07/28/2023 | 25.8 | 3.77 | 92 | 73 | 1
5360466410 | KJ38887 | 07/29/2023 | 24.81 | 3.65 | 93 | 73 | 0.05
5360466410 | KJ38887 | 07/30/2023 | 25.94 | 3.79 | 95 | 74 | Trace Value
5360466410 | KJ38887 | 07/31/2023 | 22.77 | 3.39 | 95 | 71 | 0.74
5360466410 | KJ38887 | 08/01/2023 | 24.4 | 3.59 | 95 | 71 | 0.08
5360466410 | KJ38887 | 08/02/2023 | 23.45 | 3.47 | 93 | 74 | 0
5360466410 | KJ38887 | 08/03/2023 | 22.99 | 3.42 | 91 | 73 | 0
5360466410 | KJ38887 | 08/04/2023 | 24.43 | 3.6 | 94 | 73 | 0
5360466410 | KJ38887 | 08/05/2023 | 24.39 | 3.59 | 94 | 73 | 0.17
5360466410 | KJ38887 | 08/06/2023 | 26.57 | 3.87 | 95 | 74 | 0.66
5360466410 | KJ38887 | 08/07/2023 | 25.01 | 3.67 | 97 | 75 | 0.03
5360466410 | KJ38887 | 08/08/2023 | 26.93 | 3.92 | 99 | 75 | 0
5360466410 | KJ38887 | 08/09/2023 | 23.4 | 3.47 | 99 | 74 | 0
5360466410 | KJ38887 | 08/10/2023 | 24.24 | 3.6 | 100 | 75 | 0.16
5360466410 | KJ38887 | 08/11/2023 | 25.07 | 3.7 | 99 | 75 | 0
5360466410 | KJ38887 | 08/12/2023 | 23.63 | 3.52 | 98 | 76 | 0.25
5360466410 | KJ38887 | 08/13/2023 | 21.9 | 3.29 | 97 | 74 | 0
5360466410 | KJ38887 | 08/14/2023 | 22.14 | 3.33 | 97 | 76 | 0
5360466410 | KJ38887 | 08/15/2023 | 21.71 | 3.27 | 97 | 75 | 0
5360466410 | KJ38887 | 08/16/2023 | 21.81 | 3.28 | 96 | 73 | 0.09
5360466410 | KJ38887 | 08/17/2023 | 22.2 | 3.33 | 93 | 72 | 0.36
5360466410 | KJ38887 | 08/18/2023 | 24.14 | 3.58 | 93 | 73 | 1.09
5360466410 | KJ38887 | 08/19/2023 | 26.16 | 3.84 | 93 | 72 | 0.69
5360466410 | KJ38887 | 08/20/2023 | 22.37 | 3.36 | 92 | 75 | 0
5360466410 | KJ38887 | 08/21/2023 | 23.72 | 3.53 | 92 | 74 | 0
5360466410 | KJ38887 | 08/22/2023 | 24.22 | 3.59 | 93 | 72 | 0
5360466410 | KJ38887 | 08/23/2023 | 23.97 | 3.56 | 93 | 74 | 0
5360466410 | KJ38887 | 08/24/2023 | 8.06 | 1.51 | 93 | 74 | 0.99
5360466410 | KJ38887 | 08/25/2023 | 83.59 | 11.25 | 92 | 71 | 0
5360466410 | KJ38887 | 08/26/2023 | 142.98 | 18.91 | 95 | 73 | 0
5360466410 | KJ38887 | 08/27/2023 | 145.04 | 19.18 | 95 | 72
5360466410 | KJ38887 | 08/28/2023 | 149.71 | 19.78 | 96 | 74 | Trace Value
5360466410 | KJ38887 | 08/29/2023 | 151.82 | 20.05 | 95 | 74 | 0
5360466410 | KJ38887 | 08/30/2023 | 103.13 | 13.77 | 94 | 74 | 0.93
5360466410 | KJ38887 | 08/31/2023 | 22.75 | 3.4 | 94 | 74 | 0.05
5360466410 | KJ38887 | 09/01/2023 | 47.01 | 6.53 | 92 | 73 | 0
5360466410 | KJ38887 | 09/02/2023 | 149.17 | 19.71 | 91 | 72
5360466410 | KJ38887 | 09/03/2023 | 150.03 | 19.82 | 92 | 71 | 0.05
5360466410 | KJ38887 | 09/04/2023 | 150.76 | 19.92 | 90 | 68 | 0
5360466410 | KJ38887 | 09/05/2023 | 152.96 | 20.2 | 90 | 64 | 0
5360466410 | KJ38887 | 09/06/2023 | 152.29 | 20.11 | 94 | 69 | 0
5360466410 | KJ38887 | 09/07/2023 | 152.24 | 20.11 | 95 | 70
5360466410 | KJ38887 | 09/08/2023 | 159.18 | 21 | 95 | 69 | 0
5360466410 | KJ38887 | 09/09/2023 | 60.75 | 8.31 | 94 | 64 | 0.48
5360466410 | KJ38887 | 09/10/2023 | 21.24 | 3.19 | 93 | 71 | Trace Value
5360466410 | KJ38887 | 09/11/2023 | 82.62 | 11.05 | 92 | 72 | 0
5360466410 | KJ38887 | 09/12/2023 | 80.82 | 10.82 | 92 | 71 | Trace Value
5360466410 | KJ38887 | 09/13/2023 | 26.69 | 3.89 | 92 | 72 | 0.03
5360466410 | KJ38887 | 09/14/2023 | 23.17 | 3.44 | 91 | 71 | 0.29
5360466410 | KJ38887 | 09/15/2023 | 22.28 | 3.32 | 88 | 70 | 0
5360466410 | KJ38887 | 09/16/2023 | 22.69 | 3.37 | 87 | 69 | 0.54
5360466410 | KJ38887 | 09/17/2023 | 20.56 | 3.1 | 92 | 70 | 0
5360466410 | KJ38887 | 09/18/2023 | 22.95 | 3.41 | 89 | 68 | 0.08
5360466410 | KJ38887 | 09/19/2023 | 22.09 | 3.3 | 88 | 64 | 0
5360466410 | KJ38887 | 09/20/2023 | 21.89 | 3.27 | 88 | 69 | 0
5360466410 | KJ38887 | 09/21/2023 | 23.83 | 3.52 | 87 | 68 | 0.08
5360466410 | KJ38887 | 09/22/2023 | 26.04 | 3.8 | 85 | 65 | 0.3
5360466410 | KJ38887 | 09/23/2023 | 26.35 | 3.84 | 87 | 61 | 0
5360466410 | KJ38887 | 09/24/2023 | 22.08 | 3.3 | 89 | 59 | 0
5360466410 | KJ38887 | 09/25/2023 | 23.36 | 3.46 | 90 | 66 | 0
5360466410 | KJ38887 | 09/26/2023 | 23.94 | 3.54 | 89 | 71 | 2.11
5360466410 | KJ38887 | 09/27/2023 | 24.3 | 3.58 | 88 | 71 | 0.91
5360466410 | KJ38887 | 09/28/2023 | 24.18 | 3.57 | 87 | 71 | 0.81
5360466410 | KJ38887 | 09/29/2023 | 23.67 | 3.5 | 85 | 71 | 0.02
5360466410 | KJ38887 | 09/30/2023 | 40.59 | 5.67 | 85 | 71 | 0.2
5360466410 | KJ38887 | 10/01/2023 | 39.62 | 5.54 | 85 | 70 | 2.53
5360466410 | KJ38887 | 10/02/2023 | 32.7 | 4.66 | 85 | 69 | 0.56
5360466410 | KJ38887 | 10/03/2023 | 25.79 | 3.77 | 85 | 70 | 0
5360466410 | KJ38887 | 10/04/2023 | 25.69 | 3.76 | 86 | 70 | 0.05
5360466410 | KJ38887 | 10/05/2023 | 23.66 | 3.5 | 86 | 69 | 0
5360466410 | KJ38887 | 10/06/2023 | 26.89 | 3.91 | 87 | 66 | 0
5360466410 | KJ38887 | 10/07/2023 | 25.32 | 3.71 | 90 | 56 | 0
5360466410 | KJ38887 | 10/08/2023 | 23.12 | 3.43 | 82 | 53 | 0
5360466410 | KJ38887 | 10/09/2023 | 24.52 | 3.61 | 80 | 55 | 0
5360466410 | KJ38887 | 10/10/2023 | 23.25 | 3.45 | 84 | 56 | 0
5360466410 | KJ38887 | 10/11/2023 | 20.78 | 3.15 | 84 | 65 | 0
5360466410 | KJ38887 | 10/12/2023 | 56.13 | 7.69 | 88 | 72 | 2.8
5360466410 | KJ38887 | 10/13/2023 | 29.56 | 4.27 | 89 | 68 | 1.67
5360466410 | KJ38887 | 10/14/2023 | 25.47 | 3.75 | 89 | 64 | 0
5360466410 | KJ38887 | 10/15/2023 | 23.38 | 3.48 | 82 | 55 | 0
5360466410 | KJ38887 | 10/16/2023 | 22.84 | 3.41 | 76 | 50 | 0
5360466410 | KJ38887 | 10/17/2023 | 22.23 | 3.33 | 75 | 49 | 0
5360466410 | KJ38887 | 10/18/2023 | 21.19 | 3.2 | 77 | 50 | 0
5360466410 | KJ38887 | 10/19/2023 | 22.9 | 3.42 | 81 | 55 | 0
5360466410 | KJ38887 | 10/20/2023 | 24.12 | 3.58 | 83 | 55 | 0
5360466410 | KJ38887 | 10/21/2023 | 23.44 | 3.49 | 83 | 55 | 0
5360466410 | KJ38887 | 10/22/2023 | 20.63 | 3.13 | 86 | 52 | 0
5360466410 | KJ38887 | 10/23/2023 | 21.32 | 3.22 | 83 | 58 | 0
5360466410 | KJ38887 | 10/24/2023 | 21.72 | 3.27 | 82 | 67 | 0
5360466410 | KJ38887 | 10/25/2023 | 24.45 | 3.62 | 82 | 68 | 0
5360466410 | KJ38887 | 10/26/2023 | 24.52 | 3.63 | 82 | 65 | 0
5360466410 | KJ38887 | 10/27/2023 | 25.05 | 3.7 | 83 | 64 | 0
5360466410 | KJ38887 | 10/28/2023 | 22.73 | 3.4 | 84 | 62 | 0
5360466410 | KJ38887 | 10/29/2023 | 23.53 | 3.5 | 84 | 61 | 0
5360466410 | KJ38887 | 10/30/2023 | 24.06 | 3.57 | 85 | 60 | 0
5360466410 | KJ38887 | 10/31/2023 | 22.99 | 3.43 | 84 | 58 | 0
5360466410 | KJ38887 | 11/01/2023 | 21.75 | 3.27 | 76 | 53 | 0
5360466410 | KJ38887 | 11/02/2023 | 21.71 | 3.27 | 75 | 53 | 0
5360466410 | KJ38887 | 11/03/2023 | 23.97 | 3.56 | 79 | 59 | 0
5360466410 | KJ38887 | 11/04/2023 | 24.17 | 3.58 | 79 | 55 | 0
5360466410 | KJ38887 | 11/05/2023 | 23.37 | 3.48 | 80 | 51 | 0
5360466410 | KJ38887 | 11/06/2023 | 23.45 | 3.49 | 81 | 48 | 0
5360466410 | KJ38887 | 11/07/2023 | 27.06 | 3.95 | 83 | 53 | 0
5360466410 | KJ38887 | 11/08/2023 | 25.15 | 3.71 | 84 | 50 | 0
5360466410 | KJ38887 | 11/09/2023 | 24.26 | 3.59 | 85 | 55 | 0
5360466410 | KJ38887 | 11/10/2023 | 23.7 | 3.52 | 86 | 60 | 0
5360466410 | KJ38887 | 11/11/2023 | 24.51 | 3.62 | 83 | 65 | 0.33
5360466410 | KJ38887 | 11/12/2023 | 20.62 | 3.13 | 80 | 63 | 0
5360466410 | KJ38887 | 11/13/2023 | 23.04 | 3.44 | 77 | 62 | 0
5360466410 | KJ38887 | 11/14/2023 | 21.3 | 3.21 | 77 | 61 | 0.12
5360466410 | KJ38887 | 11/15/2023 | 20.89 | 3.16 | 77 | 64 | 0.05
5360466410 | KJ38887 | 11/16/2023 | 23.26 | 3.46 | 78 | 62 | 0.16
5360466410 | KJ38887 | 11/17/2023 | 29.31 | 4.24 | 79 | 61 | 2.1
5360466410 | KJ38887 | 11/18/2023 | 24.93 | 3.68 | 78 | 55 | 0.66
5360466410 | KJ38887 | 11/19/2023 | 25.32 | 3.73 | 80 | 56 | 0
5360466410 | KJ38887 | 11/20/2023 | 26.43 | 3.87 | 79 | 59 | 0.02
5360466410 | KJ38887 | 11/21/2023 | 24.72 | 3.65 | 81 | 52 | 0.02
5360466410 | KJ38887 | 11/22/2023 | 23.31 | 3.47 | 81 | 47 | 0
5360466410 | KJ38887 | 11/23/2023 | 9.58 | 1.71 | 73 | 48 | 0.01
5360466410 | KJ38887 | 11/24/2023 | 20.62 | 3.12 | 75 | 52 | 0.01
5360466410 | KJ38887 | 11/25/2023 | 23.53 | 3.5 | 75 | 53 | 0.07
5360466410 | KJ38887 | 11/26/2023 | 18.79 | 2.89 | 75 | 55 | 0.01
5360466410 | KJ38887 | 11/27/2023 | 22.93 | 3.42 | 74 | 44 | 0.55
5360466410 | KJ38887 | 11/28/2023 | 21.37 | 3.22 | 69 | 39 | 0
5360466410 | KJ38887 | 11/29/2023 | 21.72 | 3.27 | 68 | 36 | 0
5360466410 | KJ38887 | 11/30/2023 | 22.81 | 3.41 | 86 | 41 | 0
5360466410 | KJ38887 | 12/01/2023 | 25.97 | 3.81 | 82 | 55 | 0
5360466410 | KJ38887 | 12/02/2023 | 24.24 | 3.59 | 83 | 64 | 0
5360466410 | KJ38887 | 12/03/2023 | 22.39 | 3.35 | 82 | 62 | 0.02
5360466410 | KJ38887 | 12/04/2023 | 23.19 | 3.46 | 79 | 51 | 0.23
5360466410 | KJ38887 | 12/05/2023 | 23.95 | 3.55 | 72 | 47 | 0
5360466410 | KJ38887 | 12/06/2023 | 25.35 | 3.73 | 69 | 41 | 0
5360466410 | KJ38887 | 12/07/2023 | 23.36 | 3.48 | 67 | 41 | 0
5360466410 | KJ38887 | 12/08/2023 | 24.34 | 3.53 | 74 | 47 | 0
5360466410 | KJ38887 | 12/09/2023 | 24.36 | 3.53 | 82 | 56 | 0.04
5360466410 | KJ38887 | 12/10/2023 | 23.24 | 3.39 | 83 | 44 | 0
5360466410 | KJ38887 | 12/11/2023 | 24.44 | 3.54 | 67 | 43 | 0.25
5360466410 | KJ38887 | 12/12/2023 | 24.44 | 3.54 | 71 | 43 | 0
5360466410 | KJ38887 | 12/13/2023 | 22.16 | 3.25 | 73 | 58 | 0
5360466410 | KJ38887 | 12/14/2023 | 24.03 | 3.49 | 72 | 59 | 0.66
5360466410 | KJ38887 | 12/15/2023 | 28.02 | 4 | 72 | 60 | 0.07
5360466410 | KJ38887 | 12/16/2023 | 25.7 | 3.71 | 73 | 58 | 0.11
5360466410 | KJ38887 | 12/17/2023 | 47.38 | 6.48 | 74 | 48 | 4.04
5360466410 | KJ38887 | 12/18/2023 | 28.49 | 4.06 | 68 | 40 | 0.05
5360466410 | KJ38887 | 12/19/2023 | 28.87 | 4.11 | 65 | 41 | 0
5360466410 | KJ38887 | 12/20/2023 | 28.37 | 4.05 | 66 | 44 | 0
5360466410 | KJ38887 | 12/21/2023 | 29.72 | 4.22 | 68 | 46 | 0
5360466410 | KJ38887 | 12/22/2023 | 31.42 | 4.44 | 70 | 49 | 0
5360466410 | KJ38887 | 12/23/2023 | 31.86 | 4.49 | 73 | 53 | 0
5360466410 | KJ38887 | 12/24/2023 | 24.83 | 3.59 | 73 | 53 | 0
5360466410 | KJ38887 | 12/25/2023 | 11.04 | 1.83 | 73 | 60 | 0.09
5360466410 | KJ38887 | 12/26/2023 | 25.15 | 3.64 | 74 | 54 | 0.1
5360466410 | KJ38887 | 12/27/2023 | 25.95 | 3.74 | 71 | 49 | 0
5360466410 | KJ38887 | 12/28/2023 | 23.65 | 3.44 | 66 | 44 | 0.04
5360466410 | KJ38887 | 12/29/2023 | 28.31 | 4.04 | 55 | 46 | 0
5360466410 | KJ38887 | 12/30/2023 | 27.11 | 3.89 | 59 | 37 | 0
5360466410 | KJ38887 | 12/31/2023 | 24.52 | 3.55 | 63 | 36 | 0
|  | Yearly Daily Average: | 30.4118 | 4.3785
|  | Wetter Months' Daily Average: | 33.498 | 4.7653

## 19-1
Daily Billed Information (PS 19-1 - 3 Waters Drive: 2023 Reading Data)
Bill Account | Meter Number | Date | Consumption Recorded (kWh/day) | Estimated Cost ($/day) | Avg. High Temperature (°F) | Avg. Low Temperature (°F) | Rain Recorded by NOAA (inches)
4805280049 | KJ34312 | 01/01/2023 | 131.02 | 16.14 | 79 | 58 | 0.04
4805280049 | KJ34312 | 01/02/2023 | 132.3 | 16.29 | 78 | 53 | 0
4805280049 | KJ34312 | 01/03/2023 | 119.23 | 14.72 | 81 | 51 | 0
4805280049 | KJ34312 | 01/04/2023 | 110.07 | 13.62 | 83 | 57 | 0
4805280049 | KJ34312 | 01/05/2023 | 108.9 | 13.48 | 77 | 46 | 0.04
4805280049 | KJ34312 | 01/06/2023 | 114.38 | 14.14 | 68 | 41 | 0
4805280049 | KJ34312 | 01/07/2023 | 119.51 | 14.76 | 70 | 38 | 0
4805280049 | KJ34312 | 01/08/2023 | 136.65 | 16.82 | 76 | 42 | 0
4805280049 | KJ34312 | 01/09/2023 | 135.83 | 16.72 | 74 | 47 | 0
4805280049 | KJ34312 | 01/10/2023 | 122.8 | 15.15 | 71 | 42 | 0
4805280049 | KJ34312 | 01/11/2023 | 121.01 | 15.48 | 73 | 38 | 0
4805280049 | KJ34312 | 01/12/2023 | 115.44 | 14.78 | 80 | 44 | 0
4805280049 | KJ34312 | 01/13/2023 | 121.19 | 15.5 | 71 | 35 | 0.12
4805280049 | KJ34312 | 01/14/2023 | 137.51 | 17.53 | 61 | 30 | 0
4805280049 | KJ34312 | 01/15/2023 | 150.05 | 19.09 | 63 | 30 | 0
4805280049 | KJ34312 | 01/16/2023 | 135.51 | 17.28 | 71 | 30 | 0
4805280049 | KJ34312 | 01/17/2023 | 125.91 | 16.09 | 75 | 34 | 0
4805280049 | KJ34312 | 01/18/2023 | 118.81 | 15.2 | 79 | 46 | N/A
4805280049 | KJ34312 | 01/19/2023 | 112.6 | 14.43 | 82 | 54 | 0
4805280049 | KJ34312 | 01/20/2023 | 109.93 | 14.1 | 76 | 49 | 0
4805280049 | KJ34312 | 01/21/2023 | 125.07 | 15.98 | 76 | 47 | T
4805280049 | KJ34312 | 01/22/2023 | 155.28 | 19.74 | 82 | 54 | 0.33
4805280049 | KJ34312 | 01/23/2023 | 127.49 | 16.28 | 75 | 44 | 0.05
4805280049 | KJ34312 | 01/24/2023 | 125.95 | 16.09 | 76 | 41 | 0
4805280049 | KJ34312 | 01/25/2023 | 123.36 | 15.77 | 85 | 43 | 0
4805280049 | KJ34312 | 01/26/2023 | 121.31 | 15.52 | 72 | 38 | 0.09
4805280049 | KJ34312 | 01/27/2023 | 119.96 | 15.35 | 62 | 37 | 0
4805280049 | KJ34312 | 01/28/2023 | 128.86 | 16.45 | 69 | 35 | 0
4805280049 | KJ34312 | 01/29/2023 | 145.57 | 18.53 | 78 | 55 | 0
4805280049 | KJ34312 | 01/30/2023 | 124.56 | 15.92 | 86 | 58 | 0
4805280049 | KJ34312 | 01/31/2023 | 123.03 | 15.73 | 83 | 59 | 0
4805280049 | KJ34312 | 02/01/2023 | 117.33 | 15.02 | 82 | 58 | 0
4805280049 | KJ34312 | 02/02/2023 | 111.23 | 14.26 | 82 | 57 | 0
4805280049 | KJ34312 | 02/03/2023 | 119.8 | 15.33 | 78 | 50 | 0
4805280049 | KJ34312 | 02/04/2023 | 130.08 | 16.61 | 70 | 47 | 0.17
4805280049 | KJ34312 | 02/05/2023 | 156.42 | 19.88 | 73 | 48 | 0
4805280049 | KJ34312 | 02/06/2023 | 134.36 | 17.14 | 71 | 46 | 0.01
4805280049 | KJ34312 | 02/07/2023 | 125.95 | 16.09 | 76 | 44
4805280049 | KJ34312 | 02/08/2023 | 132.81 | 16.95 | 79 | 49 | 0
4805280049 | KJ34312 | 02/09/2023 | 110.15 | 14.13 | 83 | 58 | 0
4805280049 | KJ34312 | 02/10/2023 | 112.2 | 14.4 | 85 | 46 | 0.16
4805280049 | KJ34312 | 02/11/2023 | 132.65 | 16.94 | 79 | 40 | 0.57
4805280049 | KJ34312 | 02/12/2023 | 171.02 | 21.72 | 71 | 40 | 0.12
4805280049 | KJ34312 | 02/13/2023 | 129.72 | 16.58 | 71 | 40 | Trace Value
4805280049 | KJ34312 | 02/14/2023 | 124.68 | 15.95 | 75 | 39 | 0
4805280049 | KJ34312 | 02/15/2023 | 117.71 | 15.08 | 82 | 50 | 0
4805280049 | KJ34312 | 02/16/2023 | 117.05 | 15 | 85 | 57 | 0
4805280049 | KJ34312 | 02/17/2023 | 110.64 | 14.2 | 89 | 45
4805280049 | KJ34312 | 02/18/2023 | 126.45 | 16.17 | 67 | 46 | 0.04
4805280049 | KJ34312 | 02/19/2023 | 132.61 | 16.94 | 80 | 48 | 0
4805280049 | KJ34312 | 02/20/2023 | 127.24 | 16.27 | 82 | 53 | 0
4805280049 | KJ34312 | 02/21/2023 | 124.84 | 15.97 | 85 | 57 | 0
4805280049 | KJ34312 | 02/22/2023 | 121.08 | 15.5 | 87 | 58 | 0
4805280049 | KJ34312 | 02/23/2023 | 119.01 | 15.24 | 89 | 60 | 0
4805280049 | KJ34312 | 02/24/2023 | 113.01 | 14.5 | 87 | 58 | 0
4805280049 | KJ34312 | 02/25/2023 | 116.09 | 14.88 | 87 | 58
4805280049 | KJ34312 | 02/26/2023 | 130.57 | 16.68 | 87 | 56 | 0
4805280049 | KJ34312 | 02/27/2023 | 120.2 | 15.39 | 87 | 57 | 0
4805280049 | KJ34312 | 02/28/2023 | 116.75 | 14.96 | 87 | 57 | 0
4805280049 | KJ34312 | 03/01/2023 | 111.94 | 14.36 | 86 | 58 | 0
4805280049 | KJ34312 | 03/02/2023 | 111.57 | 14.32 | 87 | 56 | 0
4805280049 | KJ34312 | 03/03/2023 | 108.53 | 13.94 | 90 | 55 | 0
4805280049 | KJ34312 | 03/04/2023 | 116.23 | 14.9 | 88 | 52 | 0
4805280049 | KJ34312 | 03/05/2023 | 130.13 | 16.63 | 81 | 54 | 0.05
4805280049 | KJ34312 | 03/06/2023 | 112.88 | 14.48 | 84 | 56 | 0
4805280049 | KJ34312 | 03/07/2023 | 109.96 | 14.12 | 87 | 56
4805280049 | KJ34312 | 03/08/2023 | 114.58 | 14.69 | 85 | 58 | 0
4805280049 | KJ34312 | 03/09/2023 | 123.1 | 15.75 | 80 | 51 | 0
4805280049 | KJ34312 | 03/10/2023 | 111.29 | 14.28 | 85 | 54
4805280049 | KJ34312 | 03/11/2023 | 125.33 | 17.7 | 81 | 51 | 1.3
4805280049 | KJ34312 | 03/12/2023 | 126.32 | 17.84 | 86 | 48 | 0
4805280049 | KJ34312 | 03/13/2023 | 172.48 | 24.19 | 81 | 46 | 1.17
4805280049 | KJ34312 | 03/14/2023 | 149.46 | 21.03 | 70 | 43 | 0.6
4805280049 | KJ34312 | 03/15/2023 | 144.52 | 20.34 | 68 | 43 | 0
4805280049 | KJ34312 | 03/16/2023 | 129.46 | 18.27 | 77 | 37 | 0
4805280049 | KJ34312 | 03/17/2023 | 119.8 | 16.94 | 84 | 48
4805280049 | KJ34312 | 03/18/2023 | 126.75 | 17.9 | 80 | 45 | 0
4805280049 | KJ34312 | 03/19/2023 | 139.39 | 19.64 | 68 | 43 | 0.02
4805280049 | KJ34312 | 03/20/2023 | 130.26 | 18.38 | 69 | 42 | 0.02
4805280049 | KJ34312 | 03/21/2023 | 119.31 | 16.87 | 77 | 42 | 0
4805280049 | KJ34312 | 03/22/2023 | 112.27 | 15.91 | 80 | 53 | 0.08
4805280049 | KJ34312 | 03/23/2023 | 108.06 | 15.33 | 83 | 53
4805280049 | KJ34312 | 03/24/2023 | 102.86 | 14.61 | 86 | 53 | 0
4805280049 | KJ34312 | 03/25/2023 | 105.08 | 14.91 | 91 | 60 | 0
4805280049 | KJ34312 | 03/26/2023 | 119.53 | 16.9 | 91 | 63 | 0.68
4805280049 | KJ34312 | 03/27/2023 | 112.66 | 15.96 | 92 | 62 | 0
4805280049 | KJ34312 | 03/28/2023 | 109.78 | 15.56 | 88 | 55 | Trace Value
4805280049 | KJ34312 | 03/29/2023 | 114.39 | 16.2 | 75 | 55 | 0
4805280049 | KJ34312 | 03/30/2023 | 113.76 | 16.11 | 79 | 51 | 0
4805280049 | KJ34312 | 03/31/2023 | 105.73 | 15 | 85 | 55 | 0
4805280049 | KJ34312 | 04/01/2023 | 107.8 | 15.29 | 90 | 60 | 0
4805280049 | KJ34312 | 04/02/2023 | 116.96 | 16.55 | 85 | 60
4805280049 | KJ34312 | 04/03/2023 | 108.32 | 15.36 | 86 | 61 | 0
4805280049 | KJ34312 | 04/04/2023 | 102.6 | 14.57 | 88 | 60 | Trace Value
4805280049 | KJ34312 | 04/05/2023 | 100.06 | 14.22 | 87 | 63 | 0
4805280049 | KJ34312 | 04/06/2023 | 98.59 | 14.02 | 87 | 64 | 0
4805280049 | KJ34312 | 04/07/2023 | 103.91 | 14.75 | 85 | 64
4805280049 | KJ34312 | 04/08/2023 | 113.47 | 16.07 | 86 | 62
4805280049 | KJ34312 | 04/09/2023 | 122.53 | 17.32 | 80 | 60 | 0.01
4805280049 | KJ34312 | 04/10/2023 | 144.68 | 20.37 | 79 | 58 | 0.68
4805280049 | KJ34312 | 04/11/2023 | 116.12 | 16.44 | 78 | 58 | 1.38
4805280049 | KJ34312 | 04/12/2023 | 107.99 | 14.88 | 79 | 59 | 0.03
4805280049 | KJ34312 | 04/13/2023 | 140.86 | 19.26 | 87 | 61 | 0.07
4805280049 | KJ34312 | 04/14/2023 | 160.18 | 21.83 | 86 | 59 | 0.57
4805280049 | KJ34312 | 04/15/2023 | 139.09 | 19.02 | 87 | 60 | 0.02
4805280049 | KJ34312 | 04/16/2023 | 129.07 | 17.69 | 88 | 59 | 0
4805280049 | KJ34312 | 04/17/2023 | 120.9 | 16.6 | 81 | 50 | 0.04
4805280049 | KJ34312 | 04/18/2023 | 115.83 | 15.92 | 81 | 46 | 0.02
4805280049 | KJ34312 | 04/19/2023 | 110.55 | 15.22 | 82 | 50 | 0
4805280049 | KJ34312 | 04/20/2023 | 100.56 | 13.89 | 84 | 55 | 0
4805280049 | KJ34312 | 04/21/2023 | 98.58 | 13.62 | 87 | 59
4805280049 | KJ34312 | 04/22/2023 | 100.83 | 13.92 | 89 | 57 | 0.3
4805280049 | KJ34312 | 04/23/2023 | 112.66 | 15.5 | 84 | 53 | 0.42
4805280049 | KJ34312 | 04/24/2023 | 103.77 | 14.31 | 80 | 55 | 0
4805280049 | KJ34312 | 04/25/2023 | 103.27 | 14.25 | 82 | 61 | 0.25
4805280049 | KJ34312 | 04/26/2023 | 97.59 | 13.49 | 84 | 62 | 0.07
4805280049 | KJ34312 | 04/27/2023 | 120.02 | 16.48 | 86 | 63 | 0
4805280049 | KJ34312 | 04/28/2023 | 146.23 | 19.97 | 87 | 62 | 1.62
4805280049 | KJ34312 | 04/29/2023 | 134.89 | 18.46 | 88 | 62 | 0
4805280049 | KJ34312 | 04/30/2023 | 143.23 | 19.57 | 85 | 57 | 0.52
4805280049 | KJ34312 | 05/01/2023 | 122.27 | 16.78 | 85 | 56 | 0
4805280049 | KJ34312 | 05/02/2023 | 108.69 | 14.97 | 87 | 56 | 0
4805280049 | KJ34312 | 05/03/2023 | 103.33 | 14.25 | 86 | 53 | 0
4805280049 | KJ34312 | 05/04/2023 | 97.91 | 13.53 | 84 | 53 | 0
4805280049 | KJ34312 | 05/05/2023 | 89.92 | 12.47 | 87 | 57 | 0
4805280049 | KJ34312 | 05/06/2023 | 96.92 | 13.4 | 86 | 65 | 0
4805280049 | KJ34312 | 05/07/2023 | 105.33 | 14.52 | 88 | 61 | 0.02
4805280049 | KJ34312 | 05/08/2023 | 94.77 | 13.11 | 87 | 55 | 0
4805280049 | KJ34312 | 05/09/2023 | 98.43 | 13.6 | 91 | 63 | 0
4805280049 | KJ34312 | 05/10/2023 | 82.53 | 11.48 | 92 | 66 | 0
4805280049 | KJ34312 | 05/11/2023 | 84 | 11.66 | 88 | 67 | 0.04
4805280049 | KJ34312 | 05/12/2023 | 78.35 | 10.91 | 86 | 66 | 0
4805280049 | KJ34312 | 05/13/2023 | 88.11 | 12.21 | 85 | 64 | 0
4805280049 | KJ34312 | 05/14/2023 | 89.93 | 12.45 | 86 | 63 | 0
4805280049 | KJ34312 | 05/15/2023 | 85.73 | 11.89 | 89 | 62 | 0
4805280049 | KJ34312 | 05/16/2023 | 80.98 | 11.26 | 88 | 64 | 0
4805280049 | KJ34312 | 05/17/2023 | 79.59 | 11.07 | 92 | 67 | 0
4805280049 | KJ34312 | 05/18/2023 | 85.07 | 11.8 | 89 | 65 | 1.24
4805280049 | KJ34312 | 05/19/2023 | 83.5 | 11.59 | 88 | 66 | 0.02
4805280049 | KJ34312 | 05/20/2023 | 88.22 | 12.22 | 88 | 66 | 0
4805280049 | KJ34312 | 05/21/2023 | 91.65 | 12.68 | 88 | 67
4805280049 | KJ34312 | 05/22/2023 | 112.48 | 15.45 | 88 | 67 | 0.65
4805280049 | KJ34312 | 05/23/2023 | 117.81 | 16.16 | 85 | 67 | 0.56
4805280049 | KJ34312 | 05/24/2023 | 113.46 | 15.58 | 83 | 66 | 0.12
4805280049 | KJ34312 | 05/25/2023 | 105.24 | 14.48 | 83 | 66 | 0.16
4805280049 | KJ34312 | 05/26/2023 | 97.02 | 13.39 | 82 | 62 | 0.05
4805280049 | KJ34312 | 05/27/2023 | 100.53 | 13.86 | 81 | 56 | Trace Value
4805280049 | KJ34312 | 05/28/2023 | 101.62 | 14 | 85 | 55 | 0
4805280049 | KJ34312 | 05/29/2023 | 101.22 | 13.95 | 87 | 60 | 0
4805280049 | KJ34312 | 05/30/2023 | 90.45 | 12.52 | 88 | 62 | 0
4805280049 | KJ34312 | 05/31/2023 | 86.94 | 12.05 | 87 | 68 | 0
4805280049 | KJ34312 | 06/01/2023 | 82.7 | 11.49 | 85 | 68 | 0
4805280049 | KJ34312 | 06/02/2023 | 84.78 | 11.76 | 85 | 67 | 0
4805280049 | KJ34312 | 06/03/2023 | 95.98 | 13.25 | 84 | 67 | 0
4805280049 | KJ34312 | 06/04/2023 | 104.92 | 14.44 | 84 | 66 | 0
4805280049 | KJ34312 | 06/05/2023 | 88.54 | 12.26 | 84 | 64 | 0.3
4805280049 | KJ34312 | 06/06/2023 | 83.57 | 11.6 | 88 | 62
4805280049 | KJ34312 | 06/07/2023 | 99.38 | 13.7 | 91 | 68 | 0
4805280049 | KJ34312 | 06/08/2023 | 125.8 | 17.22 | 92 | 68 | 1.64
4805280049 | KJ34312 | 06/09/2023 | 105.13 | 14.47 | 92 | 68 | 0
4805280049 | KJ34312 | 06/10/2023 | 108.36 | 14.46 | 88 | 67 | 0.54
4805280049 | KJ34312 | 06/11/2023 | 110.06 | 14.68 | 91 | 69 | 0.09
4805280049 | KJ34312 | 06/12/2023 | 104.51 | 13.96 | 94 | 69 | 0
4805280049 | KJ34312 | 06/13/2023 | 93.7 | 12.57 | 95 | 71
4805280049 | KJ34312 | 06/14/2023 | 85.9 | 11.56 | 95 | 71 | 0
4805280049 | KJ34312 | 06/15/2023 | 92.21 | 12.37 | 95 | 66 | 0.44
4805280049 | KJ34312 | 06/16/2023 | 40.32 | 5.67 | 95 | 68 | 0.45
4805280049 | KJ34312 | 06/17/2023 | 172.72 | 22.78 | 93 | 68 | 0.91
4805280049 | KJ34312 | 06/18/2023 | 111.33 | 14.85 | 94 | 68 | 0.28
4805280049 | KJ34312 | 06/19/2023 | 127.66 | 16.96 | 93 | 70 | 0.63
4805280049 | KJ34312 | 06/20/2023 | 139.89 | 18.54 | 91 | 69 | 0.46
4805280049 | KJ34312 | 06/21/2023 | 143.56 | 19.01 | 91 | 71 | 0.24
4805280049 | KJ34312 | 06/22/2023 | 142.31 | 18.85 | 93 | 66 | 0.04
4805280049 | KJ34312 | 06/23/2023 | 178.03 | 23.47 | 91 | 69 | 0.35
4805280049 | KJ34312 | 06/24/2023 | 155.14 | 20.51 | 92 | 70 | 0.24
4805280049 | KJ34312 | 06/25/2023 | 147.21 | 19.48 | 91 | 70 | 0.15
4805280049 | KJ34312 | 06/26/2023 | 128.15 | 17.02 | 94 | 70 | 0
4805280049 | KJ34312 | 06/27/2023 | 111.92 | 14.92 | 97 | 71 | 0
4805280049 | KJ34312 | 06/28/2023 | 164.95 | 21.78 | 95 | 72 | 0
4805280049 | KJ34312 | 06/29/2023 | 146.62 | 19.41 | 95 | 71 | 0.88
4805280049 | KJ34312 | 06/30/2023 | 94.98 | 12.73 | 94 | 71 | 0
4805280049 | KJ34312 | 07/01/2023 | 80.79 | 10.9 | 94 | 71 | 0
4805280049 | KJ34312 | 07/02/2023 | 80.6 | 10.87 | 95 | 71 | 0
4805280049 | KJ34312 | 07/03/2023 | 72.46 | 9.82 | 97 | 72 | 0
4805280049 | KJ34312 | 07/04/2023 | 73.63 | 9.97 | 95 | 73 | 0
4805280049 | KJ34312 | 07/05/2023 | 70.97 | 9.63 | 95 | 74 | 0
4805280049 | KJ34312 | 07/06/2023 | 108.95 | 14.54 | 96 | 73 | 0.04
4805280049 | KJ34312 | 07/07/2023 | 105.61 | 14.11 | 95 | 73 | 0.03
4805280049 | KJ34312 | 07/08/2023 | 100.09 | 13.39 | 94 | 74 | 0.31
4805280049 | KJ34312 | 07/09/2023 | 96.96 | 12.99 | 96 | 74 | 0.2
4805280049 | KJ34312 | 07/10/2023 | 102.43 | 13.7 | 96 | 74 | 0
4805280049 | KJ34312 | 07/11/2023 | 88.16 | 11.85 | 94 | 73 | 0.78
4805280049 | KJ34312 | 07/12/2023 | 100.08 | 13.43 | 94 | 73 | 0.1
4805280049 | KJ34312 | 07/13/2023 | 158.81 | 21.01 | 94 | 72 | Trace Value
4805280049 | KJ34312 | 07/14/2023 | 130.62 | 17.37 | 95 | 73 | 0.33
4805280049 | KJ34312 | 07/15/2023 | 145.4 | 19.28 | 96 | 73 | 0.12
4805280049 | KJ34312 | 07/16/2023 | 156.75 | 20.75 | 96 | 74 | 0.15
4805280049 | KJ34312 | 07/17/2023 | 136.32 | 18.11 | 95 | 74 | 2.8
4805280049 | KJ34312 | 07/18/2023 | 235.85 | 30.97 | 95 | 72 | 0.22
4805280049 | KJ34312 | 07/19/2023 | 117.64 | 15.69 | 95 | 71 | 0.14
4805280049 | KJ34312 | 07/20/2023 | 160.23 | 21.2 | 96 | 73 | 0
4805280049 | KJ34312 | 07/21/2023 | 107.83 | 14.43 | 99 | 74 | 0
4805280049 | KJ34312 | 07/22/2023 | 121.85 | 16.24 | 97 | 75 | 0
4805280049 | KJ34312 | 07/23/2023 | 142.3 | 18.88 | 94 | 71 | 0.7
4805280049 | KJ34312 | 07/24/2023 | 126.23 | 16.8 | 93 | 73 | 1.12
4805280049 | KJ34312 | 07/25/2023 | 111.83 | 14.94 | 93 | 73 | 0.3
4805280049 | KJ34312 | 07/26/2023 | 97.42 | 13.08 | 92 | 73 | 0
4805280049 | KJ34312 | 07/27/2023 | 89.17 | 12.01 | 91 | 73 | 0
4805280049 | KJ34312 | 07/28/2023 | 99.25 | 13.32 | 92 | 73 | 1
4805280049 | KJ34312 | 07/29/2023 | 102.45 | 13.73 | 93 | 73 | 0.05
4805280049 | KJ34312 | 07/30/2023 | 125.42 | 16.7 | 95 | 74 | Trace Value
4805280049 | KJ34312 | 07/31/2023 | 140.54 | 18.65 | 95 | 71 | 0.74
4805280049 | KJ34312 | 08/01/2023 | 126.44 | 16.83 | 95 | 71 | 0.08
4805280049 | KJ34312 | 08/02/2023 | 112.49 | 15.03 | 93 | 74 | 0
4805280049 | KJ34312 | 08/03/2023 | 102.13 | 13.69 | 91 | 73 | 0
4805280049 | KJ34312 | 08/04/2023 | 113.81 | 15.2 | 94 | 73 | 0
4805280049 | KJ34312 | 08/05/2023 | 126.94 | 16.9 | 94 | 73 | 0.17
4805280049 | KJ34312 | 08/06/2023 | 133.3 | 17.72 | 95 | 74 | 0.66
4805280049 | KJ34312 | 08/07/2023 | 129.87 | 17.27 | 97 | 75 | 0.03
4805280049 | KJ34312 | 08/08/2023 | 107.09 | 14.33 | 99 | 75 | 0
4805280049 | KJ34312 | 08/09/2023 | 123.66 | 16.47 | 99 | 74 | 0
4805280049 | KJ34312 | 08/10/2023 | 93.82 | 12.62 | 100 | 75 | 0.16
4805280049 | KJ34312 | 08/11/2023 | 80.38 | 10.84 | 99 | 75 | 0
4805280049 | KJ34312 | 08/12/2023 | 82.23 | 11.07 | 98 | 76 | 0.25
4805280049 | KJ34312 | 08/13/2023 | 85.5 | 11.5 | 97 | 74 | 0
4805280049 | KJ34312 | 08/14/2023 | 75.28 | 10.18 | 97 | 76 | 0
4805280049 | KJ34312 | 08/15/2023 | 73.72 | 9.98 | 97 | 75 | 0
4805280049 | KJ34312 | 08/16/2023 | 97.86 | 13.09 | 96 | 73 | 0.09
4805280049 | KJ34312 | 08/17/2023 | 112.71 | 15.01 | 93 | 72 | 0.36
4805280049 | KJ34312 | 08/18/2023 | 111.75 | 14.88 | 93 | 73 | 1.09
4805280049 | KJ34312 | 08/19/2023 | 111.43 | 14.84 | 93 | 72 | 0.69
4805280049 | KJ34312 | 08/20/2023 | 108.64 | 14.48 | 92 | 75 | 0
4805280049 | KJ34312 | 08/21/2023 | 90.19 | 12.1 | 92 | 74 | 0
4805280049 | KJ34312 | 08/22/2023 | 83.48 | 11.23 | 93 | 72 | 0
4805280049 | KJ34312 | 08/23/2023 | 72.2 | 9.78 | 93 | 74 | 0
4805280049 | KJ34312 | 08/24/2023 | 69.27 | 9.4 | 93 | 74 | 0.99
4805280049 | KJ34312 | 08/25/2023 | 66.6 | 9.06 | 92 | 71 | 0
4805280049 | KJ34312 | 08/26/2023 | 69.7 | 9.46 | 95 | 73 | 0
4805280049 | KJ34312 | 08/27/2023 | 74.96 | 10.13 | 95 | 72
4805280049 | KJ34312 | 08/28/2023 | 68.7 | 9.33 | 96 | 74 | Trace Value
4805280049 | KJ34312 | 08/29/2023 | 70.92 | 9.61 | 95 | 74 | 0
4805280049 | KJ34312 | 08/30/2023 | 83.77 | 11.27 | 94 | 74 | 0.93
4805280049 | KJ34312 | 08/31/2023 | 76.13 | 10.29 | 94 | 74 | 0.05
4805280049 | KJ34312 | 09/01/2023 | 74.01 | 10.01 | 92 | 73 | 0
4805280049 | KJ34312 | 09/02/2023 | 74.44 | 10.07 | 91 | 72
4805280049 | KJ34312 | 09/03/2023 | 73.92 | 10 | 92 | 71 | 0.05
4805280049 | KJ34312 | 09/04/2023 | 77.37 | 10.45 | 90 | 68 | 0
4805280049 | KJ34312 | 09/05/2023 | 68.45 | 9.29 | 90 | 64 | 0
4805280049 | KJ34312 | 09/06/2023 | 63.78 | 8.69 | 94 | 69 | 0
4805280049 | KJ34312 | 09/07/2023 | 63.97 | 8.72 | 95 | 70
4805280049 | KJ34312 | 09/08/2023 | 99.46 | 13.3 | 95 | 69 | 0
4805280049 | KJ34312 | 09/09/2023 | 92.13 | 12.35 | 94 | 64 | 0.48
4805280049 | KJ34312 | 09/10/2023 | 102.94 | 13.75 | 93 | 71 | Trace Value
4805280049 | KJ34312 | 09/11/2023 | 78.9 | 10.64 | 92 | 72 | 0
4805280049 | KJ34312 | 09/12/2023 | 80.88 | 10.94 | 92 | 71 | Trace Value
4805280049 | KJ34312 | 09/13/2023 | 139.8 | 18.56 | 92 | 72 | 0.03
4805280049 | KJ34312 | 09/14/2023 | 124.94 | 16.64 | 91 | 71 | 0.29
4805280049 | KJ34312 | 09/15/2023 | 112.15 | 14.99 | 88 | 70 | 0
4805280049 | KJ34312 | 09/16/2023 | 101.53 | 13.61 | 87 | 69 | 0.54
4805280049 | KJ34312 | 09/17/2023 | 99.61 | 13.36 | 92 | 70 | 0
4805280049 | KJ34312 | 09/18/2023 | 87.53 | 11.8 | 89 | 68 | 0.08
4805280049 | KJ34312 | 09/19/2023 | 81.56 | 11.03 | 88 | 64 | 0
4805280049 | KJ34312 | 09/20/2023 | 76.8 | 10.42 | 88 | 69 | 0
4805280049 | KJ34312 | 09/21/2023 | 75.37 | 10.23 | 87 | 68 | 0.08
4805280049 | KJ34312 | 09/22/2023 | 75.92 | 10.3 | 85 | 65 | 0.3
4805280049 | KJ34312 | 09/23/2023 | 82.51 | 11.15 | 87 | 61 | 0
4805280049 | KJ34312 | 09/24/2023 | 86.61 | 11.68 | 89 | 59 | 0
4805280049 | KJ34312 | 09/25/2023 | 104.63 | 14.01 | 90 | 66 | 0
4805280049 | KJ34312 | 09/26/2023 | 148.91 | 19.74 | 89 | 71 | 2.11
4805280049 | KJ34312 | 09/27/2023 | 196.73 | 25.92 | 88 | 71 | 0.91
4805280049 | KJ34312 | 09/28/2023 | 167.97 | 22.2 | 87 | 71 | 0.81
4805280049 | KJ34312 | 09/29/2023 | 174.69 | 23.07 | 85 | 71 | 0.02
4805280049 | KJ34312 | 09/30/2023 | 291.86 | 38.21 | 85 | 71 | 0.2
4805280049 | KJ34312 | 10/01/2023 | 393.29 | 51.32 | 85 | 70 | 2.53
4805280049 | KJ34312 | 10/02/2023 | 186.47 | 24.59 | 85 | 69 | 0.56
4805280049 | KJ34312 | 10/03/2023 | 129.88 | 17.28 | 85 | 70 | 0
4805280049 | KJ34312 | 10/04/2023 | 111.52 | 14.9 | 86 | 70 | 0.05
4805280049 | KJ34312 | 10/05/2023 | 100.98 | 13.54 | 86 | 69 | 0
4805280049 | KJ34312 | 10/06/2023 | 90.98 | 12.25 | 87 | 66 | 0
4805280049 | KJ34312 | 10/07/2023 | 90.82 | 12.23 | 90 | 56 | 0
4805280049 | KJ34312 | 10/08/2023 | 95.14 | 12.79 | 82 | 53 | 0
4805280049 | KJ34312 | 10/09/2023 | 86.08 | 11.62 | 80 | 55 | 0
4805280049 | KJ34312 | 10/10/2023 | 93.21 | 12.54 | 84 | 56 | 0
4805280049 | KJ34312 | 10/11/2023 | 79.18 | 10.72 | 84 | 65 | 0
4805280049 | KJ34312 | 10/12/2023 | 341.39 | 44.63 | 88 | 72 | 2.8
4805280049 | KJ34312 | 10/13/2023 | 284.07 | 37.22 | 89 | 68 | 1.67
4805280049 | KJ34312 | 10/14/2023 | 133.25 | 17.72 | 89 | 64 | 0
4805280049 | KJ34312 | 10/15/2023 | 136.29 | 18.11 | 82 | 55 | 0
4805280049 | KJ34312 | 10/16/2023 | 123.43 | 16.45 | 76 | 50 | 0
4805280049 | KJ34312 | 10/17/2023 | 108.93 | 14.57 | 75 | 49 | 0
4805280049 | KJ34312 | 10/18/2023 | 99.17 | 13.31 | 77 | 50 | 0
4805280049 | KJ34312 | 10/19/2023 | 92.9 | 12.5 | 81 | 55 | 0
4805280049 | KJ34312 | 10/20/2023 | 86.58 | 11.68 | 83 | 55 | 0
4805280049 | KJ34312 | 10/21/2023 | 88.75 | 11.96 | 83 | 55 | 0
4805280049 | KJ34312 | 10/22/2023 | 94.5 | 12.71 | 86 | 52 | 0
4805280049 | KJ34312 | 10/23/2023 | 83.43 | 11.28 | 83 | 58 | 0
4805280049 | KJ34312 | 10/24/2023 | 77.21 | 10.47 | 82 | 67 | 0
4805280049 | KJ34312 | 10/25/2023 | 72.76 | 9.9 | 82 | 68 | 0
4805280049 | KJ34312 | 10/26/2023 | 71.31 | 9.71 | 82 | 65 | 0
4805280049 | KJ34312 | 10/27/2023 | 70.95 | 9.66 | 83 | 64 | 0
4805280049 | KJ34312 | 10/28/2023 | 75.21 | 10.21 | 84 | 62 | 0
4805280049 | KJ34312 | 10/29/2023 | 81.23 | 10.99 | 84 | 61 | 0
4805280049 | KJ34312 | 10/30/2023 | 72.43 | 9.85 | 85 | 60 | 0
4805280049 | KJ34312 | 10/31/2023 | 67.05 | 9.16 | 84 | 58 | 0
4805280049 | KJ34312 | 11/01/2023 | 72.1 | 9.81 | 76 | 53 | 0
4805280049 | KJ34312 | 11/02/2023 | 70.05 | 9.55 | 75 | 53 | 0
4805280049 | KJ34312 | 11/03/2023 | 65.86 | 9 | 79 | 59 | 0
4805280049 | KJ34312 | 11/04/2023 | 75.55 | 10.26 | 79 | 55 | 0
4805280049 | KJ34312 | 11/05/2023 | 84.5 | 11.42 | 80 | 51 | 0
4805280049 | KJ34312 | 11/06/2023 | 72.61 | 9.88 | 81 | 48 | 0
4805280049 | KJ34312 | 11/07/2023 | 69.98 | 9.54 | 83 | 53 | 0
4805280049 | KJ34312 | 11/08/2023 | 85.47 | 11.54 | 84 | 50 | 0
4805280049 | KJ34312 | 11/09/2023 | 66.15 | 9.04 | 85 | 55 | 0
4805280049 | KJ34312 | 11/10/2023 | 66.28 | 9.06 | 86 | 60 | 0
4805280049 | KJ34312 | 11/11/2023 | 72.25 | 9.83 | 83 | 65 | 0.33
4805280049 | KJ34312 | 11/12/2023 | 80.06 | 10.84 | 80 | 63 | 0
4805280049 | KJ34312 | 11/13/2023 | 75.57 | 10.26 | 77 | 62 | 0
4805280049 | KJ34312 | 11/14/2023 | 71.88 | 9.79 | 77 | 61 | 0.12
4805280049 | KJ34312 | 11/15/2023 | 72.77 | 9.9 | 77 | 64 | 0.05
4805280049 | KJ34312 | 11/16/2023 | 112.47 | 15.03 | 78 | 62 | 0.16
4805280049 | KJ34312 | 11/17/2023 | 257.61 | 33.8 | 79 | 61 | 2.1
4805280049 | KJ34312 | 11/18/2023 | 147.88 | 19.61 | 78 | 55 | 0.66
4805280049 | KJ34312 | 11/19/2023 | 125.69 | 16.74 | 80 | 56 | 0
4805280049 | KJ34312 | 11/20/2023 | 107.5 | 14.39 | 79 | 59 | 0.02
4805280049 | KJ34312 | 11/21/2023 | 111.79 | 14.95 | 81 | 52 | 0.02
4805280049 | KJ34312 | 11/22/2023 | 114.53 | 15.3 | 81 | 47 | 0
4805280049 | KJ34312 | 11/23/2023 | 132.45 | 17.62 | 73 | 48 | 0.01
4805280049 | KJ34312 | 11/24/2023 | 110.93 | 14.84 | 75 | 52 | 0.01
4805280049 | KJ34312 | 11/25/2023 | 106.12 | 14.21 | 75 | 53 | 0.07
4805280049 | KJ34312 | 11/26/2023 | 132.98 | 17.69 | 75 | 55 | 0.01
4805280049 | KJ34312 | 11/27/2023 | 125.69 | 16.74 | 74 | 44 | 0.55
4805280049 | KJ34312 | 11/28/2023 | 112.46 | 15.03 | 69 | 39 | 0
4805280049 | KJ34312 | 11/29/2023 | 104.63 | 14.02 | 68 | 36 | 0
4805280049 | KJ34312 | 11/30/2023 | 99.23 | 13.32 | 86 | 41 | 0
4805280049 | KJ34312 | 12/01/2023 | 89.54 | 12.07 | 82 | 55 | 0
4805280049 | KJ34312 | 12/02/2023 | 92.56 | 12.46 | 83 | 64 | 0
4805280049 | KJ34312 | 12/03/2023 | 123.47 | 16.46 | 82 | 62 | 0.02
4805280049 | KJ34312 | 12/04/2023 | 122.14 | 16.28 | 79 | 51 | 0.23
4805280049 | KJ34312 | 12/05/2023 | 109.04 | 14.59 | 72 | 47 | 0
4805280049 | KJ34312 | 12/06/2023 | 103.77 | 13.91 | 69 | 41 | 0
4805280049 | KJ34312 | 12/07/2023 | 117.23 | 15.65 | 67 | 41 | 0
4805280049 | KJ34312 | 12/08/2023 | 90.96 | 12.25 | 74 | 47 | 0
4805280049 | KJ34312 | 12/09/2023 | 88.27 | 11.76 | 82 | 56 | 0.04
4805280049 | KJ34312 | 12/10/2023 | 102.63 | 13.6 | 83 | 44 | 0
4805280049 | KJ34312 | 12/11/2023 | 100.77 | 13.36 | 67 | 43 | 0.25
4805280049 | KJ34312 | 12/12/2023 | 96.5 | 12.82 | 71 | 43 | 0
4805280049 | KJ34312 | 12/13/2023 | 91.16 | 12.13 | 73 | 58 | 0
4805280049 | KJ34312 | 12/14/2023 | 100.06 | 13.27 | 72 | 59 | 0.66
4805280049 | KJ34312 | 12/15/2023 | 93.49 | 12.43 | 72 | 60 | 0.07
4805280049 | KJ34312 | 12/16/2023 | 140.14 | 18.42 | 73 | 58 | 0.11
4805280049 | KJ34312 | 12/17/2023 | 409.11 | 52.94 | 74 | 48 | 4.04
4805280049 | KJ34312 | 12/18/2023 | 190.04 | 24.82 | 68 | 40 | 0.05
4805280049 | KJ34312 | 12/19/2023 | 163.28 | 21.39 | 65 | 41 | 0
4805280049 | KJ34312 | 12/20/2023 | 145.92 | 19.16 | 66 | 44 | 0
4805280049 | KJ34312 | 12/21/2023 | 133.64 | 17.58 | 68 | 46 | 0
4805280049 | KJ34312 | 12/22/2023 | 126.01 | 16.6 | 70 | 49 | 0
4805280049 | KJ34312 | 12/23/2023 | 127.97 | 16.86 | 73 | 53 | 0
4805280049 | KJ34312 | 12/24/2023 | 135.76 | 17.86 | 73 | 53 | 0
4805280049 | KJ34312 | 12/25/2023 | 126.14 | 16.62 | 73 | 60 | 0.09
4805280049 | KJ34312 | 12/26/2023 | 122.3 | 16.13 | 74 | 54 | 0.1
4805280049 | KJ34312 | 12/27/2023 | 111.61 | 14.75 | 71 | 49 | 0
4805280049 | KJ34312 | 12/28/2023 | 112.2 | 14.83 | 66 | 44 | 0.04
4805280049 | KJ34312 | 12/29/2023 | 108.52 | 14.36 | 55 | 46 | 0
4805280049 | KJ34312 | 12/30/2023 | 110.32 | 14.59 | 59 | 37 | 0
4805280049 | KJ34312 | 12/31/2023 | 115.83 | 15.3 | 63 | 36 | 0
|  | Yearly Daily Average: | 113.4641 | 15.1469
|  | Wetter Months' Daily Average: | 113.1244 | 15.0759

## 20-1
Daily Billed Information (PS 20-1 - 316 Wellington Drive: 2023 Reading Data)
Bill Account | Meter Number | Date | Consumption Recorded (kWh/day) | Estimated Cost ($/day) | Avg. High Temperature (°F) | Avg. Low Temperature (°F) | Rain Recorded by NOAA (inches)
6826650175 | KN51093 | 01/01/2023 | 190.95 | 21.44 | 79 | 58 | 0.04
6826650175 | KN51093 | 01/02/2023 | 193.81 | 21.74 | 78 | 53 | 0
6826650175 | KN51093 | 01/03/2023 | 178.8 | 20.13 | 81 | 51 | 0
6826650175 | KN51093 | 01/04/2023 | 171.49 | 19.35 | 83 | 57 | 0
6826650175 | KN51093 | 01/05/2023 | 197.05 | 22.09 | 77 | 46 | 0.04
6826650175 | KN51093 | 01/06/2023 | 184.66 | 20.76 | 68 | 41 | 0
6826650175 | KN51093 | 01/07/2023 | 192.19 | 21.57 | 70 | 38 | 0
6826650175 | KN51093 | 01/08/2023 | 191.05 | 21.45 | 76 | 42 | 0
6826650175 | KN51093 | 01/09/2023 | 181.02 | 20.37 | 74 | 47 | 0
6826650175 | KN51093 | 01/10/2023 | 173.63 | 19.58 | 71 | 42 | 0
6826650175 | KN51093 | 01/11/2023 | 172.42 | 19.45 | 73 | 38 | 0
6826650175 | KN51093 | 01/12/2023 | 173.67 | 19.58 | 80 | 44 | 0
6826650175 | KN51093 | 01/13/2023 | 169.49 | 19.13 | 71 | 35 | 0.12
6826650175 | KN51093 | 01/14/2023 | 180.61 | 20.33 | 61 | 30 | 0
6826650175 | KN51093 | 01/15/2023 | 189.67 | 21.3 | 63 | 30 | 0
6826650175 | KN51093 | 01/16/2023 | 198.04 | 22.2 | 71 | 30 | 0
6826650175 | KN51093 | 01/17/2023 | 187.49 | 21.07 | 75 | 34 | 0
6826650175 | KN51093 | 01/18/2023 | 154.81 | 19.88 | 79 | 46 | N/A
6826650175 | KN51093 | 01/19/2023 | 177.73 | 22.67 | 82 | 54 | 0
6826650175 | KN51093 | 01/20/2023 | 162.93 | 20.87 | 76 | 49 | 0
6826650175 | KN51093 | 01/21/2023 | 195.93 | 24.89 | 76 | 47 | T
6826650175 | KN51093 | 01/22/2023 | 218.16 | 27.59 | 82 | 54 | 0.33
6826650175 | KN51093 | 01/23/2023 | 196.83 | 24.99 | 75 | 44 | 0.05
6826650175 | KN51093 | 01/24/2023 | 184.18 | 23.45 | 76 | 41 | 0
6826650175 | KN51093 | 01/25/2023 | 177.66 | 22.66 | 85 | 43 | 0
6826650175 | KN51093 | 01/26/2023 | 184.05 | 23.44 | 72 | 38 | 0.09
6826650175 | KN51093 | 01/27/2023 | 182.43 | 23.24 | 62 | 37 | 0
6826650175 | KN51093 | 01/28/2023 | 182.93 | 23.3 | 69 | 35 | 0
6826650175 | KN51093 | 01/29/2023 | 203.52 | 25.81 | 78 | 55 | 0
6826650175 | KN51093 | 01/30/2023 | 192.38 | 24.45 | 86 | 58 | 0
6826650175 | KN51093 | 01/31/2023 | 189.27 | 24.07 | 83 | 59 | 0
6826650175 | KN51093 | 02/01/2023 | 176.64 | 22.54 | 82 | 58 | 0
6826650175 | KN51093 | 02/02/2023 | 183.04 | 23.32 | 82 | 57 | 0
6826650175 | KN51093 | 02/03/2023 | 187.99 | 23.92 | 78 | 50 | 0
6826650175 | KN51093 | 02/04/2023 | 204.2 | 25.89 | 70 | 47 | 0.17
6826650175 | KN51093 | 02/05/2023 | 220.99 | 27.94 | 73 | 48 | 0
6826650175 | KN51093 | 02/06/2023 | 214.5 | 27.15 | 71 | 46 | 0.01
6826650175 | KN51093 | 02/07/2023 | 200.75 | 25.47 | 76 | 44
6826650175 | KN51093 | 02/08/2023 | 183.9 | 23.42 | 79 | 49 | 0
6826650175 | KN51093 | 02/09/2023 | 174.58 | 22.28 | 83 | 58 | 0
6826650175 | KN51093 | 02/10/2023 | 196.65 | 24.97 | 85 | 46 | 0.16
6826650175 | KN51093 | 02/11/2023 | 212.95 | 26.96 | 79 | 40 | 0.57
6826650175 | KN51093 | 02/12/2023 | 219.62 | 27.77 | 71 | 40 | 0.12
6826650175 | KN51093 | 02/13/2023 | 193.57 | 24.6 | 71 | 40 | Trace Value
6826650175 | KN51093 | 02/14/2023 | 227.04 | 28.68 | 75 | 39 | 0
6826650175 | KN51093 | 02/15/2023 | 175.51 | 22.4 | 82 | 50 | 0
6826650175 | KN51093 | 02/16/2023 | 183.3 | 29.67 | 85 | 57 | 0
6826650175 | KN51093 | 02/17/2023 | 184.37 | 29.84 | 89 | 45
6826650175 | KN51093 | 02/18/2023 | 189.42 | 30.63 | 67 | 46 | 0.04
6826650175 | KN51093 | 02/19/2023 | 196.67 | 31.76 | 80 | 48 | 0
6826650175 | KN51093 | 02/20/2023 | 192.03 | 31.03 | 82 | 53 | 0
6826650175 | KN51093 | 02/21/2023 | 184.28 | 29.82 | 85 | 57 | 0
6826650175 | KN51093 | 02/22/2023 | 175.59 | 28.46 | 87 | 58 | 0
6826650175 | KN51093 | 02/23/2023 | 189.06 | 30.57 | 89 | 60 | 0
6826650175 | KN51093 | 02/24/2023 | 171.78 | 27.87 | 87 | 58 | 0
6826650175 | KN51093 | 02/25/2023 | 171.81 | 27.87 | 87 | 58
6826650175 | KN51093 | 02/26/2023 | 210.98 | 34 | 87 | 56 | 0
6826650175 | KN51093 | 02/27/2023 | 177.2 | 28.72 | 87 | 57 | 0
6826650175 | KN51093 | 02/28/2023 | 170.38 | 27.65 | 87 | 57 | 0
6826650175 | KN51093 | 03/01/2023 | 181.73 | 29.42 | 86 | 58 | 0
6826650175 | KN51093 | 03/02/2023 | 170.96 | 27.74 | 87 | 56 | 0
6826650175 | KN51093 | 03/03/2023 | 186.5 | 30.17 | 90 | 55 | 0
6826650175 | KN51093 | 03/04/2023 | 178.94 | 28.99 | 88 | 52 | 0
6826650175 | KN51093 | 03/05/2023 | 203.02 | 32.75 | 81 | 54 | 0.05
6826650175 | KN51093 | 03/06/2023 | 172.44 | 27.97 | 84 | 56 | 0
6826650175 | KN51093 | 03/07/2023 | 173.82 | 28.19 | 87 | 56
6826650175 | KN51093 | 03/08/2023 | 171.2 | 27.78 | 85 | 58 | 0
6826650175 | KN51093 | 03/09/2023 | 156.22 | 25.44 | 80 | 51 | 0
6826650175 | KN51093 | 03/10/2023 | 200.05 | 32.29 | 85 | 54
6826650175 | KN51093 | 03/11/2023 | 203.62 | 32.84 | 81 | 51 | 1.3
6826650175 | KN51093 | 03/12/2023 | 340.01 | 54.16 | 86 | 48 | 0
6826650175 | KN51093 | 03/13/2023 | 406.7 | 64.59 | 81 | 46 | 1.17
6826650175 | KN51093 | 03/14/2023 | 380.63 | 60.51 | 70 | 43 | 0.6
6826650175 | KN51093 | 03/15/2023 | 382.26 | 60.77 | 68 | 43 | 0
6826650175 | KN51093 | 03/16/2023 | 347.64 | 55.36 | 77 | 37 | 0
6826650175 | KN51093 | 03/17/2023 | 350.05 | 53.64 | 84 | 48
6826650175 | KN51093 | 03/18/2023 | 303.76 | 46.68 | 80 | 45 | 0
6826650175 | KN51093 | 03/19/2023 | 204.51 | 31.76 | 68 | 43 | 0.02
6826650175 | KN51093 | 03/20/2023 | 201.68 | 31.33 | 69 | 42 | 0.02
6826650175 | KN51093 | 03/21/2023 | 187.51 | 29.2 | 77 | 42 | 0
6826650175 | KN51093 | 03/22/2023 | 174.36 | 27.22 | 80 | 53 | 0.08
6826650175 | KN51093 | 03/23/2023 | 183.67 | 28.62 | 83 | 53
6826650175 | KN51093 | 03/24/2023 | 182.61 | 28.46 | 86 | 53 | 0
6826650175 | KN51093 | 03/25/2023 | 192.01 | 29.88 | 91 | 60 | 0
6826650175 | KN51093 | 03/26/2023 | 227.03 | 35.14 | 91 | 63 | 0.68
6826650175 | KN51093 | 03/27/2023 | 198.3 | 30.82 | 92 | 62 | 0
6826650175 | KN51093 | 03/28/2023 | 189.49 | 29.5 | 88 | 55 | Trace Value
6826650175 | KN51093 | 03/29/2023 | 185.45 | 28.89 | 75 | 55 | 0
6826650175 | KN51093 | 03/30/2023 | 181.76 | 28.34 | 79 | 51 | 0
6826650175 | KN51093 | 03/31/2023 | 186.43 | 29.04 | 85 | 55 | 0
6826650175 | KN51093 | 04/01/2023 | 198.95 | 30.92 | 90 | 60 | 0
6826650175 | KN51093 | 04/02/2023 | 199.49 | 31 | 85 | 60
6826650175 | KN51093 | 04/03/2023 | 183.79 | 28.64 | 86 | 61 | 0
6826650175 | KN51093 | 04/04/2023 | 187.2 | 29.15 | 88 | 60 | Trace Value
6826650175 | KN51093 | 04/05/2023 | 176.44 | 27.54 | 87 | 63 | 0
6826650175 | KN51093 | 04/06/2023 | 181.82 | 28.35 | 87 | 64 | 0
6826650175 | KN51093 | 04/07/2023 | 184.46 | 28.74 | 85 | 64
6826650175 | KN51093 | 04/08/2023 | 198.53 | 30.86 | 86 | 62
6826650175 | KN51093 | 04/09/2023 | 204.61 | 31.77 | 80 | 60 | 0.01
6826650175 | KN51093 | 04/10/2023 | 228.67 | 35.39 | 79 | 58 | 0.68
6826650175 | KN51093 | 04/11/2023 | 231.65 | 35.84 | 78 | 58 | 1.38
6826650175 | KN51093 | 04/12/2023 | 205.09 | 31.84 | 79 | 59 | 0.03
6826650175 | KN51093 | 04/13/2023 | 247.13 | 38.16 | 87 | 61 | 0.07
6826650175 | KN51093 | 04/14/2023 | 312.45 | 47.98 | 86 | 59 | 0.57
6826650175 | KN51093 | 04/15/2023 | 291.46 | 44.83 | 87 | 60 | 0.02
6826650175 | KN51093 | 04/16/2023 | 322.11 | 49.44 | 88 | 59 | 0
6826650175 | KN51093 | 04/17/2023 | 249.9 | 38.58 | 81 | 50 | 0.04
6826650175 | KN51093 | 04/18/2023 | 232.66 | 27.52 | 81 | 46 | 0.02
6826650175 | KN51093 | 04/19/2023 | 221.75 | 26.28 | 82 | 50 | 0
6826650175 | KN51093 | 04/20/2023 | 223.95 | 26.53 | 84 | 55 | 0
6826650175 | KN51093 | 04/21/2023 | 219.48 | 26.02 | 87 | 59
6826650175 | KN51093 | 04/22/2023 | 226.89 | 26.86 | 89 | 57 | 0.3
6826650175 | KN51093 | 04/23/2023 | 238.9 | 28.23 | 84 | 53 | 0.42
6826650175 | KN51093 | 04/24/2023 | 223.75 | 26.51 | 80 | 55 | 0
6826650175 | KN51093 | 04/25/2023 | 219.71 | 26.05 | 82 | 61 | 0.25
6826650175 | KN51093 | 04/26/2023 | 203.52 | 24.21 | 84 | 62 | 0.07
6826650175 | KN51093 | 04/27/2023 | 239.34 | 28.28 | 86 | 63 | 0
6826650175 | KN51093 | 04/28/2023 | 284.73 | 33.43 | 87 | 62 | 1.62
6826650175 | KN51093 | 04/29/2023 | 262.25 | 30.88 | 88 | 62 | 0
6826650175 | KN51093 | 04/30/2023 | 271.32 | 31.91 | 85 | 57 | 0.52
6826650175 | KN51093 | 05/01/2023 | 252.16 | 29.73 | 85 | 56 | 0
6826650175 | KN51093 | 05/02/2023 | 238.44 | 28.18 | 87 | 56 | 0
6826650175 | KN51093 | 05/03/2023 | 212.52 | 25.23 | 86 | 53 | 0
6826650175 | KN51093 | 05/04/2023 | 208.23 | 24.74 | 84 | 53 | 0
6826650175 | KN51093 | 05/05/2023 | 216.38 | 25.67 | 87 | 57 | 0
6826650175 | KN51093 | 05/06/2023 | 213.58 | 25.35 | 86 | 65 | 0
6826650175 | KN51093 | 05/07/2023 | 225.74 | 26.73 | 88 | 61 | 0.02
6826650175 | KN51093 | 05/08/2023 | 212.96 | 25.28 | 87 | 55 | 0
6826650175 | KN51093 | 05/09/2023 | 205.49 | 24.43 | 91 | 63 | 0
6826650175 | KN51093 | 05/10/2023 | 199.65 | 23.77 | 92 | 66 | 0
6826650175 | KN51093 | 05/11/2023 | 205.5 | 24.43 | 88 | 67 | 0.04
6826650175 | KN51093 | 05/12/2023 | 201.79 | 24.01 | 86 | 66 | 0
6826650175 | KN51093 | 05/13/2023 | 209.28 | 24.86 | 85 | 64 | 0
6826650175 | KN51093 | 05/14/2023 | 204.74 | 24.35 | 86 | 63 | 0
6826650175 | KN51093 | 05/15/2023 | 243.89 | 28.8 | 89 | 62 | 0
6826650175 | KN51093 | 05/16/2023 | 195.75 | 23.33 | 88 | 64 | 0
6826650175 | KN51093 | 05/17/2023 | 188.88 | 23.05 | 92 | 67 | 0
6826650175 | KN51093 | 05/18/2023 | 192.52 | 23.47 | 89 | 65 | 1.24
6826650175 | KN51093 | 05/19/2023 | 193.14 | 23.54 | 88 | 66 | 0.02
6826650175 | KN51093 | 05/20/2023 | 204.12 | 24.82 | 88 | 66 | 0
6826650175 | KN51093 | 05/21/2023 | 200.6 | 24.41 | 88 | 67
6826650175 | KN51093 | 05/22/2023 | 207.52 | 25.21 | 88 | 67 | 0.65
6826650175 | KN51093 | 05/23/2023 | 217.46 | 26.37 | 85 | 67 | 0.56
6826650175 | KN51093 | 05/24/2023 | 242.79 | 29.31 | 83 | 66 | 0.12
6826650175 | KN51093 | 05/25/2023 | 224.51 | 27.19 | 83 | 66 | 0.16
6826650175 | KN51093 | 05/26/2023 | 214.91 | 26.07 | 82 | 62 | 0.05
6826650175 | KN51093 | 05/27/2023 | 216.27 | 26.23 | 81 | 56 | Trace Value
6826650175 | KN51093 | 05/28/2023 | 210.76 | 25.59 | 85 | 55 | 0
6826650175 | KN51093 | 05/29/2023 | 214.45 | 26.02 | 87 | 60 | 0
6826650175 | KN51093 | 05/30/2023 | 205.12 | 24.93 | 88 | 62 | 0
6826650175 | KN51093 | 05/31/2023 | 194.82 | 23.74 | 87 | 68 | 0
6826650175 | KN51093 | 06/01/2023 | 208.83 | 25.36 | 85 | 68 | 0
6826650175 | KN51093 | 06/02/2023 | 207.85 | 25.25 | 85 | 67 | 0
6826650175 | KN51093 | 06/03/2023 | 214.41 | 26.01 | 84 | 67 | 0
6826650175 | KN51093 | 06/04/2023 | 217.01 | 26.32 | 84 | 66 | 0
6826650175 | KN51093 | 06/05/2023 | 222.66 | 26.97 | 84 | 64 | 0.3
6826650175 | KN51093 | 06/06/2023 | 212.92 | 25.84 | 88 | 62
6826650175 | KN51093 | 06/07/2023 | 231.5 | 28 | 91 | 68 | 0
6826650175 | KN51093 | 06/08/2023 | 257.36 | 31.01 | 92 | 68 | 1.64
6826650175 | KN51093 | 06/09/2023 | 256.15 | 30.87 | 92 | 68 | 0
6826650175 | KN51093 | 06/10/2023 | 271.42 | 32.64 | 88 | 67 | 0.54
6826650175 | KN51093 | 06/11/2023 | 267.34 | 32.17 | 91 | 69 | 0.09
6826650175 | KN51093 | 06/12/2023 | 280 | 33.64 | 94 | 69 | 0
6826650175 | KN51093 | 06/13/2023 | 260.36 | 31.35 | 95 | 71
6826650175 | KN51093 | 06/14/2023 | 293.69 | 35.23 | 95 | 71 | 0
6826650175 | KN51093 | 06/15/2023 | 253.66 | 30.58 | 95 | 66 | 0.44
6826650175 | KN51093 | 06/16/2023 | 282.37 | 46.95 | 95 | 68 | 0.45
6826650175 | KN51093 | 06/17/2023 | 311.29 | 51.65 | 93 | 68 | 0.91
6826650175 | KN51093 | 06/18/2023 | 334.07 | 55.36 | 94 | 68 | 0.28
6826650175 | KN51093 | 06/19/2023 | 339.34 | 56.22 | 93 | 70 | 0.63
6826650175 | KN51093 | 06/20/2023 | 386.49 | 63.89 | 91 | 69 | 0.46
6826650175 | KN51093 | 06/21/2023 | 342.76 | 56.77 | 91 | 71 | 0.24
6826650175 | KN51093 | 06/22/2023 | 335.37 | 55.57 | 93 | 66 | 0.04
6826650175 | KN51093 | 06/23/2023 | 286.82 | 47.67 | 91 | 69 | 0.35
6826650175 | KN51093 | 06/24/2023 | 212.91 | 35.64 | 92 | 70 | 0.24
6826650175 | KN51093 | 06/25/2023 | 200.59 | 33.64 | 91 | 70 | 0.15
6826650175 | KN51093 | 06/26/2023 | 180.13 | 30.31 | 94 | 70 | 0
6826650175 | KN51093 | 06/27/2023 | 173.21 | 29.18 | 97 | 71 | 0
6826650175 | KN51093 | 06/28/2023 | 170.2 | 28.69 | 95 | 72 | 0
6826650175 | KN51093 | 06/29/2023 | 168.28 | 28.38 | 95 | 71 | 0.88
6826650175 | KN51093 | 06/30/2023 | 164.53 | 27.77 | 94 | 71 | 0
6826650175 | KN51093 | 07/01/2023 | 167.38 | 28.23 | 94 | 71 | 0
6826650175 | KN51093 | 07/02/2023 | 163.76 | 27.65 | 95 | 71 | 0
6826650175 | KN51093 | 07/03/2023 | 160.77 | 27.16 | 97 | 72 | 0
6826650175 | KN51093 | 07/04/2023 | 163.08 | 27.54 | 95 | 73 | 0
6826650175 | KN51093 | 07/05/2023 | 155.41 | 26.29 | 95 | 74 | 0
6826650175 | KN51093 | 07/06/2023 | 159.75 | 26.99 | 96 | 73 | 0.04
6826650175 | KN51093 | 07/07/2023 | 161.06 | 27.21 | 95 | 73 | 0.03
6826650175 | KN51093 | 07/08/2023 | 164.91 | 27.83 | 94 | 74 | 0.31
6826650175 | KN51093 | 07/09/2023 | 159.04 | 26.88 | 96 | 74 | 0.2
6826650175 | KN51093 | 07/10/2023 | 132.95 | 22.63 | 96 | 74 | 0
6826650175 | KN51093 | 07/11/2023 | 155.28 | 26.27 | 94 | 73 | 0.78
6826650175 | KN51093 | 07/12/2023 | 151.18 | 25.6 | 94 | 73 | 0.1
6826650175 | KN51093 | 07/13/2023 | 153.92 | 26.05 | 94 | 72 | Trace Value
6826650175 | KN51093 | 07/14/2023 | 164.76 | 27.81 | 95 | 73 | 0.33
6826650175 | KN51093 | 07/15/2023 | 179.94 | 30.28 | 96 | 73 | 0.12
6826650175 | KN51093 | 07/16/2023 | 215.74 | 36.1 | 96 | 74 | 0.15
6826650175 | KN51093 | 07/17/2023 | 172.7 | 29.1 | 95 | 74 | 2.8
6826650175 | KN51093 | 07/18/2023 | 180.2 | 20.05 | 95 | 72 | 0.22
6826650175 | KN51093 | 07/19/2023 | 174.09 | 19.4 | 95 | 71 | 0.14
6826650175 | KN51093 | 07/20/2023 | 177.85 | 19.8 | 96 | 73 | 0
6826650175 | KN51093 | 07/21/2023 | 171.95 | 19.18 | 99 | 74 | 0
6826650175 | KN51093 | 07/22/2023 | 181.43 | 20.18 | 97 | 75 | 0
6826650175 | KN51093 | 07/23/2023 | 213.47 | 23.55 | 94 | 71 | 0.7
6826650175 | KN51093 | 07/24/2023 | 187.06 | 20.77 | 93 | 73 | 1.12
6826650175 | KN51093 | 07/25/2023 | 180.53 | 20.08 | 93 | 73 | 0.3
6826650175 | KN51093 | 07/26/2023 | 163.96 | 18.34 | 92 | 73 | 0
6826650175 | KN51093 | 07/27/2023 | 171.73 | 19.16 | 91 | 73 | 0
6826650175 | KN51093 | 07/28/2023 | 177.43 | 19.75 | 92 | 73 | 1
6826650175 | KN51093 | 07/29/2023 | 187.91 | 20.86 | 93 | 73 | 0.05
6826650175 | KN51093 | 07/30/2023 | 208.56 | 23.03 | 95 | 74 | Trace Value
6826650175 | KN51093 | 07/31/2023 | 235.48 | 25.86 | 95 | 71 | 0.74
6826650175 | KN51093 | 08/01/2023 | 213.55 | 23.56 | 95 | 71 | 0.08
6826650175 | KN51093 | 08/02/2023 | 190.38 | 21.12 | 93 | 74 | 0
6826650175 | KN51093 | 08/03/2023 | 186.04 | 20.66 | 91 | 73 | 0
6826650175 | KN51093 | 08/04/2023 | 177.28 | 19.74 | 94 | 73 | 0
6826650175 | KN51093 | 08/05/2023 | 189.03 | 20.97 | 94 | 73 | 0.17
6826650175 | KN51093 | 08/06/2023 | 206.09 | 22.77 | 95 | 74 | 0.66
6826650175 | KN51093 | 08/07/2023 | 197.71 | 21.89 | 97 | 75 | 0.03
6826650175 | KN51093 | 08/08/2023 | 189.64 | 21.04 | 99 | 75 | 0
6826650175 | KN51093 | 08/09/2023 | 179.06 | 19.93 | 99 | 74 | 0
6826650175 | KN51093 | 08/10/2023 | 181.1 | 20.14 | 100 | 75 | 0.16
6826650175 | KN51093 | 08/11/2023 | 169.46 | 18.92 | 99 | 75 | 0
6826650175 | KN51093 | 08/12/2023 | 171.65 | 19.15 | 98 | 76 | 0.25
6826650175 | KN51093 | 08/13/2023 | 167.03 | 18.66 | 97 | 74 | 0
6826650175 | KN51093 | 08/14/2023 | 161.83 | 18.11 | 97 | 76 | 0
6826650175 | KN51093 | 08/15/2023 | 188.05 | 20.87 | 97 | 75 | 0
6826650175 | KN51093 | 08/16/2023 | 159.82 | 17.9 | 96 | 73 | 0.09
6826650175 | KN51093 | 08/17/2023 | 165.7 | 27.56 | 93 | 72 | 0.36
6826650175 | KN51093 | 08/18/2023 | 179.6 | 29.78 | 93 | 73 | 1.09
6826650175 | KN51093 | 08/19/2023 | 183.11 | 30.34 | 93 | 72 | 0.69
6826650175 | KN51093 | 08/20/2023 | 185.8 | 30.77 | 92 | 75 | 0
6826650175 | KN51093 | 08/21/2023 | 171.11 | 28.42 | 92 | 74 | 0
6826650175 | KN51093 | 08/22/2023 | 165.51 | 27.53 | 93 | 72 | 0
6826650175 | KN51093 | 08/23/2023 | 156.68 | 26.11 | 93 | 74 | 0
6826650175 | KN51093 | 08/24/2023 | 153.92 | 25.67 | 93 | 74 | 0.99
6826650175 | KN51093 | 08/25/2023 | 149.65 | 24.99 | 92 | 71 | 0
6826650175 | KN51093 | 08/26/2023 | 156.32 | 26.06 | 95 | 73 | 0
6826650175 | KN51093 | 08/27/2023 | 159.66 | 26.59 | 95 | 72
6826650175 | KN51093 | 08/28/2023 | 152.89 | 25.51 | 96 | 74 | Trace Value
6826650175 | KN51093 | 08/29/2023 | 150.15 | 25.07 | 95 | 74 | 0
6826650175 | KN51093 | 08/30/2023 | 165.46 | 27.52 | 94 | 74 | 0.93
6826650175 | KN51093 | 08/31/2023 | 162.38 | 27.03 | 94 | 74 | 0.05
6826650175 | KN51093 | 09/01/2023 | 164.45 | 27.36 | 92 | 73 | 0
6826650175 | KN51093 | 09/02/2023 | 157.16 | 26.19 | 91 | 72
6826650175 | KN51093 | 09/03/2023 | 155.19 | 25.88 | 92 | 71 | 0.05
6826650175 | KN51093 | 09/04/2023 | 156.87 | 26.15 | 90 | 68 | 0
6826650175 | KN51093 | 09/05/2023 | 149.11 | 24.9 | 90 | 64 | 0
6826650175 | KN51093 | 09/06/2023 | 140.12 | 23.47 | 94 | 69 | 0
6826650175 | KN51093 | 09/07/2023 | 142.25 | 23.81 | 95 | 70
6826650175 | KN51093 | 09/08/2023 | 221.68 | 36.5 | 95 | 69 | 0
6826650175 | KN51093 | 09/09/2023 | 201.91 | 33.34 | 94 | 64 | 0.48
6826650175 | KN51093 | 09/10/2023 | 196.71 | 32.51 | 93 | 71 | Trace Value
6826650175 | KN51093 | 09/11/2023 | 186.85 | 30.94 | 92 | 72 | 0
6826650175 | KN51093 | 09/12/2023 | 205.4 | 33.9 | 92 | 71 | Trace Value
6826650175 | KN51093 | 09/13/2023 | 275.35 | 45.08 | 92 | 72 | 0.03
6826650175 | KN51093 | 09/14/2023 | 271.87 | 44.53 | 91 | 71 | 0.29
6826650175 | KN51093 | 09/15/2023 | 206.07 | 34.01 | 88 | 70 | 0
6826650175 | KN51093 | 09/16/2023 | 199.88 | 25.29 | 87 | 69 | 0.54
6826650175 | KN51093 | 09/17/2023 | 195.39 | 24.75 | 92 | 70 | 0
6826650175 | KN51093 | 09/18/2023 | 172.34 | 21.95 | 89 | 68 | 0.08
6826650175 | KN51093 | 09/19/2023 | 173.39 | 22.08 | 88 | 64 | 0
6826650175 | KN51093 | 09/20/2023 | 164.32 | 20.97 | 88 | 69 | 0
6826650175 | KN51093 | 09/21/2023 | 165.19 | 21.08 | 87 | 68 | 0.08
6826650175 | KN51093 | 09/22/2023 | 165.53 | 21.12 | 85 | 65 | 0.3
6826650175 | KN51093 | 09/23/2023 | 165.33 | 21.1 | 87 | 61 | 0
6826650175 | KN51093 | 09/24/2023 | 166.43 | 21.23 | 89 | 59 | 0
6826650175 | KN51093 | 09/25/2023 | 196.58 | 24.89 | 90 | 66 | 0
6826650175 | KN51093 | 09/26/2023 | 341.67 | 42.51 | 89 | 71 | 2.11
6826650175 | KN51093 | 09/27/2023 | 336.7 | 41.91 | 88 | 71 | 0.91
6826650175 | KN51093 | 09/28/2023 | 348.26 | 43.31 | 87 | 71 | 0.81
6826650175 | KN51093 | 09/29/2023 | 319.67 | 39.84 | 85 | 71 | 0.02
6826650175 | KN51093 | 09/30/2023 | 497.92 | 61.49 | 85 | 71 | 0.2
6826650175 | KN51093 | 10/01/2023 | 658.67 | 81.01 | 85 | 70 | 2.53
6826650175 | KN51093 | 10/02/2023 | 397.64 | 49.31 | 85 | 69 | 0.56
6826650175 | KN51093 | 10/03/2023 | 289.67 | 36.2 | 85 | 70 | 0
6826650175 | KN51093 | 10/04/2023 | 253.04 | 31.75 | 86 | 70 | 0.05
6826650175 | KN51093 | 10/05/2023 | 242.89 | 30.52 | 86 | 69 | 0
6826650175 | KN51093 | 10/06/2023 | 230.54 | 29.02 | 87 | 66 | 0
6826650175 | KN51093 | 10/07/2023 | 222.86 | 28.08 | 90 | 56 | 0
6826650175 | KN51093 | 10/08/2023 | 213.9 | 27 | 82 | 53 | 0
6826650175 | KN51093 | 10/09/2023 | 195.81 | 24.8 | 80 | 55 | 0
6826650175 | KN51093 | 10/10/2023 | 198.71 | 25.15 | 84 | 56 | 0
6826650175 | KN51093 | 10/11/2023 | 193.15 | 24.48 | 84 | 65 | 0
6826650175 | KN51093 | 10/12/2023 | 748.19 | 91.88 | 88 | 72 | 2.8
6826650175 | KN51093 | 10/13/2023 | 452.75 | 56 | 89 | 68 | 1.67
6826650175 | KN51093 | 10/14/2023 | 302.08 | 37.7 | 89 | 64 | 0
6826650175 | KN51093 | 10/15/2023 | 275.33 | 34.46 | 82 | 55 | 0
6826650175 | KN51093 | 10/16/2023 | 300.65 | 37.53 | 76 | 50 | 0
6826650175 | KN51093 | 10/17/2023 | 223.27 | 28.13 | 75 | 49 | 0
6826650175 | KN51093 | 10/18/2023 | 221.62 | 25.77 | 77 | 50 | 0
6826650175 | KN51093 | 10/19/2023 | 214.29 | 24.95 | 81 | 55 | 0
6826650175 | KN51093 | 10/20/2023 | 198.13 | 23.15 | 83 | 55 | 0
6826650175 | KN51093 | 10/21/2023 | 208.43 | 24.3 | 83 | 55 | 0
6826650175 | KN51093 | 10/22/2023 | 204.7 | 23.88 | 86 | 52 | 0
6826650175 | KN51093 | 10/23/2023 | 194.89 | 22.79 | 83 | 58 | 0
6826650175 | KN51093 | 10/24/2023 | 186.06 | 21.81 | 82 | 67 | 0
6826650175 | KN51093 | 10/25/2023 | 179.09 | 21.03 | 82 | 68 | 0
6826650175 | KN51093 | 10/26/2023 | 176.24 | 20.72 | 82 | 65 | 0
6826650175 | KN51093 | 10/27/2023 | 171.92 | 20.23 | 83 | 64 | 0
6826650175 | KN51093 | 10/28/2023 | 178.19 | 20.93 | 84 | 62 | 0
6826650175 | KN51093 | 10/29/2023 | 177.28 | 20.83 | 84 | 61 | 0
6826650175 | KN51093 | 10/30/2023 | 172.71 | 20.32 | 85 | 60 | 0
6826650175 | KN51093 | 10/31/2023 | 166.27 | 19.61 | 84 | 58 | 0
6826650175 | KN51093 | 11/01/2023 | 157.44 | 18.62 | 76 | 53 | 0
6826650175 | KN51093 | 11/02/2023 | 157.49 | 18.63 | 75 | 53 | 0
6826650175 | KN51093 | 11/03/2023 | 155.74 | 18.43 | 79 | 59 | 0
6826650175 | KN51093 | 11/04/2023 | 161.73 | 19.1 | 79 | 55 | 0
6826650175 | KN51093 | 11/05/2023 | 173.51 | 20.41 | 80 | 51 | 0
6826650175 | KN51093 | 11/06/2023 | 156.4 | 18.51 | 81 | 48 | 0
6826650175 | KN51093 | 11/07/2023 | 150.92 | 17.9 | 83 | 53 | 0
6826650175 | KN51093 | 11/08/2023 | 151.59 | 17.97 | 84 | 50 | 0
6826650175 | KN51093 | 11/09/2023 | 153.29 | 18.16 | 85 | 55 | 0
6826650175 | KN51093 | 11/10/2023 | 150.28 | 17.82 | 86 | 60 | 0
6826650175 | KN51093 | 11/11/2023 | 160.83 | 19 | 83 | 65 | 0.33
6826650175 | KN51093 | 11/12/2023 | 166.13 | 19.59 | 80 | 63 | 0
6826650175 | KN51093 | 11/13/2023 | 158.61 | 18.75 | 77 | 62 | 0
6826650175 | KN51093 | 11/14/2023 | 189.99 | 22.25 | 77 | 61 | 0.12
6826650175 | KN51093 | 11/15/2023 | 149.79 | 17.77 | 77 | 64 | 0.05
6826650175 | KN51093 | 11/16/2023 | 187.75 | 29.87 | 78 | 62 | 0.16
6826650175 | KN51093 | 11/17/2023 | 386.93 | 60.42 | 79 | 61 | 2.1
6826650175 | KN51093 | 11/18/2023 | 260.99 | 41.1 | 78 | 55 | 0.66
6826650175 | KN51093 | 11/19/2023 | 227.95 | 36.04 | 80 | 56 | 0
6826650175 | KN51093 | 11/20/2023 | 209.06 | 33.14 | 79 | 59 | 0.02
6826650175 | KN51093 | 11/21/2023 | 200.75 | 31.86 | 81 | 52 | 0.02
6826650175 | KN51093 | 11/22/2023 | 196.69 | 31.24 | 81 | 47 | 0
6826650175 | KN51093 | 11/23/2023 | 206.1 | 32.68 | 73 | 48 | 0.01
6826650175 | KN51093 | 11/24/2023 | 186.42 | 29.66 | 75 | 52 | 0.01
6826650175 | KN51093 | 11/25/2023 | 186.08 | 29.61 | 75 | 53 | 0.07
6826650175 | KN51093 | 11/26/2023 | 210.9 | 33.42 | 75 | 55 | 0.01
6826650175 | KN51093 | 11/27/2023 | 202.05 | 32.06 | 74 | 44 | 0.55
6826650175 | KN51093 | 11/28/2023 | 184.3 | 29.34 | 69 | 39 | 0
6826650175 | KN51093 | 11/29/2023 | 170.53 | 27.23 | 68 | 36 | 0
6826650175 | KN51093 | 11/30/2023 | 174.24 | 27.8 | 86 | 41 | 0
6826650175 | KN51093 | 12/01/2023 | 171.47 | 27.37 | 82 | 55 | 0
6826650175 | KN51093 | 12/02/2023 | 181.21 | 28.87 | 83 | 64 | 0
6826650175 | KN51093 | 12/03/2023 | 199.11 | 31.61 | 82 | 62 | 0.02
6826650175 | KN51093 | 12/04/2023 | 190.46 | 30.29 | 79 | 51 | 0.23
6826650175 | KN51093 | 12/05/2023 | 179.26 | 28.57 | 72 | 47 | 0
6826650175 | KN51093 | 12/06/2023 | 166.64 | 26.63 | 69 | 41 | 0
6826650175 | KN51093 | 12/07/2023 | 166.26 | 26.57 | 67 | 41 | 0
6826650175 | KN51093 | 12/08/2023 | 165.66 | 26.48 | 74 | 47 | 0
6826650175 | KN51093 | 12/09/2023 | 170.04 | 27.15 | 82 | 56 | 0.04
6826650175 | KN51093 | 12/10/2023 | 181.35 | 28.89 | 83 | 44 | 0
6826650175 | KN51093 | 12/11/2023 | 173.29 | 27.65 | 67 | 43 | 0.25
6826650175 | KN51093 | 12/12/2023 | 163.96 | 26.22 | 71 | 43 | 0
6826650175 | KN51093 | 12/13/2023 | 198.79 | 31.56 | 73 | 58 | 0
6826650175 | KN51093 | 12/14/2023 | 187.45 | 29.82 | 72 | 59 | 0.66
6826650175 | KN51093 | 12/15/2023 | 176.21 | 25.52 | 72 | 60 | 0.07
6826650175 | KN51093 | 12/16/2023 | 212.76 | 30.62 | 73 | 58 | 0.11
6826650175 | KN51093 | 12/17/2023 | 762.33 | 107.25 | 74 | 48 | 4.04
6826650175 | KN51093 | 12/18/2023 | 285.59 | 40.77 | 68 | 40 | 0.05
6826650175 | KN51093 | 12/19/2023 | 249.75 | 35.78 | 65 | 41 | 0
6826650175 | KN51093 | 12/20/2023 | 226.13 | 32.48 | 66 | 44 | 0
6826650175 | KN51093 | 12/21/2023 | 229.28 | 32.92 | 68 | 46 | 0
6826650175 | KN51093 | 12/22/2023 | 217.45 | 31.27 | 70 | 49 | 0
6826650175 | KN51093 | 12/23/2023 | 225.08 | 32.34 | 73 | 53 | 0
6826650175 | KN51093 | 12/24/2023 | 219.8 | 31.6 | 73 | 53 | 0
6826650175 | KN51093 | 12/25/2023 | 216.95 | 31.2 | 73 | 60 | 0.09
6826650175 | KN51093 | 12/26/2023 | 211.26 | 30.41 | 74 | 54 | 0.1
6826650175 | KN51093 | 12/27/2023 | 193.26 | 27.9 | 71 | 49 | 0
6826650175 | KN51093 | 12/28/2023 | 200.98 | 28.97 | 66 | 44 | 0.04
6826650175 | KN51093 | 12/29/2023 | 194.89 | 28.13 | 55 | 46 | 0
6826650175 | KN51093 | 12/30/2023 | 193.67 | 27.96 | 59 | 37 | 0
6826650175 | KN51093 | 12/31/2023 | 194.89 | 28.13 | 63 | 36 | 0
|  | Yearly Daily Average: | 209.9965 | 28.9693
|  | Wetter Months' Daily Average: | 219.494 | 30.2848

## 20-2
Daily Billed Information (PS 20-2 - 92 Wellington Drive: 2023 Reading Data)
Bill Account | Meter Number | Date | Consumption Recorded (kWh/day) | Estimated Cost ($/day) | Avg. High Temperature (°F) | Avg. Low Temperature (°F) | Rain Recorded by NOAA (inches)
9996767175 | KJ17787 | 01/01/2023 | 39.17 | 5.09 | 79 | 58 | 0.04
9996767175 | KJ17787 | 01/02/2023 | 40.81 | 5.29 | 78 | 53 | 0
9996767175 | KJ17787 | 01/03/2023 | 38.13 | 4.97 | 81 | 51 | 0
9996767175 | KJ17787 | 01/04/2023 | 36.54 | 4.78 | 83 | 57 | 0
9996767175 | KJ17787 | 01/05/2023 | 36.66 | 4.79 | 77 | 46 | 0.04
9996767175 | KJ17787 | 01/06/2023 | 35.74 | 4.68 | 68 | 41 | 0
9996767175 | KJ17787 | 01/07/2023 | 38.1 | 4.96 | 70 | 38 | 0
9996767175 | KJ17787 | 01/08/2023 | 38.21 | 4.98 | 76 | 42 | 0
9996767175 | KJ17787 | 01/09/2023 | 36.02 | 4.71 | 74 | 47 | 0
9996767175 | KJ17787 | 01/10/2023 | 34.16 | 4.49 | 71 | 42 | 0
9996767175 | KJ17787 | 01/11/2023 | 33.68 | 4.43 | 73 | 38 | 0
9996767175 | KJ17787 | 01/12/2023 | 33.43 | 4.4 | 80 | 44 | 0
9996767175 | KJ17787 | 01/13/2023 | 33.12 | 4.37 | 71 | 35 | 0.12
9996767175 | KJ17787 | 01/14/2023 | 35.25 | 4.62 | 61 | 30 | 0
9996767175 | KJ17787 | 01/15/2023 | 37.08 | 4.84 | 63 | 30 | 0
9996767175 | KJ17787 | 01/16/2023 | 41.74 | 5.4 | 71 | 30 | 0
9996767175 | KJ17787 | 01/17/2023 | 35.33 | 4.63 | 75 | 34 | 0
9996767175 | KJ17787 | 01/18/2023 | 32.69 | 4.51 | 79 | 46 | N/A
9996767175 | KJ17787 | 01/19/2023 | 34.83 | 4.78 | 82 | 54 | 0
9996767175 | KJ17787 | 01/20/2023 | 32.94 | 4.54 | 76 | 49 | 0
9996767175 | KJ17787 | 01/21/2023 | 37.21 | 5.07 | 76 | 47 | T
9996767175 | KJ17787 | 01/22/2023 | 46 | 6.17 | 82 | 54 | 0.33
9996767175 | KJ17787 | 01/23/2023 | 39.91 | 5.41 | 75 | 44 | 0.05
9996767175 | KJ17787 | 01/24/2023 | 38.98 | 5.29 | 76 | 41 | 0
9996767175 | KJ17787 | 01/25/2023 | 40.34 | 5.46 | 85 | 43 | 0
9996767175 | KJ17787 | 01/26/2023 | 39.27 | 5.33 | 72 | 38 | 0.09
9996767175 | KJ17787 | 01/27/2023 | 37.22 | 5.07 | 62 | 37 | 0
9996767175 | KJ17787 | 01/28/2023 | 38.05 | 5.18 | 69 | 35 | 0
9996767175 | KJ17787 | 01/29/2023 | 38.78 | 5.27 | 78 | 55 | 0
9996767175 | KJ17787 | 01/30/2023 | 38.04 | 5.18 | 86 | 58 | 0
9996767175 | KJ17787 | 01/31/2023 | 37.39 | 5.09 | 83 | 59 | 0
9996767175 | KJ17787 | 02/01/2023 | 33.79 | 4.65 | 82 | 58 | 0
9996767175 | KJ17787 | 02/02/2023 | 35.61 | 4.87 | 82 | 57 | 0
9996767175 | KJ17787 | 02/03/2023 | 37.71 | 5.13 | 78 | 50 | 0
9996767175 | KJ17787 | 02/04/2023 | 38.03 | 5.17 | 70 | 47 | 0.17
9996767175 | KJ17787 | 02/05/2023 | 42.26 | 5.7 | 73 | 48 | 0
9996767175 | KJ17787 | 02/06/2023 | 39.2 | 5.32 | 71 | 46 | 0.01
9996767175 | KJ17787 | 02/07/2023 | 37.1 | 5.06 | 76 | 44
9996767175 | KJ17787 | 02/08/2023 | 36.41 | 4.97 | 79 | 49 | 0
9996767175 | KJ17787 | 02/09/2023 | 34.86 | 4.78 | 83 | 58 | 0
9996767175 | KJ17787 | 02/10/2023 | 36.05 | 4.93 | 85 | 46 | 0.16
9996767175 | KJ17787 | 02/11/2023 | 37.73 | 5.14 | 79 | 40 | 0.57
9996767175 | KJ17787 | 02/12/2023 | 42.97 | 5.79 | 71 | 40 | 0.12
9996767175 | KJ17787 | 02/13/2023 | 38.19 | 5.19 | 71 | 40 | Trace Value
9996767175 | KJ17787 | 02/14/2023 | 45.65 | 6.13 | 75 | 39 | 0
9996767175 | KJ17787 | 02/15/2023 | 35.71 | 4.88 | 82 | 50 | 0
9996767175 | KJ17787 | 02/16/2023 | 36.55 | 4.99 | 85 | 57 | 0
9996767175 | KJ17787 | 02/17/2023 | 34.89 | 4.78 | 89 | 45
9996767175 | KJ17787 | 02/18/2023 | 35.46 | 4.85 | 67 | 46 | 0.04
9996767175 | KJ17787 | 02/19/2023 | 38.42 | 5.22 | 80 | 48 | 0
9996767175 | KJ17787 | 02/20/2023 | 36.32 | 4.96 | 82 | 53 | 0
9996767175 | KJ17787 | 02/21/2023 | 35.69 | 4.88 | 85 | 57 | 0
9996767175 | KJ17787 | 02/22/2023 | 34.3 | 4.71 | 87 | 58 | 0
9996767175 | KJ17787 | 02/23/2023 | 35.27 | 4.83 | 89 | 60 | 0
9996767175 | KJ17787 | 02/24/2023 | 34.05 | 4.68 | 87 | 58 | 0
9996767175 | KJ17787 | 02/25/2023 | 35.8 | 4.9 | 87 | 58
9996767175 | KJ17787 | 02/26/2023 | 39.11 | 5.31 | 87 | 56 | 0
9996767175 | KJ17787 | 02/27/2023 | 35.74 | 4.89 | 87 | 57 | 0
9996767175 | KJ17787 | 02/28/2023 | 32.14 | 4.44 | 87 | 57 | 0
9996767175 | KJ17787 | 03/01/2023 | 30.28 | 4.21 | 86 | 58 | 0
9996767175 | KJ17787 | 03/02/2023 | 30.4 | 4.22 | 87 | 56 | 0
9996767175 | KJ17787 | 03/03/2023 | 32.2 | 4.45 | 90 | 55 | 0
9996767175 | KJ17787 | 03/04/2023 | 33.43 | 4.6 | 88 | 52 | 0
9996767175 | KJ17787 | 03/05/2023 | 34.73 | 4.76 | 81 | 54 | 0.05
9996767175 | KJ17787 | 03/06/2023 | 32.19 | 4.45 | 84 | 56 | 0
9996767175 | KJ17787 | 03/07/2023 | 33.43 | 4.6 | 87 | 56
9996767175 | KJ17787 | 03/08/2023 | 30.73 | 4.26 | 85 | 58 | 0
9996767175 | KJ17787 | 03/09/2023 | 29.62 | 4.13 | 80 | 51 | 0
9996767175 | KJ17787 | 03/10/2023 | 31.8 | 4.4 | 85 | 54
9996767175 | KJ17787 | 03/11/2023 | 34.68 | 4.76 | 81 | 51 | 1.3
9996767175 | KJ17787 | 03/12/2023 | 32.62 | 4.5 | 86 | 48 | 0
9996767175 | KJ17787 | 03/13/2023 | 43.57 | 5.87 | 81 | 46 | 1.17
9996767175 | KJ17787 | 03/14/2023 | 40.15 | 5.44 | 70 | 43 | 0.6
9996767175 | KJ17787 | 03/15/2023 | 45.12 | 6.06 | 68 | 43 | 0
9996767175 | KJ17787 | 03/16/2023 | 36.34 | 4.96 | 77 | 37 | 0
9996767175 | KJ17787 | 03/17/2023 | 34.93 | 5.23 | 84 | 48
9996767175 | KJ17787 | 03/18/2023 | 35.75 | 5.34 | 80 | 45 | 0
9996767175 | KJ17787 | 03/19/2023 | 36.02 | 5.38 | 68 | 43 | 0.02
9996767175 | KJ17787 | 03/20/2023 | 35.79 | 5.35 | 69 | 42 | 0.02
9996767175 | KJ17787 | 03/21/2023 | 33.97 | 5.1 | 77 | 42 | 0
9996767175 | KJ17787 | 03/22/2023 | 33.05 | 4.97 | 80 | 53 | 0.08
9996767175 | KJ17787 | 03/23/2023 | 32.23 | 4.86 | 83 | 53
9996767175 | KJ17787 | 03/24/2023 | 31.69 | 4.79 | 86 | 53 | 0
9996767175 | KJ17787 | 03/25/2023 | 33.4 | 5.02 | 91 | 60 | 0
9996767175 | KJ17787 | 03/26/2023 | 34.66 | 5.19 | 91 | 63 | 0.68
9996767175 | KJ17787 | 03/27/2023 | 32.99 | 4.97 | 92 | 62 | 0
9996767175 | KJ17787 | 03/28/2023 | 29.68 | 4.51 | 88 | 55 | Trace Value
9996767175 | KJ17787 | 03/29/2023 | 31.18 | 4.72 | 75 | 55 | 0
9996767175 | KJ17787 | 03/30/2023 | 32.94 | 4.96 | 79 | 51 | 0
9996767175 | KJ17787 | 03/31/2023 | 30.21 | 4.58 | 85 | 55 | 0
9996767175 | KJ17787 | 04/01/2023 | 32.92 | 4.96 | 90 | 60 | 0
9996767175 | KJ17787 | 04/02/2023 | 33.34 | 5.01 | 85 | 60
9996767175 | KJ17787 | 04/03/2023 | 31.11 | 4.71 | 86 | 61 | 0
9996767175 | KJ17787 | 04/04/2023 | 30.48 | 4.62 | 88 | 60 | Trace Value
9996767175 | KJ17787 | 04/05/2023 | 30.03 | 4.56 | 87 | 63 | 0
9996767175 | KJ17787 | 04/06/2023 | 31.9 | 4.82 | 87 | 64 | 0
9996767175 | KJ17787 | 04/07/2023 | 30.41 | 4.61 | 85 | 64
9996767175 | KJ17787 | 04/08/2023 | 32.91 | 4.96 | 86 | 62
9996767175 | KJ17787 | 04/09/2023 | 32.78 | 4.94 | 80 | 60 | 0.01
9996767175 | KJ17787 | 04/10/2023 | 39.03 | 5.79 | 79 | 58 | 0.68
9996767175 | KJ17787 | 04/11/2023 | 42.44 | 6.26 | 78 | 58 | 1.38
9996767175 | KJ17787 | 04/12/2023 | 39.01 | 5.79 | 79 | 59 | 0.03
9996767175 | KJ17787 | 04/13/2023 | 53.59 | 7.79 | 87 | 61 | 0.07
9996767175 | KJ17787 | 04/14/2023 | 68.4 | 9.81 | 86 | 59 | 0.57
9996767175 | KJ17787 | 04/15/2023 | 66.5 | 9.55 | 87 | 60 | 0.02
9996767175 | KJ17787 | 04/16/2023 | 71.76 | 10.27 | 88 | 59 | 0
9996767175 | KJ17787 | 04/17/2023 | 52.64 | 7.66 | 81 | 50 | 0.04
9996767175 | KJ17787 | 04/18/2023 | 48.84 | 6.97 | 81 | 46 | 0.02
9996767175 | KJ17787 | 04/19/2023 | 49.46 | 7.05 | 82 | 50 | 0
9996767175 | KJ17787 | 04/20/2023 | 46.41 | 6.65 | 84 | 55 | 0
9996767175 | KJ17787 | 04/21/2023 | 44.97 | 6.46 | 87 | 59
9996767175 | KJ17787 | 04/22/2023 | 45.48 | 6.52 | 89 | 57 | 0.3
9996767175 | KJ17787 | 04/23/2023 | 51.12 | 7.27 | 84 | 53 | 0.42
9996767175 | KJ17787 | 04/24/2023 | 44.95 | 6.45 | 80 | 55 | 0
9996767175 | KJ17787 | 04/25/2023 | 45.61 | 6.54 | 82 | 61 | 0.25
9996767175 | KJ17787 | 04/26/2023 | 36.79 | 5.37 | 84 | 62 | 0.07
9996767175 | KJ17787 | 04/27/2023 | 49.85 | 7.1 | 86 | 63 | 0
9996767175 | KJ17787 | 04/28/2023 | 64.13 | 9 | 87 | 62 | 1.62
9996767175 | KJ17787 | 04/29/2023 | 56.27 | 7.96 | 88 | 62 | 0
9996767175 | KJ17787 | 04/30/2023 | 60.39 | 8.5 | 85 | 57 | 0.52
9996767175 | KJ17787 | 05/01/2023 | 50.92 | 7.25 | 85 | 56 | 0
9996767175 | KJ17787 | 05/02/2023 | 49.29 | 7.03 | 87 | 56 | 0
9996767175 | KJ17787 | 05/03/2023 | 43.5 | 6.26 | 86 | 53 | 0
9996767175 | KJ17787 | 05/04/2023 | 42.75 | 6.16 | 84 | 53 | 0
9996767175 | KJ17787 | 05/05/2023 | 41.5 | 5.99 | 87 | 57 | 0
9996767175 | KJ17787 | 05/06/2023 | 44.55 | 6.4 | 86 | 65 | 0
9996767175 | KJ17787 | 05/07/2023 | 45.06 | 6.47 | 88 | 61 | 0.02
9996767175 | KJ17787 | 05/08/2023 | 40.95 | 5.92 | 87 | 55 | 0
9996767175 | KJ17787 | 05/09/2023 | 39.33 | 5.71 | 91 | 63 | 0
9996767175 | KJ17787 | 05/10/2023 | 39.1 | 5.68 | 92 | 66 | 0
9996767175 | KJ17787 | 05/11/2023 | 38.95 | 5.66 | 88 | 67 | 0.04
9996767175 | KJ17787 | 05/12/2023 | 38.76 | 5.63 | 86 | 66 | 0
9996767175 | KJ17787 | 05/13/2023 | 39.4 | 5.71 | 85 | 64 | 0
9996767175 | KJ17787 | 05/14/2023 | 39.09 | 5.67 | 86 | 63 | 0
9996767175 | KJ17787 | 05/15/2023 | 42.43 | 6.12 | 89 | 62 | 0
9996767175 | KJ17787 | 05/16/2023 | 33.75 | 4.97 | 88 | 64 | 0
9996767175 | KJ17787 | 05/17/2023 | 33.76 | 4.95 | 92 | 67 | 0
9996767175 | KJ17787 | 05/18/2023 | 34.93 | 5.11 | 89 | 65 | 1.24
9996767175 | KJ17787 | 05/19/2023 | 35.48 | 5.18 | 88 | 66 | 0.02
9996767175 | KJ17787 | 05/20/2023 | 34.99 | 5.12 | 88 | 66 | 0
9996767175 | KJ17787 | 05/21/2023 | 34.92 | 5.11 | 88 | 67
9996767175 | KJ17787 | 05/22/2023 | 38.81 | 5.62 | 88 | 67 | 0.65
9996767175 | KJ17787 | 05/23/2023 | 42.93 | 6.17 | 85 | 67 | 0.56
9996767175 | KJ17787 | 05/24/2023 | 54.88 | 7.75 | 83 | 66 | 0.12
9996767175 | KJ17787 | 05/25/2023 | 50.57 | 7.18 | 83 | 66 | 0.16
9996767175 | KJ17787 | 05/26/2023 | 44.82 | 6.42 | 82 | 62 | 0.05
9996767175 | KJ17787 | 05/27/2023 | 47.47 | 6.77 | 81 | 56 | Trace Value
9996767175 | KJ17787 | 05/28/2023 | 43.87 | 6.29 | 85 | 55 | 0
9996767175 | KJ17787 | 05/29/2023 | 43.84 | 6.29 | 87 | 60 | 0
9996767175 | KJ17787 | 05/30/2023 | 41.82 | 6.02 | 88 | 62 | 0
9996767175 | KJ17787 | 05/31/2023 | 40.34 | 5.83 | 87 | 68 | 0
9996767175 | KJ17787 | 06/01/2023 | 42.39 | 6.1 | 85 | 68 | 0
9996767175 | KJ17787 | 06/02/2023 | 40.14 | 5.8 | 85 | 67 | 0
9996767175 | KJ17787 | 06/03/2023 | 40.72 | 5.88 | 84 | 67 | 0
9996767175 | KJ17787 | 06/04/2023 | 39.87 | 5.76 | 84 | 66 | 0
9996767175 | KJ17787 | 06/05/2023 | 39.11 | 5.66 | 84 | 64 | 0.3
9996767175 | KJ17787 | 06/06/2023 | 37.64 | 5.47 | 88 | 62
9996767175 | KJ17787 | 06/07/2023 | 45.51 | 6.51 | 91 | 68 | 0
9996767175 | KJ17787 | 06/08/2023 | 49.73 | 7.07 | 92 | 68 | 1.64
9996767175 | KJ17787 | 06/09/2023 | 50.58 | 7.18 | 92 | 68 | 0
9996767175 | KJ17787 | 06/10/2023 | 52.39 | 7.42 | 88 | 67 | 0.54
9996767175 | KJ17787 | 06/11/2023 | 52.65 | 7.46 | 91 | 69 | 0.09
9996767175 | KJ17787 | 06/12/2023 | 59.55 | 8.37 | 94 | 69 | 0
9996767175 | KJ17787 | 06/13/2023 | 48.72 | 6.94 | 95 | 71
9996767175 | KJ17787 | 06/14/2023 | 58.98 | 8.3 | 95 | 71 | 0
9996767175 | KJ17787 | 06/15/2023 | 48.87 | 6.96 | 95 | 66 | 0.44
9996767175 | KJ17787 | 06/16/2023 | 54.23 | 7.44 | 95 | 68 | 0.45
9996767175 | KJ17787 | 06/17/2023 | 60.61 | 8.26 | 93 | 68 | 0.91
9996767175 | KJ17787 | 06/18/2023 | 59.77 | 8.15 | 94 | 68 | 0.28
9996767175 | KJ17787 | 06/19/2023 | 73.28 | 9.89 | 93 | 70 | 0.63
9996767175 | KJ17787 | 06/20/2023 | 79.49 | 10.69 | 91 | 69 | 0.46
9996767175 | KJ17787 | 06/21/2023 | 73.4 | 9.91 | 91 | 71 | 0.24
9996767175 | KJ17787 | 06/22/2023 | 67.48 | 9.14 | 93 | 66 | 0.04
9996767175 | KJ17787 | 06/23/2023 | 77.5 | 10.43 | 91 | 69 | 0.35
9996767175 | KJ17787 | 06/24/2023 | 72.84 | 9.83 | 92 | 70 | 0.24
9996767175 | KJ17787 | 06/25/2023 | 65.24 | 8.85 | 91 | 70 | 0.15
9996767175 | KJ17787 | 06/26/2023 | 59.24 | 8.08 | 94 | 70 | 0
9996767175 | KJ17787 | 06/27/2023 | 57.16 | 7.81 | 97 | 71 | 0
9996767175 | KJ17787 | 06/28/2023 | 55.61 | 7.61 | 95 | 72 | 0
9996767175 | KJ17787 | 06/29/2023 | 53.25 | 7.31 | 95 | 71 | 0.88
9996767175 | KJ17787 | 06/30/2023 | 50.35 | 6.94 | 94 | 71 | 0
9996767175 | KJ17787 | 07/01/2023 | 52.11 | 7.16 | 94 | 71 | 0
9996767175 | KJ17787 | 07/02/2023 | 47.59 | 6.58 | 95 | 71 | 0
9996767175 | KJ17787 | 07/03/2023 | 50.71 | 6.98 | 97 | 72 | 0
9996767175 | KJ17787 | 07/04/2023 | 50.36 | 6.94 | 95 | 73 | 0
9996767175 | KJ17787 | 07/05/2023 | 49.86 | 6.87 | 95 | 74 | 0
9996767175 | KJ17787 | 07/06/2023 | 49.5 | 6.83 | 96 | 73 | 0.04
9996767175 | KJ17787 | 07/07/2023 | 48.7 | 6.72 | 95 | 73 | 0.03
9996767175 | KJ17787 | 07/08/2023 | 49.82 | 6.87 | 94 | 74 | 0.31
9996767175 | KJ17787 | 07/09/2023 | 47.32 | 6.55 | 96 | 74 | 0.2
9996767175 | KJ17787 | 07/10/2023 | 45.8 | 6.35 | 96 | 74 | 0
9996767175 | KJ17787 | 07/11/2023 | 46.86 | 6.49 | 94 | 73 | 0.78
9996767175 | KJ17787 | 07/12/2023 | 45.59 | 6.32 | 94 | 73 | 0.1
9996767175 | KJ17787 | 07/13/2023 | 43.47 | 6.05 | 94 | 72 | Trace Value
9996767175 | KJ17787 | 07/14/2023 | 52.72 | 7.24 | 95 | 73 | 0.33
9996767175 | KJ17787 | 07/15/2023 | 59.24 | 8.08 | 96 | 73 | 0.12
9996767175 | KJ17787 | 07/16/2023 | 71.05 | 9.6 | 96 | 74 | 0.15
9996767175 | KJ17787 | 07/17/2023 | 53.55 | 7.35 | 95 | 74 | 2.8
9996767175 | KJ17787 | 07/18/2023 | 56.98 | 7.83 | 95 | 72 | 0.22
9996767175 | KJ17787 | 07/19/2023 | 51.28 | 7.1 | 95 | 71 | 0.14
9996767175 | KJ17787 | 07/20/2023 | 57.1 | 7.85 | 96 | 73 | 0
9996767175 | KJ17787 | 07/21/2023 | 47.01 | 6.55 | 99 | 74 | 0
9996767175 | KJ17787 | 07/22/2023 | 60.6 | 8.3 | 97 | 75 | 0
9996767175 | KJ17787 | 07/23/2023 | 70.33 | 9.55 | 94 | 71 | 0.7
9996767175 | KJ17787 | 07/24/2023 | 62.01 | 8.48 | 93 | 73 | 1.12
9996767175 | KJ17787 | 07/25/2023 | 59.62 | 8.17 | 93 | 73 | 0.3
9996767175 | KJ17787 | 07/26/2023 | 56.66 | 7.79 | 92 | 73 | 0
9996767175 | KJ17787 | 07/27/2023 | 54.02 | 7.45 | 91 | 73 | 0
9996767175 | KJ17787 | 07/28/2023 | 55.45 | 7.64 | 92 | 73 | 1
9996767175 | KJ17787 | 07/29/2023 | 61.66 | 8.44 | 93 | 73 | 0.05
9996767175 | KJ17787 | 07/30/2023 | 89.15 | 11.98 | 95 | 74 | Trace Value
9996767175 | KJ17787 | 07/31/2023 | 96.56 | 12.93 | 95 | 71 | 0.74
9996767175 | KJ17787 | 08/01/2023 | 80.58 | 10.87 | 95 | 71 | 0.08
9996767175 | KJ17787 | 08/02/2023 | 72.86 | 9.88 | 93 | 74 | 0
9996767175 | KJ17787 | 08/03/2023 | 68.22 | 9.28 | 91 | 73 | 0
9996767175 | KJ17787 | 08/04/2023 | 63.19 | 8.63 | 94 | 73 | 0
9996767175 | KJ17787 | 08/05/2023 | 65.21 | 8.89 | 94 | 73 | 0.17
9996767175 | KJ17787 | 08/06/2023 | 72.32 | 9.81 | 95 | 74 | 0.66
9996767175 | KJ17787 | 08/07/2023 | 76.62 | 10.36 | 97 | 75 | 0.03
9996767175 | KJ17787 | 08/08/2023 | 67.37 | 9.17 | 99 | 75 | 0
9996767175 | KJ17787 | 08/09/2023 | 63.49 | 8.67 | 99 | 74 | 0
9996767175 | KJ17787 | 08/10/2023 | 62.47 | 8.54 | 100 | 75 | 0.16
9996767175 | KJ17787 | 08/11/2023 | 55.58 | 7.65 | 99 | 75 | 0
9996767175 | KJ17787 | 08/12/2023 | 56 | 7.71 | 98 | 76 | 0.25
9996767175 | KJ17787 | 08/13/2023 | 56.35 | 7.75 | 97 | 74 | 0
9996767175 | KJ17787 | 08/14/2023 | 51.46 | 7.12 | 97 | 76 | 0
9996767175 | KJ17787 | 08/15/2023 | 60.69 | 8.31 | 97 | 75 | 0
9996767175 | KJ17787 | 08/16/2023 | 51.4 | 7.11 | 96 | 73 | 0.09
9996767175 | KJ17787 | 08/17/2023 | 57.04 | 7.83 | 93 | 72 | 0.36
9996767175 | KJ17787 | 08/18/2023 | 59.3 | 8.12 | 93 | 73 | 1.09
9996767175 | KJ17787 | 08/19/2023 | 60.87 | 8.32 | 93 | 72 | 0.69
9996767175 | KJ17787 | 08/20/2023 | 65.36 | 8.9 | 92 | 75 | 0
9996767175 | KJ17787 | 08/21/2023 | 57.88 | 7.93 | 92 | 74 | 0
9996767175 | KJ17787 | 08/22/2023 | 56.64 | 7.78 | 93 | 72 | 0
9996767175 | KJ17787 | 08/23/2023 | 52 | 7.18 | 93 | 74 | 0
9996767175 | KJ17787 | 08/24/2023 | 50.56 | 6.99 | 93 | 74 | 0.99
9996767175 | KJ17787 | 08/25/2023 | 49.76 | 6.89 | 92 | 71 | 0
9996767175 | KJ17787 | 08/26/2023 | 50.52 | 6.99 | 95 | 73 | 0
9996767175 | KJ17787 | 08/27/2023 | 50.1 | 6.93 | 95 | 72
9996767175 | KJ17787 | 08/28/2023 | 47.39 | 6.58 | 96 | 74 | Trace Value
9996767175 | KJ17787 | 08/29/2023 | 50.8 | 7.02 | 95 | 74 | 0
9996767175 | KJ17787 | 08/30/2023 | 54.45 | 7.49 | 94 | 74 | 0.93
9996767175 | KJ17787 | 08/31/2023 | 52.39 | 7.23 | 94 | 74 | 0.05
9996767175 | KJ17787 | 09/01/2023 | 48.25 | 6.69 | 92 | 73 | 0
9996767175 | KJ17787 | 09/02/2023 | 50.49 | 6.98 | 91 | 72
9996767175 | KJ17787 | 09/03/2023 | 47.05 | 6.54 | 92 | 71 | 0.05
9996767175 | KJ17787 | 09/04/2023 | 47.17 | 6.56 | 90 | 68 | 0
9996767175 | KJ17787 | 09/05/2023 | 46.26 | 6.44 | 90 | 64 | 0
9996767175 | KJ17787 | 09/06/2023 | 44.99 | 6.28 | 94 | 69 | 0
9996767175 | KJ17787 | 09/07/2023 | 43.66 | 6.1 | 95 | 70
9996767175 | KJ17787 | 09/08/2023 | 102.02 | 13.62 | 95 | 69 | 0
9996767175 | KJ17787 | 09/09/2023 | 69.5 | 9.43 | 94 | 64 | 0.48
9996767175 | KJ17787 | 09/10/2023 | 65.09 | 8.86 | 93 | 71 | Trace Value
9996767175 | KJ17787 | 09/11/2023 | 62.44 | 8.52 | 92 | 72 | 0
9996767175 | KJ17787 | 09/12/2023 | 67.93 | 9.23 | 92 | 71 | Trace Value
9996767175 | KJ17787 | 09/13/2023 | 130.5 | 17.29 | 92 | 72 | 0.03
9996767175 | KJ17787 | 09/14/2023 | 97.76 | 13.07 | 91 | 71 | 0.29
9996767175 | KJ17787 | 09/15/2023 | 69.4 | 9.42 | 88 | 70 | 0
9996767175 | KJ17787 | 09/16/2023 | 65.81 | 8.97 | 87 | 69 | 0.54
9996767175 | KJ17787 | 09/17/2023 | 65.46 | 8.92 | 92 | 70 | 0
9996767175 | KJ17787 | 09/18/2023 | 58.94 | 8.08 | 89 | 68 | 0.08
9996767175 | KJ17787 | 09/19/2023 | 55.17 | 7.59 | 88 | 64 | 0
9996767175 | KJ17787 | 09/20/2023 | 54.5 | 7.5 | 88 | 69 | 0
9996767175 | KJ17787 | 09/21/2023 | 50.97 | 7.05 | 87 | 68 | 0.08
9996767175 | KJ17787 | 09/22/2023 | 48.37 | 6.71 | 85 | 65 | 0.3
9996767175 | KJ17787 | 09/23/2023 | 49.9 | 6.91 | 87 | 61 | 0
9996767175 | KJ17787 | 09/24/2023 | 48.44 | 6.72 | 89 | 59 | 0
9996767175 | KJ17787 | 09/25/2023 | 66.52 | 9.06 | 90 | 66 | 0
9996767175 | KJ17787 | 09/26/2023 | 151.85 | 20.09 | 89 | 71 | 2.11
9996767175 | KJ17787 | 09/27/2023 | 177.81 | 23.44 | 88 | 71 | 0.91
9996767175 | KJ17787 | 09/28/2023 | 181.2 | 23.88 | 87 | 71 | 0.81
9996767175 | KJ17787 | 09/29/2023 | 125.9 | 16.73 | 85 | 71 | 0.02
9996767175 | KJ17787 | 09/30/2023 | 217.44 | 28.56 | 85 | 71 | 0.2
9996767175 | KJ17787 | 10/01/2023 | 304.74 | 39.85 | 85 | 70 | 2.53
9996767175 | KJ17787 | 10/02/2023 | 324.97 | 42.46 | 85 | 69 | 0.56
9996767175 | KJ17787 | 10/03/2023 | 128.68 | 17.09 | 85 | 70 | 0
9996767175 | KJ17787 | 10/04/2023 | 107.06 | 14.3 | 86 | 70 | 0.05
9996767175 | KJ17787 | 10/05/2023 | 99.79 | 13.36 | 86 | 69 | 0
9996767175 | KJ17787 | 10/06/2023 | 91.17 | 12.24 | 87 | 66 | 0
9996767175 | KJ17787 | 10/07/2023 | 84.48 | 11.38 | 90 | 56 | 0
9996767175 | KJ17787 | 10/08/2023 | 83.75 | 11.29 | 82 | 53 | 0
9996767175 | KJ17787 | 10/09/2023 | 74.78 | 10.13 | 80 | 55 | 0
9996767175 | KJ17787 | 10/10/2023 | 70.43 | 9.56 | 84 | 56 | 0
9996767175 | KJ17787 | 10/11/2023 | 70.25 | 9.54 | 84 | 65 | 0
9996767175 | KJ17787 | 10/12/2023 | 247.08 | 32.4 | 88 | 72 | 2.8
9996767175 | KJ17787 | 10/13/2023 | 284.92 | 37.29 | 89 | 68 | 1.67
9996767175 | KJ17787 | 10/14/2023 | 128.28 | 17.04 | 89 | 64 | 0
9996767175 | KJ17787 | 10/15/2023 | 113.31 | 15.11 | 82 | 55 | 0
9996767175 | KJ17787 | 10/16/2023 | 119.11 | 15.85 | 76 | 50 | 0
9996767175 | KJ17787 | 10/17/2023 | 87.88 | 11.82 | 75 | 49 | 0
9996767175 | KJ17787 | 10/18/2023 | 84.33 | 11.36 | 77 | 50 | 0
9996767175 | KJ17787 | 10/19/2023 | 79.48 | 10.74 | 81 | 55 | 0
9996767175 | KJ17787 | 10/20/2023 | 74.52 | 10.1 | 83 | 55 | 0
9996767175 | KJ17787 | 10/21/2023 | 75.27 | 10.19 | 83 | 55 | 0
9996767175 | KJ17787 | 10/22/2023 | 71.79 | 9.74 | 86 | 52 | 0
9996767175 | KJ17787 | 10/23/2023 | 68.46 | 9.31 | 83 | 58 | 0
9996767175 | KJ17787 | 10/24/2023 | 64.32 | 8.78 | 82 | 67 | 0
9996767175 | KJ17787 | 10/25/2023 | 61.65 | 8.44 | 82 | 68 | 0
9996767175 | KJ17787 | 10/26/2023 | 60.51 | 8.29 | 82 | 65 | 0
9996767175 | KJ17787 | 10/27/2023 | 57.16 | 7.86 | 83 | 64 | 0
9996767175 | KJ17787 | 10/28/2023 | 61.15 | 8.37 | 84 | 62 | 0
9996767175 | KJ17787 | 10/29/2023 | 58.87 | 8.08 | 84 | 61 | 0
9996767175 | KJ17787 | 10/30/2023 | 56.55 | 7.78 | 85 | 60 | 0
9996767175 | KJ17787 | 10/31/2023 | 55.44 | 7.63 | 84 | 58 | 0
9996767175 | KJ17787 | 11/01/2023 | 51.87 | 7.17 | 76 | 53 | 0
9996767175 | KJ17787 | 11/02/2023 | 50.09 | 6.94 | 75 | 53 | 0
9996767175 | KJ17787 | 11/03/2023 | 50.74 | 7.03 | 79 | 59 | 0
9996767175 | KJ17787 | 11/04/2023 | 51.39 | 7.11 | 79 | 55 | 0
9996767175 | KJ17787 | 11/05/2023 | 54.55 | 7.52 | 80 | 51 | 0
9996767175 | KJ17787 | 11/06/2023 | 47.38 | 6.59 | 81 | 48 | 0
9996767175 | KJ17787 | 11/07/2023 | 45.81 | 6.39 | 83 | 53 | 0
9996767175 | KJ17787 | 11/08/2023 | 45.59 | 6.36 | 84 | 50 | 0
9996767175 | KJ17787 | 11/09/2023 | 45.5 | 6.35 | 85 | 55 | 0
9996767175 | KJ17787 | 11/10/2023 | 44.01 | 6.16 | 86 | 60 | 0
9996767175 | KJ17787 | 11/11/2023 | 47.42 | 6.6 | 83 | 65 | 0.33
9996767175 | KJ17787 | 11/12/2023 | 47.32 | 6.59 | 80 | 63 | 0
9996767175 | KJ17787 | 11/13/2023 | 45.99 | 6.41 | 77 | 62 | 0
9996767175 | KJ17787 | 11/14/2023 | 55.33 | 7.62 | 77 | 61 | 0.12
9996767175 | KJ17787 | 11/15/2023 | 45.62 | 6.37 | 77 | 64 | 0.05
9996767175 | KJ17787 | 11/16/2023 | 60.88 | 8.35 | 78 | 62 | 0.16
9996767175 | KJ17787 | 11/17/2023 | 201.59 | 26.51 | 79 | 61 | 2.1
9996767175 | KJ17787 | 11/18/2023 | 91.83 | 12.34 | 78 | 55 | 0.66
9996767175 | KJ17787 | 11/19/2023 | 78.19 | 10.58 | 80 | 56 | 0
9996767175 | KJ17787 | 11/20/2023 | 70.33 | 9.57 | 79 | 59 | 0.02
9996767175 | KJ17787 | 11/21/2023 | 65.45 | 8.94 | 81 | 52 | 0.02
9996767175 | KJ17787 | 11/22/2023 | 66.67 | 9.1 | 81 | 47 | 0
9996767175 | KJ17787 | 11/23/2023 | 66.13 | 9.03 | 73 | 48 | 0.01
9996767175 | KJ17787 | 11/24/2023 | 59.98 | 8.23 | 75 | 52 | 0.01
9996767175 | KJ17787 | 11/25/2023 | 60.56 | 8.31 | 75 | 53 | 0.07
9996767175 | KJ17787 | 11/26/2023 | 68.23 | 9.3 | 75 | 55 | 0.01
9996767175 | KJ17787 | 11/27/2023 | 65.78 | 8.98 | 74 | 44 | 0.55
9996767175 | KJ17787 | 11/28/2023 | 56.03 | 7.72 | 69 | 39 | 0
9996767175 | KJ17787 | 11/29/2023 | 56.35 | 7.76 | 68 | 36 | 0
9996767175 | KJ17787 | 11/30/2023 | 51.38 | 7.12 | 86 | 41 | 0
9996767175 | KJ17787 | 12/01/2023 | 52.02 | 7.21 | 82 | 55 | 0
9996767175 | KJ17787 | 12/02/2023 | 54.16 | 7.48 | 83 | 64 | 0
9996767175 | KJ17787 | 12/03/2023 | 59.34 | 8.15 | 82 | 62 | 0.02
9996767175 | KJ17787 | 12/04/2023 | 57.29 | 7.89 | 79 | 51 | 0.23
9996767175 | KJ17787 | 12/05/2023 | 54.09 | 7.47 | 72 | 47 | 0
9996767175 | KJ17787 | 12/06/2023 | 52.7 | 7.29 | 69 | 41 | 0
9996767175 | KJ17787 | 12/07/2023 | 49.01 | 6.82 | 67 | 41 | 0
9996767175 | KJ17787 | 12/08/2023 | 47.42 | 6.61 | 74 | 47 | 0
9996767175 | KJ17787 | 12/09/2023 | 49.14 | 6.83 | 82 | 56 | 0.04
9996767175 | KJ17787 | 12/10/2023 | 56.86 | 7.83 | 83 | 44 | 0
9996767175 | KJ17787 | 12/11/2023 | 54.13 | 7.48 | 67 | 43 | 0.25
9996767175 | KJ17787 | 12/12/2023 | 52.05 | 7.21 | 71 | 43 | 0
9996767175 | KJ17787 | 12/13/2023 | 59.72 | 8.2 | 73 | 58 | 0
9996767175 | KJ17787 | 12/14/2023 | 55.81 | 7.69 | 72 | 59 | 0.66
9996767175 | KJ17787 | 12/15/2023 | 48.14 | 6.58 | 72 | 60 | 0.07
9996767175 | KJ17787 | 12/16/2023 | 61.72 | 8.33 | 73 | 58 | 0.11
9996767175 | KJ17787 | 12/17/2023 | 302.87 | 39.26 | 74 | 48 | 4.04
9996767175 | KJ17787 | 12/18/2023 | 148.97 | 19.52 | 68 | 40 | 0.05
9996767175 | KJ17787 | 12/19/2023 | 102.59 | 13.57 | 65 | 41 | 0
9996767175 | KJ17787 | 12/20/2023 | 91.29 | 12.12 | 66 | 44 | 0
9996767175 | KJ17787 | 12/21/2023 | 82.04 | 10.93 | 68 | 46 | 0
9996767175 | KJ17787 | 12/22/2023 | 77.09 | 10.3 | 70 | 49 | 0
9996767175 | KJ17787 | 12/23/2023 | 80.95 | 10.79 | 73 | 53 | 0
9996767175 | KJ17787 | 12/24/2023 | 79.2 | 10.57 | 73 | 53 | 0
9996767175 | KJ17787 | 12/25/2023 | 77.22 | 10.32 | 73 | 60 | 0.09
9996767175 | KJ17787 | 12/26/2023 | 75.74 | 10.13 | 74 | 54 | 0.1
9996767175 | KJ17787 | 12/27/2023 | 69.38 | 9.31 | 71 | 49 | 0
9996767175 | KJ17787 | 12/28/2023 | 70.02 | 9.39 | 66 | 44 | 0.04
9996767175 | KJ17787 | 12/29/2023 | 68.26 | 9.17 | 55 | 46 | 0
9996767175 | KJ17787 | 12/30/2023 | 67.08 | 9.01 | 59 | 37 | 0
9996767175 | KJ17787 | 12/31/2023 | 67.12 | 9.02 | 63 | 36 | 0
|  | Yearly Daily Average: | 57.7428 | 7.9186
|  | Wetter Months' Daily Average: | 81.413 | 10.9684

## 24-2 MPS
Daily Billed Information (PS 24-2 - 215 Pritchard Drive: 2023 Reading Data)
Bill Account | Meter Number | Date | Consumption Recorded (kWh/day) | Estimated Cost ($/day) | Avg. High Temperature (°F) | Avg. Low Temperature (°F) | Rain Recorded by NOAA (inches)
4245923539 | KNJ0223 | 01/01/2023 | 524 | 61.64 | 79 | 58 | 0.04
4245923539 | KNJ0223 | 01/02/2023 | 542.3 | 63.76 | 78 | 53 | 0
4245923539 | KNJ0223 | 01/03/2023 | 492.67 | 58.01 | 81 | 51 | 0
4245923539 | KNJ0223 | 01/04/2023 | 503.21 | 59.24 | 83 | 57 | 0
4245923539 | KNJ0223 | 01/05/2023 | 510.45 | 60.07 | 77 | 46 | 0.04
4245923539 | KNJ0223 | 01/06/2023 | 503.67 | 59.29 | 68 | 41 | 0
4245923539 | KNJ0223 | 01/07/2023 | 533.56 | 62.75 | 70 | 38 | 0
4245923539 | KNJ0223 | 01/08/2023 | 663.35 | 77.78 | 76 | 42 | 0
4245923539 | KNJ0223 | 01/09/2023 | 502.27 | 59.13 | 74 | 47 | 0
4245923539 | KNJ0223 | 01/10/2023 | 466.56 | 50.68 | 71 | 42 | 0
4245923539 | KNJ0223 | 01/11/2023 | 504.51 | 54.72 | 73 | 38 | 0
4245923539 | KNJ0223 | 01/12/2023 | 466.83 | 50.71 | 80 | 44 | 0
4245923539 | KNJ0223 | 01/13/2023 | 498.54 | 54.08 | 71 | 35 | 0.12
4245923539 | KNJ0223 | 01/14/2023 | 546.53 | 59.19 | 61 | 30 | 0
4245923539 | KNJ0223 | 01/15/2023 | 540.2 | 58.52 | 63 | 30 | 0
4245923539 | KNJ0223 | 01/16/2023 | 516.11 | 55.95 | 71 | 30 | 0
4245923539 | KNJ0223 | 01/17/2023 | 471.99 | 51.26 | 75 | 34 | 0
4245923539 | KNJ0223 | 01/18/2023 | 478.78 | 51.98 | 79 | 46 | N/A
4245923539 | KNJ0223 | 01/19/2023 | 473.28 | 51.4 | 82 | 54 | 0
4245923539 | KNJ0223 | 01/20/2023 | 475.18 | 51.6 | 76 | 49 | 0
4245923539 | KNJ0223 | 01/21/2023 | 509.42 | 55.24 | 76 | 47 | T
4245923539 | KNJ0223 | 01/22/2023 | 574.66 | 62.19 | 82 | 54 | 0.33
4245923539 | KNJ0223 | 01/23/2023 | 489.14 | 53.08 | 75 | 44 | 0.05
4245923539 | KNJ0223 | 01/24/2023 | 477.39 | 51.83 | 76 | 41 | 0
4245923539 | KNJ0223 | 01/25/2023 | 500.27 | 54.27 | 85 | 43 | 0
4245923539 | KNJ0223 | 01/26/2023 | 504.58 | 54.73 | 72 | 38 | 0.09
4245923539 | KNJ0223 | 01/27/2023 | 484.85 | 52.63 | 62 | 37 | 0
4245923539 | KNJ0223 | 01/28/2023 | 495.92 | 53.8 | 69 | 35 | 0
4245923539 | KNJ0223 | 01/29/2023 | 542.39 | 58.75 | 78 | 55 | 0
4245923539 | KNJ0223 | 01/30/2023 | 478.58 | 51.96 | 86 | 58 | 0
4245923539 | KNJ0223 | 01/31/2023 | 468.47 | 50.88 | 83 | 59 | 0
4245923539 | KNJ0223 | 02/01/2023 | 480 | 52.11 | 82 | 58 | 0
4245923539 | KNJ0223 | 02/02/2023 | 494.19 | 53.62 | 82 | 57 | 0
4245923539 | KNJ0223 | 02/03/2023 | 505.56 | 54.83 | 78 | 50 | 0
4245923539 | KNJ0223 | 02/04/2023 | 544.14 | 58.94 | 70 | 47 | 0.17
4245923539 | KNJ0223 | 02/05/2023 | 573.69 | 62.08 | 73 | 48 | 0
4245923539 | KNJ0223 | 02/06/2023 | 508.14 | 55.11 | 71 | 46 | 0.01
4245923539 | KNJ0223 | 02/07/2023 | 554.36 | 60.03 | 76 | 44
4245923539 | KNJ0223 | 02/08/2023 | 450.95 | 49.02 | 79 | 49 | 0
4245923539 | KNJ0223 | 02/09/2023 | 488.74 | 53.84 | 83 | 58 | 0
4245923539 | KNJ0223 | 02/10/2023 | 502.11 | 55.28 | 85 | 46 | 0.16
4245923539 | KNJ0223 | 02/11/2023 | 538.54 | 59.22 | 79 | 40 | 0.57
4245923539 | KNJ0223 | 02/12/2023 | 594.12 | 65.23 | 71 | 40 | 0.12
4245923539 | KNJ0223 | 02/13/2023 | 500.27 | 55.08 | 71 | 40 | Trace Value
4245923539 | KNJ0223 | 02/14/2023 | 484.08 | 53.34 | 75 | 39 | 0
4245923539 | KNJ0223 | 02/15/2023 | 497.39 | 54.77 | 82 | 50 | 0
4245923539 | KNJ0223 | 02/16/2023 | 499.36 | 54.99 | 85 | 57 | 0
4245923539 | KNJ0223 | 02/17/2023 | 506.27 | 55.73 | 89 | 45
4245923539 | KNJ0223 | 02/18/2023 | 519.12 | 57.12 | 67 | 46 | 0.04
4245923539 | KNJ0223 | 02/19/2023 | 553.66 | 60.86 | 80 | 48 | 0
4245923539 | KNJ0223 | 02/20/2023 | 511.37 | 56.29 | 82 | 53 | 0
4245923539 | KNJ0223 | 02/21/2023 | 450.79 | 49.74 | 85 | 57 | 0
4245923539 | KNJ0223 | 02/22/2023 | 484.59 | 53.39 | 87 | 58 | 0
4245923539 | KNJ0223 | 02/23/2023 | 483.33 | 53.25 | 89 | 60 | 0
4245923539 | KNJ0223 | 02/24/2023 | 477.54 | 52.63 | 87 | 58 | 0
4245923539 | KNJ0223 | 02/25/2023 | 512.18 | 56.37 | 87 | 58
4245923539 | KNJ0223 | 02/26/2023 | 537.67 | 59.13 | 87 | 56 | 0
4245923539 | KNJ0223 | 02/27/2023 | 483.53 | 53.28 | 87 | 57 | 0
4245923539 | KNJ0223 | 02/28/2023 | 447.57 | 49.39 | 87 | 57 | 0
4245923539 | KNJ0223 | 03/01/2023 | 468.86 | 51.69 | 86 | 58 | 0
4245923539 | KNJ0223 | 03/02/2023 | 483.41 | 53.26 | 87 | 56 | 0
4245923539 | KNJ0223 | 03/03/2023 | 469.8 | 51.79 | 90 | 55 | 0
4245923539 | KNJ0223 | 03/04/2023 | 506.34 | 55.74 | 88 | 52 | 0
4245923539 | KNJ0223 | 03/05/2023 | 552.97 | 60.78 | 81 | 54 | 0.05
4245923539 | KNJ0223 | 03/06/2023 | 486.82 | 53.63 | 84 | 56 | 0
4245923539 | KNJ0223 | 03/07/2023 | 462.58 | 51.01 | 87 | 56
4245923539 | KNJ0223 | 03/08/2023 | 552.06 | 60.68 | 85 | 58 | 0
4245923539 | KNJ0223 | 03/09/2023 | 492.78 | 54.28 | 80 | 51 | 0
4245923539 | KNJ0223 | 03/10/2023 | 490.77 | 67.18 | 85 | 54
4245923539 | KNJ0223 | 03/11/2023 | 535.92 | 73.27 | 81 | 51 | 1.3
4245923539 | KNJ0223 | 03/12/2023 | 539.21 | 73.72 | 86 | 48 | 0
4245923539 | KNJ0223 | 03/13/2023 | 624.72 | 85.25 | 81 | 46 | 1.17
4245923539 | KNJ0223 | 03/14/2023 | 508.52 | 69.58 | 70 | 43 | 0.6
4245923539 | KNJ0223 | 03/15/2023 | 526.38 | 71.99 | 68 | 43 | 0
4245923539 | KNJ0223 | 03/16/2023 | 520.88 | 71.25 | 77 | 37 | 0
4245923539 | KNJ0223 | 03/17/2023 | 523.63 | 71.62 | 84 | 48
4245923539 | KNJ0223 | 03/18/2023 | 543.44 | 74.29 | 80 | 45 | 0
4245923539 | KNJ0223 | 03/19/2023 | 537.22 | 73.45 | 68 | 43 | 0.02
4245923539 | KNJ0223 | 03/20/2023 | 505.92 | 69.23 | 69 | 42 | 0.02
4245923539 | KNJ0223 | 03/21/2023 | 486.37 | 66.59 | 77 | 42 | 0
4245923539 | KNJ0223 | 03/22/2023 | 500.54 | 68.5 | 80 | 53 | 0.08
4245923539 | KNJ0223 | 03/23/2023 | 498.16 | 68.18 | 83 | 53
4245923539 | KNJ0223 | 03/24/2023 | 501.97 | 68.7 | 86 | 53 | 0
4245923539 | KNJ0223 | 03/25/2023 | 522.85 | 71.51 | 91 | 60 | 0
4245923539 | KNJ0223 | 03/26/2023 | 562.87 | 76.91 | 91 | 63 | 0.68
4245923539 | KNJ0223 | 03/27/2023 | 496.12 | 67.91 | 92 | 62 | 0
4245923539 | KNJ0223 | 03/28/2023 | 494.45 | 67.68 | 88 | 55 | Trace Value
4245923539 | KNJ0223 | 03/29/2023 | 500.94 | 68.56 | 75 | 55 | 0
4245923539 | KNJ0223 | 03/30/2023 | 498.86 | 68.28 | 79 | 51 | 0
4245923539 | KNJ0223 | 03/31/2023 | 481.62 | 65.95 | 85 | 55 | 0
4245923539 | KNJ0223 | 04/01/2023 | 499.29 | 68.33 | 90 | 60 | 0
4245923539 | KNJ0223 | 04/02/2023 | 526.67 | 72.03 | 85 | 60
4245923539 | KNJ0223 | 04/03/2023 | 462.04 | 63.31 | 86 | 61 | 0
4245923539 | KNJ0223 | 04/04/2023 | 443.36 | 60.79 | 88 | 60 | Trace Value
4245923539 | KNJ0223 | 04/05/2023 | 465.98 | 63.84 | 87 | 63 | 0
4245923539 | KNJ0223 | 04/06/2023 | 471.34 | 64.56 | 87 | 64 | 0
4245923539 | KNJ0223 | 04/07/2023 | 498.93 | 68.29 | 85 | 64
4245923539 | KNJ0223 | 04/08/2023 | 544.55 | 74.44 | 86 | 62
4245923539 | KNJ0223 | 04/09/2023 | 660.3 | 90.04 | 80 | 60 | 0.01
4245923539 | KNJ0223 | 04/10/2023 | 674.25 | 91.93 | 79 | 58 | 0.68
4245923539 | KNJ0223 | 04/11/2023 | 545.95 | 79.21 | 78 | 58 | 1.38
4245923539 | KNJ0223 | 04/12/2023 | 527.08 | 76.51 | 79 | 59 | 0.03
4245923539 | KNJ0223 | 04/13/2023 | 955.03 | 137.75 | 87 | 61 | 0.07
4245923539 | KNJ0223 | 04/14/2023 | 1158.52 | 166.87 | 86 | 59 | 0.57
4245923539 | KNJ0223 | 04/15/2023 | 787.19 | 113.73 | 87 | 60 | 0.02
4245923539 | KNJ0223 | 04/16/2023 | 720.88 | 104.24 | 88 | 59 | 0
4245923539 | KNJ0223 | 04/17/2023 | 625.33 | 90.57 | 81 | 50 | 0.04
4245923539 | KNJ0223 | 04/18/2023 | 563.13 | 81.67 | 81 | 46 | 0.02
4245923539 | KNJ0223 | 04/19/2023 | 580.59 | 84.16 | 82 | 50 | 0
4245923539 | KNJ0223 | 04/20/2023 | 580.98 | 84.22 | 84 | 55 | 0
4245923539 | KNJ0223 | 04/21/2023 | 559.59 | 81.16 | 87 | 59
4245923539 | KNJ0223 | 04/22/2023 | 578.07 | 83.8 | 89 | 57 | 0.3
4245923539 | KNJ0223 | 04/23/2023 | 619.99 | 89.8 | 84 | 53 | 0.42
4245923539 | KNJ0223 | 04/24/2023 | 559.48 | 81.14 | 80 | 55 | 0
4245923539 | KNJ0223 | 04/25/2023 | 563.86 | 81.77 | 82 | 61 | 0.25
4245923539 | KNJ0223 | 04/26/2023 | 554.05 | 80.37 | 84 | 62 | 0.07
4245923539 | KNJ0223 | 04/27/2023 | 876.02 | 126.44 | 86 | 63 | 0
4245923539 | KNJ0223 | 04/28/2023 | 791.97 | 114.41 | 87 | 62 | 1.62
4245923539 | KNJ0223 | 04/29/2023 | 706.19 | 102.14 | 88 | 62 | 0
4245923539 | KNJ0223 | 04/30/2023 | 842.06 | 121.58 | 85 | 57 | 0.52
4245923539 | KNJ0223 | 05/01/2023 | 628.52 | 91.02 | 85 | 56 | 0
4245923539 | KNJ0223 | 05/02/2023 | 571.96 | 82.93 | 87 | 56 | 0
4245923539 | KNJ0223 | 05/03/2023 | 565.6 | 82.02 | 86 | 53 | 0
4245923539 | KNJ0223 | 05/04/2023 | 559.97 | 81.21 | 84 | 53 | 0
4245923539 | KNJ0223 | 05/05/2023 | 517.98 | 75.2 | 87 | 57 | 0
4245923539 | KNJ0223 | 05/06/2023 | 572.09 | 82.95 | 86 | 65 | 0
4245923539 | KNJ0223 | 05/07/2023 | 612.46 | 88.73 | 88 | 61 | 0.02
4245923539 | KNJ0223 | 05/08/2023 | 638.34 | 92.43 | 87 | 55 | 0
4245923539 | KNJ0223 | 05/09/2023 | 521.97 | 75.78 | 91 | 63 | 0
4245923539 | KNJ0223 | 05/10/2023 | 530.06 | 70.38 | 92 | 66 | 0
4245923539 | KNJ0223 | 05/11/2023 | 533.37 | 70.81 | 88 | 67 | 0.04
4245923539 | KNJ0223 | 05/12/2023 | 533.56 | 70.84 | 86 | 66 | 0
4245923539 | KNJ0223 | 05/13/2023 | 558.12 | 74.05 | 85 | 64 | 0
4245923539 | KNJ0223 | 05/14/2023 | 553.92 | 73.5 | 86 | 63 | 0
4245923539 | KNJ0223 | 05/15/2023 | 534.96 | 71.02 | 89 | 62 | 0
4245923539 | KNJ0223 | 05/16/2023 | 508.29 | 67.53 | 88 | 64 | 0
4245923539 | KNJ0223 | 05/17/2023 | 524.24 | 69.62 | 92 | 67 | 0
4245923539 | KNJ0223 | 05/18/2023 | 532.22 | 70.66 | 89 | 65 | 1.24
4245923539 | KNJ0223 | 05/19/2023 | 521.39 | 69.25 | 88 | 66 | 0.02
4245923539 | KNJ0223 | 05/20/2023 | 542.89 | 72.06 | 88 | 66 | 0
4245923539 | KNJ0223 | 05/21/2023 | 572.59 | 75.94 | 88 | 67
4245923539 | KNJ0223 | 05/22/2023 | 655.86 | 86.83 | 88 | 67 | 0.65
4245923539 | KNJ0223 | 05/23/2023 | 614.37 | 81.4 | 85 | 67 | 0.56
4245923539 | KNJ0223 | 05/24/2023 | 589.49 | 78.15 | 83 | 66 | 0.12
4245923539 | KNJ0223 | 05/25/2023 | 578.75 | 76.75 | 83 | 66 | 0.16
4245923539 | KNJ0223 | 05/26/2023 | 556.14 | 73.79 | 82 | 62 | 0.05
4245923539 | KNJ0223 | 05/27/2023 | 580.8 | 77.01 | 81 | 56 | Trace Value
4245923539 | KNJ0223 | 05/28/2023 | 559.23 | 74.19 | 85 | 55 | 0
4245923539 | KNJ0223 | 05/29/2023 | 583.32 | 77.34 | 87 | 60 | 0
4245923539 | KNJ0223 | 05/30/2023 | 512.95 | 68.14 | 88 | 62 | 0
4245923539 | KNJ0223 | 05/31/2023 | 533.78 | 70.87 | 87 | 68 | 0
4245923539 | KNJ0223 | 06/01/2023 | 531.89 | 70.62 | 85 | 68 | 0
4245923539 | KNJ0223 | 06/02/2023 | 524.83 | 69.7 | 85 | 67 | 0
4245923539 | KNJ0223 | 06/03/2023 | 549.98 | 72.98 | 84 | 67 | 0
4245923539 | KNJ0223 | 06/04/2023 | 558.92 | 74.15 | 84 | 66 | 0
4245923539 | KNJ0223 | 06/05/2023 | 511.44 | 67.95 | 84 | 64 | 0.3
4245923539 | KNJ0223 | 06/06/2023 | 488.6 | 64.96 | 88 | 62
4245923539 | KNJ0223 | 06/07/2023 | 714.13 | 94.45 | 91 | 68 | 0
4245923539 | KNJ0223 | 06/08/2023 | 576.01 | 76.39 | 92 | 68 | 1.64
4245923539 | KNJ0223 | 06/09/2023 | 578.37 | 80.22 | 92 | 68 | 0
4245923539 | KNJ0223 | 06/10/2023 | 595.35 | 82.54 | 88 | 67 | 0.54
4245923539 | KNJ0223 | 06/11/2023 | 594.05 | 82.37 | 91 | 69 | 0.09
4245923539 | KNJ0223 | 06/12/2023 | 574.52 | 79.69 | 94 | 69 | 0
4245923539 | KNJ0223 | 06/13/2023 | 542.33 | 75.28 | 95 | 71
4245923539 | KNJ0223 | 06/14/2023 | 551.51 | 76.54 | 95 | 71 | 0
4245923539 | KNJ0223 | 06/15/2023 | 565.5 | 78.45 | 95 | 66 | 0.44
4245923539 | KNJ0223 | 06/16/2023 | 604.42 | 83.79 | 95 | 68 | 0.45
4245923539 | KNJ0223 | 06/17/2023 | 682.63 | 94.5 | 93 | 68 | 0.91
4245923539 | KNJ0223 | 06/18/2023 | 641.38 | 88.85 | 94 | 68 | 0.28
4245923539 | KNJ0223 | 06/19/2023 | 750.99 | 103.86 | 93 | 70 | 0.63
4245923539 | KNJ0223 | 06/20/2023 | 706.91 | 97.82 | 91 | 69 | 0.46
4245923539 | KNJ0223 | 06/21/2023 | 628.39 | 87.07 | 91 | 71 | 0.24
4245923539 | KNJ0223 | 06/22/2023 | 598.12 | 82.92 | 93 | 66 | 0.04
4245923539 | KNJ0223 | 06/23/2023 | 750.41 | 103.78 | 91 | 69 | 0.35
4245923539 | KNJ0223 | 06/24/2023 | 682.69 | 94.5 | 92 | 70 | 0.24
4245923539 | KNJ0223 | 06/25/2023 | 638.57 | 88.46 | 91 | 70 | 0.15
4245923539 | KNJ0223 | 06/26/2023 | 588.13 | 81.55 | 94 | 70 | 0
4245923539 | KNJ0223 | 06/27/2023 | 549.5 | 76.26 | 97 | 71 | 0
4245923539 | KNJ0223 | 06/28/2023 | 496.69 | 69.03 | 95 | 72 | 0
4245923539 | KNJ0223 | 06/29/2023 | 357.03 | 49.9 | 95 | 71 | 0.88
4245923539 | KNJ0223 | 06/30/2023 | 572.32 | 79.39 | 94 | 71 | 0
4245923539 | KNJ0223 | 07/01/2023 | 644.9 | 89.33 | 94 | 71 | 0
4245923539 | KNJ0223 | 07/02/2023 | 662.69 | 91.77 | 95 | 71 | 0
4245923539 | KNJ0223 | 07/03/2023 | 653.41 | 90.49 | 97 | 72 | 0
4245923539 | KNJ0223 | 07/04/2023 | 667.28 | 92.39 | 95 | 73 | 0
4245923539 | KNJ0223 | 07/05/2023 | 646.76 | 89.58 | 95 | 74 | 0
4245923539 | KNJ0223 | 07/06/2023 | 470.59 | 65.46 | 96 | 73 | 0.04
4245923539 | KNJ0223 | 07/07/2023 | 577.51 | 80.1 | 95 | 73 | 0.03
4245923539 | KNJ0223 | 07/08/2023 | 592.99 | 82.22 | 94 | 74 | 0.31
4245923539 | KNJ0223 | 07/09/2023 | 719.58 | 99.56 | 96 | 74 | 0.2
4245923539 | KNJ0223 | 07/10/2023 | 587.85 | 81.52 | 96 | 74 | 0
4245923539 | KNJ0223 | 07/11/2023 | 559.72 | 75.14 | 94 | 73 | 0.78
4245923539 | KNJ0223 | 07/12/2023 | 603.18 | 80.89 | 94 | 73 | 0.1
4245923539 | KNJ0223 | 07/13/2023 | 467.05 | 62.88 | 94 | 72 | Trace Value
4245923539 | KNJ0223 | 07/14/2023 | 556.52 | 74.72 | 95 | 73 | 0.33
4245923539 | KNJ0223 | 07/15/2023 | 618.33 | 82.9 | 96 | 73 | 0.12
4245923539 | KNJ0223 | 07/16/2023 | 733.24 | 98.1 | 96 | 74 | 0.15
4245923539 | KNJ0223 | 07/17/2023 | 636.37 | 85.28 | 95 | 74 | 2.8
4245923539 | KNJ0223 | 07/18/2023 | 408.86 | 55.18 | 95 | 72 | 0.22
4245923539 | KNJ0223 | 07/19/2023 | 612.1 | 82.07 | 95 | 71 | 0.14
4245923539 | KNJ0223 | 07/20/2023 | 463.43 | 62.4 | 96 | 73 | 0
4245923539 | KNJ0223 | 07/21/2023 | 519.25 | 69.79 | 99 | 74 | 0
4245923539 | KNJ0223 | 07/22/2023 | 639.63 | 85.72 | 97 | 75 | 0
4245923539 | KNJ0223 | 07/23/2023 | 690.52 | 92.45 | 94 | 71 | 0.7
4245923539 | KNJ0223 | 07/24/2023 | 626.99 | 84.04 | 93 | 73 | 1.12
4245923539 | KNJ0223 | 07/25/2023 | 558.06 | 74.92 | 93 | 73 | 0.3
4245923539 | KNJ0223 | 07/26/2023 | 550.44 | 73.91 | 92 | 73 | 0
4245923539 | KNJ0223 | 07/27/2023 | 547.35 | 73.51 | 91 | 73 | 0
4245923539 | KNJ0223 | 07/28/2023 | 636.35 | 85.28 | 92 | 73 | 1
4245923539 | KNJ0223 | 07/29/2023 | 687.32 | 92.03 | 93 | 73 | 0.05
4245923539 | KNJ0223 | 07/30/2023 | 742.4 | 99.32 | 95 | 74 | Trace Value
4245923539 | KNJ0223 | 07/31/2023 | 901.02 | 120.3 | 95 | 71 | 0.74
4245923539 | KNJ0223 | 08/01/2023 | 662.47 | 88.74 | 95 | 71 | 0.08
4245923539 | KNJ0223 | 08/02/2023 | 612.61 | 82.14 | 93 | 74 | 0
4245923539 | KNJ0223 | 08/03/2023 | 584.8 | 78.46 | 91 | 73 | 0
4245923539 | KNJ0223 | 08/04/2023 | 709.51 | 94.96 | 94 | 73 | 0
4245923539 | KNJ0223 | 08/05/2023 | 689.13 | 92.27 | 94 | 73 | 0.17
4245923539 | KNJ0223 | 08/06/2023 | 806.25 | 107.76 | 95 | 74 | 0.66
4245923539 | KNJ0223 | 08/07/2023 | 694.46 | 92.97 | 97 | 75 | 0.03
4245923539 | KNJ0223 | 08/08/2023 | 719.46 | 96.28 | 99 | 75 | 0
4245923539 | KNJ0223 | 08/09/2023 | 697.12 | 93.32 | 99 | 74 | 0
4245923539 | KNJ0223 | 08/10/2023 | 656.8 | 86.38 | 100 | 75 | 0.16
4245923539 | KNJ0223 | 08/11/2023 | 589.68 | 77.66 | 99 | 75 | 0
4245923539 | KNJ0223 | 08/12/2023 | 651.72 | 85.72 | 98 | 76 | 0.25
4245923539 | KNJ0223 | 08/13/2023 | 671.58 | 88.3 | 97 | 74 | 0
4245923539 | KNJ0223 | 08/14/2023 | 596.73 | 78.58 | 97 | 76 | 0
4245923539 | KNJ0223 | 08/15/2023 | 557.87 | 73.53 | 97 | 75 | 0
4245923539 | KNJ0223 | 08/16/2023 | 752.46 | 98.81 | 96 | 73 | 0.09
4245923539 | KNJ0223 | 08/17/2023 | 686.95 | 90.3 | 93 | 72 | 0.36
4245923539 | KNJ0223 | 08/18/2023 | 701.76 | 92.22 | 93 | 73 | 1.09
4245923539 | KNJ0223 | 08/19/2023 | 691.49 | 90.89 | 93 | 72 | 0.69
4245923539 | KNJ0223 | 08/20/2023 | 725.88 | 95.36 | 92 | 75 | 0
4245923539 | KNJ0223 | 08/21/2023 | 600.4 | 79.06 | 92 | 74 | 0
4245923539 | KNJ0223 | 08/22/2023 | 585.57 | 77.13 | 93 | 72 | 0
4245923539 | KNJ0223 | 08/23/2023 | 559.42 | 73.73 | 93 | 74 | 0
4245923539 | KNJ0223 | 08/24/2023 | 559.12 | 73.69 | 93 | 74 | 0.99
4245923539 | KNJ0223 | 08/25/2023 | 541.01 | 71.34 | 92 | 71 | 0
4245923539 | KNJ0223 | 08/26/2023 | 581.21 | 76.56 | 95 | 73 | 0
4245923539 | KNJ0223 | 08/27/2023 | 599.25 | 78.91 | 95 | 72
4245923539 | KNJ0223 | 08/28/2023 | 511.76 | 67.54 | 96 | 74 | Trace Value
4245923539 | KNJ0223 | 08/29/2023 | 544.4 | 71.78 | 95 | 74 | 0
4245923539 | KNJ0223 | 08/30/2023 | 599.56 | 78.95 | 94 | 74 | 0.93
4245923539 | KNJ0223 | 08/31/2023 | 564.43 | 74.38 | 94 | 74 | 0.05
4245923539 | KNJ0223 | 09/01/2023 | 558.51 | 73.61 | 92 | 73 | 0
4245923539 | KNJ0223 | 09/02/2023 | 580.44 | 76.46 | 91 | 72
4245923539 | KNJ0223 | 09/03/2023 | 563.42 | 74.25 | 92 | 71 | 0.05
4245923539 | KNJ0223 | 09/04/2023 | 578.98 | 76.27 | 90 | 68 | 0
4245923539 | KNJ0223 | 09/05/2023 | 499.31 | 65.92 | 90 | 64 | 0
4245923539 | KNJ0223 | 09/06/2023 | 508.4 | 67.1 | 94 | 69 | 0
4245923539 | KNJ0223 | 09/07/2023 | 510.83 | 67.42 | 95 | 70
4245923539 | KNJ0223 | 09/08/2023 | 903.27 | 118.4 | 95 | 69 | 0
4245923539 | KNJ0223 | 09/09/2023 | 650.3 | 85.54 | 94 | 64 | 0.48
4245923539 | KNJ0223 | 09/10/2023 | 665.32 | 78.32 | 93 | 71 | Trace Value
4245923539 | KNJ0223 | 09/11/2023 | 613.04 | 72.24 | 92 | 72 | 0
4245923539 | KNJ0223 | 09/12/2023 | 593.55 | 69.98 | 92 | 71 | Trace Value
4245923539 | KNJ0223 | 09/13/2023 | 1163.91 | 136.22 | 92 | 72 | 0.03
4245923539 | KNJ0223 | 09/14/2023 | 695.26 | 81.79 | 91 | 71 | 0.29
4245923539 | KNJ0223 | 09/15/2023 | 634.22 | 74.7 | 88 | 70 | 0
4245923539 | KNJ0223 | 09/16/2023 | 649.08 | 76.43 | 87 | 69 | 0.54
4245923539 | KNJ0223 | 09/17/2023 | 712.96 | 83.85 | 92 | 70 | 0
4245923539 | KNJ0223 | 09/18/2023 | 602.61 | 71.03 | 89 | 68 | 0.08
4245923539 | KNJ0223 | 09/19/2023 | 535.11 | 63.19 | 88 | 64 | 0
4245923539 | KNJ0223 | 09/20/2023 | 556.42 | 65.67 | 88 | 69 | 0
4245923539 | KNJ0223 | 09/21/2023 | 570.51 | 67.3 | 87 | 68 | 0.08
4245923539 | KNJ0223 | 09/22/2023 | 673.66 | 79.28 | 85 | 65 | 0.3
4245923539 | KNJ0223 | 09/23/2023 | 570.31 | 67.28 | 87 | 61 | 0
4245923539 | KNJ0223 | 09/24/2023 | 617.58 | 72.77 | 89 | 59 | 0
4245923539 | KNJ0223 | 09/25/2023 | 698.21 | 82.14 | 90 | 66 | 0
4245923539 | KNJ0223 | 09/26/2023 | 1121.53 | 131.3 | 89 | 71 | 2.11
4245923539 | KNJ0223 | 09/27/2023 | 1586.92 | 185.34 | 88 | 71 | 0.91
4245923539 | KNJ0223 | 09/28/2023 | 1723.72 | 201.23 | 87 | 71 | 0.81
4245923539 | KNJ0223 | 09/29/2023 | 1421.63 | 166.15 | 85 | 71 | 0.02
4245923539 | KNJ0223 | 09/30/2023 | 1648.54 | 192.5 | 85 | 71 | 0.2
4245923539 | KNJ0223 | 10/01/2023 | 2231.76 | 260.23 | 85 | 70 | 2.53
4245923539 | KNJ0223 | 10/02/2023 | 2045.05 | 238.55 | 85 | 69 | 0.56
4245923539 | KNJ0223 | 10/03/2023 | 949.34 | 111.3 | 85 | 70 | 0
4245923539 | KNJ0223 | 10/04/2023 | 830.86 | 97.54 | 86 | 70 | 0.05
4245923539 | KNJ0223 | 10/05/2023 | 751.7 | 88.35 | 86 | 69 | 0
4245923539 | KNJ0223 | 10/06/2023 | 730.68 | 85.91 | 87 | 66 | 0
4245923539 | KNJ0223 | 10/07/2023 | 784.73 | 92.18 | 90 | 56 | 0
4245923539 | KNJ0223 | 10/08/2023 | 821.28 | 96.43 | 82 | 53 | 0
4245923539 | KNJ0223 | 10/09/2023 | 776.56 | 91.23 | 80 | 55 | 0
4245923539 | KNJ0223 | 10/10/2023 | 602.25 | 70.99 | 84 | 56 | 0
4245923539 | KNJ0223 | 10/11/2023 | 646.6 | 82.99 | 84 | 65 | 0
4245923539 | KNJ0223 | 10/12/2023 | 1887.36 | 240.16 | 88 | 72 | 2.8
4245923539 | KNJ0223 | 10/13/2023 | 2085.1 | 265.21 | 89 | 68 | 1.67
4245923539 | KNJ0223 | 10/14/2023 | 1335.93 | 170.31 | 89 | 64 | 0
4245923539 | KNJ0223 | 10/15/2023 | 1199.77 | 153.06 | 82 | 55 | 0
4245923539 | KNJ0223 | 10/16/2023 | 872.2 | 111.57 | 76 | 50 | 0
4245923539 | KNJ0223 | 10/17/2023 | 736.19 | 94.34 | 75 | 49 | 0
4245923539 | KNJ0223 | 10/18/2023 | 709.92 | 91.01 | 77 | 50 | 0
4245923539 | KNJ0223 | 10/19/2023 | 700.78 | 89.86 | 81 | 55 | 0
4245923539 | KNJ0223 | 10/20/2023 | 679.8 | 87.2 | 83 | 55 | 0
4245923539 | KNJ0223 | 10/21/2023 | 693.57 | 88.94 | 83 | 55 | 0
4245923539 | KNJ0223 | 10/22/2023 | 754.41 | 96.65 | 86 | 52 | 0
4245923539 | KNJ0223 | 10/23/2023 | 631.28 | 81.05 | 83 | 58 | 0
4245923539 | KNJ0223 | 10/24/2023 | 574.56 | 73.87 | 82 | 67 | 0
4245923539 | KNJ0223 | 10/25/2023 | 594.01 | 76.33 | 82 | 68 | 0
4245923539 | KNJ0223 | 10/26/2023 | 583.47 | 75 | 82 | 65 | 0
4245923539 | KNJ0223 | 10/27/2023 | 563.81 | 72.51 | 83 | 64 | 0
4245923539 | KNJ0223 | 10/28/2023 | 614.12 | 78.88 | 84 | 62 | 0
4245923539 | KNJ0223 | 10/29/2023 | 661.4 | 84.87 | 84 | 61 | 0
4245923539 | KNJ0223 | 10/30/2023 | 566.53 | 72.85 | 85 | 60 | 0
4245923539 | KNJ0223 | 10/31/2023 | 540.46 | 69.55 | 84 | 58 | 0
4245923539 | KNJ0223 | 11/01/2023 | 580.06 | 74.56 | 76 | 53 | 0
4245923539 | KNJ0223 | 11/02/2023 | 560.92 | 72.14 | 75 | 53 | 0
4245923539 | KNJ0223 | 11/03/2023 | 550.04 | 70.76 | 79 | 59 | 0
4245923539 | KNJ0223 | 11/04/2023 | 614.96 | 78.99 | 79 | 55 | 0
4245923539 | KNJ0223 | 11/05/2023 | 674.05 | 86.47 | 80 | 51 | 0
4245923539 | KNJ0223 | 11/06/2023 | 573.8 | 73.77 | 81 | 48 | 0
4245923539 | KNJ0223 | 11/07/2023 | 658.48 | 84.5 | 83 | 53 | 0
4245923539 | KNJ0223 | 11/08/2023 | 563.69 | 72.49 | 84 | 50 | 0
4245923539 | KNJ0223 | 11/09/2023 | 539.27 | 68.38 | 85 | 55 | 0
4245923539 | KNJ0223 | 11/10/2023 | 545.98 | 69.22 | 86 | 60 | 0
4245923539 | KNJ0223 | 11/11/2023 | 577.93 | 73.2 | 83 | 65 | 0.33
4245923539 | KNJ0223 | 11/12/2023 | 632.51 | 80.01 | 80 | 63 | 0
4245923539 | KNJ0223 | 11/13/2023 | 565.21 | 71.62 | 77 | 62 | 0
4245923539 | KNJ0223 | 11/14/2023 | 568.06 | 71.97 | 77 | 61 | 0.12
4245923539 | KNJ0223 | 11/15/2023 | 592.49 | 75.02 | 77 | 64 | 0.05
4245923539 | KNJ0223 | 11/16/2023 | 981.98 | 123.62 | 78 | 62 | 0.16
4245923539 | KNJ0223 | 11/17/2023 | 2336.34 | 292.61 | 79 | 61 | 2.1
4245923539 | KNJ0223 | 11/18/2023 | 1221.08 | 153.45 | 78 | 55 | 0.66
4245923539 | KNJ0223 | 11/19/2023 | 956.53 | 120.44 | 80 | 56 | 0
4245923539 | KNJ0223 | 11/20/2023 | 786.83 | 99.27 | 79 | 59 | 0.02
4245923539 | KNJ0223 | 11/21/2023 | 715.43 | 90.36 | 81 | 52 | 0.02
4245923539 | KNJ0223 | 11/22/2023 | 732.22 | 92.45 | 81 | 47 | 0
4245923539 | KNJ0223 | 11/23/2023 | 939.31 | 118.29 | 73 | 48 | 0.01
4245923539 | KNJ0223 | 11/24/2023 | 672.63 | 85.02 | 75 | 52 | 0.01
4245923539 | KNJ0223 | 11/25/2023 | 679.28 | 85.85 | 75 | 53 | 0.07
4245923539 | KNJ0223 | 11/26/2023 | 1059.81 | 133.33 | 75 | 55 | 0.01
4245923539 | KNJ0223 | 11/27/2023 | 753.17 | 95.07 | 74 | 44 | 0.55
4245923539 | KNJ0223 | 11/28/2023 | 685.17 | 86.58 | 69 | 39 | 0
4245923539 | KNJ0223 | 11/29/2023 | 649.41 | 82.12 | 68 | 36 | 0
4245923539 | KNJ0223 | 11/30/2023 | 634.56 | 80.27 | 86 | 41 | 0
4245923539 | KNJ0223 | 12/01/2023 | 611.47 | 77.39 | 82 | 55 | 0
4245923539 | KNJ0223 | 12/02/2023 | 651.88 | 82.43 | 83 | 64 | 0
4245923539 | KNJ0223 | 12/03/2023 | 1091.79 | 137.32 | 82 | 62 | 0.02
4245923539 | KNJ0223 | 12/04/2023 | 787.39 | 99.34 | 79 | 51 | 0.23
4245923539 | KNJ0223 | 12/05/2023 | 671.84 | 84.92 | 72 | 47 | 0
4245923539 | KNJ0223 | 12/06/2023 | 722.36 | 91.22 | 69 | 41 | 0
4245923539 | KNJ0223 | 12/07/2023 | 598.58 | 75.78 | 67 | 41 | 0
4245923539 | KNJ0223 | 12/08/2023 | 588.92 | 71.29 | 74 | 47 | 0
4245923539 | KNJ0223 | 12/09/2023 | 628.23 | 75.99 | 82 | 56 | 0.04
4245923539 | KNJ0223 | 12/10/2023 | 732.78 | 88.47 | 83 | 44 | 0
4245923539 | KNJ0223 | 12/11/2023 | 644.59 | 77.94 | 67 | 43 | 0.25
4245923539 | KNJ0223 | 12/12/2023 | 589.78 | 71.4 | 71 | 43 | 0
4245923539 | KNJ0223 | 12/13/2023 | 566.58 | 68.63 | 73 | 58 | 0
4245923539 | KNJ0223 | 12/14/2023 | 681.66 | 82.37 | 72 | 59 | 0.66
4245923539 | KNJ0223 | 12/15/2023 | 634.36 | 76.72 | 72 | 60 | 0.07
4245923539 | KNJ0223 | 12/16/2023 | 1017.08 | 122.41 | 73 | 58 | 0.11
4245923539 | KNJ0223 | 12/17/2023 | 2230.56 | 267.29 | 74 | 48 | 4.04
4245923539 | KNJ0223 | 12/18/2023 | 1479.6 | 177.63 | 68 | 40 | 0.05
4245923539 | KNJ0223 | 12/19/2023 | 946.87 | 114.03 | 65 | 41 | 0
4245923539 | KNJ0223 | 12/20/2023 | 867.88 | 104.6 | 66 | 44 | 0
4245923539 | KNJ0223 | 12/21/2023 | 792.78 | 95.63 | 68 | 46 | 0
4245923539 | KNJ0223 | 12/22/2023 | 746.13 | 90.06 | 70 | 49 | 0
4245923539 | KNJ0223 | 12/23/2023 | 852.12 | 102.72 | 73 | 53 | 0
4245923539 | KNJ0223 | 12/24/2023 | 938.74 | 113.06 | 73 | 53 | 0
4245923539 | KNJ0223 | 12/25/2023 | 896.18 | 107.98 | 73 | 60 | 0.09
4245923539 | KNJ0223 | 12/26/2023 | 827.18 | 99.74 | 74 | 54 | 0.1
4245923539 | KNJ0223 | 12/27/2023 | 754.87 | 91.11 | 71 | 49 | 0
4245923539 | KNJ0223 | 12/28/2023 | 773.7 | 93.35 | 66 | 44 | 0.04
4245923539 | KNJ0223 | 12/29/2023 | 709.18 | 85.65 | 55 | 46 | 0
4245923539 | KNJ0223 | 12/30/2023 | 729.12 | 88.03 | 59 | 37 | 0
4245923539 | KNJ0223 | 12/31/2023 | 791.51 | 95.48 | 63 | 36 | 0
|  | Yearly Daily Average: | 652.7503 | 83.077
|  | Wetter Months' Daily Average: | 817.3766 | 100.6919

## 32-2 MPS
Daily Billed Information (PS 32-2 - 92 Wellington Drive: 2023 Reading Data)
Bill Account | Meter Number | Date | Consumption Recorded (kWh/day) | Estimated Cost ($/day) | Avg. High Temperature (°F) | Avg. Low Temperature (°F) | Rain Recorded by NOAA (inches)
9996767175 | KJ17787 | 2023-01-01 | 39.17 | 5.09 | 79 | 58 | 0.04
9996767175 | KJ17787 | 2023-01-02 | 40.81 | 5.29 | 78 | 53 | 0
9996767175 | KJ17787 | 2023-01-03 | 38.13 | 4.97 | 81 | 51 | 0
9996767175 | KJ17787 | 2023-01-04 | 36.54 | 4.78 | 83 | 57 | 0
9996767175 | KJ17787 | 2023-01-05 | 36.66 | 4.79 | 77 | 46 | 0.04
9996767175 | KJ17787 | 2023-01-06 | 35.74 | 4.68 | 68 | 41 | 0
9996767175 | KJ17787 | 2023-01-07 | 38.1 | 4.96 | 70 | 38 | 0
9996767175 | KJ17787 | 2023-01-08 | 38.21 | 4.98 | 76 | 42 | 0
9996767175 | KJ17787 | 2023-01-09 | 36.02 | 4.71 | 74 | 47 | 0
9996767175 | KJ17787 | 2023-01-10 | 34.16 | 4.49 | 71 | 42 | 0
9996767175 | KJ17787 | 2023-01-11 | 33.68 | 4.43 | 73 | 38 | 0
9996767175 | KJ17787 | 2023-01-12 | 33.43 | 4.4 | 80 | 44 | 0
9996767175 | KJ17787 | 2023-01-13 | 33.12 | 4.37 | 71 | 35 | 0.12
9996767175 | KJ17787 | 2023-01-14 | 35.25 | 4.62 | 61 | 30 | 0
9996767175 | KJ17787 | 2023-01-15 | 37.08 | 4.84 | 63 | 30 | 0
9996767175 | KJ17787 | 2023-01-16 | 41.74 | 5.4 | 71 | 30 | 0
9996767175 | KJ17787 | 2023-01-17 | 35.33 | 4.63 | 75 | 34 | 0
9996767175 | KJ17787 | 2023-01-18 | 32.69 | 4.51 | 79 | 46 | N/A
9996767175 | KJ17787 | 2023-01-19 | 34.83 | 4.78 | 82 | 54 | 0
9996767175 | KJ17787 | 2023-01-20 | 32.94 | 4.54 | 76 | 49 | 0
9996767175 | KJ17787 | 2023-01-21 | 37.21 | 5.07 | 76 | 47 | T
9996767175 | KJ17787 | 2023-01-22 | 46 | 6.17 | 82 | 54 | 0.33
9996767175 | KJ17787 | 2023-01-23 | 39.91 | 5.41 | 75 | 44 | 0.05
9996767175 | KJ17787 | 2023-01-24 | 38.98 | 5.29 | 76 | 41 | 0
9996767175 | KJ17787 | 2023-01-25 | 40.34 | 5.46 | 85 | 43 | 0
9996767175 | KJ17787 | 2023-01-26 | 39.27 | 5.33 | 72 | 38 | 0.09
9996767175 | KJ17787 | 2023-01-27 | 37.22 | 5.07 | 62 | 37 | 0
9996767175 | KJ17787 | 2023-01-28 | 38.05 | 5.18 | 69 | 35 | 0
9996767175 | KJ17787 | 2023-01-29 | 38.78 | 5.27 | 78 | 55 | 0
9996767175 | KJ17787 | 2023-01-30 | 38.04 | 5.18 | 86 | 58 | 0
9996767175 | KJ17787 | 2023-01-31 | 37.39 | 5.09 | 83 | 59 | 0
9996767175 | KJ17787 | 2023-02-01 | 33.79 | 4.65 | 82 | 58 | 0
9996767175 | KJ17787 | 2023-02-02 | 35.61 | 4.87 | 82 | 57 | 0
9996767175 | KJ17787 | 2023-02-03 | 37.71 | 5.13 | 78 | 50 | 0
9996767175 | KJ17787 | 2023-02-04 | 38.03 | 5.17 | 70 | 47 | 0.17
9996767175 | KJ17787 | 2023-02-05 | 42.26 | 5.7 | 73 | 48 | 0
9996767175 | KJ17787 | 2023-02-06 | 39.2 | 5.32 | 71 | 46 | 0.01
9996767175 | KJ17787 | 2023-02-07 | 37.1 | 5.06 | 76 | 44
9996767175 | KJ17787 | 2023-02-08 | 36.41 | 4.97 | 79 | 49 | 0
9996767175 | KJ17787 | 2023-02-09 | 34.86 | 4.78 | 83 | 58 | 0
9996767175 | KJ17787 | 2023-02-10 | 36.05 | 4.93 | 85 | 46 | 0.16
9996767175 | KJ17787 | 2023-02-11 | 37.73 | 5.14 | 79 | 40 | 0.57
9996767175 | KJ17787 | 2023-02-12 | 42.97 | 5.79 | 71 | 40 | 0.12
9996767175 | KJ17787 | 2023-02-13 | 38.19 | 5.19 | 71 | 40 | Trace Value
9996767175 | KJ17787 | 2023-02-14 | 45.65 | 6.13 | 75 | 39 | 0
9996767175 | KJ17787 | 2023-02-15 | 35.71 | 4.88 | 82 | 50 | 0
9996767175 | KJ17787 | 2023-02-16 | 36.55 | 4.99 | 85 | 57 | 0
9996767175 | KJ17787 | 2023-02-17 | 34.89 | 4.78 | 89 | 45
9996767175 | KJ17787 | 2023-02-18 | 35.46 | 4.85 | 67 | 46 | 0.04
9996767175 | KJ17787 | 2023-02-19 | 38.42 | 5.22 | 80 | 48 | 0
9996767175 | KJ17787 | 2023-02-20 | 36.32 | 4.96 | 82 | 53 | 0
9996767175 | KJ17787 | 2023-02-21 | 35.69 | 4.88 | 85 | 57 | 0
9996767175 | KJ17787 | 2023-02-22 | 34.3 | 4.71 | 87 | 58 | 0
9996767175 | KJ17787 | 2023-02-23 | 35.27 | 4.83 | 89 | 60 | 0
9996767175 | KJ17787 | 2023-02-24 | 34.05 | 4.68 | 87 | 58 | 0
9996767175 | KJ17787 | 2023-02-25 | 35.8 | 4.9 | 87 | 58
9996767175 | KJ17787 | 2023-02-26 | 39.11 | 5.31 | 87 | 56 | 0
9996767175 | KJ17787 | 2023-02-27 | 35.74 | 4.89 | 87 | 57 | 0
9996767175 | KJ17787 | 2023-02-28 | 32.14 | 4.44 | 87 | 57 | 0
9996767175 | KJ17787 | 2023-03-01 | 30.28 | 4.21 | 86 | 58 | 0
9996767175 | KJ17787 | 2023-03-02 | 30.4 | 4.22 | 87 | 56 | 0
9996767175 | KJ17787 | 2023-03-03 | 32.2 | 4.45 | 90 | 55 | 0
9996767175 | KJ17787 | 2023-03-04 | 33.43 | 4.6 | 88 | 52 | 0
9996767175 | KJ17787 | 2023-03-05 | 34.73 | 4.76 | 81 | 54 | 0.05
9996767175 | KJ17787 | 2023-03-06 | 32.19 | 4.45 | 84 | 56 | 0
9996767175 | KJ17787 | 2023-03-07 | 33.43 | 4.6 | 87 | 56
9996767175 | KJ17787 | 2023-03-08 | 30.73 | 4.26 | 85 | 58 | 0
9996767175 | KJ17787 | 2023-03-09 | 29.62 | 4.13 | 80 | 51 | 0
9996767175 | KJ17787 | 2023-03-10 | 31.8 | 4.4 | 85 | 54
9996767175 | KJ17787 | 2023-03-11 | 34.68 | 4.76 | 81 | 51 | 1.3
9996767175 | KJ17787 | 2023-03-12 | 32.62 | 4.5 | 86 | 48 | 0
9996767175 | KJ17787 | 2023-03-13 | 43.57 | 5.87 | 81 | 46 | 1.17
9996767175 | KJ17787 | 2023-03-14 | 40.15 | 5.44 | 70 | 43 | 0.6
9996767175 | KJ17787 | 2023-03-15 | 45.12 | 6.06 | 68 | 43 | 0
9996767175 | KJ17787 | 2023-03-16 | 36.34 | 4.96 | 77 | 37 | 0
9996767175 | KJ17787 | 2023-03-17 | 34.93 | 5.23 | 84 | 48
9996767175 | KJ17787 | 2023-03-18 | 35.75 | 5.34 | 80 | 45 | 0
9996767175 | KJ17787 | 2023-03-19 | 36.02 | 5.38 | 68 | 43 | 0.02
9996767175 | KJ17787 | 2023-03-20 | 35.79 | 5.35 | 69 | 42 | 0.02
9996767175 | KJ17787 | 2023-03-21 | 33.97 | 5.1 | 77 | 42 | 0
9996767175 | KJ17787 | 2023-03-22 | 33.05 | 4.97 | 80 | 53 | 0.08
9996767175 | KJ17787 | 2023-03-23 | 32.23 | 4.86 | 83 | 53
9996767175 | KJ17787 | 2023-03-24 | 31.69 | 4.79 | 86 | 53 | 0
9996767175 | KJ17787 | 2023-03-25 | 33.4 | 5.02 | 91 | 60 | 0
9996767175 | KJ17787 | 2023-03-26 | 34.66 | 5.19 | 91 | 63 | 0.68
9996767175 | KJ17787 | 2023-03-27 | 32.99 | 4.97 | 92 | 62 | 0
9996767175 | KJ17787 | 2023-03-28 | 29.68 | 4.51 | 88 | 55 | Trace Value
9996767175 | KJ17787 | 2023-03-29 | 31.18 | 4.72 | 75 | 55 | 0
9996767175 | KJ17787 | 2023-03-30 | 32.94 | 4.96 | 79 | 51 | 0
9996767175 | KJ17787 | 2023-03-31 | 30.21 | 4.58 | 85 | 55 | 0
9996767175 | KJ17787 | 2023-04-01 | 32.92 | 4.96 | 90 | 60 | 0
9996767175 | KJ17787 | 2023-04-02 | 33.34 | 5.01 | 85 | 60
9996767175 | KJ17787 | 2023-04-03 | 31.11 | 4.71 | 86 | 61 | 0
9996767175 | KJ17787 | 2023-04-04 | 30.48 | 4.62 | 88 | 60 | Trace Value
9996767175 | KJ17787 | 2023-04-05 | 30.03 | 4.56 | 87 | 63 | 0
9996767175 | KJ17787 | 2023-04-06 | 31.9 | 4.82 | 87 | 64 | 0
9996767175 | KJ17787 | 2023-04-07 | 30.41 | 4.61 | 85 | 64
9996767175 | KJ17787 | 2023-04-08 | 32.91 | 4.96 | 86 | 62
9996767175 | KJ17787 | 2023-04-09 | 32.78 | 4.94 | 80 | 60 | 0.01
9996767175 | KJ17787 | 2023-04-10 | 39.03 | 5.79 | 79 | 58 | 0.68
9996767175 | KJ17787 | 2023-04-11 | 42.44 | 6.26 | 78 | 58 | 1.38
9996767175 | KJ17787 | 2023-04-12 | 39.01 | 5.79 | 79 | 59 | 0.03
9996767175 | KJ17787 | 2023-04-13 | 53.59 | 7.79 | 87 | 61 | 0.07
9996767175 | KJ17787 | 2023-04-14 | 68.4 | 9.81 | 86 | 59 | 0.57
9996767175 | KJ17787 | 2023-04-15 | 66.5 | 9.55 | 87 | 60 | 0.02
9996767175 | KJ17787 | 2023-04-16 | 71.76 | 10.27 | 88 | 59 | 0
9996767175 | KJ17787 | 2023-04-17 | 52.64 | 7.66 | 81 | 50 | 0.04
9996767175 | KJ17787 | 2023-04-18 | 48.84 | 6.97 | 81 | 46 | 0.02
9996767175 | KJ17787 | 2023-04-19 | 49.46 | 7.05 | 82 | 50 | 0
9996767175 | KJ17787 | 2023-04-20 | 46.41 | 6.65 | 84 | 55 | 0
9996767175 | KJ17787 | 2023-04-21 | 44.97 | 6.46 | 87 | 59
9996767175 | KJ17787 | 2023-04-22 | 45.48 | 6.52 | 89 | 57 | 0.3
9996767175 | KJ17787 | 2023-04-23 | 51.12 | 7.27 | 84 | 53 | 0.42
9996767175 | KJ17787 | 2023-04-24 | 44.95 | 6.45 | 80 | 55 | 0
9996767175 | KJ17787 | 2023-04-25 | 45.61 | 6.54 | 82 | 61 | 0.25
9996767175 | KJ17787 | 2023-04-26 | 36.79 | 5.37 | 84 | 62 | 0.07
9996767175 | KJ17787 | 2023-04-27 | 49.85 | 7.1 | 86 | 63 | 0
9996767175 | KJ17787 | 2023-04-28 | 64.13 | 9 | 87 | 62 | 1.62
9996767175 | KJ17787 | 2023-04-29 | 56.27 | 7.96 | 88 | 62 | 0
9996767175 | KJ17787 | 2023-04-30 | 60.39 | 8.5 | 85 | 57 | 0.52
9996767175 | KJ17787 | 2023-05-01 | 50.92 | 7.25 | 85 | 56 | 0
9996767175 | KJ17787 | 2023-05-02 | 49.29 | 7.03 | 87 | 56 | 0
9996767175 | KJ17787 | 2023-05-03 | 43.5 | 6.26 | 86 | 53 | 0
9996767175 | KJ17787 | 2023-05-04 | 42.75 | 6.16 | 84 | 53 | 0
9996767175 | KJ17787 | 2023-05-05 | 41.5 | 5.99 | 87 | 57 | 0
9996767175 | KJ17787 | 2023-05-06 | 44.55 | 6.4 | 86 | 65 | 0
9996767175 | KJ17787 | 2023-05-07 | 45.06 | 6.47 | 88 | 61 | 0.02
9996767175 | KJ17787 | 2023-05-08 | 40.95 | 5.92 | 87 | 55 | 0
9996767175 | KJ17787 | 2023-05-09 | 39.33 | 5.71 | 91 | 63 | 0
9996767175 | KJ17787 | 2023-05-10 | 39.1 | 5.68 | 92 | 66 | 0
9996767175 | KJ17787 | 2023-05-11 | 38.95 | 5.66 | 88 | 67 | 0.04
9996767175 | KJ17787 | 2023-05-12 | 38.76 | 5.63 | 86 | 66 | 0
9996767175 | KJ17787 | 2023-05-13 | 39.4 | 5.71 | 85 | 64 | 0
9996767175 | KJ17787 | 2023-05-14 | 39.09 | 5.67 | 86 | 63 | 0
9996767175 | KJ17787 | 2023-05-15 | 42.43 | 6.12 | 89 | 62 | 0
9996767175 | KJ17787 | 2023-05-16 | 33.75 | 4.97 | 88 | 64 | 0
9996767175 | KJ17787 | 2023-05-17 | 33.76 | 4.95 | 92 | 67 | 0
9996767175 | KJ17787 | 2023-05-18 | 34.93 | 5.11 | 89 | 65 | 1.24
9996767175 | KJ17787 | 2023-05-19 | 35.48 | 5.18 | 88 | 66 | 0.02
9996767175 | KJ17787 | 2023-05-20 | 34.99 | 5.12 | 88 | 66 | 0
9996767175 | KJ17787 | 2023-05-21 | 34.92 | 5.11 | 88 | 67
9996767175 | KJ17787 | 2023-05-22 | 38.81 | 5.62 | 88 | 67 | 0.65
9996767175 | KJ17787 | 2023-05-23 | 42.93 | 6.17 | 85 | 67 | 0.56
9996767175 | KJ17787 | 2023-05-24 | 54.88 | 7.75 | 83 | 66 | 0.12
9996767175 | KJ17787 | 2023-05-25 | 50.57 | 7.18 | 83 | 66 | 0.16
9996767175 | KJ17787 | 2023-05-26 | 44.82 | 6.42 | 82 | 62 | 0.05
9996767175 | KJ17787 | 2023-05-27 | 47.47 | 6.77 | 81 | 56 | Trace Value
9996767175 | KJ17787 | 2023-05-28 | 43.87 | 6.29 | 85 | 55 | 0
9996767175 | KJ17787 | 2023-05-29 | 43.84 | 6.29 | 87 | 60 | 0
9996767175 | KJ17787 | 2023-05-30 | 41.82 | 6.02 | 88 | 62 | 0
9996767175 | KJ17787 | 2023-05-31 | 40.34 | 5.83 | 87 | 68 | 0
9996767175 | KJ17787 | 2023-06-01 | 42.39 | 6.1 | 85 | 68 | 0
9996767175 | KJ17787 | 2023-06-02 | 40.14 | 5.8 | 85 | 67 | 0
9996767175 | KJ17787 | 2023-06-03 | 40.72 | 5.88 | 84 | 67 | 0
9996767175 | KJ17787 | 2023-06-04 | 39.87 | 5.76 | 84 | 66 | 0
9996767175 | KJ17787 | 2023-06-05 | 39.11 | 5.66 | 84 | 64 | 0.3
9996767175 | KJ17787 | 2023-06-06 | 37.64 | 5.47 | 88 | 62
9996767175 | KJ17787 | 2023-06-07 | 45.51 | 6.51 | 91 | 68 | 0
9996767175 | KJ17787 | 2023-06-08 | 49.73 | 7.07 | 92 | 68 | 1.64
9996767175 | KJ17787 | 2023-06-09 | 50.58 | 7.18 | 92 | 68 | 0
9996767175 | KJ17787 | 2023-06-10 | 52.39 | 7.42 | 88 | 67 | 0.54
9996767175 | KJ17787 | 2023-06-11 | 52.65 | 7.46 | 91 | 69 | 0.09
9996767175 | KJ17787 | 2023-06-12 | 59.55 | 8.37 | 94 | 69 | 0
9996767175 | KJ17787 | 2023-06-13 | 48.72 | 6.94 | 95 | 71
9996767175 | KJ17787 | 2023-06-14 | 58.98 | 8.3 | 95 | 71 | 0
9996767175 | KJ17787 | 2023-06-15 | 48.87 | 6.96 | 95 | 66 | 0.44
9996767175 | KJ17787 | 2023-06-16 | 54.23 | 7.44 | 95 | 68 | 0.45
9996767175 | KJ17787 | 2023-06-17 | 60.61 | 8.26 | 93 | 68 | 0.91
9996767175 | KJ17787 | 2023-06-18 | 59.77 | 8.15 | 94 | 68 | 0.28
9996767175 | KJ17787 | 2023-06-19 | 73.28 | 9.89 | 93 | 70 | 0.63
9996767175 | KJ17787 | 2023-06-20 | 79.49 | 10.69 | 91 | 69 | 0.46
9996767175 | KJ17787 | 2023-06-21 | 73.4 | 9.91 | 91 | 71 | 0.24
9996767175 | KJ17787 | 2023-06-22 | 67.48 | 9.14 | 93 | 66 | 0.04
9996767175 | KJ17787 | 2023-06-23 | 77.5 | 10.43 | 91 | 69 | 0.35
9996767175 | KJ17787 | 2023-06-24 | 72.84 | 9.83 | 92 | 70 | 0.24
9996767175 | KJ17787 | 2023-06-25 | 65.24 | 8.85 | 91 | 70 | 0.15
9996767175 | KJ17787 | 2023-06-26 | 59.24 | 8.08 | 94 | 70 | 0
9996767175 | KJ17787 | 2023-06-27 | 57.16 | 7.81 | 97 | 71 | 0
9996767175 | KJ17787 | 2023-06-28 | 55.61 | 7.61 | 95 | 72 | 0
9996767175 | KJ17787 | 2023-06-29 | 53.25 | 7.31 | 95 | 71 | 0.88
9996767175 | KJ17787 | 2023-06-30 | 50.35 | 6.94 | 94 | 71 | 0
9996767175 | KJ17787 | 2023-07-01 | 52.11 | 7.16 | 94 | 71 | 0
9996767175 | KJ17787 | 2023-07-02 | 47.59 | 6.58 | 95 | 71 | 0
9996767175 | KJ17787 | 2023-07-03 | 50.71 | 6.98 | 97 | 72 | 0
9996767175 | KJ17787 | 2023-07-04 | 50.36 | 6.94 | 95 | 73 | 0
9996767175 | KJ17787 | 2023-07-05 | 49.86 | 6.87 | 95 | 74 | 0
9996767175 | KJ17787 | 2023-07-06 | 49.5 | 6.83 | 96 | 73 | 0.04
9996767175 | KJ17787 | 2023-07-07 | 48.7 | 6.72 | 95 | 73 | 0.03
9996767175 | KJ17787 | 2023-07-08 | 49.82 | 6.87 | 94 | 74 | 0.31
9996767175 | KJ17787 | 2023-07-09 | 47.32 | 6.55 | 96 | 74 | 0.2
9996767175 | KJ17787 | 2023-07-10 | 45.8 | 6.35 | 96 | 74 | 0
9996767175 | KJ17787 | 2023-07-11 | 46.86 | 6.49 | 94 | 73 | 0.78
9996767175 | KJ17787 | 2023-07-12 | 45.59 | 6.32 | 94 | 73 | 0.1
9996767175 | KJ17787 | 2023-07-13 | 43.47 | 6.05 | 94 | 72 | Trace Value
9996767175 | KJ17787 | 2023-07-14 | 52.72 | 7.24 | 95 | 73 | 0.33
9996767175 | KJ17787 | 2023-07-15 | 59.24 | 8.08 | 96 | 73 | 0.12
9996767175 | KJ17787 | 2023-07-16 | 71.05 | 9.6 | 96 | 74 | 0.15
9996767175 | KJ17787 | 2023-07-17 | 53.55 | 7.35 | 95 | 74 | 2.8
9996767175 | KJ17787 | 2023-07-18 | 56.98 | 7.83 | 95 | 72 | 0.22
9996767175 | KJ17787 | 2023-07-19 | 51.28 | 7.1 | 95 | 71 | 0.14
9996767175 | KJ17787 | 2023-07-20 | 57.1 | 7.85 | 96 | 73 | 0
9996767175 | KJ17787 | 2023-07-21 | 47.01 | 6.55 | 99 | 74 | 0
9996767175 | KJ17787 | 2023-07-22 | 60.6 | 8.3 | 97 | 75 | 0
9996767175 | KJ17787 | 2023-07-23 | 70.33 | 9.55 | 94 | 71 | 0.7
9996767175 | KJ17787 | 2023-07-24 | 62.01 | 8.48 | 93 | 73 | 1.12
9996767175 | KJ17787 | 2023-07-25 | 59.62 | 8.17 | 93 | 73 | 0.3
9996767175 | KJ17787 | 2023-07-26 | 56.66 | 7.79 | 92 | 73 | 0
9996767175 | KJ17787 | 2023-07-27 | 54.02 | 7.45 | 91 | 73 | 0
9996767175 | KJ17787 | 2023-07-28 | 55.45 | 7.64 | 92 | 73 | 1
9996767175 | KJ17787 | 2023-07-29 | 61.66 | 8.44 | 93 | 73 | 0.05
9996767175 | KJ17787 | 2023-07-30 | 89.15 | 11.98 | 95 | 74 | Trace Value
9996767175 | KJ17787 | 2023-07-31 | 96.56 | 12.93 | 95 | 71 | 0.74
9996767175 | KJ17787 | 2023-08-01 | 80.58 | 10.87 | 95 | 71 | 0.08
9996767175 | KJ17787 | 2023-08-02 | 72.86 | 9.88 | 93 | 74 | 0
9996767175 | KJ17787 | 2023-08-03 | 68.22 | 9.28 | 91 | 73 | 0
9996767175 | KJ17787 | 2023-08-04 | 63.19 | 8.63 | 94 | 73 | 0
9996767175 | KJ17787 | 2023-08-05 | 65.21 | 8.89 | 94 | 73 | 0.17
9996767175 | KJ17787 | 2023-08-06 | 72.32 | 9.81 | 95 | 74 | 0.66
9996767175 | KJ17787 | 2023-08-07 | 76.62 | 10.36 | 97 | 75 | 0.03
9996767175 | KJ17787 | 2023-08-08 | 67.37 | 9.17 | 99 | 75 | 0
9996767175 | KJ17787 | 2023-08-09 | 63.49 | 8.67 | 99 | 74 | 0
9996767175 | KJ17787 | 2023-08-10 | 62.47 | 8.54 | 100 | 75 | 0.16
9996767175 | KJ17787 | 2023-08-11 | 55.58 | 7.65 | 99 | 75 | 0
9996767175 | KJ17787 | 2023-08-12 | 56 | 7.71 | 98 | 76 | 0.25
9996767175 | KJ17787 | 2023-08-13 | 56.35 | 7.75 | 97 | 74 | 0
9996767175 | KJ17787 | 2023-08-14 | 51.46 | 7.12 | 97 | 76 | 0
9996767175 | KJ17787 | 2023-08-15 | 60.69 | 8.31 | 97 | 75 | 0
9996767175 | KJ17787 | 2023-08-16 | 51.4 | 7.11 | 96 | 73 | 0.09
9996767175 | KJ17787 | 2023-08-17 | 57.04 | 7.83 | 93 | 72 | 0.36
9996767175 | KJ17787 | 2023-08-18 | 59.3 | 8.12 | 93 | 73 | 1.09
9996767175 | KJ17787 | 2023-08-19 | 60.87 | 8.32 | 93 | 72 | 0.69
9996767175 | KJ17787 | 2023-08-20 | 65.36 | 8.9 | 92 | 75 | 0
9996767175 | KJ17787 | 2023-08-21 | 57.88 | 7.93 | 92 | 74 | 0
9996767175 | KJ17787 | 2023-08-22 | 56.64 | 7.78 | 93 | 72 | 0
9996767175 | KJ17787 | 2023-08-23 | 52 | 7.18 | 93 | 74 | 0
9996767175 | KJ17787 | 2023-08-24 | 50.56 | 6.99 | 93 | 74 | 0.99
9996767175 | KJ17787 | 2023-08-25 | 49.76 | 6.89 | 92 | 71 | 0
9996767175 | KJ17787 | 2023-08-26 | 50.52 | 6.99 | 95 | 73 | 0
9996767175 | KJ17787 | 2023-08-27 | 50.1 | 6.93 | 95 | 72
9996767175 | KJ17787 | 2023-08-28 | 47.39 | 6.58 | 96 | 74 | Trace Value
9996767175 | KJ17787 | 2023-08-29 | 50.8 | 7.02 | 95 | 74 | 0
9996767175 | KJ17787 | 2023-08-30 | 54.45 | 7.49 | 94 | 74 | 0.93
9996767175 | KJ17787 | 2023-08-31 | 52.39 | 7.23 | 94 | 74 | 0.05
9996767175 | KJ17787 | 2023-09-01 | 48.25 | 6.69 | 92 | 73 | 0
9996767175 | KJ17787 | 2023-09-02 | 50.49 | 6.98 | 91 | 72
9996767175 | KJ17787 | 2023-09-03 | 47.05 | 6.54 | 92 | 71 | 0.05
9996767175 | KJ17787 | 2023-09-04 | 47.17 | 6.56 | 90 | 68 | 0
9996767175 | KJ17787 | 2023-09-05 | 46.26 | 6.44 | 90 | 64 | 0
9996767175 | KJ17787 | 2023-09-06 | 44.99 | 6.28 | 94 | 69 | 0
9996767175 | KJ17787 | 2023-09-07 | 43.66 | 6.1 | 95 | 70
9996767175 | KJ17787 | 2023-09-08 | 102.02 | 13.62 | 95 | 69 | 0
9996767175 | KJ17787 | 2023-09-09 | 69.5 | 9.43 | 94 | 64 | 0.48
9996767175 | KJ17787 | 2023-09-10 | 65.09 | 8.86 | 93 | 71 | Trace Value
9996767175 | KJ17787 | 2023-09-11 | 62.44 | 8.52 | 92 | 72 | 0
9996767175 | KJ17787 | 2023-09-12 | 67.93 | 9.23 | 92 | 71 | Trace Value
9996767175 | KJ17787 | 2023-09-13 | 130.5 | 17.29 | 92 | 72 | 0.03
9996767175 | KJ17787 | 2023-09-14 | 97.76 | 13.07 | 91 | 71 | 0.29
9996767175 | KJ17787 | 2023-09-15 | 69.4 | 9.42 | 88 | 70 | 0
9996767175 | KJ17787 | 2023-09-16 | 65.81 | 8.97 | 87 | 69 | 0.54
9996767175 | KJ17787 | 2023-09-17 | 65.46 | 8.92 | 92 | 70 | 0
9996767175 | KJ17787 | 2023-09-18 | 58.94 | 8.08 | 89 | 68 | 0.08
9996767175 | KJ17787 | 2023-09-19 | 55.17 | 7.59 | 88 | 64 | 0
9996767175 | KJ17787 | 2023-09-20 | 54.5 | 7.5 | 88 | 69 | 0
9996767175 | KJ17787 | 2023-09-21 | 50.97 | 7.05 | 87 | 68 | 0.08
9996767175 | KJ17787 | 2023-09-22 | 48.37 | 6.71 | 85 | 65 | 0.3
9996767175 | KJ17787 | 2023-09-23 | 49.9 | 6.91 | 87 | 61 | 0
9996767175 | KJ17787 | 2023-09-24 | 48.44 | 6.72 | 89 | 59 | 0
9996767175 | KJ17787 | 2023-09-25 | 66.52 | 9.06 | 90 | 66 | 0
9996767175 | KJ17787 | 2023-09-26 | 151.85 | 20.09 | 89 | 71 | 2.11
9996767175 | KJ17787 | 2023-09-27 | 177.81 | 23.44 | 88 | 71 | 0.91
9996767175 | KJ17787 | 2023-09-28 | 181.2 | 23.88 | 87 | 71 | 0.81
9996767175 | KJ17787 | 2023-09-29 | 125.9 | 16.73 | 85 | 71 | 0.02
9996767175 | KJ17787 | 2023-09-30 | 217.44 | 28.56 | 85 | 71 | 0.2
9996767175 | KJ17787 | 2023-10-01 | 304.74 | 39.85 | 85 | 70 | 2.53
9996767175 | KJ17787 | 2023-10-02 | 324.97 | 42.46 | 85 | 69 | 0.56
9996767175 | KJ17787 | 2023-10-03 | 128.68 | 17.09 | 85 | 70 | 0
9996767175 | KJ17787 | 2023-10-04 | 107.06 | 14.3 | 86 | 70 | 0.05
9996767175 | KJ17787 | 2023-10-05 | 99.79 | 13.36 | 86 | 69 | 0
9996767175 | KJ17787 | 2023-10-06 | 91.17 | 12.24 | 87 | 66 | 0
9996767175 | KJ17787 | 2023-10-07 | 84.48 | 11.38 | 90 | 56 | 0
9996767175 | KJ17787 | 2023-10-08 | 83.75 | 11.29 | 82 | 53 | 0
9996767175 | KJ17787 | 2023-10-09 | 74.78 | 10.13 | 80 | 55 | 0
9996767175 | KJ17787 | 2023-10-10 | 70.43 | 9.56 | 84 | 56 | 0
9996767175 | KJ17787 | 2023-10-11 | 70.25 | 9.54 | 84 | 65 | 0
9996767175 | KJ17787 | 2023-10-12 | 247.08 | 32.4 | 88 | 72 | 2.8
9996767175 | KJ17787 | 2023-10-13 | 284.92 | 37.29 | 89 | 68 | 1.67
9996767175 | KJ17787 | 2023-10-14 | 128.28 | 17.04 | 89 | 64 | 0
9996767175 | KJ17787 | 2023-10-15 | 113.31 | 15.11 | 82 | 55 | 0
9996767175 | KJ17787 | 2023-10-16 | 119.11 | 15.85 | 76 | 50 | 0
9996767175 | KJ17787 | 2023-10-17 | 87.88 | 11.82 | 75 | 49 | 0
9996767175 | KJ17787 | 2023-10-18 | 84.33 | 11.36 | 77 | 50 | 0
9996767175 | KJ17787 | 2023-10-19 | 79.48 | 10.74 | 81 | 55 | 0
9996767175 | KJ17787 | 2023-10-20 | 74.52 | 10.1 | 83 | 55 | 0
9996767175 | KJ17787 | 2023-10-21 | 75.27 | 10.19 | 83 | 55 | 0
9996767175 | KJ17787 | 2023-10-22 | 71.79 | 9.74 | 86 | 52 | 0
9996767175 | KJ17787 | 2023-10-23 | 68.46 | 9.31 | 83 | 58 | 0
9996767175 | KJ17787 | 2023-10-24 | 64.32 | 8.78 | 82 | 67 | 0
9996767175 | KJ17787 | 2023-10-25 | 61.65 | 8.44 | 82 | 68 | 0
9996767175 | KJ17787 | 2023-10-26 | 60.51 | 8.29 | 82 | 65 | 0
9996767175 | KJ17787 | 2023-10-27 | 57.16 | 7.86 | 83 | 64 | 0
9996767175 | KJ17787 | 2023-10-28 | 61.15 | 8.37 | 84 | 62 | 0
9996767175 | KJ17787 | 2023-10-29 | 58.87 | 8.08 | 84 | 61 | 0
9996767175 | KJ17787 | 2023-10-30 | 56.55 | 7.78 | 85 | 60 | 0
9996767175 | KJ17787 | 2023-10-31 | 55.44 | 7.63 | 84 | 58 | 0
9996767175 | KJ17787 | 2023-11-01 | 51.87 | 7.17 | 76 | 53 | 0
9996767175 | KJ17787 | 2023-11-02 | 50.09 | 6.94 | 75 | 53 | 0
9996767175 | KJ17787 | 2023-11-03 | 50.74 | 7.03 | 79 | 59 | 0
9996767175 | KJ17787 | 2023-11-04 | 51.39 | 7.11 | 79 | 55 | 0
9996767175 | KJ17787 | 2023-11-05 | 54.55 | 7.52 | 80 | 51 | 0
9996767175 | KJ17787 | 2023-11-06 | 47.38 | 6.59 | 81 | 48 | 0
9996767175 | KJ17787 | 2023-11-07 | 45.81 | 6.39 | 83 | 53 | 0
9996767175 | KJ17787 | 2023-11-08 | 45.59 | 6.36 | 84 | 50 | 0
9996767175 | KJ17787 | 2023-11-09 | 45.5 | 6.35 | 85 | 55 | 0
9996767175 | KJ17787 | 2023-11-10 | 44.01 | 6.16 | 86 | 60 | 0
9996767175 | KJ17787 | 2023-11-11 | 47.42 | 6.6 | 83 | 65 | 0.33
9996767175 | KJ17787 | 2023-11-12 | 47.32 | 6.59 | 80 | 63 | 0
9996767175 | KJ17787 | 2023-11-13 | 45.99 | 6.41 | 77 | 62 | 0
9996767175 | KJ17787 | 2023-11-14 | 55.33 | 7.62 | 77 | 61 | 0.12
9996767175 | KJ17787 | 2023-11-15 | 45.62 | 6.37 | 77 | 64 | 0.05
9996767175 | KJ17787 | 2023-11-16 | 60.88 | 8.35 | 78 | 62 | 0.16
9996767175 | KJ17787 | 2023-11-17 | 201.59 | 26.51 | 79 | 61 | 2.1
9996767175 | KJ17787 | 2023-11-18 | 91.83 | 12.34 | 78 | 55 | 0.66
9996767175 | KJ17787 | 2023-11-19 | 78.19 | 10.58 | 80 | 56 | 0
9996767175 | KJ17787 | 2023-11-20 | 70.33 | 9.57 | 79 | 59 | 0.02
9996767175 | KJ17787 | 2023-11-21 | 65.45 | 8.94 | 81 | 52 | 0.02
9996767175 | KJ17787 | 2023-11-22 | 66.67 | 9.1 | 81 | 47 | 0
9996767175 | KJ17787 | 2023-11-23 | 66.13 | 9.03 | 73 | 48 | 0.01
9996767175 | KJ17787 | 2023-11-24 | 59.98 | 8.23 | 75 | 52 | 0.01
9996767175 | KJ17787 | 2023-11-25 | 60.56 | 8.31 | 75 | 53 | 0.07
9996767175 | KJ17787 | 2023-11-26 | 68.23 | 9.3 | 75 | 55 | 0.01
9996767175 | KJ17787 | 2023-11-27 | 65.78 | 8.98 | 74 | 44 | 0.55
9996767175 | KJ17787 | 2023-11-28 | 56.03 | 7.72 | 69 | 39 | 0
9996767175 | KJ17787 | 2023-11-29 | 56.35 | 7.76 | 68 | 36 | 0
9996767175 | KJ17787 | 2023-11-30 | 51.38 | 7.12 | 86 | 41 | 0
9996767175 | KJ17787 | 2023-12-01 | 52.02 | 7.21 | 82 | 55 | 0
9996767175 | KJ17787 | 2023-12-02 | 54.16 | 7.48 | 83 | 64 | 0
9996767175 | KJ17787 | 2023-12-03 | 59.34 | 8.15 | 82 | 62 | 0.02
9996767175 | KJ17787 | 2023-12-04 | 57.29 | 7.89 | 79 | 51 | 0.23
9996767175 | KJ17787 | 2023-12-05 | 54.09 | 7.47 | 72 | 47 | 0
9996767175 | KJ17787 | 2023-12-06 | 52.7 | 7.29 | 69 | 41 | 0
9996767175 | KJ17787 | 2023-12-07 | 49.01 | 6.82 | 67 | 41 | 0
9996767175 | KJ17787 | 2023-12-08 | 47.42 | 6.61 | 74 | 47 | 0
9996767175 | KJ17787 | 2023-12-09 | 49.14 | 6.83 | 82 | 56 | 0.04
9996767175 | KJ17787 | 2023-12-10 | 56.86 | 7.83 | 83 | 44 | 0
9996767175 | KJ17787 | 2023-12-11 | 54.13 | 7.48 | 67 | 43 | 0.25
9996767175 | KJ17787 | 2023-12-12 | 52.05 | 7.21 | 71 | 43 | 0
9996767175 | KJ17787 | 2023-12-13 | 59.72 | 8.2 | 73 | 58 | 0
9996767175 | KJ17787 | 2023-12-14 | 55.81 | 7.69 | 72 | 59 | 0.66
9996767175 | KJ17787 | 2023-12-15 | 48.14 | 6.58 | 72 | 60 | 0.07
9996767175 | KJ17787 | 2023-12-16 | 61.72 | 8.33 | 73 | 58 | 0.11
9996767175 | KJ17787 | 2023-12-17 | 302.87 | 39.26 | 74 | 48 | 4.04
9996767175 | KJ17787 | 2023-12-18 | 148.97 | 19.52 | 68 | 40 | 0.05
9996767175 | KJ17787 | 2023-12-19 | 102.59 | 13.57 | 65 | 41 | 0
9996767175 | KJ17787 | 2023-12-20 | 91.29 | 12.12 | 66 | 44 | 0
9996767175 | KJ17787 | 2023-12-21 | 82.04 | 10.93 | 68 | 46 | 0
9996767175 | KJ17787 | 2023-12-22 | 77.09 | 10.3 | 70 | 49 | 0
9996767175 | KJ17787 | 2023-12-23 | 80.95 | 10.79 | 73 | 53 | 0
9996767175 | KJ17787 | 2023-12-24 | 79.2 | 10.57 | 73 | 53 | 0
9996767175 | KJ17787 | 2023-12-25 | 77.22 | 10.32 | 73 | 60 | 0.09
9996767175 | KJ17787 | 2023-12-26 | 75.74 | 10.13 | 74 | 54 | 0.1
9996767175 | KJ17787 | 2023-12-27 | 69.38 | 9.31 | 71 | 49 | 0
9996767175 | KJ17787 | 2023-12-28 | 70.02 | 9.39 | 66 | 44 | 0.04
9996767175 | KJ17787 | 2023-12-29 | 68.26 | 9.17 | 55 | 46 | 0
9996767175 | KJ17787 | 2023-12-30 | 67.08 | 9.01 | 59 | 37 | 0
9996767175 | KJ17787 | 2023-12-31 | 67.12 | 9.02 | 63 | 36 | 0
|  | Yearly Daily Average: | 57.7428 | 7.9186
|  | Wetter Months' Daily Average: | 81.413 | 10.9684

## OKR MPS
Daily Billed Information (OKR - 1795 Old Kings Road: 2023 Reading Data)
Bill Account | Meter Number | Date | Consumption Recorded (kWh/day) | Estimated Cost ($/day) | Avg High Temperature (°F) | Avg Low Temperature (°F) | Rain Recorded by NOAA (inches)
4430859332 | KNJ0198 | 01/01/2023 | 412.39 | 64.95 | 79 | 58 | 0.04
4430859332 | KNJ0198 | 01/02/2023 | 358.65 | 61.95 | 78 | 53 | 0
4430859332 | KNJ0198 | 01/03/2023 | 342.04 | 61.06 | 81 | 51 | 0
4430859332 | KNJ0198 | 01/04/2023 | 350.91 | 61.51 | 83 | 57 | 0
4430859332 | KNJ0198 | 01/05/2023 | 351.02 | 61.56 | 77 | 46 | 0.04
4430859332 | KNJ0198 | 01/06/2023 | 353.09 | 61.67 | 68 | 41 | 0
4430859332 | KNJ0198 | 01/07/2023 | 348.3 | 61.39 | 70 | 38 | 0
4430859332 | KNJ0198 | 01/08/2023 | 357.72 | 61.89 | 76 | 42 | 0
4430859332 | KNJ0198 | 01/09/2023 | 351.72 | 61.56 | 74 | 47 | 0
4430859332 | KNJ0198 | 01/10/2023 | 345.75 | 61.23 | 71 | 42 | 0
4430859332 | KNJ0198 | 01/11/2023 | 351.27 | 61.56 | 73 | 38 | 0
4430859332 | KNJ0198 | 01/12/2023 | 357.91 | 61.89 | 80 | 44 | 0
4430859332 | KNJ0198 | 01/13/2023 | 361.28 | 62.12 | 71 | 35 | 0.12
4430859332 | KNJ0198 | 01/14/2023 | 359.35 | 62 | 61 | 30 | 0
4430859332 | KNJ0198 | 01/15/2023 | 355.44 | 61.78 | 63 | 30 | 0
4430859332 | KNJ0198 | 01/16/2023 | 366.46 | 62.39 | 71 | 30 | 0
4430859332 | KNJ0198 | 01/17/2023 | 357.31 | 61.89 | 75 | 34 | 0
4430859332 | KNJ0198 | 01/18/2023 | 352.87 | 61.62 | 79 | 46 | N/A
4430859332 | KNJ0198 | 01/19/2023 | 413.85 | 65 | 82 | 54 | 0
4430859332 | KNJ0198 | 01/20/2023 | 416.37 | 65.17 | 76 | 49 | 0
4430859332 | KNJ0198 | 01/21/2023 | 412.06 | 69.23 | 76 | 47 | T
4430859332 | KNJ0198 | 01/22/2023 | 429.47 | 70.17 | 82 | 54 | 0.33
4430859332 | KNJ0198 | 01/23/2023 | 430.95 | 70.23 | 75 | 44 | 0.05
4430859332 | KNJ0198 | 01/24/2023 | 445.72 | 71.06 | 76 | 41 | 0
4430859332 | KNJ0198 | 01/25/2023 | 417.72 | 69.5 | 85 | 43 | 0
4430859332 | KNJ0198 | 01/26/2023 | 414.32 | 69.34 | 72 | 38 | 0.09
4430859332 | KNJ0198 | 01/27/2023 | 411.18 | 69.17 | 62 | 37 | 0
4430859332 | KNJ0198 | 01/28/2023 | 405.51 | 68.84 | 69 | 35 | 0
4430859332 | KNJ0198 | 01/29/2023 | 419.77 | 69.61 | 78 | 55 | 0
4430859332 | KNJ0198 | 01/30/2023 | 412.02 | 69.23 | 86 | 58 | 0
4430859332 | KNJ0198 | 01/31/2023 | 418.16 | 69.56 | 83 | 59 | 0
4430859332 | KNJ0198 | 02/01/2023 | 410.6 | 69.12 | 82 | 58 | 0
4430859332 | KNJ0198 | 02/02/2023 | 407.83 | 68.95 | 82 | 57 | 0
4430859332 | KNJ0198 | 02/03/2023 | 415.78 | 69.39 | 78 | 50 | 0
4430859332 | KNJ0198 | 02/04/2023 | 423.57 | 69.84 | 70 | 47 | 0.17
4430859332 | KNJ0198 | 02/05/2023 | 430.6 | 70.23 | 73 | 48 | 0
4430859332 | KNJ0198 | 02/06/2023 | 420.72 | 69.67 | 71 | 46 | 0.01
4430859332 | KNJ0198 | 02/07/2023 | 414.54 | 69.34 | 76 | 44
4430859332 | KNJ0198 | 02/08/2023 | 439.89 | 70.72 | 79 | 49 | 0
4430859332 | KNJ0198 | 02/09/2023 | 437.81 | 70.61 | 83 | 58 | 0
4430859332 | KNJ0198 | 02/10/2023 | 423.33 | 69.84 | 85 | 46 | 0.16
4430859332 | KNJ0198 | 02/11/2023 | 429.5 | 70.17 | 79 | 40 | 0.57
4430859332 | KNJ0198 | 02/12/2023 | 433.67 | 70.39 | 71 | 40 | 0.12
4430859332 | KNJ0198 | 02/13/2023 | 432.55 | 70.34 | 71 | 40 | Trace Value
4430859332 | KNJ0198 | 02/14/2023 | 419.57 | 69.61 | 75 | 39 | 0
4430859332 | KNJ0198 | 02/15/2023 | 412.94 | 69.23 | 82 | 50 | 0
4430859332 | KNJ0198 | 02/16/2023 | 416.24 | 69.45 | 85 | 57 | 0
4430859332 | KNJ0198 | 02/17/2023 | 500.02 | 74.11 | 89 | 45
4430859332 | KNJ0198 | 02/18/2023 | 421.31 | 69.73 | 67 | 46 | 0.04
4430859332 | KNJ0198 | 02/19/2023 | 423.39 | 67.83 | 80 | 48 | 0
4430859332 | KNJ0198 | 02/20/2023 | 426.32 | 67.99 | 82 | 53 | 0
4430859332 | KNJ0198 | 02/21/2023 | 419.21 | 67.6 | 85 | 57 | 0
4430859332 | KNJ0198 | 02/22/2023 | 421.6 | 67.72 | 87 | 58 | 0
4430859332 | KNJ0198 | 02/23/2023 | 425.53 | 67.94 | 89 | 60 | 0
4430859332 | KNJ0198 | 02/24/2023 | 423.43 | 67.83 | 87 | 58 | 0
4430859332 | KNJ0198 | 02/25/2023 | 419.07 | 67.6 | 87 | 58
4430859332 | KNJ0198 | 02/26/2023 | 437.23 | 68.6 | 87 | 56 | 0
4430859332 | KNJ0198 | 02/27/2023 | 434.12 | 68.44 | 87 | 57 | 0
4430859332 | KNJ0198 | 02/28/2023 | 420.72 | 67.66 | 87 | 57 | 0
4430859332 | KNJ0198 | 03/01/2023 | 416.57 | 67.44 | 86 | 58 | 0
4430859332 | KNJ0198 | 03/02/2023 | 415.98 | 67.38 | 87 | 56 | 0
4430859332 | KNJ0198 | 03/03/2023 | 419.69 | 67.6 | 90 | 55 | 0
4430859332 | KNJ0198 | 03/04/2023 | 423.56 | 67.83 | 88 | 52 | 0
4430859332 | KNJ0198 | 03/05/2023 | 436.2 | 68.55 | 81 | 54 | 0.05
4430859332 | KNJ0198 | 03/06/2023 | 424.03 | 67.88 | 84 | 56 | 0
4430859332 | KNJ0198 | 03/07/2023 | 413.42 | 67.27 | 87 | 56
4430859332 | KNJ0198 | 03/08/2023 | 413.1 | 67.27 | 85 | 58 | 0
4430859332 | KNJ0198 | 03/09/2023 | 412.3 | 67.22 | 80 | 51 | 0
4430859332 | KNJ0198 | 03/10/2023 | 408.26 | 66.99 | 85 | 54
4430859332 | KNJ0198 | 03/11/2023 | 419.81 | 67.6 | 81 | 51 | 1.3
4430859332 | KNJ0198 | 03/12/2023 | 412.94 | 67.22 | 86 | 48 | 0
4430859332 | KNJ0198 | 03/13/2023 | 445.7 | 69.05 | 81 | 46 | 1.17
4430859332 | KNJ0198 | 03/14/2023 | 428.07 | 68.1 | 70 | 43 | 0.6
4430859332 | KNJ0198 | 03/15/2023 | 426.78 | 67.99 | 68 | 43 | 0
4430859332 | KNJ0198 | 03/16/2023 | 421.17 | 67.72 | 77 | 37 | 0
4430859332 | KNJ0198 | 03/17/2023 | 410.3 | 67.11 | 84 | 48
4430859332 | KNJ0198 | 03/18/2023 | 410.1 | 67.11 | 80 | 45 | 0
4430859332 | KNJ0198 | 03/19/2023 | 408.95 | 66.99 | 68 | 43 | 0.02
4430859332 | KNJ0198 | 03/20/2023 | 485.49 | 71.27 | 69 | 42 | 0.02
4430859332 | KNJ0198 | 03/21/2023 | 400.69 | 66.55 | 77 | 42 | 0
4430859332 | KNJ0198 | 03/22/2023 | 406.96 | 73.57 | 80 | 53 | 0.08
4430859332 | KNJ0198 | 03/23/2023 | 405.79 | 73.51 | 83 | 53
4430859332 | KNJ0198 | 03/24/2023 | 413.45 | 74 | 86 | 53 | 0
4430859332 | KNJ0198 | 03/25/2023 | 407.71 | 73.63 | 91 | 60 | 0
4430859332 | KNJ0198 | 03/26/2023 | 428.87 | 74.92 | 91 | 63 | 0.68
4430859332 | KNJ0198 | 03/27/2023 | 417.74 | 74.25 | 92 | 62 | 0
4430859332 | KNJ0198 | 03/28/2023 | 413.38 | 74 | 88 | 55 | Trace Value
4430859332 | KNJ0198 | 03/29/2023 | 404.55 | 73.45 | 75 | 55 | 0
4430859332 | KNJ0198 | 03/30/2023 | 406.19 | 73.57 | 79 | 51 | 0
4430859332 | KNJ0198 | 03/31/2023 | 414.97 | 74.06 | 85 | 55 | 0
4430859332 | KNJ0198 | 04/01/2023 | 411.04 | 73.88 | 90 | 60 | 0
4430859332 | KNJ0198 | 04/02/2023 | 422.3 | 74.56 | 85 | 60
4430859332 | KNJ0198 | 04/03/2023 | 411.01 | 73.88 | 86 | 61 | 0
4430859332 | KNJ0198 | 04/04/2023 | 412.66 | 73.94 | 88 | 60 | Trace Value
4430859332 | KNJ0198 | 04/05/2023 | 416.26 | 74.19 | 87 | 63 | 0
4430859332 | KNJ0198 | 04/06/2023 | 413.18 | 74 | 87 | 64 | 0
4430859332 | KNJ0198 | 04/07/2023 | 419.27 | 74.37 | 85 | 64
4430859332 | KNJ0198 | 04/08/2023 | 424.32 | 74.68 | 86 | 62
4430859332 | KNJ0198 | 04/09/2023 | 420 | 74.43 | 80 | 60 | 0.01
4430859332 | KNJ0198 | 04/10/2023 | 458 | 76.71 | 79 | 58 | 0.68
4430859332 | KNJ0198 | 04/11/2023 | 459.51 | 76.83 | 78 | 58 | 1.38
4430859332 | KNJ0198 | 04/12/2023 | 442.52 | 75.79 | 79 | 59 | 0.03
4430859332 | KNJ0198 | 04/13/2023 | 450 | 76.22 | 87 | 61 | 0.07
4430859332 | KNJ0198 | 04/14/2023 | 466.79 | 77.27 | 86 | 59 | 0.57
4430859332 | KNJ0198 | 04/15/2023 | 446.54 | 76.03 | 87 | 60 | 0.02
4430859332 | KNJ0198 | 04/16/2023 | 448.69 | 76.16 | 88 | 59 | 0
4430859332 | KNJ0198 | 04/17/2023 | 431.89 | 75.11 | 81 | 50 | 0.04
4430859332 | KNJ0198 | 04/18/2023 | 428.19 | 74.92 | 81 | 46 | 0.02
4430859332 | KNJ0198 | 04/19/2023 | 503.11 | 79.54 | 82 | 50 | 0
4430859332 | KNJ0198 | 04/20/2023 | 421.57 | 74.49 | 84 | 55 | 0
4430859332 | KNJ0198 | 04/21/2023 | 430.51 | 75.26 | 87 | 59
4430859332 | KNJ0198 | 04/22/2023 | 423.91 | 74.86 | 89 | 57 | 0.3
4430859332 | KNJ0198 | 04/23/2023 | 435.59 | 75.54 | 84 | 53 | 0.42
4430859332 | KNJ0198 | 04/24/2023 | 425.2 | 74.97 | 80 | 55 | 0
4430859332 | KNJ0198 | 04/25/2023 | 432.02 | 75.37 | 82 | 61 | 0.25
4430859332 | KNJ0198 | 04/26/2023 | 424.62 | 74.92 | 84 | 62 | 0.07
4430859332 | KNJ0198 | 04/27/2023 | 459.43 | 76.91 | 86 | 63 | 0
4430859332 | KNJ0198 | 04/28/2023 | 504.91 | 79.47 | 87 | 62 | 1.62
4430859332 | KNJ0198 | 04/29/2023 | 474.67 | 77.76 | 88 | 62 | 0
4430859332 | KNJ0198 | 04/30/2023 | 473.51 | 77.7 | 85 | 57 | 0.52
4430859332 | KNJ0198 | 05/01/2023 | 459.52 | 76.91 | 85 | 56 | 0
4430859332 | KNJ0198 | 05/02/2023 | 473.15 | 77.7 | 87 | 56 | 0
4430859332 | KNJ0198 | 05/03/2023 | 476.26 | 77.87 | 86 | 53 | 0
4430859332 | KNJ0198 | 05/04/2023 | 480.4 | 78.1 | 84 | 53 | 0
4430859332 | KNJ0198 | 05/05/2023 | 475.3 | 77.82 | 87 | 57 | 0
4430859332 | KNJ0198 | 05/06/2023 | 467.91 | 77.36 | 86 | 65 | 0
4430859332 | KNJ0198 | 05/07/2023 | 482.41 | 78.22 | 88 | 61 | 0.02
4430859332 | KNJ0198 | 05/08/2023 | 470.57 | 77.53 | 87 | 55 | 0
4430859332 | KNJ0198 | 05/09/2023 | 469.17 | 77.48 | 91 | 63 | 0
4430859332 | KNJ0198 | 05/10/2023 | 462.06 | 77.08 | 92 | 66 | 0
4430859332 | KNJ0198 | 05/11/2023 | 470.89 | 77.53 | 88 | 67 | 0.04
4430859332 | KNJ0198 | 05/12/2023 | 478.25 | 77.99 | 86 | 66 | 0
4430859332 | KNJ0198 | 05/13/2023 | 465.46 | 77.25 | 85 | 64 | 0
4430859332 | KNJ0198 | 05/14/2023 | 466.44 | 77.31 | 86 | 63 | 0
4430859332 | KNJ0198 | 05/15/2023 | 458.12 | 76.85 | 89 | 62 | 0
4430859332 | KNJ0198 | 05/16/2023 | 462.81 | 77.08 | 88 | 64 | 0
4430859332 | KNJ0198 | 05/17/2023 | 458.34 | 76.85 | 92 | 67 | 0
4430859332 | KNJ0198 | 05/18/2023 | 575.64 | 83.51 | 89 | 65 | 1.24
4430859332 | KNJ0198 | 05/19/2023 | 439 | 75.77 | 88 | 66 | 0.02
4430859332 | KNJ0198 | 05/20/2023 | 410.88 | 72.26 | 88 | 66 | 0
4430859332 | KNJ0198 | 05/21/2023 | 428.98 | 73.28 | 88 | 67
4430859332 | KNJ0198 | 05/22/2023 | 477.29 | 76.07 | 88 | 67 | 0.65
4430859332 | KNJ0198 | 05/23/2023 | 464.51 | 75.33 | 85 | 67 | 0.56
4430859332 | KNJ0198 | 05/24/2023 | 443.96 | 74.14 | 83 | 66 | 0.12
4430859332 | KNJ0198 | 05/25/2023 | 440.05 | 73.97 | 83 | 66 | 0.16
4430859332 | KNJ0198 | 05/26/2023 | 456.29 | 74.88 | 82 | 62 | 0.05
4430859332 | KNJ0198 | 05/27/2023 | 453.51 | 74.71 | 81 | 56 | Trace Value
4430859332 | KNJ0198 | 05/28/2023 | 438.19 | 73.85 | 85 | 55 | 0
4430859332 | KNJ0198 | 05/29/2023 | 440.42 | 73.97 | 87 | 60 | 0
4430859332 | KNJ0198 | 05/30/2023 | 459.11 | 75.05 | 88 | 62 | 0
4430859332 | KNJ0198 | 05/31/2023 | 473.2 | 75.84 | 87 | 68 | 0
4430859332 | KNJ0198 | 06/01/2023 | 467.02 | 75.5 | 85 | 68 | 0
4430859332 | KNJ0198 | 06/02/2023 | 475.93 | 75.96 | 85 | 67 | 0
4430859332 | KNJ0198 | 06/03/2023 | 473.56 | 75.84 | 84 | 67 | 0
4430859332 | KNJ0198 | 06/04/2023 | 478.38 | 76.13 | 84 | 66 | 0
4430859332 | KNJ0198 | 06/05/2023 | 468.37 | 75.56 | 84 | 64 | 0.3
4430859332 | KNJ0198 | 06/06/2023 | 464.3 | 75.33 | 88 | 62
4430859332 | KNJ0198 | 06/07/2023 | 494.49 | 77.04 | 91 | 68 | 0
4430859332 | KNJ0198 | 06/08/2023 | 499.49 | 77.32 | 92 | 68 | 1.64
4430859332 | KNJ0198 | 06/09/2023 | 498.48 | 77.27 | 92 | 68 | 0
4430859332 | KNJ0198 | 06/10/2023 | 501.81 | 77.44 | 88 | 67 | 0.54
4430859332 | KNJ0198 | 06/11/2023 | 492.93 | 76.92 | 91 | 69 | 0.09
4430859332 | KNJ0198 | 06/12/2023 | 483.72 | 76.41 | 94 | 69 | 0
4430859332 | KNJ0198 | 06/13/2023 | 480.25 | 76.24 | 95 | 71
4430859332 | KNJ0198 | 06/14/2023 | 467.55 | 75.5 | 95 | 71 | 0
4430859332 | KNJ0198 | 06/15/2023 | 475.17 | 75.96 | 95 | 66 | 0.44
4430859332 | KNJ0198 | 06/16/2023 | 492.11 | 76.92 | 95 | 68 | 0.45
4430859332 | KNJ0198 | 06/17/2023 | 492.45 | 76.92 | 93 | 68 | 0.91
4430859332 | KNJ0198 | 06/18/2023 | 499.84 | 77.32 | 94 | 68 | 0.28
4430859332 | KNJ0198 | 06/19/2023 | 604.68 | 83.3 | 93 | 70 | 0.63
4430859332 | KNJ0198 | 06/20/2023 | 497.85 | 77.21 | 91 | 69 | 0.46
4430859332 | KNJ0198 | 06/21/2023 | 488.04 | 76.1 | 91 | 71 | 0.24
4430859332 | KNJ0198 | 06/22/2023 | 482.35 | 75.78 | 93 | 66 | 0.04
4430859332 | KNJ0198 | 06/23/2023 | 516.79 | 77.59 | 91 | 69 | 0.35
4430859332 | KNJ0198 | 06/24/2023 | 510.85 | 77.27 | 92 | 70 | 0.24
4430859332 | KNJ0198 | 06/25/2023 | 500.65 | 76.74 | 91 | 70 | 0.15
4430859332 | KNJ0198 | 06/26/2023 | 478.43 | 75.57 | 94 | 70 | 0
4430859332 | KNJ0198 | 06/27/2023 | 476.05 | 75.46 | 97 | 71 | 0
4430859332 | KNJ0198 | 06/28/2023 | 486.54 | 76 | 95 | 72 | 0
4430859332 | KNJ0198 | 06/29/2023 | 483.93 | 75.84 | 95 | 71 | 0.88
4430859332 | KNJ0198 | 06/30/2023 | 479.5 | 75.62 | 94 | 71 | 0
4430859332 | KNJ0198 | 07/01/2023 | 474.34 | 75.36 | 94 | 71 | 0
4430859332 | KNJ0198 | 07/02/2023 | 475.49 | 75.41 | 95 | 71 | 0
4430859332 | KNJ0198 | 07/03/2023 | 477.52 | 75.52 | 97 | 72 | 0
4430859332 | KNJ0198 | 07/04/2023 | 479.04 | 75.62 | 95 | 73 | 0
4430859332 | KNJ0198 | 07/05/2023 | 479.46 | 75.62 | 95 | 74 | 0
4430859332 | KNJ0198 | 07/06/2023 | 473.59 | 75.3 | 96 | 73 | 0.04
4430859332 | KNJ0198 | 07/07/2023 | 476.93 | 75.46 | 95 | 73 | 0.03
4430859332 | KNJ0198 | 07/08/2023 | 488.1 | 76.1 | 94 | 74 | 0.31
4430859332 | KNJ0198 | 07/09/2023 | 487.06 | 76.05 | 96 | 74 | 0.2
4430859332 | KNJ0198 | 07/10/2023 | 456.78 | 74.4 | 96 | 74 | 0
4430859332 | KNJ0198 | 07/11/2023 | 475.03 | 75.41 | 94 | 73 | 0.78
4430859332 | KNJ0198 | 07/12/2023 | 483.77 | 75.84 | 94 | 73 | 0.1
4430859332 | KNJ0198 | 07/13/2023 | 480.86 | 75.68 | 94 | 72 | Trace Value
4430859332 | KNJ0198 | 07/14/2023 | 483.91 | 75.84 | 95 | 73 | 0.33
4430859332 | KNJ0198 | 07/15/2023 | 491.8 | 76.26 | 96 | 73 | 0.12
4430859332 | KNJ0198 | 07/16/2023 | 516.4 | 77.59 | 96 | 74 | 0.15
4430859332 | KNJ0198 | 07/17/2023 | 500.83 | 76.74 | 95 | 74 | 2.8
4430859332 | KNJ0198 | 07/18/2023 | 515.12 | 77.54 | 95 | 72 | 0.22
4430859332 | KNJ0198 | 07/19/2023 | 608.89 | 82.49 | 95 | 71 | 0.14
4430859332 | KNJ0198 | 07/20/2023 | 489.88 | 76.15 | 96 | 73 | 0
4430859332 | KNJ0198 | 07/21/2023 | 475.31 | 82.49 | 99 | 74 | 0
4430859332 | KNJ0198 | 07/22/2023 | 490.24 | 83.29 | 97 | 75 | 0
4430859332 | KNJ0198 | 07/23/2023 | 548.75 | 86.37 | 94 | 71 | 0.7
4430859332 | KNJ0198 | 07/24/2023 | 526.87 | 85.2 | 93 | 73 | 1.12
4430859332 | KNJ0198 | 07/25/2023 | 512.72 | 84.46 | 93 | 73 | 0.3
4430859332 | KNJ0198 | 07/26/2023 | 507.07 | 84.19 | 92 | 73 | 0
4430859332 | KNJ0198 | 07/27/2023 | 497.26 | 83.66 | 91 | 73 | 0
4430859332 | KNJ0198 | 07/28/2023 | 522.32 | 84.99 | 92 | 73 | 1
4430859332 | KNJ0198 | 07/29/2023 | 532.84 | 85.52 | 93 | 73 | 0.05
4430859332 | KNJ0198 | 07/30/2023 | 555.38 | 86.75 | 95 | 74 | Trace Value
4430859332 | KNJ0198 | 07/31/2023 | 530.93 | 85.42 | 95 | 71 | 0.74
4430859332 | KNJ0198 | 08/01/2023 | 525.67 | 85.15 | 95 | 71 | 0.08
4430859332 | KNJ0198 | 08/02/2023 | 487.66 | 83.13 | 93 | 74 | 0
4430859332 | KNJ0198 | 08/03/2023 | 484.89 | 82.97 | 91 | 73 | 0
4430859332 | KNJ0198 | 08/04/2023 | 515.21 | 84.62 | 94 | 73 | 0
4430859332 | KNJ0198 | 08/05/2023 | 572.99 | 87.65 | 94 | 73 | 0.17
4430859332 | KNJ0198 | 08/06/2023 | 558.58 | 86.91 | 95 | 74 | 0.66
4430859332 | KNJ0198 | 08/07/2023 | 535.51 | 85.68 | 97 | 75 | 0.03
4430859332 | KNJ0198 | 08/08/2023 | 518 | 84.72 | 99 | 75 | 0
4430859332 | KNJ0198 | 08/09/2023 | 529.2 | 85.36 | 99 | 74 | 0
4430859332 | KNJ0198 | 08/10/2023 | 523.84 | 85.04 | 100 | 75 | 0.16
4430859332 | KNJ0198 | 08/11/2023 | 514.58 | 84.56 | 99 | 75 | 0
4430859332 | KNJ0198 | 08/12/2023 | 544.02 | 86.16 | 98 | 76 | 0.25
4430859332 | KNJ0198 | 08/13/2023 | 537.6 | 85.79 | 97 | 74 | 0
4430859332 | KNJ0198 | 08/14/2023 | 502.17 | 83.93 | 97 | 76 | 0
4430859332 | KNJ0198 | 08/15/2023 | 497.97 | 83.66 | 97 | 75 | 0
4430859332 | KNJ0198 | 08/16/2023 | 578.25 | 87.97 | 96 | 73 | 0.09
4430859332 | KNJ0198 | 08/17/2023 | 584.24 | 88.29 | 93 | 72 | 0.36
4430859332 | KNJ0198 | 08/18/2023 | 605.6 | 89.41 | 93 | 73 | 1.09
4430859332 | KNJ0198 | 08/19/2023 | 570.9 | 87.54 | 93 | 72 | 0.69
4430859332 | KNJ0198 | 08/20/2023 | 674.64 | 93.08 | 92 | 75 | 0
4430859332 | KNJ0198 | 08/21/2023 | 527.89 | 85.26 | 92 | 74 | 0
4430859332 | KNJ0198 | 08/22/2023 | 520.55 | 79.41 | 93 | 72 | 0
4430859332 | KNJ0198 | 08/23/2023 | 496.51 | 78.14 | 93 | 74 | 0
4430859332 | KNJ0198 | 08/24/2023 | 495.19 | 78.08 | 93 | 74 | 0.99
4430859332 | KNJ0198 | 08/25/2023 | 490.43 | 77.82 | 92 | 71 | 0
4430859332 | KNJ0198 | 08/26/2023 | 477.1 | 77.13 | 95 | 73 | 0
4430859332 | KNJ0198 | 08/27/2023 | 503.76 | 78.51 | 95 | 72
4430859332 | KNJ0198 | 08/28/2023 | 485.03 | 77.55 | 96 | 74 | Trace Value
4430859332 | KNJ0198 | 08/29/2023 | 495.86 | 78.08 | 95 | 74 | 0
4430859332 | KNJ0198 | 08/30/2023 | 492.59 | 77.92 | 94 | 74 | 0.93
4430859332 | KNJ0198 | 08/31/2023 | 494.3 | 78.03 | 94 | 74 | 0.05
4430859332 | KNJ0198 | 09/01/2023 | 492.17 | 77.92 | 92 | 73 | 0
4430859332 | KNJ0198 | 09/02/2023 | 477.79 | 77.13 | 91 | 72
4430859332 | KNJ0198 | 09/03/2023 | 467.1 | 76.59 | 92 | 71 | 0.05
4430859332 | KNJ0198 | 09/04/2023 | 482.37 | 77.39 | 90 | 68 | 0
4430859332 | KNJ0198 | 09/05/2023 | 475.97 | 77.02 | 90 | 64 | 0
4430859332 | KNJ0198 | 09/06/2023 | 466.46 | 76.54 | 94 | 69 | 0
4430859332 | KNJ0198 | 09/07/2023 | 472.94 | 76.86 | 95 | 70
4430859332 | KNJ0198 | 09/08/2023 | 482.3 | 77.39 | 95 | 69 | 0
4430859332 | KNJ0198 | 09/09/2023 | 481.59 | 77.34 | 94 | 64 | 0.48
4430859332 | KNJ0198 | 09/10/2023 | 491.13 | 77.87 | 93 | 71 | Trace Value
4430859332 | KNJ0198 | 09/11/2023 | 457.71 | 76.06 | 92 | 72 | 0
4430859332 | KNJ0198 | 09/12/2023 | 479.57 | 77.23 | 92 | 71 | Trace Value
4430859332 | KNJ0198 | 09/13/2023 | 505.87 | 78.62 | 92 | 72 | 0.03
4430859332 | KNJ0198 | 09/14/2023 | 496.09 | 78.14 | 91 | 71 | 0.29
4430859332 | KNJ0198 | 09/15/2023 | 475.57 | 77.02 | 88 | 70 | 0
4430859332 | KNJ0198 | 09/16/2023 | 477.18 | 77.13 | 87 | 69 | 0.54
4430859332 | KNJ0198 | 09/17/2023 | 489.51 | 77.76 | 92 | 70 | 0
4430859332 | KNJ0198 | 09/18/2023 | 463.35 | 76.38 | 89 | 68 | 0.08
4430859332 | KNJ0198 | 09/19/2023 | 564.4 | 81.75 | 88 | 64 | 0
4430859332 | KNJ0198 | 09/20/2023 | 471.8 | 76.81 | 88 | 69 | 0
4430859332 | MNJ1446 | 09/21/2023 | 473.61 | 60.21 | 87 | 68 | 0.08
4430859332 | MNJ1446 | 09/22/2023 | 465.08 | 59.79 | 85 | 65 | 0.3
4430859332 | MNJ1446 | 09/23/2023 | 474.51 | 60.27 | 87 | 61 | 0
4430859332 | MNJ1446 | 09/24/2023 | 485.38 | 60.85 | 89 | 59 | 0
4430859332 | MNJ1446 | 10/11/2023 | 49.6 | 38.63 | 84 | 65 | 2.8
4430859332 | MNJ1446 | 10/12/2023 | 2002.73 | 181.33 | 88 | 72 | 1.67
4430859332 | MNJ1446 | 10/13/2023 | 788.41 | 89.56 | 89 | 68 | 0
4430859332 | MNJ1446 | 10/14/2023 | 607.67 | 67.34 | 89 | 64 | 0
4430859332 | MNJ1446 | 09/29/2023 | 599.29 | 66.92 | 85 | 71 | 0.2
4430859332 | MNJ1446 | 09/30/2023 | 893 | 82.5 | 85 | 71 | 2.53
4430859332 | MNJ1446 | 10/01/2023 | 705.02 | 72.56 | 85 | 70 | 0.56
4430859332 | MNJ1446 | 10/02/2023 | 644.73 | 69.31 | 85 | 69 | 0
4430859332 | MNJ1446 | 10/03/2023 | 577.51 | 65.75 | 85 | 70 | 0.05
4430859332 | MNJ1446 | 10/04/2023 | 560.89 | 64.84 | 86 | 70 | 0
4430859332 | MNJ1446 | 10/05/2023 | 544.26 | 63.99 | 86 | 69 | 0
4430859332 | MNJ1446 | 10/06/2023 | 552.89 | 64.42 | 87 | 66 | 0
4430859332 | MNJ1446 | 10/07/2023 | 533.83 | 63.41 | 90 | 56 | 0
4430859332 | MNJ1446 | 10/08/2023 | 539.67 | 63.72 | 82 | 53 | 0
4430859332 | MNJ1446 | 2024-10-09 | NA | NA | 80 | 55 | 0
4430859332 | MNJ1446 | 2025-10-10 | NA | NA | 84 | 56 | 0
4430859332 | MNJ1446 | 10/11/2023 | 49.6 | 38.63 | 84 | 65 | 2.8
4430859332 | MNJ1446 | 10/12/2023 | 2002.73 | 181.33 | 88 | 72 | 1.67
4430859332 | MNJ1446 | 10/13/2023 | 788.41 | 89.56 | 89 | 68 | 0
4430859332 | MNJ1446 | 10/14/2023 | 607.67 | 67.34 | 89 | 64 | 0
4430859332 | MNJ1446 | 10/15/2023 | 592.2 | 66.54 | 82 | 55 | 0
4430859332 | MNJ1446 | 10/16/2023 | 561.83 | 75.69 | 76 | 50 | 0
4430859332 | MNJ1446 | 10/17/2023 | 549.55 | 74.46 | 75 | 49 | 0
4430859332 | MNJ1446 | 10/18/2023 | 544.39 | 74.11 | 77 | 50 | 0
4430859332 | MNJ1446 | 10/19/2023 | 658.82 | 79.96 | 81 | 55 | 0
4430859332 | MNJ1446 | 10/20/2023 | 532.54 | 73.43 | 83 | 55 | 0
4430859332 | MNJ1446 | 10/21/2023 | 523.2 | 58.87 | 83 | 55 | 0
4430859332 | MNJ1446 | 10/22/2023 | 528.88 | 59.14 | 86 | 52 | 0
4430859332 | MNJ1446 | 10/23/2023 | 506.12 | 67.68 | 83 | 58 | 0
4430859332 | MNJ1446 | 10/24/2023 | 507.32 | 67.53 | 82 | 67 | 0
4430859332 | MNJ1446 | 10/25/2023 | 480.9 | 65.64 | 82 | 68 | 0
4430859332 | MNJ1446 | 10/26/2023 | 477.98 | 65.62 | 82 | 65 | 0
4430859332 | MNJ1446 | 10/27/2023 | 471.28 | 65.18 | 83 | 64 | 0
4430859332 | MNJ1446 | 10/28/2023 | 469.55 | 56 | 84 | 62 | 0
4430859332 | MNJ1446 | 10/29/2023 | 484.03 | 56.8 | 84 | 61 | 0
4430859332 | MNJ1446 | 10/30/2023 | 459.68 | 64.54 | 85 | 60 | 0
4430859332 | MNJ1446 | 10/31/2023 | 457.57 | 63.98 | 84 | 58 | 0
4430859332 | MNJ1446 | 11/01/2023 | 461.07 | 63.4 | 76 | 53 | 0
4430859332 | MNJ1446 | 11/02/2023 | 459.61 | 63.06 | 75 | 53 | 0
4430859332 | MNJ1446 | 11/03/2023 | 463.75 | 63.34 | 79 | 59 | 0
4430859332 | MNJ1446 | 11/04/2023 | 451.74 | 55.04 | 79 | 55 | 0
4430859332 | MNJ1446 | 11/05/2023 | 503.75 | 57.81 | 80 | 51 | 0
4430859332 | MNJ1446 | 11/06/2023 | 459.72 | 63.28 | 81 | 48 | 0
4430859332 | MNJ1446 | 11/07/2023 | 464.78 | 63.77 | 83 | 53 | 0
4430859332 | MNJ1446 | 11/08/2023 | 475.26 | 64.94 | 84 | 50 | 0
4430859332 | MNJ1446 | 11/09/2023 | 466.39 | 63.66 | 85 | 55 | 0
4430859332 | MNJ1446 | 11/10/2023 | 466.55 | 63.37 | 86 | 60 | 0.33
4430859332 | MNJ1446 | 11/11/2023 | 465.45 | 55.79 | 83 | 65 | 0
4430859332 | MNJ1446 | 11/12/2023 | 477.58 | 56.43 | 80 | 63 | 0
4430859332 | MNJ1446 | 11/13/2023 | 453.95 | 62.61 | 77 | 62 | 0.12
4430859332 | MNJ1446 | 11/14/2023 | 495.58 | 66.37 | 77 | 61 | 0.05
4430859332 | MNJ1446 | 11/15/2023 | 514.8 | 67.35 | 77 | 64 | 0.16
4430859332 | MNJ1446 | 11/16/2023 | 688.05 | 80.51 | 78 | 62 | 2.1
4430859332 | MNJ1446 | 11/17/2023 | 1212.74 | 108.86 | 79 | 61 | 0.66
4430859332 | MNJ1446 | 11/18/2023 | 663.1 | 66.32 | 78 | 55 | 0
4430859332 | MNJ1446 | 11/19/2023 | 595.04 | 52.49 | 80 | 56 | 0.02
4430859332 | MNJ1446 | 11/20/2023 | 552.7 | 59.14 | 79 | 59 | 0.02
4430859332 | MNJ1446 | 11/21/2023 | 552.55 | 59.23 | 81 | 52 | 0
4430859332 | MNJ1446 | 11/22/2023 | 547.27 | 58.48 | 81 | 47 | 0.01
4430859332 | MNJ1446 | 11/23/2023 | 541.87 | 49.62 | 73 | 48 | 0.01
4430859332 | MNJ1446 | 11/24/2023 | 533.59 | 57.3 | 75 | 52 | 0.07
4430859332 | MNJ1446 | 11/25/2023 | 525.81 | 48.77 | 75 | 53 | 0.01
4430859332 | MNJ1446 | 11/26/2023 | 581.43 | 51.75 | 75 | 55 | 0.55
4430859332 | MNJ1446 | 11/27/2023 | 544.55 | 58.78 | 74 | 44 | 0
4430859332 | MNJ1446 | 11/28/2023 | 521.46 | 57.11 | 69 | 39 | 0
4430859332 | MNJ1446 | 11/29/2023 | 522.04 | 57.84 | 68 | 36 | 0
4430859332 | MNJ1446 | 11/30/2023 | 504.66 | 56.04 | 86 | 41 | 0
4430859332 | MNJ1446 | 12/01/2023 | 491.52 | 54.75 | 82 | 55 | 0
4430859332 | MNJ1446 | 12/02/2023 | 498.73 | 47.33 | 83 | 64 | 0.02
4430859332 | MNJ1446 | 12/03/2023 | 543.99 | 49.73 | 82 | 62 | 0.23
4430859332 | MNJ1446 | 12/04/2023 | 521.94 | 57.33 | 79 | 51 | 0
4430859332 | MNJ1446 | 12/05/2023 | 502.48 | 56.1 | 72 | 47 | 0
4430859332 | MNJ1446 | 12/06/2023 | 490.72 | 55.13 | 69 | 41 | 0
4430859332 | MNJ1446 | 12/07/2023 | 483.68 | 54.8 | 67 | 41 | 0
4430859332 | MNJ1446 | 12/08/2023 | 483.91 | 54.5 | 74 | 47 | 0.04
4430859332 | MNJ1446 | 12/09/2023 | 474.73 | 46.06 | 82 | 56 | 0
4430859332 | MNJ1446 | 12/10/2023 | 494.6 | 47.12 | 83 | 44 | 0.25
4430859332 | MNJ1446 | 12/11/2023 | 486.26 | 54.81 | 67 | 43 | 0
4430859332 | MNJ1446 | 12/12/2023 | 480.9 | 54.56 | 71 | 43 | 0
4430859332 | MNJ1446 | 12/13/2023 | 466.47 | 53.32 | 73 | 58 | 0.66
4430859332 | MNJ1446 | 12/14/2023 | 479.66 | 54.6 | 72 | 59 | 0.07
4430859332 | MNJ1446 | 12/15/2023 | 482.53 | 54.33 | 72 | 60 | 0.11
4430859332 | MNJ1446 | 12/16/2023 | 539.37 | 49.51 | 73 | 58 | 4.04
4430859332 | MNJ1446 | 12/17/2023 | 1127.21 | 80.8 | 74 | 48 | 0.05
4430859332 | MNJ1446 | 12/18/2023 | 745.5 | 71.18 | 68 | 40 | 0
4430859332 | MNJ1446 | 12/19/2023 | 592.47 | 62.27 | 65 | 41 | 0
4430859332 | MNJ1446 | 12/20/2023 | 568.14 | 59.18 | 66 | 44 | 0
4430859332 | MNJ1446 | 12/21/2023 | 557 | 58.58 | 68 | 46 | 0
4430859332 | MNJ1446 | 12/22/2023 | 544.25 | 56.97 | 70 | 49 | 0
4430859332 | MNJ1446 | 12/23/2023 | 552.36 | 48.79 | 73 | 53 | 0
4430859332 | MNJ1446 | 12/24/2023 | 532.82 | 47.68 | 73 | 53 | 0.09
4430859332 | MNJ1446 | 12/25/2023 | 510.08 | 46.47 | 73 | 60 | 0.1
4430859332 | MNJ1446 | 12/26/2023 | 532.95 | 56.15 | 74 | 54 | 0
4430859332 | MNJ1446 | 12/27/2023 | 519.06 | 55.18 | 71 | 49 | 0.04
4430859332 | MNJ1446 | 12/28/2023 | 519.43 | 55.37 | 66 | 44 | 0
4430859332 | MNJ1446 | 12/29/2023 | 524.35 | 55.63 | 55 | 46 | 0
4430859332 | MNJ1446 | 12/30/2023 | 515.61 | 46.75 | 59 | 37 | 0
4430859332 | MNJ1446 | 12/31/2023 | 519.55 | 46.97 | 63 | 36 | 0
|  | Yearly Daily Average: | 488.4373 | 71.6078
|  | Wetter Months' Daily Average: | 553.1026 | 65.8399